## test results
CRE test for: |  | Goldthwaite - Evant [7070 - 7068] | [5 empty] | #DIV/0!
Line Rating: |  | 150
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Goldthwaite - Evant [7070 - 7068]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.015884
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.023414
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.029092
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0068687
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Goldthwaite - Evant [7070 - 7068]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.01799
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.023952
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.029209
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.0065719
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Goldthwaite - Evant [7070 - 7068]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.039837
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.013325
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.022456
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.052623
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.016545
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.035664
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.041404 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.041404 | 0.039837
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.018253
[6 empty] | Concentration |  | -0.44085 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | #DIV/0!
[6 empty] | Concentration |  | #DIV/0! | #DIV/0!
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 18.5928
| Percent of line rating => | [6 empty] | 12.4% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -10.1612
[7 empty] | B1(N-S) | 0.0028611 | -0.40193 | -0.40479 | 0.0028611
[7 empty] | B2 (N-W) | -0.15201 | -0.016614 | 0.1354 | -0.15201
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.0090295 | -0.21915 | -0.22818 | 0.0090295
[7 empty] | B4 (S-W) | -0.14513 | 0.38958 | 0.53471 | -0.14513
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.018926 | 0.18705 | 0.16812 | 0.018926
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.1606 | -0.20179 | -0.36239 | 0.1606
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 0.6801%
Deployment Error Percent | [6 empty] | B2 | -36.13%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 2.146%
[7 empty] | B4 | -34.5%
[7 empty] | B5 | 4.499%
[7 empty] | B6 | 38.17%
[7 empty] | Max Abs Error | 38.17% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: Goldthwaite - Evant [7070 - 7068] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: Goldthwaite - Evant [7070 - 7068] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011171 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 2.8486
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011171 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.6645
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.013339 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.20009
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.013339 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.20009
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011171 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.7092
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.011567 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.735
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.011567 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.92536
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027659 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 2.0191
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027659 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 3.2914
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027659 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 5.6701
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027659 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 2.8212
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.027659 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 2.6553
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.025472 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.30566
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.025472 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.30566
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.021365 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 3.5893
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.021365 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 1.9228
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.43555
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.43555
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.91949
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 6.5102
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.3229
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.3229
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.021033 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.3662
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.017375 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.695
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.3759
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 1.8462
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 2.5429
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.017417 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.3237
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.019746 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.1848
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.019746 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.244
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.34684
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.43355
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.71102
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.002836 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 1.3131
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 1.9215
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 1.8923
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.9506
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.9506
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 1.9506
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029113 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 3.3189
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.029113 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 14.9932
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 1.9582
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.0472
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.0472
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.9879
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 1.9879
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 1.9285
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 2.0629
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 2.1631
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 2.0747
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 4.4239
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 6.4885
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029705 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 2.9408
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029705 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 1.812
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.029704 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 4.1883
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.74262
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.3575
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.3575
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.029704 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 3.5645
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.030125 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.77723
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.029531 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 2.9679
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.029782 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 3.5738
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.029463 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 1.7089
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.029492 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 6.3172
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.030909 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 4.6364
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.031131 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.20546
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.031131 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.0678
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.030909 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 3.1218
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.029789 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 3.5747
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.024832 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 9.0885
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.02621 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 6.3428
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.027701 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 11.0804
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.027695 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 6.536
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.027008 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 4.4563
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 4.6934
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 4.6244
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 5.5677
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.49824
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.49824
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.49824
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.4235
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.025706 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 3.0847
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.034952 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 2.0971
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.324
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 1.4052
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 1.5605
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 2.8301
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.7593
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 3.4668
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.7593
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 2.777
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 3.5022
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.017905 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 3.0438
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.017905 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 9.3106
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017745 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 6.5656
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 9.8119
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 10.1811
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 14.2079
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.020811 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 2.3308
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.020811 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 2.0811
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.020811 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 7.8666
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 5.2254
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 4.9296
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 6.5504
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.022982 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 17.6961
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 1.6725
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.6486
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.6486
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 1.6247
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.024769 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 28.6577
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.024769 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 28.6825
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 4.1288
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 4.1656
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.017212 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 3.7247
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.017212 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 3.7195
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 3.9076
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 3.8892
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019605 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 7.744
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.019429 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 8.4516
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019605 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 8.5282
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.018288 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 2.5237
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017545 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.0703
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017545 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.0177
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017545 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 9.755
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.0172 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 6.6736
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.0172 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 8.858
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 12.118
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 12.2724
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 12.0409
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.014914 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 2.7143
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.014914 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 7.2184
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.015037 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 3.3683
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.015018 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.7509
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.015035 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.63147
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.012642 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 7.7748
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.012642 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 7.4209
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.011234 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 6.0327
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.011234 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 8.8412
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006215 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.46613
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006215 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 1.3797
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.023864 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -13.5786
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022821 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -4.7696
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022821 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -4.9293
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.022881 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -9.3126
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0498
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.0726
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0498
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.0498
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.022898 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -9.7088
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.022898 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -9.7317
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022771 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -1.3207
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022771 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -2.0266
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.0019
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.0019
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.97915
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.0247
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.022862 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -9.4191
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.022862 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -9.1448
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.02259 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -12.3341
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.02259 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -16.9425
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -1.3951
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -2.1726
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -3.4534
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.5387
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -3.8811
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -3.5387
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.018251 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.40152
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.018251 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.20076
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.018251 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.20076
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.87835
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.68684
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.84704
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.88387
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.22886
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.20979
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.019538 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.46891
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.019538 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.46891
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.019538 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.44937
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.021106 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -8.358
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.012395 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -16.5225
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.012395 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -16.4606
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.71976
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.36556
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.28412
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.018941 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.89023
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 2.0791
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.029742 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 4.4613
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.031906 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 5.4081
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.020092 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 3.0138
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.029741 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 1.8737
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.026619 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 17.2944
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.018028 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.72112
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.018028 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.72112
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.064567 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -27.2473
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -3.4498
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -3.5021
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -8.4416
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -3.8124
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -3.8606
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -4.2226
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.022554 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -13.1715
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.022554 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -13.4196
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.022543 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -9.7611
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -5.3805
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -5.407
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -5.3974
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -5.4478
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.030156 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.24125
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.030156 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.24125
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.6198
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.6198
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -1.3498
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.077212 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -1.0578
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.056927 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.0247
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.056927 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.0247
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.3861
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -1.3465
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -1.3861
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.0655 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -1.834
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.0655 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -1.8995
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.029132 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.0196
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.029132 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.87396
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1802
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1802
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1802
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.1802
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.026781 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.16069
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.057442
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.057442
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.067015
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.023732 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.094928
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.023346 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.05603
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.023346 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.05603
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.3617
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -3.1559
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -3.2017
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -3.3617
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -4.1622
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -4.5281
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -3.8291
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -3.7538
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -5.8404
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -3.3281
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -3.3984
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -3.539
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -6.7967
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.006231 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.20562
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.006231 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.15577
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.22886
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.018442 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -1.3463
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -1.3699
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -1.4046
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.50196
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.12549
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -1.3699
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -1.3873
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -1.3595
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.43352
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.79769
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.019515 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -12.2749
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.01863 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -2.6827
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.01863 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -3.5024
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.021919 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.26303
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.010392 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.062352
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.018762 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -6.304
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018802 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -6.2799
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018802 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -6.3927
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.018823 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.71527
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.018806 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.47015
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.018806 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.47015
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.018825 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.71535
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.018908 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.54833
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -2.7827
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -2.7883
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -2.8709
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -2.9363
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -2.8434
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -1.8584
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -2.6947
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -2.7318
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -2.3602
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -2.7801
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -2.8067
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -3.283
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -3.9253
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -4.1093
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -4.589
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -2.7305
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -2.7305
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -3.2425
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.029389 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -9.1106
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.029389 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -12.1377
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -1.2231
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -1.2813
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -1.2813
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -1.3687
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -1.4251
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -1.3378
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -1.3378
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -1.3669
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -4.4788
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -4.3043
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -1.396
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -1.396
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.0531
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.0531
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 2.7218
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.3464
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.3464
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 3.3729
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 6.1061
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 4.1675
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 3.883
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 3.9886
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 4.3112
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 6.1589
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 6.0453
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 3.659
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 7.2023
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 5.6982
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 5.8986
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 3.5952
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.029189 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 4.3492
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.029645 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 5.3361
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.029645 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 5.3361
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.029635 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 6.6679
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.029321 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.6651
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.029321 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.6651
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 2.4843
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 2.502
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 5.4832
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 2.5375
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 2.5553
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 5.5009
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.016684 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 3.2701
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.016684 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 1.8519
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.018035 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.7262
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.777
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.777
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 7.0103
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 2.7431
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.7262
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 2.7601
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 6.9256
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017247 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017247 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 2.2548
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 1.9806
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 2.2091
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 6.0788
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 1.9715
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 1.9754
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 2.3207
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 1.9913
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 2.0018
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 2.3331
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.023864 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -13.865
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 5.9525
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 5.9525
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.00225 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.072
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001961 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.094128
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001961 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.090206
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.027192
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.11557
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002266 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.038522
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.049852
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.05665
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.001961 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.20591
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.029712 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 2.4958
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.027688 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 2.215
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.027675 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.1513
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.027675 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.1513
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.50268
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.47357
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.3763
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -1.0877
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -1.0898
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -1.0813
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.6816
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -1.7324
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.284
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.71243
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.65987
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.72948
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.72451
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007103 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.2273
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.007103 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.21309
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0209
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -1.0209
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -1.0944
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -1.0071
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 1.0603
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 1.0652
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.005823 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.79193
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.007799 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.25737
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.24431
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.24431
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.22105
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.22105
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009547 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.67784
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.009547 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.09547
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.2901
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -1.2901
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -1.9392
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.4095
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.378
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.4095
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.4095
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.89251
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.38995
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.58185
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.56011
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.55628
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.34847
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.078007
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.005429 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -4.0337
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.005587 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -4.1064
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.9257
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.9257
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.9257
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.77954
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.005791 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -1.0018
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.005791 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.78178
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.85796
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.85058
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.8374
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -1.4187
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.38266
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.37787
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.49387
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.44005
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.99242
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.95533
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.95776
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.95472
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -1.6358
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005437 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.027185
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.005437 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.11418
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.2515
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.25444
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.25444
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 0.61978
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.00523 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -2.0815
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.28322
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.28322
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.28322
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.33864
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.33864
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.33248
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.00866 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 7.1618
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.00866 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 7.0925
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.007981 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.36792
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.93024
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.93024
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -1.2852
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.90576
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.90576
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -1.2485
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -1.0757
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.94779
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.93823
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.006039 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.21136
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.006633 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -3.0445
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.35328
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.35871
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.38045
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.34241
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.33697
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.56524
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.32066
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.70294
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.69392
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.69392
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.004506 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.72997
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.005399 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.84764
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.42018
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.4261
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.2308
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.17754
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.006127 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.47791
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.006127 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.49016
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.00598 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.096876
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.005992 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.98868
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.005996 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -1.0133
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.005981 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -1.274
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.005978 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -1.363
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.005998 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.071976
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.005998 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.10796
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.00683 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.3415
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.58646
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.58646
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30451
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.29887
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30451
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.32142
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30451
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.30451
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.32706
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.32706
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.005495 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.06594
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28902
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.3045
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28902
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28902
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.3045
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.28902
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.011731 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.77425
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -1.2431
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -1.2817
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -1.9148
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007721 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -4.2157
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007721 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -4.9646
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -5.1592
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -4.4697
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -4.755
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.007721 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.10037
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.005433 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.065196
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.18863
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.19252
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.18142
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.25465
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.0982
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.11318
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.11041
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.19418
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.099864
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.4738
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.8211
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.61895
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.71279
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.44923
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.0083
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.85854
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.8785
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.49915
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.17969
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.9384
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.69881
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.62893
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.71878
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.6469
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -1.0083
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.96835
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -1.0282
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.75871
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.79864
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.79864
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -1.7071
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.1612
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.027097 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 2.0729
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 2.2178
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.1089
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.027845 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.2276
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.027691 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 2.2153
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.027092 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 2.1674
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.026895 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 2.2592
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.027845 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.2276
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -2.9642
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 3.7565
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 7.2938
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 5.3279
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -5.7724
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -4.7844
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -5.8244
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -2.9902
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -2.6002
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.029366 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 1.762
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.023952 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.023714 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.028196 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.13534
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.1049
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 3.1675
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 3.9778
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 3.5063
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 3.0938
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 2.3719
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.031082 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 4.6623
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 3.5307
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 4.6919
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 5.8374
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 6.7319
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.018941 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.01136 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.019497 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.48555
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.75607
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -1.2832
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -1.7798
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.77629
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.71949
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.35975
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -1.7798
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.68162
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.81416
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.41655
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.69915
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.26891
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.12549
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.26891
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.69915
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.69915
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -2.8022
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.9467
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -1.0414
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.9467
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.018584 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.22301
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.018117 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.27176
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.018117 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.41669
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.017479 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.83899
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.14399
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.018767 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -3.3781
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.018762 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -3.3772
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018802 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -3.3844
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.018802 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -3.3844
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019499 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -1.9499
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019499 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -1.9499
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46637
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46637
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46637
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.29848
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46637
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46637
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.46637
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.27982
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019499 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019499 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -9.7495
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019499 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -9.7495
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.019499 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.019709 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.006231 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.019162 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.019169 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: Goldthwaite - Evant [7070 - 7068] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | [7 empty] | 18.5928
Number of Bus | Name of Bus | ID | Max MW | L: Goldthwaite - Evant [7070 - 7068] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.011171 | north | Y | -0.0047133 | 0.034585 | -0.017921 | 0.01804 | 0.0047133 | North | N | 0.0047133 | 0
239 | BOSQUESW | 1 | 149 | 0.011171 | north | Y | -0.0047133 | 0.034585 | -0.017921 | 0.01804 | 0.0047133 | North | N | 0.0047133 | 0
244 | WHITNYDM | 1 | 15 | 0.013339 | north | N | -0.0025453 | 0.036753 | -0.015753 | 0.020208 | 0.0025453 | North | N | 0.0025453 | 0
245 | WHITNYDM | 2 | 15 | 0.013339 | north | N | -0.0025453 | 0.036753 | -0.015753 | 0.020208 | 0.0025453 | North | N | 0.0025453 | 0
247 | BOSQUESW | 2 | 153 | 0.011171 | north | Y | -0.0047133 | 0.034585 | -0.017921 | 0.01804 | 0.0047133 | North | N | 0.0047133 | 0
251 | BOSQUESW | 2 | 150 | 0.011567 | north | Y | -0.0043173 | 0.034981 | -0.017525 | 0.018436 | 0.0043173 | North | N | 0.0043173 | 0
253 | BOSQUESW | 2 | 80 | 0.011567 | north | Y | -0.0043173 | 0.034981 | -0.017525 | 0.018436 | 0.0043173 | North | N | 0.0043173 | 0
332 | RWMILLER | 1 | 73 | 0.027659 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 0.75493
333 | RWMILLER | 2 | 119 | 0.027659 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 1.2306
334 | RWMILLER | 3 | 205 | 0.027659 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 2.12
335 | RWMILLER | 4 | 102 | 0.027659 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 1.0548
336 | RWMILLER | 5 | 96 | 0.027659 | north | Y | 0.011775 | 0.051073 | -0.0014333 | 0.034528 | 0.0014333 | west | Y | 0.011775 | 0.99278
344 | MRSSHPRD | 1 | 12 | 0.025472 | north | N | 0.0095877 | 0.048886 | -0.0036203 | 0.032341 | 0.0036203 | west | Y | 0.0095877 | 0
345 | MRSSHPRD | 2 | 12 | 0.025472 | north | N | 0.0095877 | 0.048886 | -0.0036203 | 0.032341 | 0.0036203 | west | Y | 0.0095877 | 0
366 | JNSNCNTY | 1 | 168 | 0.021365 | north | Y | 0.0054807 | 0.044779 | -0.0077273 | 0.028234 | 0.0054807 | North | N | 0.0054807 | 0
367 | JNSNCNTY | 2 | 90 | 0.021365 | north | Y | 0.0054807 | 0.044779 | -0.0077273 | 0.028234 | 0.0054807 | North | N | 0.0054807 | 0
503 | NTHTEXAS | 1 | 18 | 0.024197 | north | Y | 0.0083127 | 0.047611 | -0.0048953 | 0.031066 | 0.0048953 | west | Y | 0.0083127 | 0.061514
504 | NTHTEXAS | 2 | 18 | 0.024197 | north | Y | 0.0083127 | 0.047611 | -0.0048953 | 0.031066 | 0.0048953 | west | Y | 0.0083127 | 0.061514
505 | NTHTEXAS | 3 | 38 | 0.024197 | north | Y | 0.0083127 | 0.047611 | -0.0048953 | 0.031066 | 0.0048953 | west | Y | 0.0083127 | 0.12986
580 | JCKCNTY8 | 1 | 288 | 0.022605 | north | Y | 0.0067207 | 0.046019 | -0.0064873 | 0.029474 | 0.0064873 | west | Y | 0.0067207 | 0.067238
581 | JCKCNTY8 | 2 | 147 | 0.022605 | north | Y | 0.0067207 | 0.046019 | -0.0064873 | 0.029474 | 0.0064873 | west | Y | 0.0067207 | 0.03432
582 | JCKCNTY8 | 3 | 147 | 0.022605 | north | Y | 0.0067207 | 0.046019 | -0.0064873 | 0.029474 | 0.0064873 | west | Y | 0.0067207 | 0.03432
728 | WOLFRIDG | 1 | 112.5 | 0.021033 | north | Y | 0.0051487 | 0.044447 | -0.0080593 | 0.027902 | 0.0051487 | North | N | 0.0051487 | 0
837 | NEWMAN_G | 1 | 40 | 0.017375 | north | Y | 0.0014907 | 0.040789 | -0.011717 | 0.024244 | 0.0014907 | North | N | 0.0014907 | 0
842 | OLINGER_ | 1 | 79 | 0.017417 | north | Y | 0.0015327 | 0.040831 | -0.011675 | 0.024286 | 0.0015327 | North | N | 0.0015327 | 0
843 | OLINGER_ | 1 | 106 | 0.017417 | north | Y | 0.0015327 | 0.040831 | -0.011675 | 0.024286 | 0.0015327 | North | N | 0.0015327 | 0
844 | OLINGER_ | 1 | 146 | 0.017417 | north | Y | 0.0015327 | 0.040831 | -0.011675 | 0.024286 | 0.0015327 | North | N | 0.0015327 | 0
845 | OLINGER_ | 1 | 76 | 0.017417 | north | Y | 0.0015327 | 0.040831 | -0.011675 | 0.024286 | 0.0015327 | North | N | 0.0015327 | 0
923 | SPENCER_ | 1 | 60 | 0.019746 | north | Y | 0.0038617 | 0.04316 | -0.0093463 | 0.026615 | 0.0038617 | North | N | 0.0038617 | 0
924 | SPENCER_ | 1 | 63 | 0.019746 | north | Y | 0.0038617 | 0.04316 | -0.0093463 | 0.026615 | 0.0038617 | North | N | 0.0038617 | 0
948 | STEAM1 | 1 | 20 | 0.017342 | north | Y | 0.0014577 | 0.040756 | -0.01175 | 0.024211 | 0.0014577 | North | N | 0.0014577 | 0
949 | STEAM2 | 1 | 25 | 0.017342 | north | Y | 0.0014577 | 0.040756 | -0.01175 | 0.024211 | 0.0014577 | North | N | 0.0014577 | 0
950 | STEAM3 | 1 | 41 | 0.017342 | north | Y | 0.0014577 | 0.040756 | -0.01175 | 0.024211 | 0.0014577 | North | N | 0.0014577 | 0
990 | GIBN_CRE | 1 | 463 | 0.002836 | north | Y | -0.013048 | 0.02625 | -0.026256 | 0.0097047 | 0.0097047 | houston | Y | 0.013048 | 1.5481
1002 | PBCTAGE_ | A | 66 | 0.029113 | west | Y | 0.013229 | 0.052527 | 2.0745e-05 | 0.035982 | 2.0745e-05 | west | N | 2.0745e-05 | 0
1003 | PBCTBGE_ | B | 65 | 0.029113 | west | Y | 0.013229 | 0.052527 | 2.0745e-05 | 0.035982 | 2.0745e-05 | west | N | 2.0745e-05 | 0
1004 | PBCTCGE_ | C | 67 | 0.029113 | west | Y | 0.013229 | 0.052527 | 2.0745e-05 | 0.035982 | 2.0745e-05 | west | N | 2.0745e-05 | 0
1005 | PBCTDGE_ | D | 67 | 0.029113 | west | Y | 0.013229 | 0.052527 | 2.0745e-05 | 0.035982 | 2.0745e-05 | west | N | 2.0745e-05 | 0
1006 | PBCTEGE_ | E | 67 | 0.029113 | west | Y | 0.013229 | 0.052527 | 2.0745e-05 | 0.035982 | 2.0745e-05 | west | N | 2.0745e-05 | 0
1007 | PB5GEN_6 | MB | 114 | 0.029113 | west | Y | 0.013229 | 0.052527 | 2.0745e-05 | 0.035982 | 2.0745e-05 | west | N | 2.0745e-05 | 0
1008 | PB6GEN_7 | MB | 515 | 0.029113 | west | Y | 0.013229 | 0.052527 | 2.0745e-05 | 0.035982 | 2.0745e-05 | west | N | 2.0745e-05 | 0
1039 | MRGNAG_1 | A | 66 | 0.02967 | west | Y | 0.013786 | 0.053084 | 0.00057774 | 0.036539 | 0.00057774 | west | N | 0.00057774 | 0
1040 | MRGNBG_2 | B | 69 | 0.02967 | west | Y | 0.013786 | 0.053084 | 0.00057774 | 0.036539 | 0.00057774 | west | N | 0.00057774 | 0
1041 | MRGNCG_3 | C | 69 | 0.02967 | west | Y | 0.013786 | 0.053084 | 0.00057774 | 0.036539 | 0.00057774 | west | N | 0.00057774 | 0
1042 | MRGNDG_4 | D | 67 | 0.02967 | west | Y | 0.013786 | 0.053084 | 0.00057774 | 0.036539 | 0.00057774 | west | N | 0.00057774 | 0
1043 | MRGNEG_5 | E | 67 | 0.02967 | west | Y | 0.013786 | 0.053084 | 0.00057774 | 0.036539 | 0.00057774 | west | N | 0.00057774 | 0
1044 | MRGNFG_6 | F | 65 | 0.02967 | west | Y | 0.013786 | 0.053084 | 0.00057774 | 0.036539 | 0.00057774 | west | N | 0.00057774 | 0
1045 | CALENG1G | 1 | 70 | 0.02947 | west | N | 0.013586 | 0.052884 | 0.00037774 | 0.036339 | 0.00037774 | west | N | 0.00037774 | 0
1046 | CALENG2G | 2 | 73.4 | 0.02947 | west | N | 0.013586 | 0.052884 | 0.00037774 | 0.036339 | 0.00037774 | west | N | 0.00037774 | 0
1047 | CALENG3G | 3 | 70.4 | 0.02947 | west | N | 0.013586 | 0.052884 | 0.00037774 | 0.036339 | 0.00037774 | west | N | 0.00037774 | 0
1058 | LONGSHOR | 1 | 150 | 0.029493 | west | Y | 0.013609 | 0.052907 | 0.00040074 | 0.036362 | 0.00040074 | west | N | 0.00040074 | 0
1058 | LONGSHOR | 2 | 220 | 0.029493 | west | Y | 0.013609 | 0.052907 | 0.00040074 | 0.036362 | 0.00040074 | west | N | 0.00040074 | 0
1061 | CIELOGEN | 1 | 99 | 0.029705 | west | Y | 0.013821 | 0.053119 | 0.00061274 | 0.036574 | 0.00061274 | west | N | 0.00061274 | 0
1062 | CIELOGEN | 1 | 61 | 0.029705 | west | Y | 0.013821 | 0.053119 | 0.00061274 | 0.036574 | 0.00061274 | west | N | 0.00061274 | 0
1068 | SCURRYCW | 1 | 141 | 0.029704 | west | Y | 0.01382 | 0.053118 | 0.00061174 | 0.036573 | 0.00061174 | west | N | 0.00061174 | 0
1069 | KINDERMG | 1 | 25 | 0.029705 | west | N | 0.013821 | 0.053119 | 0.00061274 | 0.036574 | 0.00061274 | west | N | 0.00061274 | 0
1070 | KINDERMG | 1 | 45.7 | 0.029705 | west | N | 0.013821 | 0.053119 | 0.00061274 | 0.036574 | 0.00061274 | west | N | 0.00061274 | 0
1071 | KINDERMG | 1 | 45.7 | 0.029705 | west | N | 0.013821 | 0.053119 | 0.00061274 | 0.036574 | 0.00061274 | west | N | 0.00061274 | 0
1073 | SCURRYCW | 2 | 120 | 0.029704 | west | Y | 0.01382 | 0.053118 | 0.00061174 | 0.036573 | 0.00061174 | west | N | 0.00061174 | 0
1320 | BSP 1 | 1 | 25.8 | 0.030125 | west | N | 0.014241 | 0.053539 | 0.0010327 | 0.036994 | 0.0010327 | west | N | 0.0010327 | 0
1326 | STANTONW | 1 | 100.5 | 0.029531 | west | Y | 0.013647 | 0.052945 | 0.00043874 | 0.0364 | 0.00043874 | west | N | 0.00043874 | 0
1327 | WILDHRSE | 1 | 120 | 0.029782 | west | Y | 0.013898 | 0.053196 | 0.00068974 | 0.036651 | 0.00068974 | west | N | 0.00068974 | 0
1328 | OCOTILLO | 1 | 58 | 0.029463 | west | Y | 0.013579 | 0.052877 | 0.00037074 | 0.036332 | 0.00037074 | west | N | 0.00037074 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.029492 | west | Y | 0.013608 | 0.052906 | 0.00039974 | 0.036361 | 0.00039974 | west | N | 0.00039974 | 0
1343 | TRENTIPP | 1 | 150 | 0.030909 | west | Y | 0.015025 | 0.054323 | 0.0018167 | 0.037778 | 0.0018167 | west | N | 0.0018167 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.031131 | west | Y | 0.015247 | 0.054545 | 0.0020387 | 0.038 | 0.0020387 | west | N | 0.0020387 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.031131 | west | Y | 0.015247 | 0.054545 | 0.0020387 | 0.038 | 0.0020387 | west | N | 0.0020387 | 0
1354 | AEPWIND_ | 1 | 101 | 0.030909 | west | Y | 0.015025 | 0.054323 | 0.0018167 | 0.037778 | 0.0018167 | west | N | 0.0018167 | 0
1360 | GUNSIGHT | 1 | 120 | 0.029789 | west | Y | 0.013905 | 0.053203 | 0.00069674 | 0.036658 | 0.00069674 | west | N | 0.00069674 | 0
1432 | GRHAMSES | 2 | 366 | 0.024832 | north | Y | 0.0089477 | 0.048246 | -0.0042603 | 0.031701 | 0.0042603 | west | Y | 0.0089477 | 1.7156
1433 | GRHAMSES | 1 | 242 | 0.02621 | north | Y | 0.010326 | 0.049624 | -0.0028823 | 0.033079 | 0.0028823 | west | Y | 0.010326 | 1.8013
1437 | MESQUITW | 1 | 400 | 0.027701 | west | Y | 0.011817 | 0.051115 | -0.0013913 | 0.03457 | 0.0013913 | west | N | 0.0013913 | 0
1438 | MESQUITW | 1 | 236 | 0.027695 | west | Y | 0.011811 | 0.051109 | -0.0013973 | 0.034564 | 0.0013973 | west | N | 0.0013973 | 0
1442 | COKFIELD | 1 | 165 | 0.027008 | west | Y | 0.011124 | 0.050422 | -0.0020843 | 0.033877 | 0.0020843 | west | N | 0.0020843 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.023007 | north | Y | 0.0071227 | 0.046421 | -0.0060853 | 0.029876 | 0.0060853 | west | Y | 0.0071227 | 0.21164
1454 | WCPWRCO_ | 2 | 201 | 0.023007 | north | Y | 0.0071227 | 0.046421 | -0.0060853 | 0.029876 | 0.0060853 | west | Y | 0.0071227 | 0.20853
1455 | WCPWRCO_ | 3 | 242 | 0.023007 | north | Y | 0.0071227 | 0.046421 | -0.0060853 | 0.029876 | 0.0060853 | west | Y | 0.0071227 | 0.25107
1479 | WFCOGEN_ | 1 | 20 | 0.024912 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.024912 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.024912 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.024912 | west | Y | 0.0090277 | 0.048326 | -0.0041803 | 0.031781 | 0.0041803 | west | N | 0.0041803 | 0
1600 | BARTNWND | 1 | 120 | 0.025706 | north | Y | 0.0098217 | 0.04912 | -0.0033863 | 0.032575 | 0.0033863 | west | Y | 0.0098217 | 0.77226
1643 | SLSTR1PP | 1 | 60 | 0.034952 | north | Y | 0.019068 | 0.058366 | 0.0058597 | 0.041821 | 0.0058597 | west | Y | 0.019068 | 0.79248
1675 | PEC_1G | 1 | 75 | 0.017653 | north | N | 0.0017687 | 0.041067 | -0.011439 | 0.024522 | 0.0017687 | North | N | 0.0017687 | 0
1676 | PEC_2G | 2 | 79.6 | 0.017653 | north | N | 0.0017687 | 0.041067 | -0.011439 | 0.024522 | 0.0017687 | North | N | 0.0017687 | 0
1677 | PEC_3G | 3 | 88.4 | 0.017653 | north | N | 0.0017687 | 0.041067 | -0.011439 | 0.024522 | 0.0017687 | North | N | 0.0017687 | 0
1678 | LAMARPWR | 1 | 160 | 0.017688 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1679 | LAMARPWR | 2 | 156 | 0.017688 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1680 | LAMARPWR | 3 | 196 | 0.017688 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1681 | LAMARPWR | 4 | 156 | 0.017688 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1682 | LAMARPWR | 5 | 157 | 0.017688 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1683 | LAMARPWR | 6 | 198 | 0.017688 | north | Y | 0.0018037 | 0.041102 | -0.011404 | 0.024557 | 0.0018037 | North | N | 0.0018037 | 0
1687 | VALLEY_1 | 1 | 170 | 0.017905 | north | Y | 0.0020207 | 0.041319 | -0.011187 | 0.024774 | 0.0020207 | North | N | 0.0020207 | 0
1688 | VALLEY_2 | 2 | 520 | 0.017905 | north | Y | 0.0020207 | 0.041319 | -0.011187 | 0.024774 | 0.0020207 | North | N | 0.0020207 | 0
1689 | VALLEY_3 | 3 | 370 | 0.017745 | north | Y | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
1701 | MOSES_1G | 1 | 558 | 0.017584 | north | Y | 0.0016997 | 0.040998 | -0.011508 | 0.024453 | 0.0016997 | North | N | 0.0016997 | 0
1702 | MOSES_2G | 2 | 579 | 0.017584 | north | Y | 0.0016997 | 0.040998 | -0.011508 | 0.024453 | 0.0016997 | North | N | 0.0016997 | 0
1703 | MOSES_3G | 3 | 808 | 0.017584 | north | Y | 0.0016997 | 0.040998 | -0.011508 | 0.024453 | 0.0016997 | North | N | 0.0016997 | 0
1861 | EAGLEMNT | MB | 112 | 0.020811 | north | Y | 0.0049267 | 0.044225 | -0.0082813 | 0.02768 | 0.0049267 | North | N | 0.0049267 | 0
1862 | EAGLEMNT | MB | 100 | 0.020811 | north | Y | 0.0049267 | 0.044225 | -0.0082813 | 0.02768 | 0.0049267 | North | N | 0.0049267 | 0
1863 | EAGLEMNT | MB | 378 | 0.020811 | north | Y | 0.0049267 | 0.044225 | -0.0082813 | 0.02768 | 0.0049267 | North | N | 0.0049267 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.024047 | north | Y | 0.0081627 | 0.047461 | -0.0050453 | 0.030916 | 0.0050453 | west | Y | 0.0081627 | 0.67743
1878 | WLFHOLW_ | 2 | 205 | 0.024047 | north | Y | 0.0081627 | 0.047461 | -0.0050453 | 0.030916 | 0.0050453 | west | Y | 0.0081627 | 0.63908
1879 | WLFHOLW_ | 3 | 272.4 | 0.024047 | north | Y | 0.0081627 | 0.047461 | -0.0050453 | 0.030916 | 0.0050453 | west | Y | 0.0081627 | 0.8492
1889 | DECRDOVA | MB | 770 | 0.022982 | north | Y | 0.0070977 | 0.046396 | -0.0061103 | 0.029851 | 0.0061103 | west | Y | 0.0070977 | 0
1892 | DECRDOVA | A | 70 | 0.023893 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19666
1893 | DECRDOVA | B | 69 | 0.023893 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19385
1894 | DECRDOVA | C | 69 | 0.023893 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19385
1895 | DECRDOVA | D | 68 | 0.023893 | north | Y | 0.0080087 | 0.047307 | -0.0051993 | 0.030762 | 0.0051993 | west | Y | 0.0080087 | 0.19104
1898 | COMCHEPK | 1 | 1157 | 0.024769 | north | N | 0.0088847 | 0.048183 | -0.0043233 | 0.031638 | 0.0043233 | west | Y | 0.0088847 | 0
1899 | COMCHEPK | 2 | 1158 | 0.024769 | north | N | 0.0088847 | 0.048183 | -0.0043233 | 0.031638 | 0.0043233 | west | Y | 0.0088847 | 0
1937 | MDLTHELP | 5 | 224 | 0.018432 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1938 | MDLTHELP | 6 | 226 | 0.018432 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.017212 | north | Y | 0.0013277 | 0.040626 | -0.01188 | 0.024081 | 0.0013277 | North | N | 0.0013277 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.017212 | north | Y | 0.0013277 | 0.040626 | -0.01188 | 0.024081 | 0.0013277 | North | N | 0.0013277 | 0
1943 | MDLTHELP | 3 | 212 | 0.018432 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1944 | MDLTHELP | 4 | 211 | 0.018432 | north | Y | 0.0025477 | 0.041846 | -0.01066 | 0.025301 | 0.0025477 | North | N | 0.0025477 | 0
1947 | HANDLEY_ | 3 | 395 | 0.019605 | north | Y | 0.0037207 | 0.043019 | -0.0094873 | 0.026474 | 0.0037207 | North | N | 0.0037207 | 0
1948 | HANDLEY_ | 4 | 435 | 0.019429 | north | Y | 0.0035447 | 0.042843 | -0.0096633 | 0.026298 | 0.0035447 | North | N | 0.0035447 | 0
1949 | HANDLEY_ | 5 | 435 | 0.019605 | north | Y | 0.0037207 | 0.043019 | -0.0094873 | 0.026474 | 0.0037207 | North | N | 0.0037207 | 0
2371 | COLLIN_1 | MB | 138 | 0.018288 | north | Y | 0.0024037 | 0.041702 | -0.010804 | 0.025157 | 0.0024037 | North | N | 0.0024037 | 0
2413 | MTCK6_G | 6 | 118 | 0.017545 | north | Y | 0.0016607 | 0.040959 | -0.011547 | 0.024414 | 0.0016607 | North | N | 0.0016607 | 0
2414 | MTCK7_G | 7 | 115 | 0.017545 | north | Y | 0.0016607 | 0.040959 | -0.011547 | 0.024414 | 0.0016607 | North | N | 0.0016607 | 0
2417 | MTCK8_G | 8 | 556 | 0.017545 | north | Y | 0.0016607 | 0.040959 | -0.011547 | 0.024414 | 0.0016607 | North | N | 0.0016607 | 0
2451 | LKHB1_G | 1 | 388 | 0.0172 | north | Y | 0.0013157 | 0.040614 | -0.011892 | 0.024069 | 0.0013157 | North | N | 0.0013157 | 0
2452 | LKHB2_G | 2 | 515 | 0.0172 | north | Y | 0.0013157 | 0.040614 | -0.011892 | 0.024069 | 0.0013157 | North | N | 0.0013157 | 0
3097 | MARTLAKE | 1 | 785 | 0.015437 | north | Y | -0.00044728 | 0.038851 | -0.013655 | 0.022306 | 0.00044728 | North | N | 0.00044728 | 0
3098 | MARTLAKE | 2 | 795 | 0.015437 | north | Y | -0.00044728 | 0.038851 | -0.013655 | 0.022306 | 0.00044728 | North | N | 0.00044728 | 0
3099 | MARTLAKE | 3 | 780 | 0.015437 | north | Y | -0.00044728 | 0.038851 | -0.013655 | 0.022306 | 0.00044728 | North | N | 0.00044728 | 0
3107 | STRYKER_ | 1 | 182 | 0.014914 | north | Y | -0.00097028 | 0.038328 | -0.014178 | 0.021783 | 0.00097028 | North | N | 0.00097028 | 0
3108 | STRYKER_ | 2 | 484 | 0.014914 | north | Y | -0.00097028 | 0.038328 | -0.014178 | 0.021783 | 0.00097028 | North | N | 0.00097028 | 0
3126 | TRINIDAD | 1 | 224 | 0.015037 | north | Y | -0.00084728 | 0.038451 | -0.014055 | 0.021906 | 0.00084728 | North | N | 0.00084728 | 0
3309 | ASPN_G | 1 | 50 | 0.015018 | north | Y | -0.00086628 | 0.038432 | -0.014074 | 0.021887 | 0.00086628 | North | N | 0.00086628 | 0
3348 | CHAMPION | MB | 42 | 0.015035 | north | N | -0.00084928 | 0.038449 | -0.014057 | 0.021904 | 0.00084928 | North | N | 0.00084928 | 0
3381 | BBRN_1G | 1 | 615 | 0.012642 | north | Y | -0.0032423 | 0.036056 | -0.01645 | 0.019511 | 0.0032423 | North | N | 0.0032423 | 0
3382 | BBRN_2G | 2 | 587 | 0.012642 | north | Y | -0.0032423 | 0.036056 | -0.01645 | 0.019511 | 0.0032423 | North | N | 0.0032423 | 0
3403 | THOUSE_1 | MB | 537 | 0.011234 | north | Y | -0.0046503 | 0.034648 | -0.017858 | 0.018103 | 0.0046503 | North | N | 0.0046503 | 0
3404 | THOUSE_2 | 2 | 787 | 0.011234 | north | Y | -0.0046503 | 0.034648 | -0.017858 | 0.018103 | 0.0046503 | North | N | 0.0046503 | 0
3416 | LAKE_CRK | MB | 75 | 0.006215 | north | Y | -0.0096693 | 0.029629 | -0.022877 | 0.013084 | 0.0096693 | North | N | 0.0096693 | 0
3417 | LAKE_CRK | MB | 222 | 0.006215 | north | Y | -0.0096693 | 0.029629 | -0.022877 | 0.013084 | 0.0096693 | North | N | 0.0096693 | 0
3432 | SANDOW_4 | 4 | 569 | -0.023864 | south | Y | -0.039748 | -0.00045001 | -0.052956 | -0.016995 | 0.00045001 | south | N | 0.00045001 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.022821 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.022821 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.022881 | south | Y | -0.038765 | 0.00053299 | -0.051973 | -0.016012 | 0.00053299 | south | N | 0.00053299 | 0
5031 | BRA_VHBC | 1 | 46 | -0.022821 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5032 | BRA_VHBC | 2 | 47 | -0.022821 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5033 | BRA_VHBC | 3 | 46 | -0.022821 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5034 | BRA_VHBC | 4 | 46 | -0.022821 | south | Y | -0.038705 | 0.00059299 | -0.051913 | -0.015952 | 0.00059299 | south | N | 0.00059299 | 0
5111 | CALAVER_ | 1 | 424 | -0.022898 | south | Y | -0.038782 | 0.00051599 | -0.05199 | -0.016029 | 0.00051599 | south | N | 0.00051599 | 0
5112 | CALAVER_ | 2 | 425 | -0.022898 | south | Y | -0.038782 | 0.00051599 | -0.05199 | -0.016029 | 0.00051599 | south | N | 0.00051599 | 0
5264 | LEON_LCP | 3 | 58 | -0.022771 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5265 | LEON_LCP | 4 | 89 | -0.022771 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5266 | LEON_LCP | 1 | 44 | -0.022771 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5267 | LEON_LCP | 2 | 44 | -0.022771 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5268 | LEON_LCP | 3 | 43 | -0.022771 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5269 | LEON_LCP | 4 | 45 | -0.022771 | south | Y | -0.038655 | 0.00064299 | -0.051863 | -0.015902 | 0.00064299 | south | N | 0.00064299 | 0
5396 | CALAVER_ | 1 | 412 | -0.022862 | south | Y | -0.038746 | 0.00055199 | -0.051954 | -0.015993 | 0.00055199 | south | N | 0.00055199 | 0
5397 | CALAVER_ | 2 | 400 | -0.022862 | south | Y | -0.038746 | 0.00055199 | -0.051954 | -0.015993 | 0.00055199 | south | N | 0.00055199 | 0
5401 | CALAVER_ | 1 | 546 | -0.02259 | south | Y | -0.038474 | 0.00082399 | -0.051682 | -0.015721 | 0.00082399 | south | N | 0.00082399 | 0
5402 | CALAVER_ | 2 | 750 | -0.02259 | south | Y | -0.038474 | 0.00082399 | -0.051682 | -0.015721 | 0.00082399 | south | N | 0.00082399 | 0
5436 | TUTTL_WB | MB | 61 | -0.02287 | south | Y | -0.038754 | 0.00054399 | -0.051962 | -0.016001 | 0.00054399 | south | N | 0.00054399 | 0
5438 | TUTTL_WB | MB | 95 | -0.02287 | south | Y | -0.038754 | 0.00054399 | -0.051962 | -0.016001 | 0.00054399 | south | N | 0.00054399 | 0
5439 | TUTTL_WB | MB | 151 | -0.02287 | south | Y | -0.038754 | 0.00054399 | -0.051962 | -0.016001 | 0.00054399 | south | N | 0.00054399 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.02283 | south | Y | -0.038714 | 0.00058399 | -0.051922 | -0.015961 | 0.00058399 | south | N | 0.00058399 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.02283 | south | Y | -0.038714 | 0.00058399 | -0.051922 | -0.015961 | 0.00058399 | south | N | 0.00058399 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.02283 | south | Y | -0.038714 | 0.00058399 | -0.051922 | -0.015961 | 0.00058399 | south | N | 0.00058399 | 0
5503 | RAYBURNG | 1 | 22 | -0.018251 | south | Y | -0.034135 | 0.005163 | -0.047343 | -0.011382 | 0.005163 | south | N | 0.005163 | 0
5505 | RAYBURNG | 1 | 11 | -0.018251 | south | Y | -0.034135 | 0.005163 | -0.047343 | -0.011382 | 0.005163 | south | N | 0.005163 | 0
5506 | RAYBURNG | 1 | 11 | -0.018251 | south | Y | -0.034135 | 0.005163 | -0.047343 | -0.011382 | 0.005163 | south | N | 0.005163 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.018414 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.018414 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5511 | RAYBURNC | 1 | 46 | -0.018414 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5512 | RAYBURNC | 1 | 48 | -0.018414 | south | Y | -0.034298 | 0.005 | -0.047506 | -0.011545 | 0.005 | south | N | 0.005 | 0
5728 | FALCONHY | 2 | 12 | -0.019072 | south | N | -0.034956 | 0.004342 | -0.048164 | -0.012203 | 0.004342 | south | N | 0.004342 | 0
5729 | FALCONHY | 3 | 11 | -0.019072 | south | N | -0.034956 | 0.004342 | -0.048164 | -0.012203 | 0.004342 | south | N | 0.004342 | 0
5890 | PEARSALL | 1 | 24 | -0.019538 | south | Y | -0.035422 | 0.003876 | -0.04863 | -0.012669 | 0.003876 | south | N | 0.003876 | 0
5891 | PEARSALL | 1 | 24 | -0.019538 | south | Y | -0.035422 | 0.003876 | -0.04863 | -0.012669 | 0.003876 | south | N | 0.003876 | 0
5892 | PEARSALL | 1 | 23 | -0.019538 | south | Y | -0.035422 | 0.003876 | -0.04863 | -0.012669 | 0.003876 | south | N | 0.003876 | 0
5903 | SANMIGUE | 1 | 396 | -0.021106 | south | Y | -0.03699 | 0.002308 | -0.050198 | -0.014237 | 0.002308 | south | N | 0.002308 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.012395 | houston | N | -0.028279 | 0.011019 | -0.041487 | -0.0055263 | 0.0055263 | houston | N | 0.0055263 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.012395 | houston | N | -0.028279 | 0.011019 | -0.041487 | -0.0055263 | 0.0055263 | houston | N | 0.0055263 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.015884 | 0
5932 | SI_RAY9 | 9 | 38 | -0.018941 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.018941 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
5934 | SI_RAY5 | 5 | 15 | -0.018941 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
5935 | SI_RAY10 | 10 | 47 | -0.018941 | south | Y | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
6016 | SWMESA | 1 | 75 | 0.027722 | west | Y | 0.011838 | 0.051136 | -0.0013703 | 0.034591 | 0.0013703 | west | N | 0.0013703 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.029092 | 0
6144 | MCADOO1A | 1 | 150 | 0.029742 | west | Y | 0.013858 | 0.053156 | 0.00064974 | 0.036611 | 0.00064974 | west | N | 0.00064974 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.031906 | west | Y | 0.016022 | 0.05532 | 0.0028137 | 0.038775 | 0.0028137 | west | N | 0.0028137 | 0
6476 | LANGFORD | 1 | 150 | 0.020092 | west | Y | 0.0042077 | 0.043506 | -0.0090003 | 0.026961 | 0.0042077 | North | Y | 0.0090003 | 0.71888
6637 | SNYDERW1 | 1 | 63 | 0.029741 | west | Y | 0.013857 | 0.053155 | 0.00064874 | 0.03661 | 0.00064874 | west | N | 0.00064874 | 0
6752 | OKLA0A | 1 | 649.7 | 0.026619 | west | Y | 0.010735 | 0.050033 | -0.0024733 | 0.033488 | 0.0024733 | west | N | 0.0024733 | 0
6948 | DENISNDM | 1 | 40 | 0.018028 | north | N | 0.0021437 | 0.041442 | -0.011064 | 0.024897 | 0.0021437 | North | N | 0.0021437 | 0
6948 | DENISNDM | 2 | 40 | 0.018028 | north | N | 0.0021437 | 0.041442 | -0.011064 | 0.024897 | 0.0021437 | North | N | 0.0021437 | 0
7000 | L_FERGUS | 1 | 422 | -0.064567 | south | Y | -0.080451 | -0.041153 | -0.093659 | -0.057698 | 0.041153 | south | N | 0.041153 | 0
7004 | L_SIMGID | 1 | 132 | -0.026135 | south | Y | -0.042019 | -0.002721 | -0.055227 | -0.019266 | 0.002721 | south | N | 0.002721 | 0
7005 | L_SIMGID | 2 | 134 | -0.026135 | south | Y | -0.042019 | -0.002721 | -0.055227 | -0.019266 | 0.002721 | south | N | 0.002721 | 0
7006 | L_SIMGID | 3 | 323 | -0.026135 | south | Y | -0.042019 | -0.002721 | -0.055227 | -0.019266 | 0.002721 | south | N | 0.002721 | 0
7007 | L_LOSTPI | 1 | 158 | -0.024129 | south | Y | -0.040013 | -0.00071501 | -0.053221 | -0.01726 | 0.00071501 | south | N | 0.00071501 | 0
7008 | L_LOSTPI | 2 | 160 | -0.024129 | south | Y | -0.040013 | -0.00071501 | -0.053221 | -0.01726 | 0.00071501 | south | N | 0.00071501 | 0
7009 | L_LOSTPI | 3 | 175 | -0.024129 | south | Y | -0.040013 | -0.00071501 | -0.053221 | -0.01726 | 0.00071501 | south | N | 0.00071501 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.022554 | south | Y | -0.038438 | 0.00085999 | -0.051646 | -0.015685 | 0.00085999 | south | N | 0.00085999 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.022554 | south | Y | -0.038438 | 0.00085999 | -0.051646 | -0.015685 | 0.00085999 | south | N | 0.00085999 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.022543 | south | Y | -0.038427 | 0.00087099 | -0.051635 | -0.015674 | 0.00087099 | south | N | 0.00087099 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.024031 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7015 | L_HAYSEN | 2 | 225 | -0.024031 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.024031 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.024031 | south | Y | -0.039915 | -0.00061701 | -0.053123 | -0.017162 | 0.00061701 | south | N | 0.00061701 | 0
7020 | L_AUSTPL | 1 | 8 | -0.030156 | south | N | -0.04604 | -0.006742 | -0.059248 | -0.023287 | 0.006742 | south | N | 0.006742 | 0
7020 | L_AUSTPL | 2 | 8 | -0.030156 | south | N | -0.04604 | -0.006742 | -0.059248 | -0.023287 | 0.006742 | south | N | 0.006742 | 0
7022 | L_BUCHAN | 1 | 18 | -0.089988 | south | N | -0.10587 | -0.066574 | -0.11908 | -0.083119 | 0.066574 | south | N | 0.066574 | 0
7023 | L_BUCHAN | 2 | 18 | -0.089988 | south | N | -0.10587 | -0.066574 | -0.11908 | -0.083119 | 0.066574 | south | N | 0.066574 | 0
7024 | L_BUCHAN | 3 | 15 | -0.089988 | south | N | -0.10587 | -0.066574 | -0.11908 | -0.083119 | 0.066574 | south | N | 0.066574 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.077212 | south | N | -0.093096 | -0.053798 | -0.1063 | -0.070343 | 0.053798 | south | N | 0.053798 | 0
7028 | L_MARBFA | 1 | 18 | -0.056927 | south | N | -0.072811 | -0.033513 | -0.086019 | -0.050058 | 0.033513 | south | N | 0.033513 | 0
7029 | L_MARBFA | 2 | 18 | -0.056927 | south | N | -0.072811 | -0.033513 | -0.086019 | -0.050058 | 0.033513 | south | N | 0.033513 | 0
7031 | L_MARSFO | 1 | 35 | -0.039602 | south | N | -0.055486 | -0.016188 | -0.068694 | -0.032733 | 0.016188 | south | N | 0.016188 | 0
7032 | L_MARSFO | 2 | 34 | -0.039602 | south | N | -0.055486 | -0.016188 | -0.068694 | -0.032733 | 0.016188 | south | N | 0.016188 | 0
7033 | L_MARSFO | 3 | 35 | -0.039602 | south | N | -0.055486 | -0.016188 | -0.068694 | -0.032733 | 0.016188 | south | N | 0.016188 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.0655 | south | N | -0.081384 | -0.042086 | -0.094592 | -0.058631 | 0.042086 | south | N | 0.042086 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.0655 | south | N | -0.081384 | -0.042086 | -0.094592 | -0.058631 | 0.042086 | south | N | 0.042086 | 0
7038 | L_DELAWA | 1 | 35 | 0.029132 | west | Y | 0.013248 | 0.052546 | 3.9745e-05 | 0.036001 | 3.9745e-05 | west | N | 3.9745e-05 | 0
7038 | L_DELAWA | 2 | 30 | 0.029132 | west | Y | 0.013248 | 0.052546 | 3.9745e-05 | 0.036001 | 3.9745e-05 | west | N | 3.9745e-05 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.023603 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.023603 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.023603 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.023603 | south | Y | -0.039487 | -0.00018901 | -0.052695 | -0.016734 | 0.00018901 | south | N | 0.00018901 | 0
7487 | L_CANYHY | 1 | 6 | -0.026781 | south | N | -0.042665 | -0.003367 | -0.055873 | -0.019912 | 0.003367 | south | N | 0.003367 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.023934 | south | N | -0.039818 | -0.00052001 | -0.053026 | -0.017065 | 0.00052001 | south | N | 0.00052001 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.023934 | south | N | -0.039818 | -0.00052001 | -0.053026 | -0.017065 | 0.00052001 | south | N | 0.00052001 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.023934 | south | N | -0.039818 | -0.00052001 | -0.053026 | -0.017065 | 0.00052001 | south | N | 0.00052001 | 0
7609 | L_SCHUMA | 1 | 4 | -0.023732 | south | N | -0.039616 | -0.00031801 | -0.052824 | -0.016863 | 0.00031801 | south | N | 0.00031801 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.023346 | south | N | -0.03923 | 6.7991e-05 | -0.052438 | -0.016477 | 6.7991e-05 | south | N | 6.7991e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.023346 | south | N | -0.03923 | 6.7991e-05 | -0.052438 | -0.016477 | 6.7991e-05 | south | N | 6.7991e-05 | 0
7800 | L_GUADGE | 1 | 147 | -0.022869 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7801 | L_GUADGE | 2 | 138 | -0.022869 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7802 | L_GUADGE | 3 | 140 | -0.022869 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7803 | L_GUADGE | 4 | 147 | -0.022869 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7804 | L_GUADGE | 5 | 182 | -0.022869 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7805 | L_GUADGE | 6 | 198 | -0.022869 | south | Y | -0.038753 | 0.00054499 | -0.051961 | -0.016 | 0.00054499 | south | N | 0.00054499 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.025109 | south | Y | -0.040993 | -0.001695 | -0.054201 | -0.01824 | 0.001695 | south | N | 0.001695 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.025109 | south | Y | -0.040993 | -0.001695 | -0.054201 | -0.01824 | 0.001695 | south | N | 0.001695 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.025109 | south | Y | -0.040993 | -0.001695 | -0.054201 | -0.01824 | 0.001695 | south | N | 0.001695 | 0
7810 | L_RIONOG | 1 | 142 | -0.023437 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
7811 | L_RIONOG | 2 | 145 | -0.023437 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
7812 | L_RIONOG | 3 | 151 | -0.023437 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
7813 | L_RIONOG | 4 | 290 | -0.023437 | south | Y | -0.039321 | -2.3009e-05 | -0.052529 | -0.016568 | 2.3009e-05 | south | N | 2.3009e-05 | 0
8032 | AMISTADH | 1 | 33 | -0.006231 | south | N | -0.022115 | 0.017183 | -0.035323 | 0.00063768 | 0.00063768 | houston | Y | 0.017183 | 0
8033 | AMISTADH | 2 | 25 | -0.006231 | south | N | -0.022115 | 0.017183 | -0.035323 | 0.00063768 | 0.00063768 | houston | Y | 0.017183 | 0
8048 | FALCONHY | 1 | 12 | -0.019072 | south | N | -0.034956 | 0.004342 | -0.048164 | -0.012203 | 0.004342 | south | N | 0.004342 | 0
8066 | DUP1V#1 | 1 | 73 | -0.018442 | south | N | -0.034326 | 0.004972 | -0.047534 | -0.011573 | 0.004972 | south | N | 0.004972 | 0
8134 | FOR69CG0 | 1 | 79 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8138 | FOR69CG0 | 2 | 81 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8147 | UCAR #2 | 10 | 28 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
8148 | UCAR #1 | 2 | 7 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
8153 | FOR69CG0 | 3 | 79 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8154 | FOR69CG0 | 4 | 80 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8156 | FOR69CG0 | 6 | 25 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8157 | FOR69CG0 | 7 | 46 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
8161 | COLETOU1 | 1 | 629 | -0.019515 | south | Y | -0.035399 | 0.003899 | -0.048607 | -0.012646 | 0.003899 | south | N | 0.003899 | 0
8173 | VICEC51A | 5 | 144 | -0.01863 | south | Y | -0.034514 | 0.004784 | -0.047722 | -0.011761 | 0.004784 | south | N | 0.004784 | 0
8174 | VICEC61A | 6 | 188 | -0.01863 | south | Y | -0.034514 | 0.004784 | -0.047722 | -0.011761 | 0.004784 | south | N | 0.004784 | 0
8189 | CUERO 2 | 1 | 12 | -0.021919 | south | N | -0.037803 | 0.001495 | -0.051011 | -0.01505 | 0.001495 | south | N | 0.001495 | 0
8262 | ELPS | 1 | 6 | -0.010392 | south | N | -0.026276 | 0.013022 | -0.039484 | -0.0035233 | 0.0035233 | houston | Y | 0.013022 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8442 | NBEC71A | 1 | 336 | -0.018762 | south | Y | -0.034646 | 0.004652 | -0.047854 | -0.011893 | 0.004652 | south | N | 0.004652 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.015884 | 0.023414 | -0.029092 | 0.0068687 | 0.0068687 | houston | Y | 0.023414 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.018802 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.018802 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.018823 | south | N | -0.034707 | 0.004591 | -0.047915 | -0.011954 | 0.004591 | south | N | 0.004591 | 0
8506 | VAL #1 | 1 | 25 | -0.018806 | south | N | -0.03469 | 0.004608 | -0.047898 | -0.011937 | 0.004608 | south | N | 0.004608 | 0
8507 | VAL #2 | 2 | 25 | -0.018806 | south | N | -0.03469 | 0.004608 | -0.047898 | -0.011937 | 0.004608 | south | N | 0.004608 | 0
8511 | OXY_CC0A | 1 | 38 | -0.018825 | south | N | -0.034709 | 0.004589 | -0.047917 | -0.011956 | 0.004589 | south | N | 0.004589 | 0
8517 | CELANEBI | 1 | 29 | -0.018908 | south | N | -0.034792 | 0.004506 | -0.048 | -0.012039 | 0.004506 | south | N | 0.004506 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.018764 | south | N | -0.034648 | 0.00465 | -0.047856 | -0.011895 | 0.00465 | south | N | 0.00465 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.018764 | south | N | -0.034648 | 0.00465 | -0.047856 | -0.011895 | 0.00465 | south | N | 0.00465 | 0
8562 | CNOPST1 | 3 | 153 | -0.018764 | south | N | -0.034648 | 0.00465 | -0.047856 | -0.011895 | 0.00465 | south | N | 0.00465 | 0
8926 | LGE_GT10 | 1 | 158 | -0.018584 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8927 | LGE_GT20 | 2 | 153 | -0.018584 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8928 | LGE_STG0 | 3 | 100 | -0.018584 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8930 | ICPGN10A | 1 | 145 | -0.018584 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8931 | ICPGN20A | 2 | 147 | -0.018584 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8932 | ICPGN30A | 3 | 127 | -0.018584 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.018977 | south | Y | -0.034861 | 0.004437 | -0.048069 | -0.012108 | 0.004437 | south | N | 0.004437 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.018977 | south | Y | -0.034861 | 0.004437 | -0.048069 | -0.012108 | 0.004437 | south | N | 0.004437 | 0
8935 | FGNTS201 | 3 | 173 | -0.018977 | south | Y | -0.034861 | 0.004437 | -0.048069 | -0.012108 | 0.004437 | south | N | 0.004437 | 0
8936 | MVGN#1 | 1 | 207 | -0.018963 | south | Y | -0.034847 | 0.004451 | -0.048055 | -0.012094 | 0.004451 | south | N | 0.004451 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.018963 | south | Y | -0.034847 | 0.004451 | -0.048055 | -0.012094 | 0.004451 | south | N | 0.004451 | 0
8938 | MVGN#3 | 3 | 242 | -0.018963 | south | Y | -0.034847 | 0.004451 | -0.048055 | -0.012094 | 0.004451 | south | N | 0.004451 | 0
8981 | HECN1 | 1 | 144 | -0.018962 | south | Y | -0.034846 | 0.004452 | -0.048054 | -0.012093 | 0.004452 | south | N | 0.004452 | 0
8982 | HECN2 | 2 | 144 | -0.018962 | south | Y | -0.034846 | 0.004452 | -0.048054 | -0.012093 | 0.004452 | south | N | 0.004452 | 0
8983 | HECN3 | 3 | 171 | -0.018962 | south | Y | -0.034846 | 0.004452 | -0.048054 | -0.012093 | 0.004452 | south | N | 0.004452 | 0
9000 | DECKR_G1 | 1 | 310 | -0.029389 | south | Y | -0.045273 | -0.005975 | -0.058481 | -0.02252 | 0.005975 | south | N | 0.005975 | 0
9001 | DECKR_G2 | 2 | 413 | -0.029389 | south | Y | -0.045273 | -0.005975 | -0.058481 | -0.02252 | 0.005975 | south | N | 0.005975 | 0
9002 | DECKR_G3 | 3 | 42 | -0.029121 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9003 | DECKR_G4 | 4 | 44 | -0.029121 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9004 | DECKR_G5 | 5 | 44 | -0.029121 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9005 | DECKR_G6 | 6 | 47 | -0.029121 | south | Y | -0.045005 | -0.005707 | -0.058213 | -0.022252 | 0.005707 | south | N | 0.005707 | 0
9016 | SANDH_G1 | 1 | 49 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9017 | SANDH_G2 | 2 | 46 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9018 | SANDH_G3 | 3 | 46 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9019 | SANDH_G4 | 4 | 47 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9020 | SANDHG5A | 5A | 154 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9021 | SANDHG5C | 5C | 148 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9022 | SANDH_G6 | 6 | 48 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
9023 | SANDH_G7 | 7 | 48 | -0.029083 | south | Y | -0.044967 | -0.005669 | -0.058175 | -0.022214 | 0.005669 | south | N | 0.005669 | 0
11001 | NAV1CT | 1 | 70 | 0.02933 | west | Y | 0.013446 | 0.052744 | 0.00023774 | 0.036199 | 0.00023774 | west | N | 0.00023774 | 0
11009 | NAV2CT | 1 | 70 | 0.02933 | west | Y | 0.013446 | 0.052744 | 0.00023774 | 0.036199 | 0.00023774 | west | N | 0.00023774 | 0
11011 | NAV3ST | 1 | 92.8 | 0.02933 | west | Y | 0.013446 | 0.052744 | 0.00023774 | 0.036199 | 0.00023774 | west | N | 0.00023774 | 0
11012 | NAV4CT | 1 | 80 | 0.02933 | west | Y | 0.013446 | 0.052744 | 0.00023774 | 0.036199 | 0.00023774 | west | N | 0.00023774 | 0
11013 | NAV5CT | 1 | 80 | 0.02933 | west | Y | 0.013446 | 0.052744 | 0.00023774 | 0.036199 | 0.00023774 | west | N | 0.00023774 | 0
11014 | NAV6ST | 1 | 115 | 0.02933 | west | Y | 0.013446 | 0.052744 | 0.00023774 | 0.036199 | 0.00023774 | west | N | 0.00023774 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.029328 | west | Y | 0.013444 | 0.052742 | 0.00023574 | 0.036197 | 0.00023574 | west | N | 0.00023574 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.029328 | west | Y | 0.013444 | 0.052742 | 0.00023574 | 0.036197 | 0.00023574 | west | N | 0.00023574 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.029328 | west | Y | 0.013444 | 0.052742 | 0.00023574 | 0.036197 | 0.00023574 | west | N | 0.00023574 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.029328 | west | Y | 0.013444 | 0.052742 | 0.00023574 | 0.036197 | 0.00023574 | west | N | 0.00023574 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.029328 | west | Y | 0.013444 | 0.052742 | 0.00023574 | 0.036197 | 0.00023574 | west | N | 0.00023574 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.029328 | west | Y | 0.013444 | 0.052742 | 0.00023574 | 0.036197 | 0.00023574 | west | N | 0.00023574 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.028925 | west | Y | 0.013041 | 0.052339 | -0.00016726 | 0.035794 | 0.00016726 | west | N | 0.00016726 | 0
11057 | CHAMPION | 1 | 126.5 | 0.028925 | west | Y | 0.013041 | 0.052339 | -0.00016726 | 0.035794 | 0.00016726 | west | N | 0.00016726 | 0
11058 | PYRON_1G | 1 | 249 | 0.028925 | west | Y | 0.013041 | 0.052339 | -0.00016726 | 0.035794 | 0.00016726 | west | N | 0.00016726 | 0
11059 | INADALE_ | 1 | 197 | 0.028925 | west | Y | 0.013041 | 0.052339 | -0.00016726 | 0.035794 | 0.00016726 | west | N | 0.00016726 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.029493 | west | Y | 0.013609 | 0.052907 | 0.00040074 | 0.036362 | 0.00040074 | west | N | 0.00040074 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.029493 | west | Y | 0.013609 | 0.052907 | 0.00040074 | 0.036362 | 0.00040074 | west | N | 0.00040074 | 0
11147 | NOTREES_ | 1 | 149 | 0.029189 | west | Y | 0.013305 | 0.052603 | 9.6745e-05 | 0.036058 | 9.6745e-05 | west | N | 9.6745e-05 | 0
11309 | BULLCREK | 1 | 180 | 0.029645 | west | Y | 0.013761 | 0.053059 | 0.00055274 | 0.036514 | 0.00055274 | west | N | 0.00055274 | 0
11310 | BULLCREK | 1 | 180 | 0.029645 | west | Y | 0.013761 | 0.053059 | 0.00055274 | 0.036514 | 0.00055274 | west | N | 0.00055274 | 0
11320 | COYOTE_1 | 1 | 225 | 0.029635 | west | Y | 0.013751 | 0.053049 | 0.00054274 | 0.036504 | 0.00054274 | west | N | 0.00054274 | 0
11415 | LORAINE_ | 1 | 125 | 0.029321 | west | Y | 0.013437 | 0.052735 | 0.00022874 | 0.03619 | 0.00022874 | west | N | 0.00022874 | 0
11416 | LORAINE_ | 1 | 125 | 0.029321 | west | Y | 0.013437 | 0.052735 | 0.00022874 | 0.03619 | 0.00022874 | west | N | 0.00022874 | 0
11691 | KMICHICT | 1 | 140 | 0.017745 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11692 | KMICHICT | 2 | 141 | 0.017745 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11693 | KMICHIST | 3 | 309 | 0.017745 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11694 | KMICHICT | 4 | 143 | 0.017745 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11695 | KMICHICT | 5 | 144 | 0.017745 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
11696 | KMICHIST | 6 | 310 | 0.017745 | north | N | 0.0018607 | 0.041159 | -0.011347 | 0.024614 | 0.0018607 | North | N | 0.0018607 | 0
12322 | ENNSTRAC | 1 | 196 | 0.016684 | north | Y | 0.00079972 | 0.040098 | -0.012408 | 0.023553 | 0.00079972 | North | N | 0.00079972 | 0
12323 | ENNSTRAC | 2 | 111 | 0.016684 | north | Y | 0.00079972 | 0.040098 | -0.012408 | 0.023553 | 0.00079972 | North | N | 0.00079972 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.018035 | north | N | 0.0021507 | 0.041449 | -0.011057 | 0.024904 | 0.0021507 | North | N | 0.0021507 | 0
12411 | FPLEFR1A | 1 | 161 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12412 | FPLEFR1B | 2 | 164 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12413 | FPLEFR1C | 3 | 164 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12414 | FPLEFR1S | 4 | 414 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12421 | FPLEFR2A | 1 | 162 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12422 | FPLEFR2B | 2 | 161 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12423 | FPLEFR2C | 3 | 163 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12424 | FPLEFR2S | 4 | 409 | 0.016933 | north | Y | 0.0010487 | 0.040347 | -0.012159 | 0.023802 | 0.0010487 | North | N | 0.0010487 | 0
12440 | PARKD_1S | 1 | 0 | 0.017247 | north | N | 0.0013627 | 0.040661 | -0.011845 | 0.024116 | 0.0013627 | North | N | 0.0013627 | 0
12449 | PARKD_2S | 1 | 0 | 0.017247 | north | N | 0.0013627 | 0.040661 | -0.011845 | 0.024116 | 0.0013627 | North | N | 0.0013627 | 0
13116 | TGATEWAY | 1 | 148 | 0.015235 | north | N | -0.00064928 | 0.038649 | -0.013857 | 0.022104 | 0.00064928 | North | N | 0.00064928 | 0
13117 | TGATEWAY | 2 | 130 | 0.015235 | north | N | -0.00064928 | 0.038649 | -0.013857 | 0.022104 | 0.00064928 | North | N | 0.00064928 | 0
13118 | TGATEWAY | 3 | 145 | 0.015235 | north | N | -0.00064928 | 0.038649 | -0.013857 | 0.022104 | 0.00064928 | North | N | 0.00064928 | 0
13119 | TGATEWAY | 4 | 399 | 0.015235 | north | N | -0.00064928 | 0.038649 | -0.013857 | 0.022104 | 0.00064928 | North | N | 0.00064928 | 0
13131 | CALFREST | 1 | 150.7 | 0.013082 | north | Y | -0.0028023 | 0.036496 | -0.01601 | 0.019951 | 0.0028023 | North | N | 0.0028023 | 0
13132 | CALFREST | 2 | 151 | 0.013082 | north | Y | -0.0028023 | 0.036496 | -0.01601 | 0.019951 | 0.0028023 | North | N | 0.0028023 | 0
13133 | CALFREST | 3 | 177.4 | 0.013082 | north | Y | -0.0028023 | 0.036496 | -0.01601 | 0.019951 | 0.0028023 | North | N | 0.0028023 | 0
13134 | CALFREST | 4 | 151.5 | 0.013144 | north | Y | -0.0027403 | 0.036558 | -0.015948 | 0.020013 | 0.0027403 | North | N | 0.0027403 | 0
13135 | CALFREST | 5 | 152.3 | 0.013144 | north | Y | -0.0027403 | 0.036558 | -0.015948 | 0.020013 | 0.0027403 | North | N | 0.0027403 | 0
13136 | CALFREST | 6 | 177.5 | 0.013144 | north | Y | -0.0027403 | 0.036558 | -0.015948 | 0.020013 | 0.0027403 | North | N | 0.0027403 | 0
13432 | SANDOW_5 | 5 | 581 | -0.023864 | south | Y | -0.039748 | -0.00045001 | -0.052956 | -0.016995 | 0.00045001 | south | N | 0.00045001 | 0
13691 | OAKGROVE | 1 | 855 | 0.006962 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
13692 | OAKGROVE | 2 | 855 | 0.006962 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
32798 | BRYN_TAM | 1 | 32 | 0.00225 | north | N | -0.013634 | 0.025664 | -0.026842 | 0.0091187 | 0.0091187 | houston | Y | 0.013634 | 0
32883 | BRYN_DNS | 1 | 48 | 0.001961 | north | Y | -0.013923 | 0.025375 | -0.027131 | 0.0088297 | 0.0088297 | houston | Y | 0.013923 | 0.24449
32884 | BRYN_DNS | 1 | 46 | 0.001961 | north | Y | -0.013923 | 0.025375 | -0.027131 | 0.0088297 | 0.0088297 | houston | Y | 0.013923 | 0.23431
32886 | BRYN_ATK | MB | 12 | 0.002266 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32887 | BRYN_ATK | MB | 51 | 0.002266 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32888 | BRYN_ATK | 1 | 17 | 0.002266 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0.076221
32890 | BRYN_ATK | MB | 22 | 0.002266 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32891 | BRYN_ATK | MB | 25 | 0.002266 | north | Y | -0.013618 | 0.02568 | -0.026826 | 0.0091347 | 0.0091347 | houston | Y | 0.013618 | 0
32892 | BRYN_DNS | 1 | 105 | 0.001961 | north | Y | -0.013923 | 0.025375 | -0.027131 | 0.0088297 | 0.0088297 | houston | Y | 0.013923 | 0.53483
36998 | RDCNYNG1 | 1 | 84 | 0.029712 | west | Y | 0.013828 | 0.053126 | 0.00061974 | 0.036581 | 0.00061974 | west | N | 0.00061974 | 0
38332 | WDWRDU2 | 1 | 80 | 0.027688 | west | Y | 0.011804 | 0.051102 | -0.0014043 | 0.034557 | 0.0014043 | west | N | 0.0014043 | 0
38437 | TNSRBNMS | 1 | 150 | 0.027675 | west | Y | 0.011791 | 0.051089 | -0.0014173 | 0.034544 | 0.0014173 | west | N | 0.0014173 | 0
38438 | TNSRBNMS | 1 | 150 | 0.027675 | west | Y | 0.011791 | 0.051089 | -0.0014173 | 0.034544 | 0.0014173 | west | N | 0.0014173 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38600 | TNBP_CGN | 5 | 53 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38614 | TNBPAMCG | 4 | 96 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38615 | TNBPAMCG | 1 | 244 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38690 | TNBP_CGN | 3 | 40 | -0.0071 | houston | N | -0.022984 | 0.016314 | -0.036192 | -0.00023132 | 0.00023132 | houston | N | 0.00023132 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.007103 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.007103 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.007103 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.007103 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
39470 | TNDOWCGN | 1 | 32 | -0.007103 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
39480 | TNDOWCGN | 1 | 30 | -0.007103 | houston | N | -0.022987 | 0.016311 | -0.036195 | -0.00023432 | 0.00023432 | houston | N | 0.00023432 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.009197 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.009197 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.009197 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.009197 | houston | N | -0.025081 | 0.014217 | -0.038289 | -0.0023283 | 0.0023283 | houston | N | 0.0023283 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.006962 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
39970 | TNTNPONE | 1 | 153 | 0.006962 | north | Y | -0.0089223 | 0.030376 | -0.02213 | 0.013831 | 0.0089223 | North | N | 0.0089223 | 0
48500 | APD_GT1_ | 1 | 136 | -0.005823 | houston | N | -0.021707 | 0.017591 | -0.034915 | 0.0010457 | 0.0010457 | houston | N | 0.0010457 | 0
48510 | AK_GT1__ | 1 | 33 | -0.007799 | houston | N | -0.023683 | 0.015615 | -0.036891 | -0.00093032 | 0.00093032 | houston | N | 0.00093032 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.005817 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.005817 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.005817 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.005817 | houston | Y | -0.021701 | 0.017597 | -0.034909 | 0.0010517 | 0.0010517 | houston | N | 0.0010517 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.009547 | houston | N | -0.025431 | 0.013867 | -0.038639 | -0.0026783 | 0.0026783 | houston | N | 0.0026783 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.009547 | houston | N | -0.025431 | 0.013867 | -0.038639 | -0.0026783 | 0.0026783 | houston | N | 0.0026783 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.007915 | houston | N | -0.023799 | 0.015499 | -0.037007 | -0.0010463 | 0.0010463 | houston | N | 0.0010463 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.007915 | houston | N | -0.023799 | 0.015499 | -0.037007 | -0.0010463 | 0.0010463 | houston | N | 0.0010463 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.007915 | houston | N | -0.023799 | 0.015499 | -0.037007 | -0.0010463 | 0.0010463 | houston | N | 0.0010463 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.0063 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.0063 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.0063 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.0063 | houston | N | -0.022184 | 0.017114 | -0.035392 | 0.00056868 | 0.00056868 | houston | N | 0.00056868 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.00599 | houston | N | -0.021874 | 0.017424 | -0.035082 | 0.00087868 | 0.00087868 | houston | N | 0.00087868 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.00599 | houston | N | -0.021874 | 0.017424 | -0.035082 | 0.00087868 | 0.00087868 | houston | N | 0.00087868 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.006394 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.006394 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.006394 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.006394 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.006394 | houston | N | -0.022278 | 0.01702 | -0.035486 | 0.00047468 | 0.00047468 | houston | N | 0.00047468 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.005429 | houston | Y | -0.021313 | 0.017985 | -0.034521 | 0.0014397 | 0.0014397 | houston | N | 0.0014397 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.005587 | houston | Y | -0.021471 | 0.017827 | -0.034679 | 0.0012817 | 0.0012817 | houston | N | 0.0012817 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.005382 | houston | Y | -0.021266 | 0.018032 | -0.034474 | 0.0014867 | 0.0014867 | houston | N | 0.0014867 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.005382 | houston | Y | -0.021266 | 0.018032 | -0.034474 | 0.0014867 | 0.0014867 | houston | N | 0.0014867 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.005382 | houston | Y | -0.021266 | 0.018032 | -0.034474 | 0.0014867 | 0.0014867 | houston | N | 0.0014867 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.004506 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.005791 | houston | N | -0.021675 | 0.017623 | -0.034883 | 0.0010777 | 0.0010777 | houston | N | 0.0010777 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.005791 | houston | N | -0.021675 | 0.017623 | -0.034883 | 0.0010777 | 0.0010777 | houston | N | 0.0010777 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.00527 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.00527 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.00527 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.00527 | houston | N | -0.021154 | 0.018144 | -0.034362 | 0.0015987 | 0.0015987 | houston | N | 0.0015987 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.005979 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.005979 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.005979 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.005979 | houston | N | -0.021863 | 0.017435 | -0.035071 | 0.00088968 | 0.00088968 | houston | N | 0.00088968 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.006081 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.006081 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.006081 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.006081 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.006081 | houston | N | -0.021965 | 0.017333 | -0.035173 | 0.00078768 | 0.00078768 | houston | N | 0.00078768 | 0
48651 | EP_1_2 | 1 | 5 | -0.005437 | houston | N | -0.021321 | 0.017977 | -0.034529 | 0.0014317 | 0.0014317 | houston | N | 0.0014317 | 0
48651 | EP_1_2 | 2 | 21 | -0.005437 | houston | N | -0.021321 | 0.017977 | -0.034529 | 0.0014317 | 0.0014317 | houston | N | 0.0014317 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.001631 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.001631 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.001631 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.001631 | north | N | -0.014253 | 0.025045 | -0.027461 | 0.0084997 | 0.0084997 | houston | Y | 0.014253 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.00523 | houston | Y | -0.021114 | 0.018184 | -0.034322 | 0.0016387 | 0.0016387 | houston | N | 0.0016387 | 0
48691 | GBY_7374 | A | 46 | -0.006157 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48691 | GBY_7374 | B | 46 | -0.006157 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48692 | GBY_8182 | C | 46 | -0.006157 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48692 | GBY_8182 | D | 55 | -0.006157 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48693 | GBY_8384 | E | 55 | -0.006157 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48693 | GBY_8384 | F | 54 | -0.006157 | houston | Y | -0.022041 | 0.017257 | -0.035249 | 0.00071168 | 0.00071168 | houston | N | 0.00071168 | 0
48721 | LEG_1___ | 1 | 827 | 0.00866 | north | Y | -0.0072243 | 0.032074 | -0.020432 | 0.015529 | 0.0072243 | North | N | 0.0072243 | 0
48722 | LEG_2___ | 2 | 819 | 0.00866 | north | Y | -0.0072243 | 0.032074 | -0.020432 | 0.015529 | 0.0072243 | North | N | 0.0072243 | 0
48730 | MNS_GT | 1 | 46.1 | -0.007981 | houston | N | -0.023865 | 0.015433 | -0.037073 | -0.0011123 | 0.0011123 | houston | N | 0.0011123 | 0
48731 | CBE_GT1 | 1 | 76 | -0.01224 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48732 | CBE_GT2 | 1 | 76 | -0.01224 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48733 | CBE_ST12 | 1 | 105 | -0.01224 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48734 | CBE_GT3 | 1 | 74 | -0.01224 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48735 | CBE_GT4 | 1 | 74 | -0.01224 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48736 | CBE_ST34 | 1 | 102 | -0.01224 | houston | Y | -0.028124 | 0.011174 | -0.041332 | -0.0053713 | 0.0053713 | houston | N | 0.0053713 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.005976 | houston | N | -0.02186 | 0.017438 | -0.035068 | 0.00089268 | 0.00089268 | houston | N | 0.00089268 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.005976 | houston | N | -0.02186 | 0.017438 | -0.035068 | 0.00089268 | 0.00089268 | houston | N | 0.00089268 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.005976 | houston | N | -0.02186 | 0.017438 | -0.035068 | 0.00089268 | 0.00089268 | houston | N | 0.00089268 | 0
48761 | PR_GT1__ | 1 | 35 | -0.006039 | houston | N | -0.021923 | 0.017375 | -0.035131 | 0.00082968 | 0.00082968 | houston | N | 0.00082968 | 0
48772 | PHR_GN2_ | MB | 459 | -0.006633 | houston | Y | -0.022517 | 0.016781 | -0.035725 | 0.00023568 | 0.00023568 | houston | N | 0.00023568 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.005435 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.005435 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.005435 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.005435 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.005435 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.005435 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.005435 | houston | N | -0.021319 | 0.017979 | -0.034527 | 0.0014337 | 0.0014337 | houston | N | 0.0014337 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.004506 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.004506 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.004506 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.004506 | houston | N | -0.02039 | 0.018908 | -0.033598 | 0.0023627 | 0.0023627 | houston | N | 0.0023627 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.005399 | houston | N | -0.021283 | 0.018015 | -0.034491 | 0.0014697 | 0.0014697 | houston | N | 0.0014697 | 0
48820 | SHELLG1_ | 1 | 71 | -0.005918 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48821 | SHELLG2 | 2 | 72 | -0.005918 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48822 | SHELLG3_ | 1 | 39 | -0.005918 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48822 | SHELLG3_ | 2 | 30 | -0.005918 | houston | N | -0.021802 | 0.017496 | -0.03501 | 0.00095068 | 0.00095068 | houston | N | 0.00095068 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.006127 | houston | N | -0.022011 | 0.017287 | -0.035219 | 0.00074168 | 0.00074168 | houston | N | 0.00074168 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.006127 | houston | N | -0.022011 | 0.017287 | -0.035219 | 0.00074168 | 0.00074168 | houston | N | 0.00074168 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.00598 | houston | N | -0.021864 | 0.017434 | -0.035072 | 0.00088868 | 0.00088868 | houston | N | 0.00088868 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.005992 | houston | Y | -0.021876 | 0.017422 | -0.035084 | 0.00087668 | 0.00087668 | houston | N | 0.00087668 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.005996 | houston | Y | -0.02188 | 0.017418 | -0.035088 | 0.00087268 | 0.00087268 | houston | N | 0.00087268 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.005981 | houston | Y | -0.021865 | 0.017433 | -0.035073 | 0.00088768 | 0.00088768 | houston | N | 0.00088768 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.005978 | houston | Y | -0.021862 | 0.017436 | -0.03507 | 0.00089068 | 0.00089068 | houston | N | 0.00089068 | 0
48855 | SRB_GT21 | B2 | 12 | -0.005998 | houston | Y | -0.021882 | 0.017416 | -0.03509 | 0.00087068 | 0.00087068 | houston | N | 0.00087068 | 0
48855 | SRB_GT21 | MB | 18 | -0.005998 | houston | Y | -0.021882 | 0.017416 | -0.03509 | 0.00087068 | 0.00087068 | houston | N | 0.00087068 | 0
48865 | TECO_GT1 | 1 | 50 | -0.00683 | houston | Y | -0.022714 | 0.016584 | -0.035922 | 3.8679e-05 | 3.8679e-05 | houston | N | 3.8679e-05 | 0
48873 | THW_ST3_ | 3 | 104 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48874 | THW_ST4_ | 4 | 104 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48875 | THW_3132 | A | 54 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48875 | THW_3132 | B | 53 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48877 | THW_3334 | C | 54 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48877 | THW_3334 | D | 57 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48879 | THW_4142 | E | 54 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48879 | THW_4142 | F | 54 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48881 | THW_4344 | G | 58 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48881 | THW_4344 | H | 58 | -0.005639 | houston | Y | -0.021523 | 0.017775 | -0.034731 | 0.0012297 | 0.0012297 | houston | N | 0.0012297 | 0
48883 | THW_GT1_ | B2 | 12 | -0.005495 | houston | Y | -0.021379 | 0.017919 | -0.034587 | 0.0013737 | 0.0013737 | houston | N | 0.0013737 | 0
48885 | THW_5152 | A | 56 | -0.005161 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48885 | THW_5152 | B | 59 | -0.005161 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48886 | THW_5354 | C | 56 | -0.005161 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48886 | THW_5354 | D | 56 | -0.005161 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48887 | THW_5556 | E | 59 | -0.005161 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48887 | THW_5556 | F | 56 | -0.005161 | houston | Y | -0.021045 | 0.018253 | -0.034253 | 0.0017077 | 0.0017077 | houston | N | 0.0017077 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.011731 | houston | Y | -0.027615 | 0.011683 | -0.040823 | -0.0048623 | 0.0048623 | houston | N | 0.0048623 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.007721 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.007721 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.007721 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.007721 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.007721 | houston | N | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.007925 | houston | Y | -0.023809 | 0.015489 | -0.037017 | -0.0010563 | 0.0010563 | houston | N | 0.0010563 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.007925 | houston | Y | -0.023809 | 0.015489 | -0.037017 | -0.0010563 | 0.0010563 | houston | N | 0.0010563 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.007925 | houston | Y | -0.023809 | 0.015489 | -0.037017 | -0.0010563 | 0.0010563 | houston | N | 0.0010563 | 0
48929 | WAPGT21_ | B1 | 13 | -0.007721 | houston | Y | -0.023605 | 0.015693 | -0.036813 | -0.00085232 | 0.00085232 | houston | N | 0.00085232 | 0
48940 | WARVUE_G | G1 | 12 | -0.005433 | houston | Y | -0.021317 | 0.017981 | -0.034525 | 0.0014357 | 0.0014357 | houston | N | 0.0014357 | 0
49803 | EXN_15GT | 1 | 34 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49826 | EXN938GT | 5 | 45.9 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49828 | EXN941GT | 10 | 17.7 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49829 | EXN942GT | 11 | 20.4 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49830 | EXN943GT | 12 | 19.9 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49831 | EXN944GT | 13 | 35 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49832 | EXN945GT | 9 | 18 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49837 | EXN_GT | 4 | 85.4 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49838 | EXN_14GT | 14 | 148 | -0.005548 | houston | N | -0.021432 | 0.017866 | -0.03464 | 0.0013207 | 0.0013207 | houston | N | 0.0013207 | 0
49851 | DOW17000 | 37 | 62 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49858 | DOW38100 | 31 | 71.4 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49859 | DOW38200 | 33 | 45 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49860 | DOW38300 | 32 | 101 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49862 | DOW39100 | 36 | 86 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49863 | DOW39200 | 35 | 88 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49865 | DOW41000 | 41 | 50 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49866 | DOW42000 | 42 | 18 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49869 | DOW49000 | 45 | 94 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49870 | DOW61000 | 61 | 70 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49871 | DOW62000 | 62 | 63 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49872 | DOW63000 | 63 | 72 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49873 | DOW64000 | 64 | 64.8 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49876 | DOW65000 | 65 | 101 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49877 | DOW66000 | 66 | 97 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49878 | DOW67000 | 67 | 103 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49882 | DOW81000 | 81 | 76 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49884 | DOW82000 | 82 | 80 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49885 | DOW83000 | 83 | 80 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
49886 | DOW84000 | 84 | 171 | -0.009983 | houston | N | -0.025867 | 0.013431 | -0.039075 | -0.0031143 | 0.0031143 | houston | N | 0.0031143 | 0
58909 | PEARSALL | 1 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 2 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 3 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 4 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 5 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58909 | PEARSALL | 6 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 1 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 2 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 3 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 4 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 5 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58919 | PEARSALL | 6 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 1 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 2 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 3 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 4 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 5 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58929 | PEARSALL | 6 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 1 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 2 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 3 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 4 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 5 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
58949 | PEARSALL | 6 | 8.4 | -0.019191 | south | Y | -0.035075 | 0.004223 | -0.048283 | -0.012322 | 0.004223 | south | N | 0.004223 | 0
60000 | DSKY2 | 1 | 76.5 | 0.027097 | west | Y | 0.011213 | 0.050511 | -0.0019953 | 0.033966 | 0.0019953 | west | N | 0.0019953 | 0
60003 | KING_NE1 | 1 | 80 | 0.027722 | west | Y | 0.011838 | 0.051136 | -0.0013703 | 0.034591 | 0.0013703 | west | N | 0.0013703 | 0
60005 | KING_SE1 | 1 | 40 | 0.027722 | west | Y | 0.011838 | 0.051136 | -0.0013703 | 0.034591 | 0.0013703 | west | N | 0.0013703 | 0
60007 | KING_SW1 | 1 | 80 | 0.027845 | west | Y | 0.011961 | 0.051259 | -0.0012473 | 0.034714 | 0.0012473 | west | N | 0.0012473 | 0
60016 | WOODWRD1 | 1 | 80 | 0.027691 | west | Y | 0.011807 | 0.051105 | -0.0014013 | 0.03456 | 0.0014013 | west | N | 0.0014013 | 0
60017 | ORNNWP1 | 1 | 80 | 0.027092 | west | Y | 0.011208 | 0.050506 | -0.0020003 | 0.033961 | 0.0020003 | west | N | 0.0020003 | 0
60018 | DSKY1 | 1 | 84 | 0.026895 | west | Y | 0.011011 | 0.050309 | -0.0021973 | 0.033764 | 0.0021973 | west | N | 0.0021973 | 0
60019 | KING_NW1 | 1 | 80 | 0.027845 | west | Y | 0.011961 | 0.051259 | -0.0012473 | 0.034714 | 0.0012473 | west | N | 0.0012473 | 0
60057 | CALLAHAN | 1 | 114 | -0.026002 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60058 | BUFF_GAP | 1 | 120 | 0.031304 | west | Y | 0.01542 | 0.054718 | 0.0022117 | 0.038173 | 0.0022117 | west | N | 0.0022117 | 0
60060 | CIRELLO | 1 | 233 | 0.031304 | west | Y | 0.01542 | 0.054718 | 0.0022117 | 0.038173 | 0.0022117 | west | N | 0.0022117 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.031304 | west | Y | 0.01542 | 0.054718 | 0.0022117 | 0.038173 | 0.0022117 | west | N | 0.0022117 | 0
60066 | H_HOLLOW | 1 | 222 | -0.026002 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.026002 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.026002 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.026002 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60074 | HORSH5 | 1 | 100 | -0.026002 | south | Y | -0.041886 | -0.002588 | -0.055094 | -0.019133 | 0.002588 | south | N | 0.002588 | 0
60081 | WHRLWIND | 1 | 60 | 0.029366 | west | Y | 0.013482 | 0.05278 | 0.00027374 | 0.036235 | 0.00027374 | west | N | 0.00027374 | 0
60201 | RIO DRCS | F | 0 | -0.023952 | south | N | -0.039836 | -0.00053801 | -0.053044 | -0.017083 | 0.00053801 | south | N | 0.00053801 | 0
60202 | FRIEND_R | F | 0 | 0.023714 | west | N | 0.0078297 | 0.047128 | -0.0053783 | 0.030583 | 0.0053783 | west | N | 0.0053783 | 0
60203 | PRES0A | BT | 4.8 | 0.028196 | west | N | 0.012312 | 0.05161 | -0.00089626 | 0.035065 | 0.00089626 | west | N | 0.00089626 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.029465 | west | Y | 0.013581 | 0.052879 | 0.00037274 | 0.036334 | 0.00037274 | west | N | 0.00037274 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.029465 | west | Y | 0.013581 | 0.052879 | 0.00037274 | 0.036334 | 0.00037274 | west | N | 0.00037274 | 0
71057 | L_SWEETW | W1 | 135 | 0.029465 | west | Y | 0.013581 | 0.052879 | 0.00037274 | 0.036334 | 0.00037274 | west | N | 0.00037274 | 0
71059 | L_SWEETW | W1 | 119 | 0.029465 | west | Y | 0.013581 | 0.052879 | 0.00037274 | 0.036334 | 0.00037274 | west | N | 0.00037274 | 0
71060 | L_SWEETW | W1 | 105 | 0.029465 | west | Y | 0.013581 | 0.052879 | 0.00037274 | 0.036334 | 0.00037274 | west | N | 0.00037274 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.029465 | west | Y | 0.013581 | 0.052879 | 0.00037274 | 0.036334 | 0.00037274 | west | N | 0.00037274 | 0
76031 | L_GASCCR | W1 | 150 | 0.031082 | west | Y | 0.015198 | 0.054496 | 0.0019897 | 0.037951 | 0.0019897 | west | N | 0.0019897 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.031384 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.031384 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
76096 | L_CAPRSI | W1 | 186 | 0.031384 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.031384 | west | Y | 0.0155 | 0.054798 | 0.0022917 | 0.038253 | 0.0022917 | west | N | 0.0022917 | 0
80003 | MILHWYS | F | 0 | -0.018941 | south | N | -0.034825 | 0.004473 | -0.048033 | -0.012072 | 0.004473 | south | N | 0.004473 | 0
80010 | EPLVT1 | F | 0 | -0.01136 | south | N | -0.027244 | 0.012054 | -0.040452 | -0.0044913 | 0.0044913 | houston | Y | 0.012054 | 0
80012 | LAR | F | 0 | -0.019497 | south | N | -0.035381 | 0.003917 | -0.048589 | -0.012628 | 0.003917 | south | N | 0.003917 | 0
80051 | FORPVCM0 | 8 | 28 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
80053 | FOR69CG0 | 10 | 74 | -0.017341 | south | N | -0.033225 | 0.006073 | -0.046433 | -0.010472 | 0.006073 | south | N | 0.006073 | 0
80080 | GWINDT11 | 1 | 94 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80080 | GWINDT11 | 2 | 41 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80080 | GWINDT11 | 3 | 38 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80080 | GWINDT11 | 4 | 19 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 1 | 94 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 2 | 36 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 3 | 43 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80081 | GWINDT21 | 4 | 22 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80137 | CSDR89 | 8 | 39 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80137 | CSDR89 | 9 | 15 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80138 | CSDR7 | 7 | 7 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80139 | CSDR56 | 5 | 15 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80139 | CSDR56 | 6 | 39 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80140 | CSDR11 | 11 | 39 | -0.017927 | south | N | -0.033811 | 0.005487 | -0.047019 | -0.011058 | 0.005487 | south | N | 0.005487 | 0
80180 | PNSCALT1 | 1 | 148 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80180 | PNSCALT1 | 2 | 50 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80181 | PNSCALT2 | 1 | 55 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80181 | PNSCALT2 | 2 | 50 | -0.018934 | south | Y | -0.034818 | 0.00448 | -0.048026 | -0.012065 | 0.00448 | south | N | 0.00448 | 0
80223 | REYSHR G | 1 | 12 | -0.018584 | south | N | -0.034468 | 0.00483 | -0.047676 | -0.011715 | 0.00483 | south | N | 0.00483 | 0
80224 | VISTRONG | 1 | 15 | -0.018117 | south | N | -0.034001 | 0.005297 | -0.047209 | -0.011248 | 0.005297 | south | N | 0.005297 | 0
80225 | VISTRONG | 2 | 23 | -0.018117 | south | N | -0.034001 | 0.005297 | -0.047209 | -0.011248 | 0.005297 | south | N | 0.005297 | 0
80226 | ALCOA G | 1 | 48 | -0.017479 | south | N | -0.033363 | 0.005935 | -0.046571 | -0.01061 | 0.005935 | south | N | 0.005935 | 0
80227 | AIRCO G | 1 | 8 | -0.017999 | south | N | -0.033883 | 0.005415 | -0.047091 | -0.01113 | 0.005415 | south | N | 0.005415 | 0
80261 | NBEC81A | 1 | 180 | -0.018767 | south | Y | -0.034651 | 0.004647 | -0.047859 | -0.011898 | 0.004647 | south | N | 0.004647 | 0
80262 | NBEC91A | 1 | 180 | -0.018762 | south | Y | -0.034646 | 0.004652 | -0.047854 | -0.011893 | 0.004652 | south | N | 0.004652 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.018802 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.018802 | south | Y | -0.034686 | 0.004612 | -0.047894 | -0.011933 | 0.004612 | south | N | 0.004612 | 0
80265 | LARECU40 | 4 | 100 | -0.019499 | south | Y | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
80266 | LARECU50 | 5 | 100 | -0.019499 | south | Y | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
80291 | PAPALOTE | 1 | 25 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80291 | PAPALOTE | 2 | 25 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80291 | PAPALOTE | 3 | 25 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80291 | PAPALOTE | 4 | 16 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 5 | 25 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 6 | 25 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 7 | 25 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
80294 | PAPALOTE | 8 | 15 | -0.018655 | south | Y | -0.034539 | 0.004759 | -0.047747 | -0.011786 | 0.004759 | south | N | 0.004759 | 0
86104 | CID-138 | EQ | 0 | -0.019499 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
86105 | CID-230 | EQ | 500 | -0.019499 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
86106 | CUF-230 | EQ | 500 | -0.019499 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
86107 | CUF-138 | EQ | 0 | -0.019499 | south | N | -0.035383 | 0.003915 | -0.048591 | -0.01263 | 0.003915 | south | N | 0.003915 | 0
88198 | BEEVILLE | F | 0 | -0.019709 | south | N | -0.035593 | 0.003705 | -0.048801 | -0.01284 | 0.003705 | south | N | 0.003705 | 0
88253 | HAMILTON | F | 0 | -0.006231 | south | N | -0.022115 | 0.017183 | -0.035323 | 0.00063768 | 0.00063768 | houston | Y | 0.017183 | 0
88299 | ZAPATA | F | 0 | -0.019162 | south | N | -0.035046 | 0.004252 | -0.048254 | -0.012293 | 0.004252 | south | N | 0.004252 | 0
88508 | FALFURRI | F | 0 | -0.019169 | south | N | -0.035053 | 0.004245 | -0.048261 | -0.0123 | 0.004245 | south | N | 0.004245 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Goldthwaite - Evant [7070 - 7068] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0 | Weighted Shift Factors
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0 | South | -0.023414
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0 | North | 0.01799
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0 |  | -0.041404
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023414 | 0 | 0 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.77954 | 0 | 0.018908 | 0 | 0 | 0 | Line Rating | 150
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.70294 | 0 | 0.018908 | 0 | 0 | 0 | Conc Gen | 286
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69392 | 0 | 0.018908 | 0 | 0 | 0 | Weighted Imp. | 5.2204
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69392 | 0 | 0.018908 | 0 | 0 | 0 | PTDF | 0.018253
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.004506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72997 | 0 | 0.018908 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222 | 56 | 1.0222 | Concentration | -0.44085
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3045 | 59 | 0.018253 | 1.0769 | 115 | 2.0991
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222 | 171 | 3.1213
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222 | 227 | 4.1434
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3045 | 59 | 0.018253 | 1.0769 | 286 | 5.2204
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.00523 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.0815 | 398 | 0.018184 | 7.2372
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85796 | 0 | 0.018144 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85058 | 0 | 0.018144 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8374 | 0 | 0.018144 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4187 | 0 | 0.018144 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.9257 | 172 | 0.018032 | 3.1015
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.9257 | 172 | 0.018032 | 3.1015
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.9257 | 172 | 0.018032 | 3.1015
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005399 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.84764 | 0 | 0.018015 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005429 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.0337 | 743 | 0.017985 | 13.3628
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.005433 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.065196 | 12 | 0.017981 | 0.21577
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35328 | 0 | 0.017979 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35871 | 0 | 0.017979 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38045 | 0 | 0.017979 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34241 | 0 | 0.017979 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33697 | 0 | 0.017979 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56524 | 0 | 0.017979 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32066 | 0 | 0.017979 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005437 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027185 | 0 | 0.017977 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005437 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11418 | 0 | 0.017977 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005495 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.06594 | 12 | 0.017919 | 0.21503
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18863 | 0 | 0.017866 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19252 | 0 | 0.017866 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18142 | 0 | 0.017866 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25465 | 0 | 0.017866 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0982 | 0 | 0.017866 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11318 | 0 | 0.017866 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11041 | 0 | 0.017866 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19418 | 0 | 0.017866 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.099864 | 0 | 0.017866 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4738 | 0 | 0.017866 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8211 | 0 | 0.017866 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.005587 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.1064 | 735 | 0.017827 | 13.1028
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58646 | 104 | 0.017775 | 1.8486
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58646 | 104 | 0.017775 | 1.8486
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.29887 | 53 | 0.017775 | 0.94207
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32142 | 57 | 0.017775 | 1.0132
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32706 | 58 | 0.017775 | 1.0309
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32706 | 58 | 0.017775 | 1.0309
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.005791 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0018 | 0 | 0.017623 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.005791 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.78178 | 0 | 0.017623 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24431 | 42 | 0.017597 | 0.73907
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24431 | 42 | 0.017597 | 0.73907
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22105 | 38 | 0.017597 | 0.66869
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22105 | 38 | 0.017597 | 0.66869
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.005823 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79193 | 0 | 0.017591 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42018 | 0 | 0.017496 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4261 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2308 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17754 | 0 | 0.017496 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0757 | 0 | 0.017438 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.94779 | 0 | 0.017438 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.93823 | 0 | 0.017438 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.005978 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.363 | 228 | 0.017436 | 3.9754
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38266 | 0 | 0.017435 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37787 | 0 | 0.017435 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49387 | 0 | 0.017435 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44005 | 0 | 0.017435 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.00598 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096876 | 0 | 0.017434 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.005981 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.274 | 213 | 0.017433 | 3.7132
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89251 | 0 | 0.017424 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38995 | 0 | 0.017424 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.005992 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.98868 | 165 | 0.017422 | 2.8746
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.005996 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0133 | 169 | 0.017418 | 2.9436
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005998 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.071976 | 12 | 0.017416 | 0.20899
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.005998 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.017416 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21136 | 0 | 0.017375 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.99242 | 0 | 0.017333 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95533 | 0 | 0.017333 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95776 | 0 | 0.017333 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95472 | 0 | 0.017333 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6358 | 0 | 0.017333 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.006127 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47791 | 0 | 0.017287 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.006127 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49016 | 0 | 0.017287 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28322 | 46 | 0.017257 | 0.79382
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28322 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28322 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33864 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33864 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33248 | 54 | 0.017257 | 0.93188
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.006231 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.20562 | 0 | 0.017183 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.006231 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15577 | 0 | 0.017183 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.006231 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.017183 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4095 | 0 | 0.017114 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.378 | 0 | 0.017114 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4095 | 0 | 0.017114 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4095 | 0 | 0.017114 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.58185 | 0 | 0.01702 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56011 | 0 | 0.01702 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55628 | 0 | 0.01702 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34847 | 0 | 0.01702 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078007 | 0 | 0.01702 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.034952 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0971 | 60 | 0.016962 | 1.0177
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.006633 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016781 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.00683 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3415 | 50 | 0.016584 | 0.8292
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50268 | 0 | 0.016314 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47357 | 0 | 0.016314 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3763 | 0 | 0.016314 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0877 | 0 | 0.016314 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0898 | 0 | 0.016314 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0813 | 0 | 0.016314 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.6816 | 0 | 0.016314 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7324 | 0 | 0.016314 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.284 | 0 | 0.016314 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007103 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2273 | 0 | 0.016311 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007103 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21309 | 0 | 0.016311 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.71243 | 0 | 0.016311 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.65987 | 0 | 0.016311 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72948 | 0 | 0.016311 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72451 | 0 | 0.016311 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2431 | 161 | 0.015693 | 2.5266
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2817 | 166 | 0.015693 | 2.605
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.9148 | 248 | 0.015693 | 3.8919
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.007721 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.2157 | 546 | 0.015693 | 8.5684
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.007721 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -4.9646 | 0 | 0.015693 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.007721 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10037 | 13 | 0.015693 | 0.20401
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.007799 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25737 | 0 | 0.015615 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2901 | 0 | 0.015499 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2901 | 0 | 0.015499 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9392 | 0 | 0.015499 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.1592 | 651 | 0.015489 | 10.0833
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.4697 | 564 | 0.015489 | 8.7358
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.755 | 600 | 0.015489 | 9.2934
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.007981 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36792 | 0 | 0.015433 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0209 | 0 | 0.014217 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0209 | 0 | 0.014217 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0944 | 0 | 0.014217 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0071 | 0 | 0.014217 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.031906 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4081 | 169.5 | 0.013916 | 2.3588
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67784 | 0 | 0.013867 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09547 | 0 | 0.013867 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61895 | 0 | 0.013431 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71279 | 0 | 0.013431 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44923 | 0 | 0.013431 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0083 | 0 | 0.013431 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85854 | 0 | 0.013431 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8785 | 0 | 0.013431 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49915 | 0 | 0.013431 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17969 | 0 | 0.013431 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9384 | 0 | 0.013431 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69881 | 0 | 0.013431 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62893 | 0 | 0.013431 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71878 | 0 | 0.013431 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6469 | 0 | 0.013431 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0083 | 0 | 0.013431 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.96835 | 0 | 0.013431 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0282 | 0 | 0.013431 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75871 | 0 | 0.013431 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79864 | 0 | 0.013431 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79864 | 0 | 0.013431 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7071 | 0 | 0.013431 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5307 | 112.5 | 0.013394 | 1.5069
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6919 | 149.5 | 0.013394 | 2.0024
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8374 | 186 | 0.013394 | 2.4913
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7319 | 214.5 | 0.013394 | 2.8731
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7565 | 120 | 0.013314 | 1.5977
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2938 | 233 | 0.013314 | 3.1022
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3279 | 170.2 | 0.013314 | 2.2661
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.031131 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20546 | 6.6 | 0.013141 | 0.086732
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.031131 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0678 | 34.3 | 0.013141 | 0.45074
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.031082 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6623 | 150 | 0.013092 | 1.9638
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.010392 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.062352 | 0 | 0.013022 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.030909 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6364 | 150 | 0.012919 | 1.9379
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.030909 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1218 | 101 | 0.012919 | 1.3048
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.030125 | west | 8 | N | N | Nwest | Nwest | 1 | 0.77723 | 0 | 0.012135 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.01136 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012054 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.029789 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5747 | 120 | 0.011799 | 1.4159
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.029782 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5738 | 120 | 0.011792 | 1.4151
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.029742 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4613 | 150 | 0.011752 | 1.7628
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.029741 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8737 | 63 | 0.011751 | 0.74033
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.029712 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4958 | 84 | 0.011722 | 0.98467
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.029705 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9408 | 99 | 0.011715 | 1.1598
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.029705 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.812 | 61 | 0.011715 | 0.71463
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 1 | 0.74262 | 0 | 0.011715 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3575 | 0 | 0.011715 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3575 | 0 | 0.011715 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.029704 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1883 | 141 | 0.011714 | 1.6517
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.029704 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5645 | 120 | 0.011714 | 1.4057
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.011731 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.77425 | 66 | 0.011683 | 0.77108
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9582 | 66 | 0.01168 | 0.7709
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0472 | 69 | 0.01168 | 0.80594
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0472 | 69 | 0.01168 | 0.80594
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9879 | 67 | 0.01168 | 0.78258
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9879 | 67 | 0.01168 | 0.78258
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9285 | 65 | 0.01168 | 0.75922
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029645 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3361 | 180 | 0.011655 | 2.0979
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029645 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3361 | 180 | 0.011655 | 2.0979
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.029635 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6679 | 225 | 0.011645 | 2.6202
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.029531 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9679 | 100.5 | 0.011541 | 1.1599
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4239 | 150 | 0.011503 | 1.7255
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4885 | 220 | 0.011503 | 2.5307
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8986 | 200 | 0.011503 | 2.3006
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5952 | 121.9 | 0.011503 | 1.4022
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.029492 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3172 | 214.2 | 0.011502 | 2.4638
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0629 | 0 | 0.01148 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1631 | 0 | 0.01148 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0747 | 0 | 0.01148 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1049 | 37.5 | 0.011475 | 0.43032
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1675 | 107.5 | 0.011475 | 1.2336
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9778 | 135 | 0.011475 | 1.5492
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5063 | 119 | 0.011475 | 1.3656
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0938 | 105 | 0.011475 | 1.2049
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3719 | 80.5 | 0.011475 | 0.92376
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.029463 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7089 | 58 | 0.011473 | 0.66545
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.029366 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.762 | 60 | 0.011376 | 0.68257
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0531 | 70 | 0.01134 | 0.79382
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0531 | 70 | 0.01134 | 0.79382
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7218 | 92.8 | 0.01134 | 1.0524
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3464 | 80 | 0.01134 | 0.90722
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3464 | 80 | 0.01134 | 0.90722
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.3729 | 115 | 0.01134 | 1.3041
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.1061 | 208.2 | 0.011338 | 2.3606
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.1675 | 142.1 | 0.011338 | 1.6112
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.883 | 132.4 | 0.011338 | 1.5012
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9886 | 136 | 0.011338 | 1.542
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3112 | 147 | 0.011338 | 1.6667
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.1589 | 210 | 0.011338 | 2.381
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029321 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6651 | 125 | 0.011331 | 1.4164
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029321 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6651 | 125 | 0.011331 | 1.4164
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.029189 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3492 | 149 | 0.011199 | 1.6687
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93024 | 76 | 0.011174 | 0.84922
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93024 | 76 | 0.011174 | 0.84922
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2852 | 105 | 0.011174 | 1.1733
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.90576 | 74 | 0.011174 | 0.82688
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.90576 | 74 | 0.011174 | 0.82688
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2485 | 102 | 0.011174 | 1.1397
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.029132 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0196 | 35 | 0.011142 | 0.38998
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.029132 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.87396 | 30 | 0.011142 | 0.33427
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9215 | 66 | 0.011123 | 0.73413
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8923 | 65 | 0.011123 | 0.72301
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9506 | 67 | 0.011123 | 0.74526
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9506 | 67 | 0.011123 | 0.74526
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9506 | 67 | 0.011123 | 0.74526
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.029113 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.029113 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.012395 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.5225 | 0 | 0.011019 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.012395 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.4606 | 0 | 0.011019 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0453 | 209 | 0.010935 | 2.2855
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.659 | 126.5 | 0.010935 | 1.3833
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2023 | 249 | 0.010935 | 2.7229
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6982 | 197 | 0.010935 | 2.1542
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.028196 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.13534 | 0 | 0.010206 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027845 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2276 | 80 | 0.0098552 | 0.78842
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027845 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2276 | 80 | 0.0098552 | 0.78842
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0791 | 75 | 0.0097322 | 0.72992
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2178 | 80 | 0.0097322 | 0.77858
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1089 | 40 | 0.0097322 | 0.38929
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.027701 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0804 | 400 | 0.0097112 | 3.8845
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.027695 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.536 | 236 | 0.0097052 | 2.2904
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027691 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2153 | 80 | 0.0097012 | 0.7761
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.027688 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.215 | 80 | 0.0096982 | 0.77586
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.027675 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1513 | 150 | 0.0096852 | 1.4528
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.027675 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1513 | 150 | 0.0096852 | 1.4528
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.027659 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0191 | 73 | 0.0096692 | 0.70585
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.027659 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.2914 | 119 | 0.0096692 | 1.1506
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.027659 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.6701 | 205 | 0.0096692 | 1.9822
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.027659 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8212 | 102 | 0.0096692 | 0.98626
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.027659 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.6553 | 96 | 0.0096692 | 0.92825
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.027097 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0729 | 76.5 | 0.0091072 | 0.6967
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027092 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1674 | 80 | 0.0091022 | 0.72818
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.027008 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4563 | 165 | 0.0090182 | 1.488
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.026895 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2592 | 84 | 0.0089052 | 0.74804
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026619 | west | 4 | Y | N | Ywest | Nwest | 1 | 17.2944 | 649.7 | 0.0086292 | 5.6064
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.02621 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.3428 | 242 | 0.0082202 | 1.9893
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.025706 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.0847 | 120 | 0.0077162 | 0.92595
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.025472 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.30566 | 0 | 0.0074822 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.025472 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.30566 | 0 | 0.0074822 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49824 | 20 | 0.0069222 | 0.13844
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49824 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49824 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4235 | 17 | 0.0069222 | 0.11768
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.024832 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.0885 | 366 | 0.0068422 | 2.5043
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.024769 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.6577 | 0 | 0.0067792 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.024769 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.6825 | 0 | 0.0067792 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43555 | 18 | 0.0062072 | 0.11173
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43555 | 18 | 0.0062072 | 0.11173
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.91949 | 38 | 0.0062072 | 0.23587
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3699 | 0 | 0.006073 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4046 | 0 | 0.006073 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3699 | 0 | 0.006073 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3873 | 0 | 0.006073 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3595 | 0 | 0.006073 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.43352 | 0 | 0.006073 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.79769 | 0 | 0.006073 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48555 | 0 | 0.006073 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.75607 | 0 | 0.006073 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2832 | 0 | 0.006073 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.2254 | 217.3 | 0.0060572 | 1.3162
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9296 | 205 | 0.0060572 | 1.2417
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5504 | 272.4 | 0.0060572 | 1.65
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.017479 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.83899 | 0 | 0.005935 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6725 | 70 | 0.0059032 | 0.41323
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6486 | 69 | 0.0059032 | 0.40732
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6486 | 69 | 0.0059032 | 0.40732
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6247 | 68 | 0.0059032 | 0.40142
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.023714 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0057242 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50196 | 0 | 0.005487 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12549 | 0 | 0.005487 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69915 | 0 | 0.005487 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26891 | 0 | 0.005487 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12549 | 0 | 0.005487 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26891 | 0 | 0.005487 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69915 | 0 | 0.005487 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69915 | 0 | 0.005487 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14399 | 0 | 0.005415 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.018117 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27176 | 0 | 0.005297 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.018117 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.41669 | 0 | 0.005297 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.018251 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.40152 | 22 | 0.005163 | 0.11359
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018251 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20076 | 11 | 0.005163 | 0.056793
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018251 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20076 | 11 | 0.005163 | 0.056793
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6934 | 204 | 0.0050172 | 1.0235
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6244 | 201 | 0.0050172 | 1.0085
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5677 | 242 | 0.0050172 | 1.2142
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.87835 | 47.7 | 0.005 | 0.2385
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.68684 | 37.3 | 0.005 | 0.1865
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.84704 | 46 | 0.005 | 0.23
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.88387 | 48 | 0.005 | 0.24
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.022982 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0049922 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.018442 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3463 | 0 | 0.004972 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.9363 | 0 | 0.00483 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8434 | 0 | 0.00483 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8584 | 0 | 0.00483 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.6947 | 0 | 0.00483 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7318 | 0 | 0.00483 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.3602 | 0 | 0.00483 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018584 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.22301 | 0 | 0.00483 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.01863 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6827 | 144 | 0.004784 | 0.68889
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.01863 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5024 | 188 | 0.004784 | 0.89939
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 25 | 0.004759 | 0.11897
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 25 | 0.004759 | 0.11897
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 25 | 0.004759 | 0.11897
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.29848 | 16 | 0.004759 | 0.076144
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 25 | 0.004759 | 0.11897
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 25 | 0.004759 | 0.11897
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 25 | 0.004759 | 0.11897
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.27982 | 15 | 0.004759 | 0.071385
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018762 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.304 | 336 | 0.004652 | 1.5631
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018762 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3772 | 180 | 0.004652 | 0.83736
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7827 | 0 | 0.00465 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7883 | 0 | 0.00465 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8709 | 0 | 0.00465 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3781 | 180 | 0.004647 | 0.83646
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5102 | 288 | 0.0046152 | 1.3292
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3229 | 147 | 0.0046152 | 0.67844
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3229 | 147 | 0.0046152 | 0.67844
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018802 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.2799 | 334 | 0.004612 | 1.5404
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018802 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3927 | 340 | 0.004612 | 1.5681
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3844 | 180 | 0.004612 | 0.83016
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3844 | 180 | 0.004612 | 0.83016
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.018806 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47015 | 0 | 0.004608 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.018806 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47015 | 0 | 0.004608 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.018823 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71527 | 0 | 0.004591 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.018825 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71535 | 0 | 0.004589 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.018908 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54833 | 0 | 0.004506 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7798 | 94 | 0.00448 | 0.42112
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77629 | 41 | 0.00448 | 0.18368
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.71949 | 38 | 0.00448 | 0.17024
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.35975 | 19 | 0.00448 | 0.08512
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7798 | 94 | 0.00448 | 0.42112
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.68162 | 36 | 0.00448 | 0.16128
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.81416 | 43 | 0.00448 | 0.19264
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41655 | 22 | 0.00448 | 0.09856
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8022 | 148 | 0.00448 | 0.66304
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9467 | 50 | 0.00448 | 0.224
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0414 | 55 | 0.00448 | 0.2464
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9467 | 50 | 0.00448 | 0.224
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.018941 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004473 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.71976 | 38 | 0.004473 | 0.16997
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.36556 | 19.3 | 0.004473 | 0.086329
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.28412 | 15 | 0.004473 | 0.067095
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.018941 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.89023 | 47 | 0.004473 | 0.21023
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7305 | 144 | 0.004452 | 0.64109
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7305 | 144 | 0.004452 | 0.64109
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2425 | 171 | 0.004452 | 0.76129
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9253 | 207 | 0.004451 | 0.92136
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1093 | 216.7 | 0.004451 | 0.96453
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.589 | 242 | 0.004451 | 1.0771
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7801 | 146.5 | 0.004437 | 0.65002
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8067 | 147.9 | 0.004437 | 0.65623
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.283 | 173 | 0.004437 | 0.7676
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22886 | 0 | 0.004342 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.20979 | 0 | 0.004342 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22886 | 0 | 0.004342 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.019162 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004252 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.019169 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004245 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.019497 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003917 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.019499 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9499 | 100 | 0.003915 | 0.3915
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.019499 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9499 | 100 | 0.003915 | 0.3915
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.019515 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.2749 | 629 | 0.003899 | 2.4525
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.019538 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.46891 | 24 | 0.003876 | 0.093024
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.019538 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.46891 | 24 | 0.003876 | 0.093024
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.019538 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.44937 | 23 | 0.003876 | 0.089148
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.019709 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003705 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.021365 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5893 | 168 | 0.0033752 | 0.56704
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.021365 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9228 | 90 | 0.0033752 | 0.30377
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.021033 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.3662 | 112.5 | 0.0030432 | 0.34236
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.020811 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.020811 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.020811 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.021106 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.358 | 396 | 0.002308 | 0.91396
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.020092 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0138 | 150 | 0.0021022 | 0.31533
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.019746 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1848 | 60 | 0.0017562 | 0.10537
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.019746 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.244 | 63 | 0.0017562 | 0.11064
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019605 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.744 | 395 | 0.0016152 | 0.63802
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019605 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.5282 | 435 | 0.0016152 | 0.70263
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.021919 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26303 | 0 | 0.001495 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019429 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.4516 | 435 | 0.0014392 | 0.62607
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.022543 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7611 | 433 | 0.00087099 | 0.37714
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.022554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.1715 | 584 | 0.00085999 | 0.50223
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.022554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.4196 | 595 | 0.00085999 | 0.51169
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.02259 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.3341 | 546 | 0.00082399 | 0.4499
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.02259 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.9425 | 750 | 0.00082399 | 0.61799
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.022771 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3207 | 58 | 0.00064299 | 0.037293
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.022771 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0266 | 89 | 0.00064299 | 0.057226
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0019 | 44 | 0.00064299 | 0.028292
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0019 | 44 | 0.00064299 | 0.028292
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97915 | 43 | 0.00064299 | 0.027649
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0247 | 45 | 0.00064299 | 0.028935
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.022821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7696 | 209 | 0.00059299 | 0.12394
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.022821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9293 | 216 | 0.00059299 | 0.12809
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0498 | 46 | 0.00059299 | 0.027278
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0726 | 47 | 0.00059299 | 0.027871
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0498 | 46 | 0.00059299 | 0.027278
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0498 | 46 | 0.00059299 | 0.027278
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5387 | 155 | 0.00058399 | 0.090519
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8811 | 170 | 0.00058399 | 0.099279
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5387 | 155 | 0.00058399 | 0.090519
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.022862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.4191 | 412 | 0.00055199 | 0.22742
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.022862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1448 | 400 | 0.00055199 | 0.2208
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3617 | 147 | 0.00054499 | 0.080114
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1559 | 138 | 0.00054499 | 0.075209
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2017 | 140 | 0.00054499 | 0.076299
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3617 | 147 | 0.00054499 | 0.080114
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1622 | 182 | 0.00054499 | 0.099188
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5281 | 198 | 0.00054499 | 0.10791
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.022881 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.3126 | 407 | 0.00053299 | 0.21693
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.022898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7088 | 424 | 0.00051599 | 0.21878
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.022898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7317 | 425 | 0.00051599 | 0.2193
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1288 | 224 | 0.00044223 | 0.09906
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1656 | 226 | 0.00044223 | 0.099945
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9076 | 212 | 0.00044223 | 0.093753
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8892 | 211 | 0.00044223 | 0.093311
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.018288 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00029823 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.023346 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.05603 | 0 | 6.7991e-05 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.023346 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.05603 | 0 | 6.7991e-05 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.018035 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 4.5232e-05 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.018028 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72112 | 0 | 3.8232e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.018028 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72112 | 0 | 3.8232e-05 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3281 | 142 | -2.3009e-05 | -0.0032672
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3984 | 145 | -2.3009e-05 | -0.0033363
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.539 | 151 | -2.3009e-05 | -0.0034743
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7967 | 290 | -2.3009e-05 | -0.0066725
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.017905 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0438 | 170 | -8.4768e-05 | -0.014411
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.017905 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.3106 | 520 | -8.4768e-05 | -0.044079
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.017745 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.5656 | 370 | -0.00024477 | -0.090564
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4843 | 0 | -0.00024477 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.502 | 0 | -0.00024477 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.4832 | 0 | -0.00024477 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5375 | 0 | -0.00024477 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5553 | 0 | -0.00024477 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5009 | 0 | -0.00024477 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8301 | 160 | -0.00030177 | -0.048283
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7593 | 156 | -0.00030177 | -0.047076
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4668 | 196 | -0.00030177 | -0.059146
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7593 | 156 | -0.00030177 | -0.047076
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.777 | 157 | -0.00030177 | -0.047378
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5022 | 198 | -0.00030177 | -0.05975
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.023732 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.094928 | 0 | -0.00031801 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.324 | 0 | -0.00033677 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4052 | 0 | -0.00033677 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5605 | 0 | -0.00033677 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.8119 | 558 | -0.00040577 | -0.22642
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.1811 | 579 | -0.00040577 | -0.23494
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.2079 | 808 | -0.00040577 | -0.32786
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017545 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0703 | 118 | -0.00044477 | -0.052483
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017545 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0177 | 115 | -0.00044477 | -0.051148
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017545 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.755 | 556 | -0.00044477 | -0.24729
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.023864 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.5786 | 569 | -0.00045001 | -0.25605
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.023864 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.865 | 581 | -0.00045001 | -0.26146
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057442 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057442 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.067015 | 0 | -0.00052001 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3759 | 79 | -0.00057277 | -0.045249
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8462 | 106 | -0.00057277 | -0.060713
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5429 | 146 | -0.00057277 | -0.083624
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.017417 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3237 | 76 | -0.00057277 | -0.04353
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.017375 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.695 | 40 | -0.00061477 | -0.024591
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3805 | 223.9 | -0.00061701 | -0.13815
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.407 | 225 | -0.00061701 | -0.13883
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3974 | 224.6 | -0.00061701 | -0.13858
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4478 | 226.7 | -0.00061701 | -0.13988
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.34684 | 20 | -0.00064777 | -0.012955
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.43355 | 25 | -0.00064777 | -0.016194
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.71102 | 41 | -0.00064777 | -0.026558
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8124 | 158 | -0.00071501 | -0.11297
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8606 | 160 | -0.00071501 | -0.1144
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2226 | 175 | -0.00071501 | -0.12513
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017247 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074277 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017247 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074277 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.017212 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7247 | 216.4 | -0.00077777 | -0.16831
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.017212 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7195 | 216.1 | -0.00077777 | -0.16808
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.0172 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.6736 | 388 | -0.00078977 | -0.30643
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.0172 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.858 | 515 | -0.00078977 | -0.40673
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7262 | 161 | -0.0010568 | -0.17014
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.777 | 164 | -0.0010568 | -0.17331
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.777 | 164 | -0.0010568 | -0.17331
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0103 | 414 | -0.0010568 | -0.4375
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7431 | 162 | -0.0010568 | -0.1712
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7262 | 161 | -0.0010568 | -0.17014
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7601 | 163 | -0.0010568 | -0.17225
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9256 | 409 | -0.0010568 | -0.43222
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.016684 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2701 | 196 | -0.0013058 | -0.25593
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.016684 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8519 | 111 | -0.0013058 | -0.14494
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8291 | 152.5 | -0.001695 | -0.25849
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7538 | 149.5 | -0.001695 | -0.2534
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8404 | 232.6 | -0.001695 | -0.39426
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.118 | 785 | -0.0025528 | -2.0039
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.2724 | 795 | -0.0025528 | -2.0295
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.0409 | 780 | -0.0025528 | -1.9912
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9642 | 114 | -0.002588 | -0.29503
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7724 | 222 | -0.002588 | -0.57454
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7844 | 184 | -0.002588 | -0.47619
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8244 | 224 | -0.002588 | -0.57971
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9902 | 115 | -0.002588 | -0.29762
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.4498 | 132 | -0.002721 | -0.35917
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5021 | 134 | -0.002721 | -0.36462
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.4416 | 323 | -0.002721 | -0.87889
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2548 | 0 | -0.0027548 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9806 | 0 | -0.0027548 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2091 | 0 | -0.0027548 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.0788 | 0 | -0.0027548 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.015037 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.3683 | 224 | -0.0029528 | -0.66142
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.015035 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0029548 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.015018 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.7509 | 50 | -0.0029718 | -0.14859
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.014914 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7143 | 182 | -0.0030758 | -0.55979
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.014914 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.2184 | 484 | -0.0030758 | -1.4887
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.026781 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16069 | 0 | -0.003367 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.013339 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20009 | 0 | -0.0046508 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.013339 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20009 | 0 | -0.0046508 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9913 | 151.5 | -0.0048458 | -0.73413
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0018 | 152.3 | -0.0048458 | -0.73801
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3331 | 177.5 | -0.0048458 | -0.86012
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9715 | 150.7 | -0.0049078 | -0.7396
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9754 | 151 | -0.0049078 | -0.74107
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3207 | 177.4 | -0.0049078 | -0.87064
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.012642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7748 | 615 | -0.0053478 | -3.2889
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.012642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.4209 | 587 | -0.0053478 | -3.1391
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4251 | 49 | -0.005669 | -0.27778
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3378 | 46 | -0.005669 | -0.26077
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3378 | 46 | -0.005669 | -0.26077
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3669 | 47 | -0.005669 | -0.26644
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.029083 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4788 | 154 | -0.005669 | -0.87303
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.029083 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3043 | 148 | -0.005669 | -0.83901
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.396 | 48 | -0.005669 | -0.27211
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.396 | 48 | -0.005669 | -0.27211
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2231 | 42 | -0.005707 | -0.23969
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2813 | 44 | -0.005707 | -0.25111
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2813 | 44 | -0.005707 | -0.25111
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3687 | 47 | -0.005707 | -0.26823
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.029389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1106 | 310 | -0.005975 | -1.8523
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.029389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1377 | 413 | -0.005975 | -2.4677
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.011567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.735 | 150 | -0.0064228 | -0.96342
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.011567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.92536 | 80 | -0.0064228 | -0.51382
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.030156 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24125 | 0 | -0.006742 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.030156 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24125 | 0 | -0.006742 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.011234 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0067558 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.011234 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.8412 | 787 | -0.0067558 | -5.3168
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8486 | 255 | -0.0068188 | -1.7388
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011171 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6645 | 149 | -0.0068188 | -1.016
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011171 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7092 | 153 | -0.0068188 | -1.0433
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.00866 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.1618 | 827 | -0.0093298 | -7.7157
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.00866 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0925 | 819 | -0.0093298 | -7.6411
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.9525 | 855 | -0.011028 | -9.4287
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.9525 | 855 | -0.011028 | -9.4287
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0603 | 152.3 | -0.011028 | -1.6795
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0652 | 153 | -0.011028 | -1.6872
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006215 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006215 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.002836 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.3131 | 463 | -0.015154 | -7.0162
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002266 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.038522 | 17 | -0.015724 | -0.2673
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.00225 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.072 | 0 | -0.01574 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001961 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.094128 | 48 | -0.016029 | -0.76938
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001961 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.090206 | 46 | -0.016029 | -0.73732
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001961 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.20591 | 105 | -0.016029 | -1.683
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3861 | 0 | -0.016188 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3465 | 0 | -0.016188 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3861 | 0 | -0.016188 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2515 | 0 | -0.016359 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.25444 | 0 | -0.016359 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.25444 | 0 | -0.016359 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.61978 | 0 | -0.016359 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.01799 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.01799 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.056927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0247 | 0 | -0.033513 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.056927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0247 | 0 | -0.033513 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.064567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -27.2473 | 422 | -0.041153 | -17.3666
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.023952 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.041942 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.0655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.834 | 0 | -0.042086 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.0655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8995 | 0 | -0.042086 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.6002 | 100 | -0.043992 | -4.3992
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.077212 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0578 | 0 | -0.053798 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6198 | 0 | -0.066574 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6198 | 0 | -0.066574 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3498 | 0 | -0.066574 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Goldthwaite - Evant [7070 - 7068] C: DCKT Temple Pecan Crk - Tradinghouse Ses & Temple Sw - Lake Crk Ses 345kV [3412 - 3405] and [3414 - 3409] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6198 | 0 | -0.066574 | 0 | 0 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6198 | 0 | -0.066574 | 0 | 0 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.089988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3498 | 0 | -0.066574 | 0 | 0 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.077212 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0578 | 0 | -0.053798 | 0 | 0 | 0 | Weighted Shift Factors
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.6002 | 0 | -0.043992 | 0 | 0 | 0 | South | -0.023414
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.0655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.834 | 0 | -0.042086 | 0 | 0 | 0 | North | 0.01799
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.0655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8995 | 0 | -0.042086 | 0 |  |  |  | -0.041404
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.023952 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.041942 | 0 | 0 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.064567 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -27.2473 | 422 | -0.041153 | -17.3666 |  |  | Line Rating | 150
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.056927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0247 | 0 | -0.033513 | 0 |  |  | Conc Gen | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.056927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0247 | 0 | -0.033513 | 0 |  |  | Weighted Imp. | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.01799 | 0 |  |  | PTDF | #DIV/0!
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.01799 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2515 | 0 | -0.016359 | 0 |  |  | Concentration | #DIV/0!
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.25444 | 0 | -0.016359 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.25444 | 0 | -0.016359 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.001631 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.61978 | 0 | -0.016359 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3861 | 0 | -0.016188 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3465 | 0 | -0.016188 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.039602 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3861 | 0 | -0.016188 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.001961 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.094128 | 48 | -0.016029 | -0.76938
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.001961 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.090206 | 46 | -0.016029 | -0.73732
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.001961 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.20591 | 105 | -0.016029 | -1.683
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.00225 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.072 | 0 | -0.01574 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.002266 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.038522 | 17 | -0.015724 | -0.2673
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.002266 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.015724 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.002836 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.3131 | 0 | -0.015154 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006215 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006215 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.011775 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.9525 | 0 | -0.011028 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.9525 | 0 | -0.011028 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0603 | 0 | -0.011028 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.006962 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.0652 | 0 | -0.011028 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.00866 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.1618 | 0 | -0.0093298 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.00866 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0925 | 0 | -0.0093298 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011171 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8486 | 255 | -0.0068188 | -1.7388
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011171 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6645 | 149 | -0.0068188 | -1.016
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011171 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7092 | 153 | -0.0068188 | -1.0433
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.011234 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0067558 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.011234 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.8412 | 787 | -0.0067558 | -5.3168
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.030156 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24125 | 0 | -0.006742 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.030156 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.24125 | 0 | -0.006742 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.011567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.735 | 150 | -0.0064228 | -0.96342
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.011567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.92536 | 80 | -0.0064228 | -0.51382
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.029389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1106 | 310 | -0.005975 | -1.8523
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.029389 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1377 | 413 | -0.005975 | -2.4677
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2231 | 42 | -0.005707 | -0.23969
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2813 | 44 | -0.005707 | -0.25111
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2813 | 44 | -0.005707 | -0.25111
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.029121 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3687 | 47 | -0.005707 | -0.26823
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4251 | 49 | -0.005669 | -0.27778
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3378 | 46 | -0.005669 | -0.26077
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3378 | 46 | -0.005669 | -0.26077
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.3669 | 47 | -0.005669 | -0.26644
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.029083 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.4788 | 154 | -0.005669 | -0.87303
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.029083 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.3043 | 148 | -0.005669 | -0.83901
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.396 | 48 | -0.005669 | -0.27211
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.029083 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.396 | 48 | -0.005669 | -0.27211
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.012642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.7748 | 0 | -0.0053478 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.012642 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.4209 | 0 | -0.0053478 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9715 | 150.7 | -0.0049078 | -0.7396
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9754 | 151 | -0.0049078 | -0.74107
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.013082 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3207 | 177.4 | -0.0049078 | -0.87064
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9913 | 151.5 | -0.0048458 | -0.73413
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0018 | 152.3 | -0.0048458 | -0.73801
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.013144 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3331 | 177.5 | -0.0048458 | -0.86012
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.013339 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20009 | 0 | -0.0046508 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.013339 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.20009 | 0 | -0.0046508 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.026781 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.16069 | 0 | -0.003367 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.014914 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7143 | 182 | -0.0030758 | -0.55979
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.014914 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.2184 | 484 | -0.0030758 | -1.4887
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.015018 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.7509 | 0 | -0.0029718 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.015035 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0029548 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.015037 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.3683 | 224 | -0.0029528 | -0.66142
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2548 | 0 | -0.0027548 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.9806 | 0 | -0.0027548 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2091 | 0 | -0.0027548 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.015235 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.0788 | 0 | -0.0027548 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.4498 | 132 | -0.002721 | -0.35917
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.5021 | 134 | -0.002721 | -0.36462
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026135 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.4416 | 323 | -0.002721 | -0.87889
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9642 | 0 | -0.002588 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7724 | 0 | -0.002588 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7844 | 0 | -0.002588 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8244 | 0 | -0.002588 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.026002 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9902 | 0 | -0.002588 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.118 | 0 | -0.0025528 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.2724 | 0 | -0.0025528 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.015437 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.0409 | 0 | -0.0025528 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8291 | 152.5 | -0.001695 | -0.25849
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.7538 | 149.5 | -0.001695 | -0.2534
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.025109 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8404 | 232.6 | -0.001695 | -0.39426
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.016684 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2701 | 196 | -0.0013058 | -0.25593
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.016684 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8519 | 111 | -0.0013058 | -0.14494
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7262 | 161 | -0.0010568 | -0.17014
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.777 | 164 | -0.0010568 | -0.17331
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.777 | 164 | -0.0010568 | -0.17331
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0103 | 414 | -0.0010568 | -0.4375
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7431 | 162 | -0.0010568 | -0.1712
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7262 | 161 | -0.0010568 | -0.17014
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7601 | 163 | -0.0010568 | -0.17225
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.016933 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.9256 | 409 | -0.0010568 | -0.43222
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.0172 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.6736 | 388 | -0.00078977 | -0.30643
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.0172 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.858 | 515 | -0.00078977 | -0.40673
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.017212 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7247 | 216.4 | -0.00077777 | -0.16831
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.017212 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7195 | 216.1 | -0.00077777 | -0.16808
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017247 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074277 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017247 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.00074277 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8124 | 158 | -0.00071501 | -0.11297
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8606 | 160 | -0.00071501 | -0.1144
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.024129 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.2226 | 175 | -0.00071501 | -0.12513
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.34684 | 20 | -0.00064777 | -0.012955
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.43355 | 25 | -0.00064777 | -0.016194
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.017342 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.71102 | 41 | -0.00064777 | -0.026558
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3805 | 223.9 | -0.00061701 | -0.13815
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.407 | 225 | -0.00061701 | -0.13883
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.3974 | 224.6 | -0.00061701 | -0.13858
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.024031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.4478 | 226.7 | -0.00061701 | -0.13988
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.017375 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.695 | 40 | -0.00061477 | -0.024591
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3759 | 79 | -0.00057277 | -0.045249
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8462 | 106 | -0.00057277 | -0.060713
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.017417 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.5429 | 146 | -0.00057277 | -0.083624
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.017417 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.3237 | 76 | -0.00057277 | -0.04353
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057442 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.057442 | 0 | -0.00052001 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.023934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.067015 | 0 | -0.00052001 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.023864 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.5786 | 0 | -0.00045001 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.023864 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.865 | 0 | -0.00045001 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017545 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0703 | 118 | -0.00044477 | -0.052483
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017545 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0177 | 115 | -0.00044477 | -0.051148
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017545 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.755 | 556 | -0.00044477 | -0.24729
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.8119 | 0 | -0.00040577 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.1811 | 0 | -0.00040577 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.017584 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.2079 | 0 | -0.00040577 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.324 | 0 | -0.00033677 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4052 | 0 | -0.00033677 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.017653 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5605 | 0 | -0.00033677 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.023732 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.094928 | 0 | -0.00031801 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8301 | 160 | -0.00030177 | -0.048283
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7593 | 156 | -0.00030177 | -0.047076
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4668 | 196 | -0.00030177 | -0.059146
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7593 | 156 | -0.00030177 | -0.047076
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.777 | 157 | -0.00030177 | -0.047378
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.017688 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5022 | 198 | -0.00030177 | -0.05975
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.017745 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 6.5656 | 370 | -0.00024477 | -0.090564
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4843 | 0 | -0.00024477 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.502 | 0 | -0.00024477 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.4832 | 0 | -0.00024477 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5375 | 0 | -0.00024477 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5553 | 0 | -0.00024477 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.017745 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5009 | 0 | -0.00024477 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.023603 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.1802 | 50 | -0.00018901 | -0.0094504
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.017905 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0438 | 170 | -8.4768e-05 | -0.014411
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.017905 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.3106 | 520 | -8.4768e-05 | -0.044079
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3281 | 142 | -2.3009e-05 | -0.0032672
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3984 | 145 | -2.3009e-05 | -0.0033363
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.539 | 151 | -2.3009e-05 | -0.0034743
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.023437 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.7967 | 290 | -2.3009e-05 | -0.0066725
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.018028 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72112 | 0 | 3.8232e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.018028 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72112 | 0 | 3.8232e-05 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.018035 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 4.5232e-05 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.023346 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.05603 | 0 | 6.7991e-05 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.023346 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.05603 | 0 | 6.7991e-05 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.018288 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00029823 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1288 | 224 | 0.00044223 | 0.09906
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1656 | 226 | 0.00044223 | 0.099945
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9076 | 212 | 0.00044223 | 0.093753
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.018432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8892 | 211 | 0.00044223 | 0.093311
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.022898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7088 | 0 | 0.00051599 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.022898 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7317 | 0 | 0.00051599 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.022881 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.3126 | 407 | 0.00053299 | 0.21693
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.02287 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.00054399 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3617 | 147 | 0.00054499 | 0.080114
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.1559 | 138 | 0.00054499 | 0.075209
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2017 | 140 | 0.00054499 | 0.076299
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3617 | 147 | 0.00054499 | 0.080114
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1622 | 182 | 0.00054499 | 0.099188
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.022869 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.5281 | 198 | 0.00054499 | 0.10791
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.022862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.4191 | 412 | 0.00055199 | 0.22742
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.022862 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.1448 | 400 | 0.00055199 | 0.2208
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5387 | 155 | 0.00058399 | 0.090519
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.8811 | 170 | 0.00058399 | 0.099279
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.02283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5387 | 155 | 0.00058399 | 0.090519
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.022821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.7696 | 209 | 0.00059299 | 0.12394
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.022821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9293 | 216 | 0.00059299 | 0.12809
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0498 | 46 | 0.00059299 | 0.027278
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0726 | 47 | 0.00059299 | 0.027871
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0498 | 46 | 0.00059299 | 0.027278
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.022821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0498 | 46 | 0.00059299 | 0.027278
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.022771 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.3207 | 58 | 0.00064299 | 0.037293
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.022771 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0266 | 89 | 0.00064299 | 0.057226
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0019 | 44 | 0.00064299 | 0.028292
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0019 | 44 | 0.00064299 | 0.028292
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.97915 | 43 | 0.00064299 | 0.027649
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.022771 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.0247 | 45 | 0.00064299 | 0.028935
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.02259 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.3341 | 0 | 0.00082399 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.02259 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.9425 | 0 | 0.00082399 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.022554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.1715 | 0 | 0.00085999 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.022554 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -13.4196 | 0 | 0.00085999 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.022543 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -9.7611 | 0 | 0.00087099 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019429 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.4516 | 435 | 0.0014392 | 0.62607
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.021919 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.26303 | 0 | 0.001495 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019605 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.744 | 395 | 0.0016152 | 0.63802
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019605 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.5282 | 435 | 0.0016152 | 0.70263
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.019746 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1848 | 60 | 0.0017562 | 0.10537
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.019746 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.244 | 63 | 0.0017562 | 0.11064
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.020092 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0138 | 0 | 0.0021022 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.021106 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -8.358 | 0 | 0.002308 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.020811 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.020811 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.020811 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028212 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.021033 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.3662 | 0 | 0.0030432 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.021365 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5893 | 168 | 0.0033752 | 0.56704
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.021365 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9228 | 90 | 0.0033752 | 0.30377
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.019709 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003705 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.019538 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.46891 | 24 | 0.003876 | 0.093024
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.019538 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.46891 | 24 | 0.003876 | 0.093024
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.019538 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.44937 | 23 | 0.003876 | 0.089148
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.019515 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.2749 | 0 | 0.003899 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.019499 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9499 | 100 | 0.003915 | 0.3915
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.019499 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.9499 | 100 | 0.003915 | 0.3915
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.019499 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003915 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.019497 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.003917 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.019191 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.1612 | 8.4 | 0.004223 | 0.035473
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.019169 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004245 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.019162 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004252 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22886 | 0 | 0.004342 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.20979 | 0 | 0.004342 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.019072 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22886 | 0 | 0.004342 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7801 | 146.5 | 0.004437 | 0.65002
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8067 | 147.9 | 0.004437 | 0.65623
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.018977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.283 | 173 | 0.004437 | 0.7676
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.9253 | 207 | 0.004451 | 0.92136
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.1093 | 216.7 | 0.004451 | 0.96453
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.018963 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.589 | 242 | 0.004451 | 1.0771
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7305 | 144 | 0.004452 | 0.64109
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7305 | 144 | 0.004452 | 0.64109
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.018962 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.2425 | 171 | 0.004452 | 0.76129
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.71976 | 38 | 0.004473 | 0.16997
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.36556 | 19.3 | 0.004473 | 0.086329
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.018941 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.28412 | 15 | 0.004473 | 0.067095
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.018941 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.89023 | 47 | 0.004473 | 0.21023
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.018941 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.004473 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7798 | 0 | 0.00448 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.77629 | 0 | 0.00448 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.71949 | 0 | 0.00448 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.35975 | 0 | 0.00448 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.7798 | 0 | 0.00448 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.68162 | 0 | 0.00448 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.81416 | 0 | 0.00448 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.41655 | 0 | 0.00448 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8022 | 0 | 0.00448 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9467 | 0 | 0.00448 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0414 | 0 | 0.00448 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.018934 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.9467 | 0 | 0.00448 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.018908 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.54833 | 0 | 0.004506 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.018825 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71535 | 0 | 0.004589 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.018823 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.71527 | 0 | 0.004591 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.018806 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47015 | 0 | 0.004608 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.018806 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.47015 | 0 | 0.004608 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018802 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.2799 | 334 | 0.004612 | 1.5404
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018802 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -6.3927 | 340 | 0.004612 | 1.5681
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3844 | 180 | 0.004612 | 0.83016
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018802 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3844 | 180 | 0.004612 | 0.83016
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5102 | 288 | 0.0046152 | 1.3292
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3229 | 147 | 0.0046152 | 0.67844
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.022605 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3229 | 147 | 0.0046152 | 0.67844
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3781 | 180 | 0.004647 | 0.83646
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7827 | 0 | 0.00465 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7883 | 0 | 0.00465 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018764 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8709 | 0 | 0.00465 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018762 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.304 | 336 | 0.004652 | 1.5631
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018762 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3772 | 180 | 0.004652 | 0.83736
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 0 | 0.004759 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 0 | 0.004759 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 0 | 0.004759 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.29848 | 0 | 0.004759 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 0 | 0.004759 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 0 | 0.004759 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46637 | 0 | 0.004759 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018655 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.27982 | 0 | 0.004759 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.01863 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6827 | 144 | 0.004784 | 0.68889
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.01863 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.5024 | 188 | 0.004784 | 0.89939
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.9363 | 0 | 0.00483 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.8434 | 0 | 0.00483 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -1.8584 | 0 | 0.00483 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.6947 | 0 | 0.00483 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.7318 | 0 | 0.00483 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018584 | south | 8 | N | N | Nsouth | Nsouth | -1 | -2.3602 | 0 | 0.00483 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018584 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.22301 | 0 | 0.00483 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.018442 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3463 | 0 | 0.004972 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.022982 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0049922 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.87835 | 47.7 | 0.005 | 0.2385
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.68684 | 37.3 | 0.005 | 0.1865
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.84704 | 46 | 0.005 | 0.23
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.018414 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.88387 | 48 | 0.005 | 0.24
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6934 | 204 | 0.0050172 | 1.0235
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6244 | 201 | 0.0050172 | 1.0085
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.023007 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.5677 | 242 | 0.0050172 | 1.2142
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.018251 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.40152 | 22 | 0.005163 | 0.11359
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018251 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20076 | 11 | 0.005163 | 0.056793
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.018251 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.20076 | 11 | 0.005163 | 0.056793
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.018117 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.27176 | 0 | 0.005297 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.018117 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.41669 | 0 | 0.005297 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.017999 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14399 | 0 | 0.005415 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.50196 | 0 | 0.005487 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12549 | 0 | 0.005487 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69915 | 0 | 0.005487 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26891 | 0 | 0.005487 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.12549 | 0 | 0.005487 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26891 | 0 | 0.005487 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69915 | 0 | 0.005487 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.017927 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.69915 | 0 | 0.005487 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.023714 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0057242 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6725 | 70 | 0.0059032 | 0.41323
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6486 | 69 | 0.0059032 | 0.40732
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6486 | 69 | 0.0059032 | 0.40732
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.023893 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6247 | 68 | 0.0059032 | 0.40142
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.017479 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.83899 | 0 | 0.005935 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.2254 | 217.3 | 0.0060572 | 1.3162
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9296 | 205 | 0.0060572 | 1.2417
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.024047 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.5504 | 272.4 | 0.0060572 | 1.65
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3699 | 0 | 0.006073 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4046 | 0 | 0.006073 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3699 | 0 | 0.006073 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3873 | 0 | 0.006073 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.3595 | 0 | 0.006073 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.43352 | 0 | 0.006073 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.79769 | 0 | 0.006073 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.48555 | 0 | 0.006073 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.75607 | 0 | 0.006073 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.017341 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.2832 | 0 | 0.006073 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43555 | 18 | 0.0062072 | 0.11173
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.43555 | 18 | 0.0062072 | 0.11173
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.024197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.91949 | 38 | 0.0062072 | 0.23587
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.024769 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.6577 | 0 | 0.0067792 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.024769 | north | 3 | N | N | Nnorth | Nnorth | 1 | 28.6825 | 0 | 0.0067792 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.024832 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.0885 | 366 | 0.0068422 | 2.5043
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49824 | 20 | 0.0069222 | 0.13844
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49824 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.49824 | 20 | 0.0069222 | 0.13844
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.024912 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4235 | 17 | 0.0069222 | 0.11768
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.025472 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.30566 | 0 | 0.0074822 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.025472 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.30566 | 0 | 0.0074822 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.025706 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.0847 | 0 | 0.0077162 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.02621 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.3428 | 242 | 0.0082202 | 1.9893
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.026619 | west | 4 | Y | N | Ywest | Nwest | 1 | 17.2944 | 0 | 0.0086292 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.026895 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2592 | 0 | 0.0089052 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.027008 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4563 | 0 | 0.0090182 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027092 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1674 | 0 | 0.0091022 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.027097 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0729 | 0 | 0.0091072 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.027659 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0191 | 73 | 0.0096692 | 0.70585
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.027659 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.2914 | 119 | 0.0096692 | 1.1506
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.027659 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.6701 | 205 | 0.0096692 | 1.9822
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.027659 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8212 | 102 | 0.0096692 | 0.98626
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.027659 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.6553 | 96 | 0.0096692 | 0.92825
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.027675 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1513 | 0 | 0.0096852 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.027675 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1513 | 0 | 0.0096852 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.027688 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.215 | 0 | 0.0096982 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027691 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2153 | 0 | 0.0097012 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.027695 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.536 | 0 | 0.0097052 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.027701 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.0804 | 0 | 0.0097112 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0791 | 0 | 0.0097322 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2178 | 0 | 0.0097322 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.027722 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1089 | 0 | 0.0097322 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027845 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2276 | 0 | 0.0098552 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.027845 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2276 | 0 | 0.0098552 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.028196 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.13534 | 0 | 0.010206 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0453 | 0 | 0.010935 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.659 | 0 | 0.010935 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2023 | 0 | 0.010935 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.028925 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6982 | 0 | 0.010935 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.012395 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.5225 | 0 | 0.011019 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.012395 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -16.4606 | 0 | 0.011019 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9215 | 66 | 0.011123 | 0.73413
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.8923 | 65 | 0.011123 | 0.72301
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9506 | 67 | 0.011123 | 0.74526
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9506 | 67 | 0.011123 | 0.74526
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.029113 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9506 | 67 | 0.011123 | 0.74526
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.029113 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.029113 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.011123 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.029132 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0196 | 0 | 0.011142 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.029132 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.87396 | 0 | 0.011142 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93024 | 76 | 0.011174 | 0.84922
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.93024 | 76 | 0.011174 | 0.84922
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2852 | 105 | 0.011174 | 1.1733
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.90576 | 74 | 0.011174 | 0.82688
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.90576 | 74 | 0.011174 | 0.82688
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.01224 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2485 | 102 | 0.011174 | 1.1397
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.029189 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3492 | 0 | 0.011199 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029321 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6651 | 0 | 0.011331 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.029321 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6651 | 0 | 0.011331 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.1061 | 208.2 | 0.011338 | 2.3606
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.1675 | 142.1 | 0.011338 | 1.6112
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.883 | 132.4 | 0.011338 | 1.5012
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.9886 | 136 | 0.011338 | 1.542
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3112 | 147 | 0.011338 | 1.6667
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.029328 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.1589 | 210 | 0.011338 | 2.381
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0531 | 70 | 0.01134 | 0.79382
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.0531 | 70 | 0.01134 | 0.79382
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.7218 | 92.8 | 0.01134 | 1.0524
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3464 | 80 | 0.01134 | 0.90722
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.3464 | 80 | 0.01134 | 0.90722
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.02933 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.3729 | 115 | 0.01134 | 1.3041
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.029366 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.762 | 0 | 0.011376 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.029463 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7089 | 0 | 0.011473 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1049 | 0 | 0.011475 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1675 | 0 | 0.011475 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9778 | 0 | 0.011475 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5063 | 0 | 0.011475 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0938 | 0 | 0.011475 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.029465 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3719 | 0 | 0.011475 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0629 | 0 | 0.01148 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1631 | 0 | 0.01148 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.02947 | west | 8 | N | N | Nwest | Nwest | 1 | 2.0747 | 0 | 0.01148 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.029492 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3172 | 0 | 0.011502 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4239 | 0 | 0.011503 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4885 | 0 | 0.011503 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8986 | 0 | 0.011503 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.029493 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5952 | 0 | 0.011503 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.029531 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9679 | 0 | 0.011541 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.029635 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6679 | 0 | 0.011645 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029645 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3361 | 0 | 0.011655 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.029645 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3361 | 0 | 0.011655 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9582 | 66 | 0.01168 | 0.7709
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0472 | 69 | 0.01168 | 0.80594
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0472 | 69 | 0.01168 | 0.80594
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9879 | 67 | 0.01168 | 0.78258
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9879 | 67 | 0.01168 | 0.78258
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.02967 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.9285 | 65 | 0.01168 | 0.75922
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.011731 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.77425 | 66 | 0.011683 | 0.77108
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.029704 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1883 | 0 | 0.011714 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.029704 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5645 | 0 | 0.011714 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.029705 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.9408 | 0 | 0.011715 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.029705 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.812 | 0 | 0.011715 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 1 | 0.74262 | 0 | 0.011715 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3575 | 0 | 0.011715 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.029705 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3575 | 0 | 0.011715 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.029712 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.4958 | 0 | 0.011722 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.029741 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8737 | 0 | 0.011751 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.029742 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4613 | 0 | 0.011752 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.029782 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5738 | 0 | 0.011792 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.029789 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5747 | 0 | 0.011799 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.01136 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.012054 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.030125 | west | 8 | N | N | Nwest | Nwest | 1 | 0.77723 | 0 | 0.012135 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.030909 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6364 | 0 | 0.012919 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.030909 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1218 | 0 | 0.012919 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.010392 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.062352 | 0 | 0.013022 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.031082 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6623 | 0 | 0.013092 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.031131 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20546 | 0 | 0.013141 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.031131 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0678 | 0 | 0.013141 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7565 | 0 | 0.013314 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2938 | 0 | 0.013314 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.031304 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3279 | 0 | 0.013314 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5307 | 0 | 0.013394 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.6919 | 0 | 0.013394 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8374 | 0 | 0.013394 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.031384 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7319 | 0 | 0.013394 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.61895 | 0 | 0.013431 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71279 | 0 | 0.013431 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44923 | 0 | 0.013431 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0083 | 0 | 0.013431 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85854 | 0 | 0.013431 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8785 | 0 | 0.013431 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49915 | 0 | 0.013431 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17969 | 0 | 0.013431 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.9384 | 0 | 0.013431 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69881 | 0 | 0.013431 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62893 | 0 | 0.013431 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71878 | 0 | 0.013431 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6469 | 0 | 0.013431 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0083 | 0 | 0.013431 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.96835 | 0 | 0.013431 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0282 | 0 | 0.013431 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.75871 | 0 | 0.013431 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79864 | 0 | 0.013431 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.79864 | 0 | 0.013431 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.009983 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7071 | 0 | 0.013431 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.009547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.67784 | 0 | 0.013867 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.009547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09547 | 0 | 0.013867 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.031906 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4081 | 0 | 0.013916 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0209 | 0 | 0.014217 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0209 | 0 | 0.014217 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0944 | 0 | 0.014217 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.009197 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0071 | 0 | 0.014217 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.007981 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.36792 | 0 | 0.015433 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -5.1592 | 0 | 0.015489 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.4697 | 0 | 0.015489 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.007925 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -4.755 | 0 | 0.015489 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2901 | 0 | 0.015499 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.2901 | 0 | 0.015499 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.007915 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9392 | 0 | 0.015499 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.007799 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25737 | 0 | 0.015615 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2431 | 161 | 0.015693 | 2.5266
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.2817 | 166 | 0.015693 | 2.605
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.007721 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.9148 | 248 | 0.015693 | 3.8919
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.007721 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.2157 | 546 | 0.015693 | 8.5684
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.007721 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -4.9646 | 0 | 0.015693 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.007721 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.10037 | 13 | 0.015693 | 0.20401
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.71243 | 0 | 0.016311 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.65987 | 0 | 0.016311 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72948 | 0 | 0.016311 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.007103 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.72451 | 0 | 0.016311 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.007103 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2273 | 0 | 0.016311 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.007103 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21309 | 0 | 0.016311 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.50268 | 0 | 0.016314 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47357 | 0 | 0.016314 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3763 | 0 | 0.016314 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0877 | 0 | 0.016314 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0898 | 0 | 0.016314 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0813 | 0 | 0.016314 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.6816 | 0 | 0.016314 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0071 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.7324 | 0 | 0.016314 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0071 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.284 | 0 | 0.016314 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.00683 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.3415 | 50 | 0.016584 | 0.8292
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.006633 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.016781 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.034952 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0971 | 0 | 0.016962 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.58185 | 0 | 0.01702 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56011 | 0 | 0.01702 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.55628 | 0 | 0.01702 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34847 | 0 | 0.01702 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.006394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.078007 | 0 | 0.01702 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4095 | 0 | 0.017114 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.378 | 0 | 0.017114 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4095 | 0 | 0.017114 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.0063 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4095 | 0 | 0.017114 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.006231 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.20562 | 0 | 0.017183 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.006231 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15577 | 0 | 0.017183 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.006231 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.017183 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28322 | 46 | 0.017257 | 0.79382
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28322 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28322 | 46 | 0.017257 | 0.79382
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33864 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33864 | 55 | 0.017257 | 0.94913
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.006157 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.33248 | 54 | 0.017257 | 0.93188
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.006127 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.47791 | 0 | 0.017287 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.006127 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49016 | 0 | 0.017287 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.99242 | 0 | 0.017333 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95533 | 0 | 0.017333 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95776 | 0 | 0.017333 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.95472 | 0 | 0.017333 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.006081 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.6358 | 0 | 0.017333 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.006039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21136 | 0 | 0.017375 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005998 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.071976 | 12 | 0.017416 | 0.20899
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.005998 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.017416 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.005996 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.0133 | 169 | 0.017418 | 2.9436
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.005992 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.98868 | 165 | 0.017422 | 2.8746
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89251 | 0 | 0.017424 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00599 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38995 | 0 | 0.017424 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.005981 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.274 | 213 | 0.017433 | 3.7132
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.00598 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096876 | 0 | 0.017434 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38266 | 0 | 0.017435 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37787 | 0 | 0.017435 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.49387 | 0 | 0.017435 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.005979 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.44005 | 0 | 0.017435 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.005978 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.363 | 228 | 0.017436 | 3.9754
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.0757 | 0 | 0.017438 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.94779 | 0 | 0.017438 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.005976 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.93823 | 0 | 0.017438 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42018 | 0 | 0.017496 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4261 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2308 | 0 | 0.017496 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.005918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17754 | 0 | 0.017496 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.005823 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79193 | 0 | 0.017591 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24431 | 42 | 0.017597 | 0.73907
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.24431 | 42 | 0.017597 | 0.73907
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22105 | 38 | 0.017597 | 0.66869
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.005817 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.22105 | 38 | 0.017597 | 0.66869
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.005791 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0018 | 0 | 0.017623 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.005791 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.78178 | 0 | 0.017623 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58646 | 104 | 0.017775 | 1.8486
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.58646 | 104 | 0.017775 | 1.8486
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.29887 | 53 | 0.017775 | 0.94207
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32142 | 57 | 0.017775 | 1.0132
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30451 | 54 | 0.017775 | 0.95985
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32706 | 58 | 0.017775 | 1.0309
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.005639 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.32706 | 58 | 0.017775 | 1.0309
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.005587 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.1064 | 735 | 0.017827 | 13.1028
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18863 | 0 | 0.017866 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19252 | 0 | 0.017866 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18142 | 0 | 0.017866 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25465 | 0 | 0.017866 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0982 | 0 | 0.017866 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11318 | 0 | 0.017866 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11041 | 0 | 0.017866 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19418 | 0 | 0.017866 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.099864 | 0 | 0.017866 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.4738 | 0 | 0.017866 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.005548 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8211 | 0 | 0.017866 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.005495 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.06594 | 12 | 0.017919 | 0.21503
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.005437 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027185 | 0 | 0.017977 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.005437 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11418 | 0 | 0.017977 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35328 | 0 | 0.017979 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.35871 | 0 | 0.017979 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38045 | 0 | 0.017979 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.34241 | 0 | 0.017979 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33697 | 0 | 0.017979 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.56524 | 0 | 0.017979 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.005435 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32066 | 0 | 0.017979 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.005433 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.065196 | 0 | 0.017981 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.005429 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -4.0337 | 743 | 0.017985 | 13.3628
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.005399 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.84764 | 0 | 0.018015 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.9257 | 172 | 0.018032 | 3.1015
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.9257 | 172 | 0.018032 | 3.1015
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.005382 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.9257 | 172 | 0.018032 | 3.1015
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85796 | 0 | 0.018144 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85058 | 0 | 0.018144 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8374 | 0 | 0.018144 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.00527 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4187 | 0 | 0.018144 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.00523 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -2.0815 | 398 | 0.018184 | 7.2372
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3045 | 59 | 0.018253 | 1.0769
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.3045 | 59 | 0.018253 | 1.0769
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.005161 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.28902 | 56 | 0.018253 | 1.0222
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.77954 | 0 | 0.018908 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.70294 | 0 | 0.018908 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69392 | 0 | 0.018908 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.004506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.69392 | 0 | 0.018908 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.004506 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72997 | 0 | 0.018908 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.023414 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023414 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023414 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown