## test results
CRE test for: |  | 3409 LAKE_CRK - 3414 TEMP_SS_ | [5 empty] | PASS
Line Rating: |  | 1239.6
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3409 LAKE_CRK - 3414 TEMP_SS_
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.12881
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.1789
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.11525
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.03822
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3409 LAKE_CRK - 3414 TEMP_SS_
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.13885
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.17557
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.11581
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.035514
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3409 LAKE_CRK - 3414 TEMP_SS_
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.30438
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.013002
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.16432
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.29471
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.14068
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.15076
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.31775 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.31775 | 0.30438
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.1547
[6 empty] | Concentration |  | -0.48687 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.047157
[6 empty] | Concentration |  | -0.14841 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 69.6293
| Percent of line rating => | [6 empty] | 5.617% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -1.324
[7 empty] | B1(N-S) | 0.0010754 | -0.40193 | -0.403 | 0.0010754
[7 empty] | B2 (N-W) | 0.00060049 | -0.016614 | -0.017214 | 0.00060049
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0015873 | -0.21915 | -0.21756 | -0.0015873
[7 empty] | B4 (S-W) | -0.00061403 | 0.38958 | 0.3902 | -0.00061403
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.00078058 | 0.18705 | 0.18627 | 0.00078058
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0021804 | -0.20179 | -0.19961 | -0.0021804
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | 0.2556%
Deployment Error Percent | [6 empty] | B2 | 0.1427%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -0.3773%
[7 empty] | B4 | -0.146%
[7 empty] | B5 | 0.1855%
[7 empty] | B6 | -0.5183%
[7 empty] | Max Abs Error | 0.5183% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | S-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.18349 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 46.7897
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.18349 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 27.3399
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.15659 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.3489
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.15659 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.3489
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.18349 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 28.0738
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.16155 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 24.2329
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.16155 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 12.9242
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13343 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 9.7406
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13343 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 15.8785
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13343 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 27.3538
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13343 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 13.6102
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.13343 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 12.8096
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13161 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.5793
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.13161 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.5793
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.14092 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 23.6744
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.14092 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 12.6827
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.4204
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.4204
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 5.1098
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 38.7046
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 19.7555
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 19.7555
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.13408 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 15.084
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.13363 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 5.3451
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 10.5548
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 14.1621
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 19.5063
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.13361 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 10.154
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13477 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 8.086
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.13477 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 8.4903
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.6691
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.3363
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 5.4716
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.05008 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 23.187
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 7.4681
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 7.3549
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.5813
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.5813
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.5813
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.11315 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 12.8994
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.11315 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 58.2738
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 7.7473
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.0995
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 8.0995
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.8647
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.8647
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 7.63
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 8.1745
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 8.5715
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 8.2212
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 17.568
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 25.7664
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 11.6449
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 7.1751
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.11759 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 16.5803
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 2.9406
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.3755
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 5.3755
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.11759 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 14.1109
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.11564 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 2.9836
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.11535 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 11.5928
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.11638 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 13.9656
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.11533 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 6.6892
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.11562 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 24.7654
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.11807 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 17.71
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.11392 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.75189
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.11392 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 3.9075
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.11807 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 11.9248
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.11643 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 13.9716
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.12934 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 47.3384
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.12882 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 31.1732
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.12331 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 49.324
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.12332 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 29.103
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 20.5859
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 27.0845
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 26.6862
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 32.1296
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.5895
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.5895
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.5895
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 2.2011
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.13148 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 15.7777
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.12842 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 7.7051
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 10.0201
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 10.6346
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 11.8103
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 21.3898
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 20.855
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 26.2025
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 20.855
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 20.9887
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 26.4698
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.13386 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 22.7555
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.13386 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 69.6051
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13377 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 49.4938
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 74.5293
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 77.3341
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 107.9205
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13616 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 15.2499
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13616 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 13.616
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.13616 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 51.4685
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 29.7073
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 28.0258
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 37.2401
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.13718 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 105.6271
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 9.6151
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 9.4778
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 9.4778
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 9.3404
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13617 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 157.5452
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.13617 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 157.6814
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 32.4025
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 32.6918
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 31.3477
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 31.3042
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 30.6666
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 30.522
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13881 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 54.8311
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.13858 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 60.2827
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.13881 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 60.3837
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.1345 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 18.5611
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13583 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 16.0278
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13583 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 15.6203
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.13583 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 75.5209
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.13363 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 51.8488
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.13363 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 68.82
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 100.9808
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 102.2672
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 100.3376
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.12683 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 23.0834
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.12683 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 61.3867
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.13152 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 29.4607
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.12742 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 6.3712
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.12746 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.3534
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12111 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 74.4827
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.12111 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 71.0916
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.2147 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 115.2928
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.2147 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 168.9673
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.18641 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 13.9807
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.18641 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 41.3828
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.2644 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -150.4453
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17095 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -35.7296
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17095 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -36.9263
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.17087 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -69.5461
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.8639
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -8.0349
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.8639
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.8639
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.17128 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -72.6223
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.17128 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -72.7936
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.16991 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -9.8548
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.16991 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -15.122
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.476
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -7.476
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -7.3061
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -7.646
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.17115 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -70.5134
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.17115 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -68.4596
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.16971 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -92.6617
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.16971 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -127.2825
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -10.4791
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -16.32
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -25.9401
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -26.4352
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -28.9935
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -26.4352
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.1371 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -3.0162
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.1371 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.5081
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.1371 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.5081
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -6.6001
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -5.1611
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -6.3649
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -6.6416
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.7367
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -1.592
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15134 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.6321
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15134 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.6321
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.15134 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -3.4808
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.16051 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -63.5628
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.087766 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -116.9921
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.087766 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -116.5532
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -5.4107
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -2.7481
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -2.1358
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.14239 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -6.6922
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 7.6038
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.11929 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 17.8932
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.1127 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 19.1018
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.051171 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 7.6757
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.11749 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 7.4019
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.12587 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 81.7797
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.13395 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.3578
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.13395 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 5.3578
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.18463 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -77.9117
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -28.1989
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -28.6262
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -69.0018
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -34.5845
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -35.0222
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -38.3056
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.19418 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -113.4017
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.19418 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -115.5377
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.19398 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -83.9942
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -42.3617
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -42.5698
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -42.4941
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -42.8914
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.22048 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.7639
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.22048 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.7639
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.2367
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -3.2367
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -2.6973
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.17815 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -2.4406
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.19272 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.4689
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.19272 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -3.4689
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.3873
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -7.1762
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -7.3873
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.18593 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -5.2059
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.18593 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -5.3919
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.11326 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 3.964
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.11326 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.3977
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.7528
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.7528
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.7528
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -9.7528
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.19291 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -1.1575
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.43848
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.43848
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.51155
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.18013 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.72051
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.1801 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.43223
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.1801 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.43223
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -25.8364
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -24.2546
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -24.6061
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -25.8364
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -31.988
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -34.8001
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -33.5387
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -32.8789
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -51.1548
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -25.8859
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -26.4328
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -27.5265
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -52.8655
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.082417 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.7198
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.082417 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -2.0604
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.7367
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.13866 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -10.122
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.225
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -10.4839
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -3.7612
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.94029
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -10.225
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -10.3545
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -10.1474
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -3.2358
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -5.9538
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.147 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -92.4643
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14023 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -20.1938
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.14023 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -26.3642
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.16911 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -2.0293
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.10385 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.62308
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.14085 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -47.3246
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14117 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -47.1525
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14117 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -47.9995
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.14138 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -5.3723
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.14123 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.5307
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.14123 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.5307
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.14137 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -5.372
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.14206 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -4.1198
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -20.8901
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -20.9324
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -21.5522
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -22.0208
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -21.3239
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -13.9372
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -20.2089
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -20.4877
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -17.7002
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -20.9428
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -21.1429
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -24.731
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -29.5325
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -30.9164
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -34.5259
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -20.5438
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -20.5438
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -24.3957
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.22188 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -68.7819
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.22188 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -91.6352
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -9.4256
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -9.8744
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -9.8744
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -10.5476
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -10.7689
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.1096
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -10.1096
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -10.3293
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -33.845
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -32.5264
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -10.5491
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -10.5491
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.0692
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 8.0692
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 10.6974
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.2219
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 9.2219
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 13.2565
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 23.9959
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 16.3776
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 15.2596
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 15.6745
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 16.9423
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 24.2033
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 24.9005
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 15.0713
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 29.6661
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 23.4708
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 23.424
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 14.2769
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.11362 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 16.9291
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.11679 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 21.0217
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.11679 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 21.0217
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.11668 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 26.2519
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.11828 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 14.7855
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.11828 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 14.7855
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 18.7274
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 18.8611
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 41.334
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 19.1287
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 19.2624
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 41.4678
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13629 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 26.713
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.13629 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 15.1283
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.13459 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 21.3549
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 21.7528
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 21.7528
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 54.9125
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 21.4875
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 21.3549
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 21.6202
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 54.2494
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.13409 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.13409 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 18.9649
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 16.6583
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 18.5804
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 51.1283
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 18.4445
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 18.4812
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 21.7123
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 18.5718
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 18.6698
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 21.759
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.2644 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -153.6181
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 73.8805
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 73.8805
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.042217 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 1.3509
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.038598 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 1.8527
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.038598 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 1.7755
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.50767
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 2.1576
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.042306 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.7192
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.93073
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 1.0576
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.038598 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 4.0528
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.11793 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 9.9065
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.10117 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 8.0938
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10106 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 15.1596
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.10106 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 15.1596
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -2.8501
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -2.6851
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.1336
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -6.1672
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -6.1793
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -6.131
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -3.8646
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -9.8225
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.6102
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.0408
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -3.7427
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.1375
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.1093
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.040286 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.2892
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.040286 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.2086
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.58
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -6.58
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -7.0542
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -6.4911
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 13.1602
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 13.2207
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.028675 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -3.8998
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.046593 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.5376
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.2015
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.2015
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.0871
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.0871
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.062332 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -4.4256
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.062332 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.62332
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -7.7844
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -7.7844
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -11.7005
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.1449
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -1.9799
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.1449
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.1449
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.030178 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -4.4965
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.030178 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -1.9646
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -3.0803
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -2.9652
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -2.9449
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.8448
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.41296
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.025067 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -18.6248
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.026503 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -19.4797
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.237
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.237
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -4.237
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -2.8829
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.028389 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -4.9113
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.028389 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -3.8325
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -3.8452
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -3.8121
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -3.7531
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -6.3582
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -1.9254
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -1.9013
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -2.4849
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -2.2142
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -5.0566
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -4.8676
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -4.88
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -4.8645
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -8.3347
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.025143 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.12571
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.025143 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.528
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 6.0958
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 6.167
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 6.167
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 15.0222
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.023267 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -9.2603
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.4599
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.4599
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.4599
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.7455
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.7455
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -1.7137
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10203 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 84.3755
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.10203 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 83.5593
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.048242 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -2.224
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.6242
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.6242
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -9.1518
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.4498
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.4498
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -8.8903
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -5.4103
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -4.767
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -4.7189
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.030631 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -1.0721
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.036016 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -16.5313
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -1.6337
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -1.6588
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -1.7594
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -1.5834
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -1.5583
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -2.6139
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -1.4829
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -2.5996
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5663
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5663
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016664 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -2.6996
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.024805 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -3.8944
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -2.0961
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -2.1257
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -1.1514
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.88569
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.03142 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -2.4508
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.03142 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -2.5136
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.030091 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.48747
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.030201 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -4.9832
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.030231 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -5.109
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.0301 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -6.4113
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.03007 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -6.856
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.030252 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.36302
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.030252 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.54454
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.037875 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -1.8938
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8109
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.8109
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4595
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.4325
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4595
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.5406
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4595
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.4595
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5676
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.5676
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.025709 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.30851
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2683
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3363
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2683
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2683
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.3363
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.2683
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.0821 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -5.4186
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -7.4218
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -7.6523
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -11.4323
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046098 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -25.1695
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046098 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -29.641
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -31.1503
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -26.9874
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -28.71
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.046098 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.59927
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.025107 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.30128
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.88924
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.90754
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.85524
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.2005
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.46293
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.53354
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.52046
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.91539
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.47077
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -2.2336
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -3.8708
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -4.104
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -4.7263
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -2.9787
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -6.6856
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -5.6927
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -5.8251
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -3.3097
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.1915
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -6.2222
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -4.6336
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -4.1702
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -4.766
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -4.2894
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -6.6856
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -6.4208
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -6.818
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -5.0307
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.2955
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.2955
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -11.3192
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.2568
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.096032 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 7.3464
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 8.1107
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 4.0554
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.10224 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.1794
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.1012 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 8.0958
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.096776 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 7.7421
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.095329 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 8.0076
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.10224 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 8.1794
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -20.3741
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 13.9585
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 27.1028
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 19.7978
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -39.6758
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -32.8845
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -40.0333
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -20.5528
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -17.872
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 7.2597
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.091897 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.072271 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.10544 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.5061
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.4587
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 12.7815
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 16.0512
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 14.1489
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 12.4843
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 9.5713
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.115 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 17.2494
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 12.8796
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 17.1155
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 21.2942
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 24.557
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.14239 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.10883 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.15025 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -3.6241
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -5.6432
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -9.5779
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -13.3753
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -5.8339
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -5.407
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -2.7035
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -13.3753
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -5.1224
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -6.1185
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -3.1304
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.2388
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.0149
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.94029
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -2.0149
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.2388
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -5.2388
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -21.0589
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.1145
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -7.8259
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -7.1145
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13937 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -1.6725
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.13589 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -2.0384
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.13589 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -3.1256
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.13058 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -6.268
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.13488 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -1.0791
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.14089 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -25.3606
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.14085 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -25.3525
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -25.4115
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.14117 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -25.4115
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15027 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -15.0268
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15027 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -15.0268
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.4989
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.4989
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.4989
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -2.2393
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.4989
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.4989
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.4989
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -2.0993
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15027 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15027 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -75.134
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15027 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -75.134
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.15027 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.14897 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.082417 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.14642 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.14475 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | [7 empty] | 69.6293
Number of Bus | Name of Bus | ID | Max MW | L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.18349 | north | Y | 0.054682 | 0.36239 | 0.06824 | 0.22171 | 0.054682 | North | N | 0.054682 | 0
239 | BOSQUESW | 1 | 149 | 0.18349 | north | Y | 0.054682 | 0.36239 | 0.06824 | 0.22171 | 0.054682 | North | N | 0.054682 | 0
244 | WHITNYDM | 1 | 15 | 0.15659 | north | N | 0.027787 | 0.33549 | 0.041345 | 0.19481 | 0.027787 | North | N | 0.027787 | 0
245 | WHITNYDM | 2 | 15 | 0.15659 | north | N | 0.027787 | 0.33549 | 0.041345 | 0.19481 | 0.027787 | North | N | 0.027787 | 0
247 | BOSQUESW | 2 | 153 | 0.18349 | north | Y | 0.054682 | 0.36239 | 0.06824 | 0.22171 | 0.054682 | North | N | 0.054682 | 0
251 | BOSQUESW | 2 | 150 | 0.16155 | north | Y | 0.032746 | 0.34045 | 0.046304 | 0.19977 | 0.032746 | North | N | 0.032746 | 0
253 | BOSQUESW | 2 | 80 | 0.16155 | north | Y | 0.032746 | 0.34045 | 0.046304 | 0.19977 | 0.032746 | North | N | 0.032746 | 0
332 | RWMILLER | 1 | 73 | 0.13343 | north | Y | 0.0046259 | 0.31233 | 0.018184 | 0.17165 | 0.0046259 | North | N | 0.0046259 | 0
333 | RWMILLER | 2 | 119 | 0.13343 | north | Y | 0.0046259 | 0.31233 | 0.018184 | 0.17165 | 0.0046259 | North | N | 0.0046259 | 0
334 | RWMILLER | 3 | 205 | 0.13343 | north | Y | 0.0046259 | 0.31233 | 0.018184 | 0.17165 | 0.0046259 | North | N | 0.0046259 | 0
335 | RWMILLER | 4 | 102 | 0.13343 | north | Y | 0.0046259 | 0.31233 | 0.018184 | 0.17165 | 0.0046259 | North | N | 0.0046259 | 0
336 | RWMILLER | 5 | 96 | 0.13343 | north | Y | 0.0046259 | 0.31233 | 0.018184 | 0.17165 | 0.0046259 | North | N | 0.0046259 | 0
344 | MRSSHPRD | 1 | 12 | 0.13161 | north | N | 0.0028049 | 0.31051 | 0.016363 | 0.16983 | 0.0028049 | North | N | 0.0028049 | 0
345 | MRSSHPRD | 2 | 12 | 0.13161 | north | N | 0.0028049 | 0.31051 | 0.016363 | 0.16983 | 0.0028049 | North | N | 0.0028049 | 0
366 | JNSNCNTY | 1 | 168 | 0.14092 | north | Y | 0.012112 | 0.31982 | 0.02567 | 0.17914 | 0.012112 | North | N | 0.012112 | 0
367 | JNSNCNTY | 2 | 90 | 0.14092 | north | Y | 0.012112 | 0.31982 | 0.02567 | 0.17914 | 0.012112 | North | N | 0.012112 | 0
503 | NTHTEXAS | 1 | 18 | 0.13447 | north | Y | 0.0056609 | 0.31337 | 0.019219 | 0.17269 | 0.0056609 | North | N | 0.0056609 | 0
504 | NTHTEXAS | 2 | 18 | 0.13447 | north | Y | 0.0056609 | 0.31337 | 0.019219 | 0.17269 | 0.0056609 | North | N | 0.0056609 | 0
505 | NTHTEXAS | 3 | 38 | 0.13447 | north | Y | 0.0056609 | 0.31337 | 0.019219 | 0.17269 | 0.0056609 | North | N | 0.0056609 | 0
580 | JCKCNTY8 | 1 | 288 | 0.13439 | north | Y | 0.0055839 | 0.31329 | 0.019142 | 0.17261 | 0.0055839 | North | N | 0.0055839 | 0
581 | JCKCNTY8 | 2 | 147 | 0.13439 | north | Y | 0.0055839 | 0.31329 | 0.019142 | 0.17261 | 0.0055839 | North | N | 0.0055839 | 0
582 | JCKCNTY8 | 3 | 147 | 0.13439 | north | Y | 0.0055839 | 0.31329 | 0.019142 | 0.17261 | 0.0055839 | North | N | 0.0055839 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.13408 | north | Y | 0.0052729 | 0.31298 | 0.018831 | 0.1723 | 0.0052729 | North | N | 0.0052729 | 0
837 | NEWMAN_G | 1 | 40 | 0.13363 | north | Y | 0.0048209 | 0.31253 | 0.018379 | 0.17185 | 0.0048209 | North | N | 0.0048209 | 0
842 | OLINGER_ | 1 | 79 | 0.13361 | north | Y | 0.0047979 | 0.31251 | 0.018356 | 0.17182 | 0.0047979 | North | N | 0.0047979 | 0
843 | OLINGER_ | 1 | 106 | 0.13361 | north | Y | 0.0047979 | 0.31251 | 0.018356 | 0.17182 | 0.0047979 | North | N | 0.0047979 | 0
844 | OLINGER_ | 1 | 146 | 0.13361 | north | Y | 0.0047979 | 0.31251 | 0.018356 | 0.17182 | 0.0047979 | North | N | 0.0047979 | 0
845 | OLINGER_ | 1 | 76 | 0.13361 | north | Y | 0.0047979 | 0.31251 | 0.018356 | 0.17182 | 0.0047979 | North | N | 0.0047979 | 0
923 | SPENCER_ | 1 | 60 | 0.13477 | north | Y | 0.0059589 | 0.31367 | 0.019517 | 0.17299 | 0.0059589 | North | N | 0.0059589 | 0
924 | SPENCER_ | 1 | 63 | 0.13477 | north | Y | 0.0059589 | 0.31367 | 0.019517 | 0.17299 | 0.0059589 | North | N | 0.0059589 | 0
948 | STEAM1 | 1 | 20 | 0.13345 | north | Y | 0.0046459 | 0.31235 | 0.018204 | 0.17167 | 0.0046459 | North | N | 0.0046459 | 0
949 | STEAM2 | 1 | 25 | 0.13345 | north | Y | 0.0046459 | 0.31235 | 0.018204 | 0.17167 | 0.0046459 | North | N | 0.0046459 | 0
950 | STEAM3 | 1 | 41 | 0.13345 | north | Y | 0.0046459 | 0.31235 | 0.018204 | 0.17167 | 0.0046459 | North | N | 0.0046459 | 0
990 | GIBN_CRE | 1 | 463 | 0.05008 | north | Y | -0.078727 | 0.22898 | -0.065169 | 0.0883 | 0.065169 | west | Y | 0.078727 | 6.2773
1002 | PBCTAGE_ | A | 66 | 0.11315 | west | Y | -0.015654 | 0.29205 | -0.0020962 | 0.15137 | 0.0020962 | west | N | 0.0020962 | 0
1003 | PBCTBGE_ | B | 65 | 0.11315 | west | Y | -0.015654 | 0.29205 | -0.0020962 | 0.15137 | 0.0020962 | west | N | 0.0020962 | 0
1004 | PBCTCGE_ | C | 67 | 0.11315 | west | Y | -0.015654 | 0.29205 | -0.0020962 | 0.15137 | 0.0020962 | west | N | 0.0020962 | 0
1005 | PBCTDGE_ | D | 67 | 0.11315 | west | Y | -0.015654 | 0.29205 | -0.0020962 | 0.15137 | 0.0020962 | west | N | 0.0020962 | 0
1006 | PBCTEGE_ | E | 67 | 0.11315 | west | Y | -0.015654 | 0.29205 | -0.0020962 | 0.15137 | 0.0020962 | west | N | 0.0020962 | 0
1007 | PB5GEN_6 | MB | 114 | 0.11315 | west | Y | -0.015654 | 0.29205 | -0.0020962 | 0.15137 | 0.0020962 | west | N | 0.0020962 | 0
1008 | PB6GEN_7 | MB | 515 | 0.11315 | west | Y | -0.015654 | 0.29205 | -0.0020962 | 0.15137 | 0.0020962 | west | N | 0.0020962 | 0
1039 | MRGNAG_1 | A | 66 | 0.11738 | west | Y | -0.011423 | 0.29628 | 0.0021348 | 0.1556 | 0.0021348 | west | N | 0.0021348 | 0
1040 | MRGNBG_2 | B | 69 | 0.11738 | west | Y | -0.011423 | 0.29628 | 0.0021348 | 0.1556 | 0.0021348 | west | N | 0.0021348 | 0
1041 | MRGNCG_3 | C | 69 | 0.11738 | west | Y | -0.011423 | 0.29628 | 0.0021348 | 0.1556 | 0.0021348 | west | N | 0.0021348 | 0
1042 | MRGNDG_4 | D | 67 | 0.11738 | west | Y | -0.011423 | 0.29628 | 0.0021348 | 0.1556 | 0.0021348 | west | N | 0.0021348 | 0
1043 | MRGNEG_5 | E | 67 | 0.11738 | west | Y | -0.011423 | 0.29628 | 0.0021348 | 0.1556 | 0.0021348 | west | N | 0.0021348 | 0
1044 | MRGNFG_6 | F | 65 | 0.11738 | west | Y | -0.011423 | 0.29628 | 0.0021348 | 0.1556 | 0.0021348 | west | N | 0.0021348 | 0
1045 | CALENG1G | 1 | 70 | 0.11678 | west | N | -0.012029 | 0.29568 | 0.0015288 | 0.155 | 0.0015288 | west | N | 0.0015288 | 0
1046 | CALENG2G | 2 | 73.4 | 0.11678 | west | N | -0.012029 | 0.29568 | 0.0015288 | 0.155 | 0.0015288 | west | N | 0.0015288 | 0
1047 | CALENG3G | 3 | 70.4 | 0.11678 | west | N | -0.012029 | 0.29568 | 0.0015288 | 0.155 | 0.0015288 | west | N | 0.0015288 | 0
1058 | LONGSHOR | 1 | 150 | 0.11712 | west | Y | -0.011687 | 0.29602 | 0.0018708 | 0.15534 | 0.0018708 | west | N | 0.0018708 | 0
1058 | LONGSHOR | 2 | 220 | 0.11712 | west | Y | -0.011687 | 0.29602 | 0.0018708 | 0.15534 | 0.0018708 | west | N | 0.0018708 | 0
1061 | CIELOGEN | 1 | 99 | 0.11762 | west | Y | -0.011182 | 0.29653 | 0.0023758 | 0.15584 | 0.0023758 | west | N | 0.0023758 | 0
1062 | CIELOGEN | 1 | 61 | 0.11762 | west | Y | -0.011182 | 0.29653 | 0.0023758 | 0.15584 | 0.0023758 | west | N | 0.0023758 | 0
1068 | SCURRYCW | 1 | 141 | 0.11759 | west | Y | -0.011216 | 0.29649 | 0.0023418 | 0.15581 | 0.0023418 | west | N | 0.0023418 | 0
1069 | KINDERMG | 1 | 25 | 0.11762 | west | N | -0.011182 | 0.29653 | 0.0023758 | 0.15584 | 0.0023758 | west | N | 0.0023758 | 0
1070 | KINDERMG | 1 | 45.7 | 0.11762 | west | N | -0.011182 | 0.29653 | 0.0023758 | 0.15584 | 0.0023758 | west | N | 0.0023758 | 0
1071 | KINDERMG | 1 | 45.7 | 0.11762 | west | N | -0.011182 | 0.29653 | 0.0023758 | 0.15584 | 0.0023758 | west | N | 0.0023758 | 0
1073 | SCURRYCW | 2 | 120 | 0.11759 | west | Y | -0.011216 | 0.29649 | 0.0023418 | 0.15581 | 0.0023418 | west | N | 0.0023418 | 0
1320 | BSP 1 | 1 | 25.8 | 0.11564 | west | N | -0.013165 | 0.29454 | 0.00039282 | 0.15386 | 0.00039282 | west | N | 0.00039282 | 0
1326 | STANTONW | 1 | 100.5 | 0.11535 | west | Y | -0.013456 | 0.29425 | 0.00010182 | 0.15357 | 0.00010182 | west | N | 0.00010182 | 0
1327 | WILDHRSE | 1 | 120 | 0.11638 | west | Y | -0.012427 | 0.29528 | 0.0011308 | 0.1546 | 0.0011308 | west | N | 0.0011308 | 0
1328 | OCOTILLO | 1 | 58 | 0.11533 | west | Y | -0.013476 | 0.29423 | 8.1821e-05 | 0.15355 | 8.1821e-05 | west | N | 8.1821e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.11562 | west | Y | -0.013189 | 0.29452 | 0.00036882 | 0.15384 | 0.00036882 | west | N | 0.00036882 | 0
1343 | TRENTIPP | 1 | 150 | 0.11807 | west | Y | -0.01074 | 0.29697 | 0.0028178 | 0.15629 | 0.0028178 | west | N | 0.0028178 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.11392 | west | Y | -0.014885 | 0.29282 | -0.0013272 | 0.15214 | 0.0013272 | west | N | 0.0013272 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.11392 | west | Y | -0.014885 | 0.29282 | -0.0013272 | 0.15214 | 0.0013272 | west | N | 0.0013272 | 0
1354 | AEPWIND_ | 1 | 101 | 0.11807 | west | Y | -0.01074 | 0.29697 | 0.0028178 | 0.15629 | 0.0028178 | west | N | 0.0028178 | 0
1360 | GUNSIGHT | 1 | 120 | 0.11643 | west | Y | -0.012377 | 0.29533 | 0.0011808 | 0.15465 | 0.0011808 | west | N | 0.0011808 | 0
1432 | GRHAMSES | 2 | 366 | 0.12934 | north | Y | 0.00053293 | 0.30824 | 0.014091 | 0.16756 | 0.00053293 | North | N | 0.00053293 | 0
1433 | GRHAMSES | 1 | 242 | 0.12882 | north | Y | 7.9267e-06 | 0.30772 | 0.013566 | 0.16703 | 7.9267e-06 | North | N | 7.9267e-06 | 0
1437 | MESQUITW | 1 | 400 | 0.12331 | west | Y | -0.0054971 | 0.30221 | 0.0080608 | 0.16153 | 0.0054971 | North | Y | 0.0080608 | 1.0255
1438 | MESQUITW | 1 | 236 | 0.12332 | west | Y | -0.0054891 | 0.30222 | 0.0080688 | 0.16154 | 0.0054891 | North | Y | 0.0080688 | 0.60882
1442 | COKFIELD | 1 | 165 | 0.12476 | west | Y | -0.0040441 | 0.30366 | 0.0095138 | 0.16298 | 0.0040441 | North | Y | 0.0095138 | 0.90251
1453 | WCPWRCO_ | 1 | 204 | 0.13277 | north | Y | 0.0039599 | 0.31167 | 0.017518 | 0.17099 | 0.0039599 | North | N | 0.0039599 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.13277 | north | Y | 0.0039599 | 0.31167 | 0.017518 | 0.17099 | 0.0039599 | North | N | 0.0039599 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.13277 | north | Y | 0.0039599 | 0.31167 | 0.017518 | 0.17099 | 0.0039599 | North | N | 0.0039599 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.12947 | west | Y | 0.00066693 | 0.30837 | 0.014225 | 0.16769 | 0.00066693 | North | Y | 0.014225 | 0.27116
1479 | WFCOGEN_ | 2 | 20 | 0.12947 | west | Y | 0.00066693 | 0.30837 | 0.014225 | 0.16769 | 0.00066693 | North | Y | 0.014225 | 0.27116
1482 | WFCOGEN_ | 1 | 20 | 0.12947 | west | Y | 0.00066693 | 0.30837 | 0.014225 | 0.16769 | 0.00066693 | North | Y | 0.014225 | 0.27116
1482 | WFCOGEN_ | 2 | 17 | 0.12947 | west | Y | 0.00066693 | 0.30837 | 0.014225 | 0.16769 | 0.00066693 | North | Y | 0.014225 | 0.23048
1600 | BARTNWND | 1 | 120 | 0.13148 | north | Y | 0.0026739 | 0.31038 | 0.016232 | 0.1697 | 0.0026739 | North | N | 0.0026739 | 0
1643 | SLSTR1PP | 1 | 60 | 0.12842 | north | Y | -0.00038907 | 0.30732 | 0.013169 | 0.16664 | 0.00038907 | North | N | 0.00038907 | 0
1675 | PEC_1G | 1 | 75 | 0.1336 | north | N | 0.0047939 | 0.3125 | 0.018352 | 0.17182 | 0.0047939 | North | N | 0.0047939 | 0
1676 | PEC_2G | 2 | 79.6 | 0.1336 | north | N | 0.0047939 | 0.3125 | 0.018352 | 0.17182 | 0.0047939 | North | N | 0.0047939 | 0
1677 | PEC_3G | 3 | 88.4 | 0.1336 | north | N | 0.0047939 | 0.3125 | 0.018352 | 0.17182 | 0.0047939 | North | N | 0.0047939 | 0
1678 | LAMARPWR | 1 | 160 | 0.13369 | north | Y | 0.0048789 | 0.31259 | 0.018437 | 0.17191 | 0.0048789 | North | N | 0.0048789 | 0
1679 | LAMARPWR | 2 | 156 | 0.13369 | north | Y | 0.0048789 | 0.31259 | 0.018437 | 0.17191 | 0.0048789 | North | N | 0.0048789 | 0
1680 | LAMARPWR | 3 | 196 | 0.13369 | north | Y | 0.0048789 | 0.31259 | 0.018437 | 0.17191 | 0.0048789 | North | N | 0.0048789 | 0
1681 | LAMARPWR | 4 | 156 | 0.13369 | north | Y | 0.0048789 | 0.31259 | 0.018437 | 0.17191 | 0.0048789 | North | N | 0.0048789 | 0
1682 | LAMARPWR | 5 | 157 | 0.13369 | north | Y | 0.0048789 | 0.31259 | 0.018437 | 0.17191 | 0.0048789 | North | N | 0.0048789 | 0
1683 | LAMARPWR | 6 | 198 | 0.13369 | north | Y | 0.0048789 | 0.31259 | 0.018437 | 0.17191 | 0.0048789 | North | N | 0.0048789 | 0
1687 | VALLEY_1 | 1 | 170 | 0.13386 | north | Y | 0.0050489 | 0.31276 | 0.018607 | 0.17208 | 0.0050489 | North | N | 0.0050489 | 0
1688 | VALLEY_2 | 2 | 520 | 0.13386 | north | Y | 0.0050489 | 0.31276 | 0.018607 | 0.17208 | 0.0050489 | North | N | 0.0050489 | 0
1689 | VALLEY_3 | 3 | 370 | 0.13377 | north | Y | 0.0049599 | 0.31267 | 0.018518 | 0.17199 | 0.0049599 | North | N | 0.0049599 | 0
1701 | MOSES_1G | 1 | 558 | 0.13356 | north | Y | 0.0047579 | 0.31247 | 0.018316 | 0.17178 | 0.0047579 | North | N | 0.0047579 | 0
1702 | MOSES_2G | 2 | 579 | 0.13356 | north | Y | 0.0047579 | 0.31247 | 0.018316 | 0.17178 | 0.0047579 | North | N | 0.0047579 | 0
1703 | MOSES_3G | 3 | 808 | 0.13356 | north | Y | 0.0047579 | 0.31247 | 0.018316 | 0.17178 | 0.0047579 | North | N | 0.0047579 | 0
1861 | EAGLEMNT | MB | 112 | 0.13616 | north | Y | 0.0073529 | 0.31506 | 0.020911 | 0.17438 | 0.0073529 | North | N | 0.0073529 | 0
1862 | EAGLEMNT | MB | 100 | 0.13616 | north | Y | 0.0073529 | 0.31506 | 0.020911 | 0.17438 | 0.0073529 | North | N | 0.0073529 | 0
1863 | EAGLEMNT | MB | 378 | 0.13616 | north | Y | 0.0073529 | 0.31506 | 0.020911 | 0.17438 | 0.0073529 | North | N | 0.0073529 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.13671 | north | Y | 0.0079039 | 0.31561 | 0.021462 | 0.17493 | 0.0079039 | North | N | 0.0079039 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.13671 | north | Y | 0.0079039 | 0.31561 | 0.021462 | 0.17493 | 0.0079039 | North | N | 0.0079039 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.13671 | north | Y | 0.0079039 | 0.31561 | 0.021462 | 0.17493 | 0.0079039 | North | N | 0.0079039 | 0
1889 | DECRDOVA | MB | 770 | 0.13718 | north | Y | 0.0083709 | 0.31608 | 0.021929 | 0.1754 | 0.0083709 | North | N | 0.0083709 | 0
1892 | DECRDOVA | A | 70 | 0.13736 | north | Y | 0.0085519 | 0.31626 | 0.02211 | 0.17558 | 0.0085519 | North | N | 0.0085519 | 0
1893 | DECRDOVA | B | 69 | 0.13736 | north | Y | 0.0085519 | 0.31626 | 0.02211 | 0.17558 | 0.0085519 | North | N | 0.0085519 | 0
1894 | DECRDOVA | C | 69 | 0.13736 | north | Y | 0.0085519 | 0.31626 | 0.02211 | 0.17558 | 0.0085519 | North | N | 0.0085519 | 0
1895 | DECRDOVA | D | 68 | 0.13736 | north | Y | 0.0085519 | 0.31626 | 0.02211 | 0.17558 | 0.0085519 | North | N | 0.0085519 | 0
1898 | COMCHEPK | 1 | 1157 | 0.13617 | north | N | 0.0073599 | 0.31507 | 0.020918 | 0.17439 | 0.0073599 | North | N | 0.0073599 | 0
1899 | COMCHEPK | 2 | 1158 | 0.13617 | north | N | 0.0073599 | 0.31507 | 0.020918 | 0.17439 | 0.0073599 | North | N | 0.0073599 | 0
1937 | MDLTHELP | 5 | 224 | 0.14465 | north | Y | 0.015847 | 0.32355 | 0.029405 | 0.18287 | 0.015847 | North | N | 0.015847 | 0
1938 | MDLTHELP | 6 | 226 | 0.14465 | north | Y | 0.015847 | 0.32355 | 0.029405 | 0.18287 | 0.015847 | North | N | 0.015847 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.14486 | north | Y | 0.016053 | 0.32376 | 0.029611 | 0.18308 | 0.016053 | North | N | 0.016053 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.14486 | north | Y | 0.016053 | 0.32376 | 0.029611 | 0.18308 | 0.016053 | North | N | 0.016053 | 0
1943 | MDLTHELP | 3 | 212 | 0.14465 | north | Y | 0.015847 | 0.32355 | 0.029405 | 0.18287 | 0.015847 | North | N | 0.015847 | 0
1944 | MDLTHELP | 4 | 211 | 0.14465 | north | Y | 0.015847 | 0.32355 | 0.029405 | 0.18287 | 0.015847 | North | N | 0.015847 | 0
1947 | HANDLEY_ | 3 | 395 | 0.13881 | north | Y | 0.010006 | 0.31771 | 0.023564 | 0.17703 | 0.010006 | North | N | 0.010006 | 0
1948 | HANDLEY_ | 4 | 435 | 0.13858 | north | Y | 0.0097739 | 0.31748 | 0.023332 | 0.1768 | 0.0097739 | North | N | 0.0097739 | 0
1949 | HANDLEY_ | 5 | 435 | 0.13881 | north | Y | 0.010006 | 0.31771 | 0.023564 | 0.17703 | 0.010006 | North | N | 0.010006 | 0
2371 | COLLIN_1 | MB | 138 | 0.1345 | north | Y | 0.0056939 | 0.3134 | 0.019252 | 0.17272 | 0.0056939 | North | N | 0.0056939 | 0
2413 | MTCK6_G | 6 | 118 | 0.13583 | north | Y | 0.0070219 | 0.31473 | 0.02058 | 0.17405 | 0.0070219 | North | N | 0.0070219 | 0
2414 | MTCK7_G | 7 | 115 | 0.13583 | north | Y | 0.0070219 | 0.31473 | 0.02058 | 0.17405 | 0.0070219 | North | N | 0.0070219 | 0
2417 | MTCK8_G | 8 | 556 | 0.13583 | north | Y | 0.0070219 | 0.31473 | 0.02058 | 0.17405 | 0.0070219 | North | N | 0.0070219 | 0
2451 | LKHB1_G | 1 | 388 | 0.13363 | north | Y | 0.0048239 | 0.31253 | 0.018382 | 0.17185 | 0.0048239 | North | N | 0.0048239 | 0
2452 | LKHB2_G | 2 | 515 | 0.13363 | north | Y | 0.0048239 | 0.31253 | 0.018382 | 0.17185 | 0.0048239 | North | N | 0.0048239 | 0
3097 | MARTLAKE | 1 | 785 | 0.12864 | north | Y | -0.00016907 | 0.30754 | 0.013389 | 0.16686 | 0.00016907 | North | N | 0.00016907 | 0
3098 | MARTLAKE | 2 | 795 | 0.12864 | north | Y | -0.00016907 | 0.30754 | 0.013389 | 0.16686 | 0.00016907 | North | N | 0.00016907 | 0
3099 | MARTLAKE | 3 | 780 | 0.12864 | north | Y | -0.00016907 | 0.30754 | 0.013389 | 0.16686 | 0.00016907 | North | N | 0.00016907 | 0
3107 | STRYKER_ | 1 | 182 | 0.12683 | north | Y | -0.0019751 | 0.30573 | 0.011583 | 0.16505 | 0.0019751 | North | N | 0.0019751 | 0
3108 | STRYKER_ | 2 | 484 | 0.12683 | north | Y | -0.0019751 | 0.30573 | 0.011583 | 0.16505 | 0.0019751 | North | N | 0.0019751 | 0
3126 | TRINIDAD | 1 | 224 | 0.13152 | north | Y | 0.0027139 | 0.31042 | 0.016272 | 0.16974 | 0.0027139 | North | N | 0.0027139 | 0
3309 | ASPN_G | 1 | 50 | 0.12742 | north | Y | -0.0013831 | 0.30632 | 0.012175 | 0.16564 | 0.0013831 | North | N | 0.0013831 | 0
3348 | CHAMPION | MB | 42 | 0.12746 | north | N | -0.0013441 | 0.30636 | 0.012214 | 0.16568 | 0.0013441 | North | N | 0.0013441 | 0
3381 | BBRN_1G | 1 | 615 | 0.12111 | north | Y | -0.0076971 | 0.30001 | 0.0058608 | 0.15933 | 0.0058608 | west | Y | 0.0076971 | 1.1293
3382 | BBRN_2G | 2 | 587 | 0.12111 | north | Y | -0.0076971 | 0.30001 | 0.0058608 | 0.15933 | 0.0058608 | west | Y | 0.0076971 | 1.0779
3403 | THOUSE_1 | MB | 537 | 0.2147 | north | Y | 0.085891 | 0.3936 | 0.099449 | 0.25292 | 0.085891 | North | N | 0.085891 | 0
3404 | THOUSE_2 | 2 | 787 | 0.2147 | north | Y | 0.085891 | 0.3936 | 0.099449 | 0.25292 | 0.085891 | North | N | 0.085891 | 0
3416 | LAKE_CRK | MB | 75 | 0.18641 | north | Y | 0.057602 | 0.36531 | 0.07116 | 0.22463 | 0.057602 | North | N | 0.057602 | 0
3417 | LAKE_CRK | MB | 222 | 0.18641 | north | Y | 0.057602 | 0.36531 | 0.07116 | 0.22463 | 0.057602 | North | N | 0.057602 | 0
3432 | SANDOW_4 | 4 | 569 | -0.2644 | south | Y | -0.39321 | -0.085502 | -0.37965 | -0.22618 | 0.085502 | south | N | 0.085502 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.17095 | south | Y | -0.29976 | 0.0079459 | -0.2862 | -0.13274 | 0.0079459 | south | N | 0.0079459 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.17095 | south | Y | -0.29976 | 0.0079459 | -0.2862 | -0.13274 | 0.0079459 | south | N | 0.0079459 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.17087 | south | Y | -0.29968 | 0.0080259 | -0.28612 | -0.13266 | 0.0080259 | south | N | 0.0080259 | 0
5031 | BRA_VHBC | 1 | 46 | -0.17095 | south | Y | -0.29976 | 0.0079459 | -0.2862 | -0.13274 | 0.0079459 | south | N | 0.0079459 | 0
5032 | BRA_VHBC | 2 | 47 | -0.17095 | south | Y | -0.29976 | 0.0079459 | -0.2862 | -0.13274 | 0.0079459 | south | N | 0.0079459 | 0
5033 | BRA_VHBC | 3 | 46 | -0.17095 | south | Y | -0.29976 | 0.0079459 | -0.2862 | -0.13274 | 0.0079459 | south | N | 0.0079459 | 0
5034 | BRA_VHBC | 4 | 46 | -0.17095 | south | Y | -0.29976 | 0.0079459 | -0.2862 | -0.13274 | 0.0079459 | south | N | 0.0079459 | 0
5111 | CALAVER_ | 1 | 424 | -0.17128 | south | Y | -0.30009 | 0.0076219 | -0.28653 | -0.13306 | 0.0076219 | south | N | 0.0076219 | 0
5112 | CALAVER_ | 2 | 425 | -0.17128 | south | Y | -0.30009 | 0.0076219 | -0.28653 | -0.13306 | 0.0076219 | south | N | 0.0076219 | 0
5264 | LEON_LCP | 3 | 58 | -0.16991 | south | Y | -0.29872 | 0.0089909 | -0.28516 | -0.13169 | 0.0089909 | south | N | 0.0089909 | 0
5265 | LEON_LCP | 4 | 89 | -0.16991 | south | Y | -0.29872 | 0.0089909 | -0.28516 | -0.13169 | 0.0089909 | south | N | 0.0089909 | 0
5266 | LEON_LCP | 1 | 44 | -0.16991 | south | Y | -0.29872 | 0.0089909 | -0.28516 | -0.13169 | 0.0089909 | south | N | 0.0089909 | 0
5267 | LEON_LCP | 2 | 44 | -0.16991 | south | Y | -0.29872 | 0.0089909 | -0.28516 | -0.13169 | 0.0089909 | south | N | 0.0089909 | 0
5268 | LEON_LCP | 3 | 43 | -0.16991 | south | Y | -0.29872 | 0.0089909 | -0.28516 | -0.13169 | 0.0089909 | south | N | 0.0089909 | 0
5269 | LEON_LCP | 4 | 45 | -0.16991 | south | Y | -0.29872 | 0.0089909 | -0.28516 | -0.13169 | 0.0089909 | south | N | 0.0089909 | 0
5396 | CALAVER_ | 1 | 412 | -0.17115 | south | Y | -0.29996 | 0.0077519 | -0.2864 | -0.13293 | 0.0077519 | south | N | 0.0077519 | 0
5397 | CALAVER_ | 2 | 400 | -0.17115 | south | Y | -0.29996 | 0.0077519 | -0.2864 | -0.13293 | 0.0077519 | south | N | 0.0077519 | 0
5401 | CALAVER_ | 1 | 546 | -0.16971 | south | Y | -0.29852 | 0.0091909 | -0.28496 | -0.13149 | 0.0091909 | south | N | 0.0091909 | 0
5402 | CALAVER_ | 2 | 750 | -0.16971 | south | Y | -0.29852 | 0.0091909 | -0.28496 | -0.13149 | 0.0091909 | south | N | 0.0091909 | 0
5436 | TUTTL_WB | MB | 61 | -0.17179 | south | Y | -0.3006 | 0.0071119 | -0.28704 | -0.13357 | 0.0071119 | south | N | 0.0071119 | 0
5438 | TUTTL_WB | MB | 95 | -0.17179 | south | Y | -0.3006 | 0.0071119 | -0.28704 | -0.13357 | 0.0071119 | south | N | 0.0071119 | 0
5439 | TUTTL_WB | MB | 151 | -0.17179 | south | Y | -0.3006 | 0.0071119 | -0.28704 | -0.13357 | 0.0071119 | south | N | 0.0071119 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.17055 | south | Y | -0.29936 | 0.0083509 | -0.2858 | -0.13233 | 0.0083509 | south | N | 0.0083509 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.17055 | south | Y | -0.29936 | 0.0083509 | -0.2858 | -0.13233 | 0.0083509 | south | N | 0.0083509 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.17055 | south | Y | -0.29936 | 0.0083509 | -0.2858 | -0.13233 | 0.0083509 | south | N | 0.0083509 | 0
5503 | RAYBURNG | 1 | 22 | -0.1371 | south | Y | -0.26591 | 0.0418 | -0.25235 | -0.098881 | 0.0418 | south | N | 0.0418 | 0
5505 | RAYBURNG | 1 | 11 | -0.1371 | south | Y | -0.26591 | 0.0418 | -0.25235 | -0.098881 | 0.0418 | south | N | 0.0418 | 0
5506 | RAYBURNG | 1 | 11 | -0.1371 | south | Y | -0.26591 | 0.0418 | -0.25235 | -0.098881 | 0.0418 | south | N | 0.0418 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.13837 | south | Y | -0.26717 | 0.040534 | -0.25362 | -0.10015 | 0.040534 | south | N | 0.040534 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.13837 | south | Y | -0.26717 | 0.040534 | -0.25362 | -0.10015 | 0.040534 | south | N | 0.040534 | 0
5511 | RAYBURNC | 1 | 46 | -0.13837 | south | Y | -0.26717 | 0.040534 | -0.25362 | -0.10015 | 0.040534 | south | N | 0.040534 | 0
5512 | RAYBURNC | 1 | 48 | -0.13837 | south | Y | -0.26717 | 0.040534 | -0.25362 | -0.10015 | 0.040534 | south | N | 0.040534 | 0
5728 | FALCONHY | 2 | 12 | -0.14473 | south | N | -0.27353 | 0.034174 | -0.25998 | -0.10651 | 0.034174 | south | N | 0.034174 | 0
5729 | FALCONHY | 3 | 11 | -0.14473 | south | N | -0.27353 | 0.034174 | -0.25998 | -0.10651 | 0.034174 | south | N | 0.034174 | 0
5890 | PEARSALL | 1 | 24 | -0.15134 | south | Y | -0.28014 | 0.027564 | -0.26659 | -0.11312 | 0.027564 | south | N | 0.027564 | 0
5891 | PEARSALL | 1 | 24 | -0.15134 | south | Y | -0.28014 | 0.027564 | -0.26659 | -0.11312 | 0.027564 | south | N | 0.027564 | 0
5892 | PEARSALL | 1 | 23 | -0.15134 | south | Y | -0.28014 | 0.027564 | -0.26659 | -0.11312 | 0.027564 | south | N | 0.027564 | 0
5903 | SANMIGUE | 1 | 396 | -0.16051 | south | Y | -0.28932 | 0.018389 | -0.27576 | -0.12229 | 0.018389 | south | N | 0.018389 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.087766 | houston | N | -0.21657 | 0.091135 | -0.20302 | -0.049546 | 0.049546 | houston | N | 0.049546 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.087766 | houston | N | -0.21657 | 0.091135 | -0.20302 | -0.049546 | 0.049546 | houston | N | 0.049546 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.12881 | 0
5932 | SI_RAY9 | 9 | 38 | -0.14239 | south | Y | -0.2712 | 0.036513 | -0.25764 | -0.10417 | 0.036513 | south | N | 0.036513 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.14239 | south | Y | -0.2712 | 0.036513 | -0.25764 | -0.10417 | 0.036513 | south | N | 0.036513 | 0
5934 | SI_RAY5 | 5 | 15 | -0.14239 | south | Y | -0.2712 | 0.036513 | -0.25764 | -0.10417 | 0.036513 | south | N | 0.036513 | 0
5935 | SI_RAY10 | 10 | 47 | -0.14239 | south | Y | -0.2712 | 0.036513 | -0.25764 | -0.10417 | 0.036513 | south | N | 0.036513 | 0
6016 | SWMESA | 1 | 75 | 0.10138 | west | Y | -0.027423 | 0.28028 | -0.013865 | 0.1396 | 0.013865 | west | N | 0.013865 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.11525 | 0
6144 | MCADOO1A | 1 | 150 | 0.11929 | west | Y | -0.0095191 | 0.29819 | 0.0040388 | 0.15751 | 0.0040388 | west | N | 0.0040388 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.1127 | west | Y | -0.016112 | 0.2916 | -0.0025542 | 0.15091 | 0.0025542 | west | N | 0.0025542 | 0
6476 | LANGFORD | 1 | 150 | 0.051171 | west | Y | -0.077636 | 0.23007 | -0.064078 | 0.089391 | 0.064078 | west | N | 0.064078 | 0
6637 | SNYDERW1 | 1 | 63 | 0.11749 | west | Y | -0.011316 | 0.29639 | 0.0022418 | 0.15571 | 0.0022418 | west | N | 0.0022418 | 0
6752 | OKLA0A | 1 | 649.7 | 0.12587 | west | Y | -0.0029341 | 0.30477 | 0.010624 | 0.16409 | 0.0029341 | North | Y | 0.010624 | 4.996
6948 | DENISNDM | 1 | 40 | 0.13395 | north | N | 0.0051379 | 0.31285 | 0.018696 | 0.17216 | 0.0051379 | North | N | 0.0051379 | 0
6948 | DENISNDM | 2 | 40 | 0.13395 | north | N | 0.0051379 | 0.31285 | 0.018696 | 0.17216 | 0.0051379 | North | N | 0.0051379 | 0
7000 | L_FERGUS | 1 | 422 | -0.18463 | south | Y | -0.31343 | -0.0057241 | -0.29987 | -0.14641 | 0.0057241 | south | N | 0.0057241 | 0
7004 | L_SIMGID | 1 | 132 | -0.21363 | south | Y | -0.34244 | -0.034727 | -0.32888 | -0.17541 | 0.034727 | south | N | 0.034727 | 0
7005 | L_SIMGID | 2 | 134 | -0.21363 | south | Y | -0.34244 | -0.034727 | -0.32888 | -0.17541 | 0.034727 | south | N | 0.034727 | 0
7006 | L_SIMGID | 3 | 323 | -0.21363 | south | Y | -0.34244 | -0.034727 | -0.32888 | -0.17541 | 0.034727 | south | N | 0.034727 | 0
7007 | L_LOSTPI | 1 | 158 | -0.21889 | south | Y | -0.3477 | -0.039988 | -0.33414 | -0.18067 | 0.039988 | south | N | 0.039988 | 0
7008 | L_LOSTPI | 2 | 160 | -0.21889 | south | Y | -0.3477 | -0.039988 | -0.33414 | -0.18067 | 0.039988 | south | N | 0.039988 | 0
7009 | L_LOSTPI | 3 | 175 | -0.21889 | south | Y | -0.3477 | -0.039988 | -0.33414 | -0.18067 | 0.039988 | south | N | 0.039988 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.19418 | south | Y | -0.32299 | -0.01528 | -0.30943 | -0.15596 | 0.01528 | south | N | 0.01528 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.19418 | south | Y | -0.32299 | -0.01528 | -0.30943 | -0.15596 | 0.01528 | south | N | 0.01528 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.19398 | south | Y | -0.32279 | -0.015081 | -0.30923 | -0.15576 | 0.015081 | south | N | 0.015081 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.1892 | south | Y | -0.31801 | -0.010298 | -0.30445 | -0.15098 | 0.010298 | south | N | 0.010298 | 0
7015 | L_HAYSEN | 2 | 225 | -0.1892 | south | Y | -0.31801 | -0.010298 | -0.30445 | -0.15098 | 0.010298 | south | N | 0.010298 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.1892 | south | Y | -0.31801 | -0.010298 | -0.30445 | -0.15098 | 0.010298 | south | N | 0.010298 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.1892 | south | Y | -0.31801 | -0.010298 | -0.30445 | -0.15098 | 0.010298 | south | N | 0.010298 | 0
7020 | L_AUSTPL | 1 | 8 | -0.22048 | south | N | -0.34929 | -0.041583 | -0.33573 | -0.18226 | 0.041583 | south | N | 0.041583 | 0
7020 | L_AUSTPL | 2 | 8 | -0.22048 | south | N | -0.34929 | -0.041583 | -0.33573 | -0.18226 | 0.041583 | south | N | 0.041583 | 0
7022 | L_BUCHAN | 1 | 18 | -0.17982 | south | N | -0.30863 | -0.00091805 | -0.29507 | -0.1416 | 0.00091805 | south | N | 0.00091805 | 0
7023 | L_BUCHAN | 2 | 18 | -0.17982 | south | N | -0.30863 | -0.00091805 | -0.29507 | -0.1416 | 0.00091805 | south | N | 0.00091805 | 0
7024 | L_BUCHAN | 3 | 15 | -0.17982 | south | N | -0.30863 | -0.00091805 | -0.29507 | -0.1416 | 0.00091805 | south | N | 0.00091805 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.17815 | south | N | -0.30695 | 0.00075495 | -0.2934 | -0.13993 | 0.00075495 | south | N | 0.00075495 | 0
7028 | L_MARBFA | 1 | 18 | -0.19272 | south | N | -0.32152 | -0.013815 | -0.30797 | -0.1545 | 0.013815 | south | N | 0.013815 | 0
7029 | L_MARBFA | 2 | 18 | -0.19272 | south | N | -0.32152 | -0.013815 | -0.30797 | -0.1545 | 0.013815 | south | N | 0.013815 | 0
7031 | L_MARSFO | 1 | 35 | -0.21107 | south | N | -0.33987 | -0.032165 | -0.32632 | -0.17285 | 0.032165 | south | N | 0.032165 | 0
7032 | L_MARSFO | 2 | 34 | -0.21107 | south | N | -0.33987 | -0.032165 | -0.32632 | -0.17285 | 0.032165 | south | N | 0.032165 | 0
7033 | L_MARSFO | 3 | 35 | -0.21107 | south | N | -0.33987 | -0.032165 | -0.32632 | -0.17285 | 0.032165 | south | N | 0.032165 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.18593 | south | N | -0.31473 | -0.0070251 | -0.30118 | -0.14771 | 0.0070251 | south | N | 0.0070251 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.18593 | south | N | -0.31473 | -0.0070251 | -0.30118 | -0.14771 | 0.0070251 | south | N | 0.0070251 | 0
7038 | L_DELAWA | 1 | 35 | 0.11326 | west | Y | -0.015549 | 0.29216 | -0.0019912 | 0.15148 | 0.0019912 | west | N | 0.0019912 | 0
7038 | L_DELAWA | 2 | 30 | 0.11326 | west | Y | -0.015549 | 0.29216 | -0.0019912 | 0.15148 | 0.0019912 | west | N | 0.0019912 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.19506 | south | Y | -0.32386 | -0.016155 | -0.31031 | -0.15684 | 0.016155 | south | N | 0.016155 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.19506 | south | Y | -0.32386 | -0.016155 | -0.31031 | -0.15684 | 0.016155 | south | N | 0.016155 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.19506 | south | Y | -0.32386 | -0.016155 | -0.31031 | -0.15684 | 0.016155 | south | N | 0.016155 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.19506 | south | Y | -0.32386 | -0.016155 | -0.31031 | -0.15684 | 0.016155 | south | N | 0.016155 | 0
7487 | L_CANYHY | 1 | 6 | -0.19291 | south | N | -0.32172 | -0.01401 | -0.30816 | -0.15469 | 0.01401 | south | N | 0.01401 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.1827 | south | N | -0.31151 | -0.0037971 | -0.29795 | -0.14448 | 0.0037971 | south | N | 0.0037971 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.1827 | south | N | -0.31151 | -0.0037971 | -0.29795 | -0.14448 | 0.0037971 | south | N | 0.0037971 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.1827 | south | N | -0.31151 | -0.0037971 | -0.29795 | -0.14448 | 0.0037971 | south | N | 0.0037971 | 0
7609 | L_SCHUMA | 1 | 4 | -0.18013 | south | N | -0.30894 | -0.0012271 | -0.29538 | -0.14191 | 0.0012271 | south | N | 0.0012271 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.1801 | south | N | -0.3089 | -0.0011941 | -0.29534 | -0.14188 | 0.0011941 | south | N | 0.0011941 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.1801 | south | N | -0.3089 | -0.0011941 | -0.29534 | -0.14188 | 0.0011941 | south | N | 0.0011941 | 0
7800 | L_GUADGE | 1 | 147 | -0.17576 | south | Y | -0.30457 | 0.0031429 | -0.29101 | -0.13754 | 0.0031429 | south | N | 0.0031429 | 0
7801 | L_GUADGE | 2 | 138 | -0.17576 | south | Y | -0.30457 | 0.0031429 | -0.29101 | -0.13754 | 0.0031429 | south | N | 0.0031429 | 0
7802 | L_GUADGE | 3 | 140 | -0.17576 | south | Y | -0.30457 | 0.0031429 | -0.29101 | -0.13754 | 0.0031429 | south | N | 0.0031429 | 0
7803 | L_GUADGE | 4 | 147 | -0.17576 | south | Y | -0.30457 | 0.0031429 | -0.29101 | -0.13754 | 0.0031429 | south | N | 0.0031429 | 0
7804 | L_GUADGE | 5 | 182 | -0.17576 | south | Y | -0.30457 | 0.0031429 | -0.29101 | -0.13754 | 0.0031429 | south | N | 0.0031429 | 0
7805 | L_GUADGE | 6 | 198 | -0.17576 | south | Y | -0.30457 | 0.0031429 | -0.29101 | -0.13754 | 0.0031429 | south | N | 0.0031429 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.21993 | south | Y | -0.34873 | -0.041025 | -0.33518 | -0.18171 | 0.041025 | south | N | 0.041025 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.21993 | south | Y | -0.34873 | -0.041025 | -0.33518 | -0.18171 | 0.041025 | south | N | 0.041025 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.21993 | south | Y | -0.34873 | -0.041025 | -0.33518 | -0.18171 | 0.041025 | south | N | 0.041025 | 0
7810 | L_RIONOG | 1 | 142 | -0.1823 | south | Y | -0.3111 | -0.0033941 | -0.29754 | -0.14408 | 0.0033941 | south | N | 0.0033941 | 0
7811 | L_RIONOG | 2 | 145 | -0.1823 | south | Y | -0.3111 | -0.0033941 | -0.29754 | -0.14408 | 0.0033941 | south | N | 0.0033941 | 0
7812 | L_RIONOG | 3 | 151 | -0.1823 | south | Y | -0.3111 | -0.0033941 | -0.29754 | -0.14408 | 0.0033941 | south | N | 0.0033941 | 0
7813 | L_RIONOG | 4 | 290 | -0.1823 | south | Y | -0.3111 | -0.0033941 | -0.29754 | -0.14408 | 0.0033941 | south | N | 0.0033941 | 0
8032 | AMISTADH | 1 | 33 | -0.082417 | south | N | -0.21122 | 0.096484 | -0.19767 | -0.044197 | 0.044197 | houston | Y | 0.096484 | 0
8033 | AMISTADH | 2 | 25 | -0.082417 | south | N | -0.21122 | 0.096484 | -0.19767 | -0.044197 | 0.044197 | houston | Y | 0.096484 | 0
8048 | FALCONHY | 1 | 12 | -0.14473 | south | N | -0.27353 | 0.034174 | -0.25998 | -0.10651 | 0.034174 | south | N | 0.034174 | 0
8066 | DUP1V#1 | 1 | 73 | -0.13866 | south | N | -0.26746 | 0.040244 | -0.25391 | -0.10044 | 0.040244 | south | N | 0.040244 | 0
8134 | FOR69CG0 | 1 | 79 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
8138 | FOR69CG0 | 2 | 81 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8147 | UCAR #2 | 10 | 28 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
8148 | UCAR #1 | 2 | 7 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
8153 | FOR69CG0 | 3 | 79 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
8154 | FOR69CG0 | 4 | 80 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
8156 | FOR69CG0 | 6 | 25 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
8157 | FOR69CG0 | 7 | 46 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
8161 | COLETOU1 | 1 | 629 | -0.147 | south | Y | -0.27581 | 0.031899 | -0.26225 | -0.10878 | 0.031899 | south | N | 0.031899 | 0
8173 | VICEC51A | 5 | 144 | -0.14023 | south | Y | -0.26904 | 0.038666 | -0.25548 | -0.10202 | 0.038666 | south | N | 0.038666 | 0
8174 | VICEC61A | 6 | 188 | -0.14023 | south | Y | -0.26904 | 0.038666 | -0.25548 | -0.10202 | 0.038666 | south | N | 0.038666 | 0
8189 | CUERO 2 | 1 | 12 | -0.16911 | south | N | -0.29792 | 0.0097929 | -0.28436 | -0.13089 | 0.0097929 | south | N | 0.0097929 | 0
8262 | ELPS | 1 | 6 | -0.10385 | south | N | -0.23265 | 0.075054 | -0.2191 | -0.065627 | 0.065627 | houston | Y | 0.075054 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8442 | NBEC71A | 1 | 336 | -0.14085 | south | Y | -0.26965 | 0.038054 | -0.2561 | -0.10263 | 0.038054 | south | N | 0.038054 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.12881 | 0.1789 | -0.11525 | 0.03822 | 0.03822 | houston | Y | 0.1789 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.14117 | south | Y | -0.26998 | 0.037726 | -0.25642 | -0.10296 | 0.037726 | south | N | 0.037726 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.14117 | south | Y | -0.26998 | 0.037726 | -0.25642 | -0.10296 | 0.037726 | south | N | 0.037726 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.14138 | south | N | -0.27018 | 0.037524 | -0.25663 | -0.10316 | 0.037524 | south | N | 0.037524 | 0
8506 | VAL #1 | 1 | 25 | -0.14123 | south | N | -0.27003 | 0.037675 | -0.25648 | -0.10301 | 0.037675 | south | N | 0.037675 | 0
8507 | VAL #2 | 2 | 25 | -0.14123 | south | N | -0.27003 | 0.037675 | -0.25648 | -0.10301 | 0.037675 | south | N | 0.037675 | 0
8511 | OXY_CC0A | 1 | 38 | -0.14137 | south | N | -0.27018 | 0.037533 | -0.25662 | -0.10315 | 0.037533 | south | N | 0.037533 | 0
8517 | CELANEBI | 1 | 29 | -0.14206 | south | N | -0.27087 | 0.036839 | -0.25731 | -0.10384 | 0.036839 | south | N | 0.036839 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.14086 | south | N | -0.26967 | 0.038037 | -0.25611 | -0.10264 | 0.038037 | south | N | 0.038037 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.14086 | south | N | -0.26967 | 0.038037 | -0.25611 | -0.10264 | 0.038037 | south | N | 0.038037 | 0
8562 | CNOPST1 | 3 | 153 | -0.14086 | south | N | -0.26967 | 0.038037 | -0.25611 | -0.10264 | 0.038037 | south | N | 0.038037 | 0
8926 | LGE_GT10 | 1 | 158 | -0.13937 | south | N | -0.26818 | 0.039529 | -0.25462 | -0.10115 | 0.039529 | south | N | 0.039529 | 0
8927 | LGE_GT20 | 2 | 153 | -0.13937 | south | N | -0.26818 | 0.039529 | -0.25462 | -0.10115 | 0.039529 | south | N | 0.039529 | 0
8928 | LGE_STG0 | 3 | 100 | -0.13937 | south | N | -0.26818 | 0.039529 | -0.25462 | -0.10115 | 0.039529 | south | N | 0.039529 | 0
8930 | ICPGN10A | 1 | 145 | -0.13937 | south | N | -0.26818 | 0.039529 | -0.25462 | -0.10115 | 0.039529 | south | N | 0.039529 | 0
8931 | ICPGN20A | 2 | 147 | -0.13937 | south | N | -0.26818 | 0.039529 | -0.25462 | -0.10115 | 0.039529 | south | N | 0.039529 | 0
8932 | ICPGN30A | 3 | 127 | -0.13937 | south | N | -0.26818 | 0.039529 | -0.25462 | -0.10115 | 0.039529 | south | N | 0.039529 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.14295 | south | Y | -0.27176 | 0.035947 | -0.2582 | -0.10473 | 0.035947 | south | N | 0.035947 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.14295 | south | Y | -0.27176 | 0.035947 | -0.2582 | -0.10473 | 0.035947 | south | N | 0.035947 | 0
8935 | FGNTS201 | 3 | 173 | -0.14295 | south | Y | -0.27176 | 0.035947 | -0.2582 | -0.10473 | 0.035947 | south | N | 0.035947 | 0
8936 | MVGN#1 | 1 | 207 | -0.14267 | south | Y | -0.27148 | 0.036232 | -0.25792 | -0.10445 | 0.036232 | south | N | 0.036232 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.14267 | south | Y | -0.27148 | 0.036232 | -0.25792 | -0.10445 | 0.036232 | south | N | 0.036232 | 0
8938 | MVGN#3 | 3 | 242 | -0.14267 | south | Y | -0.27148 | 0.036232 | -0.25792 | -0.10445 | 0.036232 | south | N | 0.036232 | 0
8981 | HECN1 | 1 | 144 | -0.14266 | south | Y | -0.27147 | 0.036236 | -0.25791 | -0.10445 | 0.036236 | south | N | 0.036236 | 0
8982 | HECN2 | 2 | 144 | -0.14266 | south | Y | -0.27147 | 0.036236 | -0.25791 | -0.10445 | 0.036236 | south | N | 0.036236 | 0
8983 | HECN3 | 3 | 171 | -0.14266 | south | Y | -0.27147 | 0.036236 | -0.25791 | -0.10445 | 0.036236 | south | N | 0.036236 | 0
9000 | DECKR_G1 | 1 | 310 | -0.22188 | south | Y | -0.35068 | -0.042976 | -0.33713 | -0.18366 | 0.042976 | south | N | 0.042976 | 0
9001 | DECKR_G2 | 2 | 413 | -0.22188 | south | Y | -0.35068 | -0.042976 | -0.33713 | -0.18366 | 0.042976 | south | N | 0.042976 | 0
9002 | DECKR_G3 | 3 | 42 | -0.22442 | south | Y | -0.35323 | -0.045517 | -0.33967 | -0.1862 | 0.045517 | south | N | 0.045517 | 0
9003 | DECKR_G4 | 4 | 44 | -0.22442 | south | Y | -0.35323 | -0.045517 | -0.33967 | -0.1862 | 0.045517 | south | N | 0.045517 | 0
9004 | DECKR_G5 | 5 | 44 | -0.22442 | south | Y | -0.35323 | -0.045517 | -0.33967 | -0.1862 | 0.045517 | south | N | 0.045517 | 0
9005 | DECKR_G6 | 6 | 47 | -0.22442 | south | Y | -0.35323 | -0.045517 | -0.33967 | -0.1862 | 0.045517 | south | N | 0.045517 | 0
9016 | SANDH_G1 | 1 | 49 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
9017 | SANDH_G2 | 2 | 46 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
9018 | SANDH_G3 | 3 | 46 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
9019 | SANDH_G4 | 4 | 47 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
9020 | SANDHG5A | 5A | 154 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
9021 | SANDHG5C | 5C | 148 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
9022 | SANDH_G6 | 6 | 48 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
9023 | SANDH_G7 | 7 | 48 | -0.21977 | south | Y | -0.34858 | -0.040872 | -0.33502 | -0.18155 | 0.040872 | south | N | 0.040872 | 0
11001 | NAV1CT | 1 | 70 | 0.11527 | west | Y | -0.013533 | 0.29417 | 2.4821e-05 | 0.15349 | 2.4821e-05 | west | N | 2.4821e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.11527 | west | Y | -0.013533 | 0.29417 | 2.4821e-05 | 0.15349 | 2.4821e-05 | west | N | 2.4821e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.11527 | west | Y | -0.013533 | 0.29417 | 2.4821e-05 | 0.15349 | 2.4821e-05 | west | N | 2.4821e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.11527 | west | Y | -0.013533 | 0.29417 | 2.4821e-05 | 0.15349 | 2.4821e-05 | west | N | 2.4821e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.11527 | west | Y | -0.013533 | 0.29417 | 2.4821e-05 | 0.15349 | 2.4821e-05 | west | N | 2.4821e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.11527 | west | Y | -0.013533 | 0.29417 | 2.4821e-05 | 0.15349 | 2.4821e-05 | west | N | 2.4821e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.11525 | west | Y | -0.013553 | 0.29415 | 4.8214e-06 | 0.15347 | 4.8214e-06 | west | N | 4.8214e-06 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.11525 | west | Y | -0.013553 | 0.29415 | 4.8214e-06 | 0.15347 | 4.8214e-06 | west | N | 4.8214e-06 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.11525 | west | Y | -0.013553 | 0.29415 | 4.8214e-06 | 0.15347 | 4.8214e-06 | west | N | 4.8214e-06 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.11525 | west | Y | -0.013553 | 0.29415 | 4.8214e-06 | 0.15347 | 4.8214e-06 | west | N | 4.8214e-06 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.11525 | west | Y | -0.013553 | 0.29415 | 4.8214e-06 | 0.15347 | 4.8214e-06 | west | N | 4.8214e-06 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.11525 | west | Y | -0.013553 | 0.29415 | 4.8214e-06 | 0.15347 | 4.8214e-06 | west | N | 4.8214e-06 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.11914 | west | Y | -0.0096661 | 0.29804 | 0.0038918 | 0.15736 | 0.0038918 | west | N | 0.0038918 | 0
11057 | CHAMPION | 1 | 126.5 | 0.11914 | west | Y | -0.0096661 | 0.29804 | 0.0038918 | 0.15736 | 0.0038918 | west | N | 0.0038918 | 0
11058 | PYRON_1G | 1 | 249 | 0.11914 | west | Y | -0.0096661 | 0.29804 | 0.0038918 | 0.15736 | 0.0038918 | west | N | 0.0038918 | 0
11059 | INADALE_ | 1 | 197 | 0.11914 | west | Y | -0.0096661 | 0.29804 | 0.0038918 | 0.15736 | 0.0038918 | west | N | 0.0038918 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.11712 | west | Y | -0.011687 | 0.29602 | 0.0018708 | 0.15534 | 0.0018708 | west | N | 0.0018708 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.11712 | west | Y | -0.011687 | 0.29602 | 0.0018708 | 0.15534 | 0.0018708 | west | N | 0.0018708 | 0
11147 | NOTREES_ | 1 | 149 | 0.11362 | west | Y | -0.015189 | 0.29252 | -0.0016312 | 0.15184 | 0.0016312 | west | N | 0.0016312 | 0
11309 | BULLCREK | 1 | 180 | 0.11679 | west | Y | -0.01202 | 0.29569 | 0.0015378 | 0.15501 | 0.0015378 | west | N | 0.0015378 | 0
11310 | BULLCREK | 1 | 180 | 0.11679 | west | Y | -0.01202 | 0.29569 | 0.0015378 | 0.15501 | 0.0015378 | west | N | 0.0015378 | 0
11320 | COYOTE_1 | 1 | 225 | 0.11668 | west | Y | -0.012132 | 0.29558 | 0.0014258 | 0.15489 | 0.0014258 | west | N | 0.0014258 | 0
11415 | LORAINE_ | 1 | 125 | 0.11828 | west | Y | -0.010523 | 0.29718 | 0.0030348 | 0.1565 | 0.0030348 | west | N | 0.0030348 | 0
11416 | LORAINE_ | 1 | 125 | 0.11828 | west | Y | -0.010523 | 0.29718 | 0.0030348 | 0.1565 | 0.0030348 | west | N | 0.0030348 | 0
11691 | KMICHICT | 1 | 140 | 0.13377 | north | N | 0.0049599 | 0.31267 | 0.018518 | 0.17199 | 0.0049599 | North | N | 0.0049599 | 0
11692 | KMICHICT | 2 | 141 | 0.13377 | north | N | 0.0049599 | 0.31267 | 0.018518 | 0.17199 | 0.0049599 | North | N | 0.0049599 | 0
11693 | KMICHIST | 3 | 309 | 0.13377 | north | N | 0.0049599 | 0.31267 | 0.018518 | 0.17199 | 0.0049599 | North | N | 0.0049599 | 0
11694 | KMICHICT | 4 | 143 | 0.13377 | north | N | 0.0049599 | 0.31267 | 0.018518 | 0.17199 | 0.0049599 | North | N | 0.0049599 | 0
11695 | KMICHICT | 5 | 144 | 0.13377 | north | N | 0.0049599 | 0.31267 | 0.018518 | 0.17199 | 0.0049599 | North | N | 0.0049599 | 0
11696 | KMICHIST | 6 | 310 | 0.13377 | north | N | 0.0049599 | 0.31267 | 0.018518 | 0.17199 | 0.0049599 | North | N | 0.0049599 | 0
12322 | ENNSTRAC | 1 | 196 | 0.13629 | north | Y | 0.0074839 | 0.31519 | 0.021042 | 0.17451 | 0.0074839 | North | N | 0.0074839 | 0
12323 | ENNSTRAC | 2 | 111 | 0.13629 | north | Y | 0.0074839 | 0.31519 | 0.021042 | 0.17451 | 0.0074839 | North | N | 0.0074839 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.13459 | north | N | 0.0057789 | 0.31349 | 0.019337 | 0.17281 | 0.0057789 | North | N | 0.0057789 | 0
12411 | FPLEFR1A | 1 | 161 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12412 | FPLEFR1B | 2 | 164 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12413 | FPLEFR1C | 3 | 164 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12414 | FPLEFR1S | 4 | 414 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12421 | FPLEFR2A | 1 | 162 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12422 | FPLEFR2B | 2 | 161 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12423 | FPLEFR2C | 3 | 163 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12424 | FPLEFR2S | 4 | 409 | 0.13264 | north | Y | 0.0038319 | 0.31154 | 0.01739 | 0.17086 | 0.0038319 | North | N | 0.0038319 | 0
12440 | PARKD_1S | 1 | 0 | 0.13409 | north | N | 0.0052849 | 0.31299 | 0.018843 | 0.17231 | 0.0052849 | North | N | 0.0052849 | 0
12449 | PARKD_2S | 1 | 0 | 0.13409 | north | N | 0.0052849 | 0.31299 | 0.018843 | 0.17231 | 0.0052849 | North | N | 0.0052849 | 0
13116 | TGATEWAY | 1 | 148 | 0.12814 | north | N | -0.00066607 | 0.30704 | 0.012892 | 0.16636 | 0.00066607 | North | N | 0.00066607 | 0
13117 | TGATEWAY | 2 | 130 | 0.12814 | north | N | -0.00066607 | 0.30704 | 0.012892 | 0.16636 | 0.00066607 | North | N | 0.00066607 | 0
13118 | TGATEWAY | 3 | 145 | 0.12814 | north | N | -0.00066607 | 0.30704 | 0.012892 | 0.16636 | 0.00066607 | North | N | 0.00066607 | 0
13119 | TGATEWAY | 4 | 399 | 0.12814 | north | N | -0.00066607 | 0.30704 | 0.012892 | 0.16636 | 0.00066607 | North | N | 0.00066607 | 0
13131 | CALFREST | 1 | 150.7 | 0.12239 | north | Y | -0.0064151 | 0.30129 | 0.0071428 | 0.16061 | 0.0064151 | North | N | 0.0064151 | 0
13132 | CALFREST | 2 | 151 | 0.12239 | north | Y | -0.0064151 | 0.30129 | 0.0071428 | 0.16061 | 0.0064151 | North | N | 0.0064151 | 0
13133 | CALFREST | 3 | 177.4 | 0.12239 | north | Y | -0.0064151 | 0.30129 | 0.0071428 | 0.16061 | 0.0064151 | North | N | 0.0064151 | 0
13134 | CALFREST | 4 | 151.5 | 0.12259 | north | Y | -0.0062211 | 0.30149 | 0.0073368 | 0.16081 | 0.0062211 | North | N | 0.0062211 | 0
13135 | CALFREST | 5 | 152.3 | 0.12259 | north | Y | -0.0062211 | 0.30149 | 0.0073368 | 0.16081 | 0.0062211 | North | N | 0.0062211 | 0
13136 | CALFREST | 6 | 177.5 | 0.12259 | north | Y | -0.0062211 | 0.30149 | 0.0073368 | 0.16081 | 0.0062211 | North | N | 0.0062211 | 0
13432 | SANDOW_5 | 5 | 581 | -0.2644 | south | Y | -0.39321 | -0.085502 | -0.37965 | -0.22618 | 0.085502 | south | N | 0.085502 | 0
13691 | OAKGROVE | 1 | 855 | 0.08641 | north | Y | -0.042397 | 0.26531 | -0.028839 | 0.12463 | 0.028839 | west | Y | 0.042397 | 11.592
13692 | OAKGROVE | 2 | 855 | 0.08641 | north | Y | -0.042397 | 0.26531 | -0.028839 | 0.12463 | 0.028839 | west | Y | 0.042397 | 11.592
32798 | BRYN_TAM | 1 | 32 | 0.042217 | north | N | -0.08659 | 0.22112 | -0.073032 | 0.080437 | 0.073032 | west | Y | 0.08659 | 0
32883 | BRYN_DNS | 1 | 48 | 0.038598 | north | Y | -0.090209 | 0.2175 | -0.076651 | 0.076818 | 0.076651 | west | Y | 0.090209 | 0.65078
32884 | BRYN_DNS | 1 | 46 | 0.038598 | north | Y | -0.090209 | 0.2175 | -0.076651 | 0.076818 | 0.076651 | west | Y | 0.090209 | 0.62366
32886 | BRYN_ATK | MB | 12 | 0.042306 | north | Y | -0.086501 | 0.22121 | -0.072943 | 0.080526 | 0.072943 | west | Y | 0.086501 | 0
32887 | BRYN_ATK | MB | 51 | 0.042306 | north | Y | -0.086501 | 0.22121 | -0.072943 | 0.080526 | 0.072943 | west | Y | 0.086501 | 0
32888 | BRYN_ATK | 1 | 17 | 0.042306 | north | Y | -0.086501 | 0.22121 | -0.072943 | 0.080526 | 0.072943 | west | Y | 0.086501 | 0.23048
32890 | BRYN_ATK | MB | 22 | 0.042306 | north | Y | -0.086501 | 0.22121 | -0.072943 | 0.080526 | 0.072943 | west | Y | 0.086501 | 0
32891 | BRYN_ATK | MB | 25 | 0.042306 | north | Y | -0.086501 | 0.22121 | -0.072943 | 0.080526 | 0.072943 | west | Y | 0.086501 | 0
32892 | BRYN_DNS | 1 | 105 | 0.038598 | north | Y | -0.090209 | 0.2175 | -0.076651 | 0.076818 | 0.076651 | west | Y | 0.090209 | 1.4236
36998 | RDCNYNG1 | 1 | 84 | 0.11793 | west | Y | -0.010873 | 0.29683 | 0.0026848 | 0.15615 | 0.0026848 | west | N | 0.0026848 | 0
38332 | WDWRDU2 | 1 | 80 | 0.10117 | west | Y | -0.027634 | 0.28007 | -0.014076 | 0.13939 | 0.014076 | west | N | 0.014076 | 0
38437 | TNSRBNMS | 1 | 150 | 0.10106 | west | Y | -0.027743 | 0.27996 | -0.014185 | 0.13928 | 0.014185 | west | N | 0.014185 | 0
38438 | TNSRBNMS | 1 | 150 | 0.10106 | west | Y | -0.027743 | 0.27996 | -0.014185 | 0.13928 | 0.014185 | west | N | 0.014185 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38600 | TNBP_CGN | 5 | 53 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38614 | TNBPAMCG | 4 | 96 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38615 | TNBPAMCG | 1 | 244 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38690 | TNBP_CGN | 3 | 40 | -0.040256 | houston | N | -0.16906 | 0.13864 | -0.15551 | -0.0020364 | 0.0020364 | houston | N | 0.0020364 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.040287 | houston | N | -0.16909 | 0.13861 | -0.15554 | -0.0020674 | 0.0020674 | houston | N | 0.0020674 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.040287 | houston | N | -0.16909 | 0.13861 | -0.15554 | -0.0020674 | 0.0020674 | houston | N | 0.0020674 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.040287 | houston | N | -0.16909 | 0.13861 | -0.15554 | -0.0020674 | 0.0020674 | houston | N | 0.0020674 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.040287 | houston | N | -0.16909 | 0.13861 | -0.15554 | -0.0020674 | 0.0020674 | houston | N | 0.0020674 | 0
39470 | TNDOWCGN | 1 | 32 | -0.040286 | houston | N | -0.16909 | 0.13861 | -0.15554 | -0.0020664 | 0.0020664 | houston | N | 0.0020664 | 0
39480 | TNDOWCGN | 1 | 30 | -0.040286 | houston | N | -0.16909 | 0.13861 | -0.15554 | -0.0020664 | 0.0020664 | houston | N | 0.0020664 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.059279 | houston | N | -0.18809 | 0.11962 | -0.17453 | -0.021059 | 0.021059 | houston | N | 0.021059 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.059279 | houston | N | -0.18809 | 0.11962 | -0.17453 | -0.021059 | 0.021059 | houston | N | 0.021059 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.059279 | houston | N | -0.18809 | 0.11962 | -0.17453 | -0.021059 | 0.021059 | houston | N | 0.021059 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.059279 | houston | N | -0.18809 | 0.11962 | -0.17453 | -0.021059 | 0.021059 | houston | N | 0.021059 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.08641 | north | Y | -0.042397 | 0.26531 | -0.028839 | 0.12463 | 0.028839 | west | Y | 0.042397 | 2.0649
39970 | TNTNPONE | 1 | 153 | 0.08641 | north | Y | -0.042397 | 0.26531 | -0.028839 | 0.12463 | 0.028839 | west | Y | 0.042397 | 2.0744
48500 | APD_GT1_ | 1 | 136 | -0.028675 | houston | N | -0.15748 | 0.15023 | -0.14392 | 0.0095446 | 0.0095446 | houston | N | 0.0095446 | 0
48510 | AK_GT1__ | 1 | 33 | -0.046593 | houston | N | -0.1754 | 0.13231 | -0.16184 | -0.0083734 | 0.0083734 | houston | N | 0.0083734 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.028607 | houston | Y | -0.15741 | 0.15029 | -0.14386 | 0.0096126 | 0.0096126 | houston | N | 0.0096126 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.028607 | houston | Y | -0.15741 | 0.15029 | -0.14386 | 0.0096126 | 0.0096126 | houston | N | 0.0096126 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.028607 | houston | Y | -0.15741 | 0.15029 | -0.14386 | 0.0096126 | 0.0096126 | houston | N | 0.0096126 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.028607 | houston | Y | -0.15741 | 0.15029 | -0.14386 | 0.0096126 | 0.0096126 | houston | N | 0.0096126 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.062332 | houston | N | -0.19114 | 0.11657 | -0.17758 | -0.024112 | 0.024112 | houston | N | 0.024112 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.062332 | houston | N | -0.19114 | 0.11657 | -0.17758 | -0.024112 | 0.024112 | houston | N | 0.024112 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.047757 | houston | N | -0.17656 | 0.13114 | -0.16301 | -0.0095374 | 0.0095374 | houston | N | 0.0095374 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.047757 | houston | N | -0.17656 | 0.13114 | -0.16301 | -0.0095374 | 0.0095374 | houston | N | 0.0095374 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.047757 | houston | N | -0.17656 | 0.13114 | -0.16301 | -0.0095374 | 0.0095374 | houston | N | 0.0095374 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.032999 | houston | N | -0.16181 | 0.1459 | -0.14825 | 0.0052206 | 0.0052206 | houston | N | 0.0052206 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.032999 | houston | N | -0.16181 | 0.1459 | -0.14825 | 0.0052206 | 0.0052206 | houston | N | 0.0052206 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.032999 | houston | N | -0.16181 | 0.1459 | -0.14825 | 0.0052206 | 0.0052206 | houston | N | 0.0052206 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.032999 | houston | N | -0.16181 | 0.1459 | -0.14825 | 0.0052206 | 0.0052206 | houston | N | 0.0052206 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.030178 | houston | N | -0.15899 | 0.14872 | -0.14543 | 0.0080416 | 0.0080416 | houston | N | 0.0080416 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.030178 | houston | N | -0.15899 | 0.14872 | -0.14543 | 0.0080416 | 0.0080416 | houston | N | 0.0080416 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.033849 | houston | N | -0.16266 | 0.14505 | -0.1491 | 0.0043706 | 0.0043706 | houston | N | 0.0043706 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.033849 | houston | N | -0.16266 | 0.14505 | -0.1491 | 0.0043706 | 0.0043706 | houston | N | 0.0043706 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.033849 | houston | N | -0.16266 | 0.14505 | -0.1491 | 0.0043706 | 0.0043706 | houston | N | 0.0043706 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.033849 | houston | N | -0.16266 | 0.14505 | -0.1491 | 0.0043706 | 0.0043706 | houston | N | 0.0043706 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.033849 | houston | N | -0.16266 | 0.14505 | -0.1491 | 0.0043706 | 0.0043706 | houston | N | 0.0043706 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.025067 | houston | Y | -0.15387 | 0.15383 | -0.14032 | 0.013153 | 0.013153 | houston | N | 0.013153 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.026503 | houston | Y | -0.15531 | 0.1524 | -0.14175 | 0.011717 | 0.011717 | houston | N | 0.011717 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.024634 | houston | Y | -0.15344 | 0.15427 | -0.13988 | 0.013586 | 0.013586 | houston | N | 0.013586 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.024634 | houston | Y | -0.15344 | 0.15427 | -0.13988 | 0.013586 | 0.013586 | houston | N | 0.013586 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.024634 | houston | Y | -0.15344 | 0.15427 | -0.13988 | 0.013586 | 0.013586 | houston | N | 0.013586 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.016664 | houston | N | -0.14547 | 0.16224 | -0.13191 | 0.021556 | 0.021556 | houston | N | 0.021556 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.028389 | houston | N | -0.1572 | 0.15051 | -0.14364 | 0.0098306 | 0.0098306 | houston | N | 0.0098306 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.028389 | houston | N | -0.1572 | 0.15051 | -0.14364 | 0.0098306 | 0.0098306 | houston | N | 0.0098306 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.023619 | houston | N | -0.15243 | 0.15528 | -0.13887 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.023619 | houston | N | -0.15243 | 0.15528 | -0.13887 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.023619 | houston | N | -0.15243 | 0.15528 | -0.13887 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.023619 | houston | N | -0.15243 | 0.15528 | -0.13887 | 0.014601 | 0.014601 | houston | N | 0.014601 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.030084 | houston | N | -0.15889 | 0.14882 | -0.14533 | 0.0081356 | 0.0081356 | houston | N | 0.0081356 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.030084 | houston | N | -0.15889 | 0.14882 | -0.14533 | 0.0081356 | 0.0081356 | houston | N | 0.0081356 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.030084 | houston | N | -0.15889 | 0.14882 | -0.14533 | 0.0081356 | 0.0081356 | houston | N | 0.0081356 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.030084 | houston | N | -0.15889 | 0.14882 | -0.14533 | 0.0081356 | 0.0081356 | houston | N | 0.0081356 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.030984 | houston | N | -0.15979 | 0.14792 | -0.14623 | 0.0072356 | 0.0072356 | houston | N | 0.0072356 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.030984 | houston | N | -0.15979 | 0.14792 | -0.14623 | 0.0072356 | 0.0072356 | houston | N | 0.0072356 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.030984 | houston | N | -0.15979 | 0.14792 | -0.14623 | 0.0072356 | 0.0072356 | houston | N | 0.0072356 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.030984 | houston | N | -0.15979 | 0.14792 | -0.14623 | 0.0072356 | 0.0072356 | houston | N | 0.0072356 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.030984 | houston | N | -0.15979 | 0.14792 | -0.14623 | 0.0072356 | 0.0072356 | houston | N | 0.0072356 | 0
48651 | EP_1_2 | 1 | 5 | -0.025143 | houston | N | -0.15395 | 0.15376 | -0.14039 | 0.013077 | 0.013077 | houston | N | 0.013077 | 0
48651 | EP_1_2 | 2 | 21 | -0.025143 | houston | N | -0.15395 | 0.15376 | -0.14039 | 0.013077 | 0.013077 | houston | N | 0.013077 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.039532 | north | N | -0.089275 | 0.21843 | -0.075717 | 0.077752 | 0.075717 | west | Y | 0.089275 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.039532 | north | N | -0.089275 | 0.21843 | -0.075717 | 0.077752 | 0.075717 | west | Y | 0.089275 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.039532 | north | N | -0.089275 | 0.21843 | -0.075717 | 0.077752 | 0.075717 | west | Y | 0.089275 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.039532 | north | N | -0.089275 | 0.21843 | -0.075717 | 0.077752 | 0.075717 | west | Y | 0.089275 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.023267 | houston | Y | -0.15207 | 0.15563 | -0.13852 | 0.014953 | 0.014953 | houston | N | 0.014953 | 0
48691 | GBY_7374 | A | 46 | -0.031736 | houston | Y | -0.16054 | 0.14716 | -0.14699 | 0.0064836 | 0.0064836 | houston | N | 0.0064836 | 0
48691 | GBY_7374 | B | 46 | -0.031736 | houston | Y | -0.16054 | 0.14716 | -0.14699 | 0.0064836 | 0.0064836 | houston | N | 0.0064836 | 0
48692 | GBY_8182 | C | 46 | -0.031736 | houston | Y | -0.16054 | 0.14716 | -0.14699 | 0.0064836 | 0.0064836 | houston | N | 0.0064836 | 0
48692 | GBY_8182 | D | 55 | -0.031736 | houston | Y | -0.16054 | 0.14716 | -0.14699 | 0.0064836 | 0.0064836 | houston | N | 0.0064836 | 0
48693 | GBY_8384 | E | 55 | -0.031736 | houston | Y | -0.16054 | 0.14716 | -0.14699 | 0.0064836 | 0.0064836 | houston | N | 0.0064836 | 0
48693 | GBY_8384 | F | 54 | -0.031736 | houston | Y | -0.16054 | 0.14716 | -0.14699 | 0.0064836 | 0.0064836 | houston | N | 0.0064836 | 0
48721 | LEG_1___ | 1 | 827 | 0.10203 | north | Y | -0.026781 | 0.28093 | -0.013223 | 0.14025 | 0.013223 | west | Y | 0.026781 | 11.2124
48722 | LEG_2___ | 2 | 819 | 0.10203 | north | Y | -0.026781 | 0.28093 | -0.013223 | 0.14025 | 0.013223 | west | Y | 0.026781 | 11.1039
48730 | MNS_GT | 1 | 46.1 | -0.048242 | houston | N | -0.17705 | 0.13066 | -0.16349 | -0.010022 | 0.010022 | houston | N | 0.010022 | 0
48731 | CBE_GT1 | 1 | 76 | -0.08716 | houston | Y | -0.21597 | 0.091741 | -0.20241 | -0.04894 | 0.04894 | houston | N | 0.04894 | 0
48732 | CBE_GT2 | 1 | 76 | -0.08716 | houston | Y | -0.21597 | 0.091741 | -0.20241 | -0.04894 | 0.04894 | houston | N | 0.04894 | 0
48733 | CBE_ST12 | 1 | 105 | -0.08716 | houston | Y | -0.21597 | 0.091741 | -0.20241 | -0.04894 | 0.04894 | houston | N | 0.04894 | 0
48734 | CBE_GT3 | 1 | 74 | -0.08716 | houston | Y | -0.21597 | 0.091741 | -0.20241 | -0.04894 | 0.04894 | houston | N | 0.04894 | 0
48735 | CBE_GT4 | 1 | 74 | -0.08716 | houston | Y | -0.21597 | 0.091741 | -0.20241 | -0.04894 | 0.04894 | houston | N | 0.04894 | 0
48736 | CBE_ST34 | 1 | 102 | -0.08716 | houston | Y | -0.21597 | 0.091741 | -0.20241 | -0.04894 | 0.04894 | houston | N | 0.04894 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.030057 | houston | N | -0.15886 | 0.14884 | -0.14531 | 0.0081626 | 0.0081626 | houston | N | 0.0081626 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.030057 | houston | N | -0.15886 | 0.14884 | -0.14531 | 0.0081626 | 0.0081626 | houston | N | 0.0081626 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.030057 | houston | N | -0.15886 | 0.14884 | -0.14531 | 0.0081626 | 0.0081626 | houston | N | 0.0081626 | 0
48761 | PR_GT1__ | 1 | 35 | -0.030631 | houston | N | -0.15944 | 0.14827 | -0.14588 | 0.0075886 | 0.0075886 | houston | N | 0.0075886 | 0
48772 | PHR_GN2_ | MB | 459 | -0.036016 | houston | Y | -0.16482 | 0.14288 | -0.15127 | 0.0022036 | 0.0022036 | houston | N | 0.0022036 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.025134 | houston | N | -0.15394 | 0.15377 | -0.14038 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.025134 | houston | N | -0.15394 | 0.15377 | -0.14038 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.025134 | houston | N | -0.15394 | 0.15377 | -0.14038 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.025134 | houston | N | -0.15394 | 0.15377 | -0.14038 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.025134 | houston | N | -0.15394 | 0.15377 | -0.14038 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.025134 | houston | N | -0.15394 | 0.15377 | -0.14038 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.025134 | houston | N | -0.15394 | 0.15377 | -0.14038 | 0.013086 | 0.013086 | houston | N | 0.013086 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.016664 | houston | N | -0.14547 | 0.16224 | -0.13191 | 0.021556 | 0.021556 | houston | N | 0.021556 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.016664 | houston | N | -0.14547 | 0.16224 | -0.13191 | 0.021556 | 0.021556 | houston | N | 0.021556 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.016664 | houston | N | -0.14547 | 0.16224 | -0.13191 | 0.021556 | 0.021556 | houston | N | 0.021556 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.016664 | houston | N | -0.14547 | 0.16224 | -0.13191 | 0.021556 | 0.021556 | houston | N | 0.021556 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.024805 | houston | N | -0.15361 | 0.1541 | -0.14005 | 0.013415 | 0.013415 | houston | N | 0.013415 | 0
48820 | SHELLG1_ | 1 | 71 | -0.029523 | houston | N | -0.15833 | 0.14938 | -0.14477 | 0.0086966 | 0.0086966 | houston | N | 0.0086966 | 0
48821 | SHELLG2 | 2 | 72 | -0.029523 | houston | N | -0.15833 | 0.14938 | -0.14477 | 0.0086966 | 0.0086966 | houston | N | 0.0086966 | 0
48822 | SHELLG3_ | 1 | 39 | -0.029523 | houston | N | -0.15833 | 0.14938 | -0.14477 | 0.0086966 | 0.0086966 | houston | N | 0.0086966 | 0
48822 | SHELLG3_ | 2 | 30 | -0.029523 | houston | N | -0.15833 | 0.14938 | -0.14477 | 0.0086966 | 0.0086966 | houston | N | 0.0086966 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.03142 | houston | N | -0.16023 | 0.14748 | -0.14667 | 0.0067996 | 0.0067996 | houston | N | 0.0067996 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.03142 | houston | N | -0.16023 | 0.14748 | -0.14667 | 0.0067996 | 0.0067996 | houston | N | 0.0067996 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.030091 | houston | N | -0.1589 | 0.14881 | -0.14534 | 0.0081286 | 0.0081286 | houston | N | 0.0081286 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.030201 | houston | Y | -0.15901 | 0.1487 | -0.14545 | 0.0080186 | 0.0080186 | houston | N | 0.0080186 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.030231 | houston | Y | -0.15904 | 0.14867 | -0.14548 | 0.0079886 | 0.0079886 | houston | N | 0.0079886 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.0301 | houston | Y | -0.15891 | 0.1488 | -0.14535 | 0.0081196 | 0.0081196 | houston | N | 0.0081196 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.03007 | houston | Y | -0.15888 | 0.14883 | -0.14532 | 0.0081496 | 0.0081496 | houston | N | 0.0081496 | 0
48855 | SRB_GT21 | B2 | 12 | -0.030252 | houston | Y | -0.15906 | 0.14865 | -0.1455 | 0.0079676 | 0.0079676 | houston | N | 0.0079676 | 0
48855 | SRB_GT21 | MB | 18 | -0.030252 | houston | Y | -0.15906 | 0.14865 | -0.1455 | 0.0079676 | 0.0079676 | houston | N | 0.0079676 | 0
48865 | TECO_GT1 | 1 | 50 | -0.037875 | houston | Y | -0.16668 | 0.14103 | -0.15312 | 0.0003446 | 0.0003446 | houston | N | 0.0003446 | 0
48873 | THW_ST3_ | 3 | 104 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48874 | THW_ST4_ | 4 | 104 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48875 | THW_3132 | A | 54 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48875 | THW_3132 | B | 53 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48877 | THW_3334 | C | 54 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48877 | THW_3334 | D | 57 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48879 | THW_4142 | E | 54 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48879 | THW_4142 | F | 54 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48881 | THW_4344 | G | 58 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48881 | THW_4344 | H | 58 | -0.027028 | houston | Y | -0.15584 | 0.15187 | -0.14228 | 0.011192 | 0.011192 | houston | N | 0.011192 | 0
48883 | THW_GT1_ | B2 | 12 | -0.025709 | houston | Y | -0.15452 | 0.15319 | -0.14096 | 0.012511 | 0.012511 | houston | N | 0.012511 | 0
48885 | THW_5152 | A | 56 | -0.022649 | houston | Y | -0.15146 | 0.15625 | -0.1379 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48885 | THW_5152 | B | 59 | -0.022649 | houston | Y | -0.15146 | 0.15625 | -0.1379 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48886 | THW_5354 | C | 56 | -0.022649 | houston | Y | -0.15146 | 0.15625 | -0.1379 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48886 | THW_5354 | D | 56 | -0.022649 | houston | Y | -0.15146 | 0.15625 | -0.1379 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48887 | THW_5556 | E | 59 | -0.022649 | houston | Y | -0.15146 | 0.15625 | -0.1379 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48887 | THW_5556 | F | 56 | -0.022649 | houston | Y | -0.15146 | 0.15625 | -0.1379 | 0.015571 | 0.015571 | houston | N | 0.015571 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.0821 | houston | Y | -0.21091 | 0.096801 | -0.19735 | -0.04388 | 0.04388 | houston | N | 0.04388 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.046098 | houston | Y | -0.17491 | 0.1328 | -0.16135 | -0.0078784 | 0.0078784 | houston | N | 0.0078784 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.046098 | houston | Y | -0.17491 | 0.1328 | -0.16135 | -0.0078784 | 0.0078784 | houston | N | 0.0078784 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.046098 | houston | Y | -0.17491 | 0.1328 | -0.16135 | -0.0078784 | 0.0078784 | houston | N | 0.0078784 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.046098 | houston | Y | -0.17491 | 0.1328 | -0.16135 | -0.0078784 | 0.0078784 | houston | N | 0.0078784 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.046098 | houston | N | -0.17491 | 0.1328 | -0.16135 | -0.0078784 | 0.0078784 | houston | N | 0.0078784 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.04785 | houston | Y | -0.17666 | 0.13105 | -0.1631 | -0.0096304 | 0.0096304 | houston | N | 0.0096304 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.04785 | houston | Y | -0.17666 | 0.13105 | -0.1631 | -0.0096304 | 0.0096304 | houston | N | 0.0096304 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.04785 | houston | Y | -0.17666 | 0.13105 | -0.1631 | -0.0096304 | 0.0096304 | houston | N | 0.0096304 | 0
48929 | WAPGT21_ | B1 | 13 | -0.046098 | houston | Y | -0.17491 | 0.1328 | -0.16135 | -0.0078784 | 0.0078784 | houston | N | 0.0078784 | 0
48940 | WARVUE_G | G1 | 12 | -0.025107 | houston | Y | -0.15391 | 0.15379 | -0.14036 | 0.013113 | 0.013113 | houston | N | 0.013113 | 0
49803 | EXN_15GT | 1 | 34 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49826 | EXN938GT | 5 | 45.9 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49828 | EXN941GT | 10 | 17.7 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49829 | EXN942GT | 11 | 20.4 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49830 | EXN943GT | 12 | 19.9 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49831 | EXN944GT | 13 | 35 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49832 | EXN945GT | 9 | 18 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49837 | EXN_GT | 4 | 85.4 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49838 | EXN_14GT | 14 | 148 | -0.026154 | houston | N | -0.15496 | 0.15275 | -0.1414 | 0.012066 | 0.012066 | houston | N | 0.012066 | 0
49851 | DOW17000 | 37 | 62 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49858 | DOW38100 | 31 | 71.4 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49859 | DOW38200 | 33 | 45 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49860 | DOW38300 | 32 | 101 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49862 | DOW39100 | 36 | 86 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49863 | DOW39200 | 35 | 88 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49865 | DOW41000 | 41 | 50 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49866 | DOW42000 | 42 | 18 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49869 | DOW49000 | 45 | 94 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49870 | DOW61000 | 61 | 70 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49871 | DOW62000 | 62 | 63 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49872 | DOW63000 | 63 | 72 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49873 | DOW64000 | 64 | 64.8 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49876 | DOW65000 | 65 | 101 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49877 | DOW66000 | 66 | 97 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49878 | DOW67000 | 67 | 103 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49882 | DOW81000 | 81 | 76 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49884 | DOW82000 | 82 | 80 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49885 | DOW83000 | 83 | 80 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
49886 | DOW84000 | 84 | 171 | -0.066194 | houston | N | -0.195 | 0.11271 | -0.18144 | -0.027974 | 0.027974 | houston | N | 0.027974 | 0
58909 | PEARSALL | 1 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58909 | PEARSALL | 2 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58909 | PEARSALL | 3 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58909 | PEARSALL | 4 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58909 | PEARSALL | 5 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58909 | PEARSALL | 6 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58919 | PEARSALL | 1 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58919 | PEARSALL | 2 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58919 | PEARSALL | 3 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58919 | PEARSALL | 4 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58919 | PEARSALL | 5 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58919 | PEARSALL | 6 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58929 | PEARSALL | 1 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58929 | PEARSALL | 2 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58929 | PEARSALL | 3 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58929 | PEARSALL | 4 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58929 | PEARSALL | 5 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58929 | PEARSALL | 6 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58949 | PEARSALL | 1 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58949 | PEARSALL | 2 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58949 | PEARSALL | 3 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58949 | PEARSALL | 4 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58949 | PEARSALL | 5 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
58949 | PEARSALL | 6 | 8.4 | -0.14962 | south | Y | -0.27843 | 0.029279 | -0.26487 | -0.1114 | 0.029279 | south | N | 0.029279 | 0
60000 | DSKY2 | 1 | 76.5 | 0.096032 | west | Y | -0.032775 | 0.27493 | -0.019217 | 0.13425 | 0.019217 | west | N | 0.019217 | 0
60003 | KING_NE1 | 1 | 80 | 0.10138 | west | Y | -0.027423 | 0.28028 | -0.013865 | 0.1396 | 0.013865 | west | N | 0.013865 | 0
60005 | KING_SE1 | 1 | 40 | 0.10138 | west | Y | -0.027423 | 0.28028 | -0.013865 | 0.1396 | 0.013865 | west | N | 0.013865 | 0
60007 | KING_SW1 | 1 | 80 | 0.10224 | west | Y | -0.026565 | 0.28114 | -0.013007 | 0.14046 | 0.013007 | west | N | 0.013007 | 0
60016 | WOODWRD1 | 1 | 80 | 0.1012 | west | Y | -0.027609 | 0.2801 | -0.014051 | 0.13942 | 0.014051 | west | N | 0.014051 | 0
60017 | ORNNWP1 | 1 | 80 | 0.096776 | west | Y | -0.032031 | 0.27568 | -0.018473 | 0.135 | 0.018473 | west | N | 0.018473 | 0
60018 | DSKY1 | 1 | 84 | 0.095329 | west | Y | -0.033478 | 0.27423 | -0.01992 | 0.13355 | 0.01992 | west | N | 0.01992 | 0
60019 | KING_NW1 | 1 | 80 | 0.10224 | west | Y | -0.026565 | 0.28114 | -0.013007 | 0.14046 | 0.013007 | west | N | 0.013007 | 0
60057 | CALLAHAN | 1 | 114 | -0.17872 | south | Y | -0.30753 | 0.00018095 | -0.29397 | -0.1405 | 0.00018095 | south | N | 0.00018095 | 0
60058 | BUFF_GAP | 1 | 120 | 0.11632 | west | Y | -0.012486 | 0.29522 | 0.0010718 | 0.15454 | 0.0010718 | west | N | 0.0010718 | 0
60060 | CIRELLO | 1 | 233 | 0.11632 | west | Y | -0.012486 | 0.29522 | 0.0010718 | 0.15454 | 0.0010718 | west | N | 0.0010718 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.11632 | west | Y | -0.012486 | 0.29522 | 0.0010718 | 0.15454 | 0.0010718 | west | N | 0.0010718 | 0
60066 | H_HOLLOW | 1 | 222 | -0.17872 | south | Y | -0.30753 | 0.00018095 | -0.29397 | -0.1405 | 0.00018095 | south | N | 0.00018095 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.17872 | south | Y | -0.30753 | 0.00018095 | -0.29397 | -0.1405 | 0.00018095 | south | N | 0.00018095 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.17872 | south | Y | -0.30753 | 0.00018095 | -0.29397 | -0.1405 | 0.00018095 | south | N | 0.00018095 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.17872 | south | Y | -0.30753 | 0.00018095 | -0.29397 | -0.1405 | 0.00018095 | south | N | 0.00018095 | 0
60074 | HORSH5 | 1 | 100 | -0.17872 | south | Y | -0.30753 | 0.00018095 | -0.29397 | -0.1405 | 0.00018095 | south | N | 0.00018095 | 0
60081 | WHRLWIND | 1 | 60 | 0.121 | west | Y | -0.0078121 | 0.2999 | 0.0057458 | 0.15921 | 0.0057458 | west | N | 0.0057458 | 0
60201 | RIO DRCS | F | 0 | -0.091897 | south | N | -0.2207 | 0.087004 | -0.20715 | -0.053677 | 0.053677 | houston | Y | 0.087004 | 0
60202 | FRIEND_R | F | 0 | 0.072271 | west | N | -0.056536 | 0.25117 | -0.042978 | 0.11049 | 0.042978 | west | N | 0.042978 | 0
60203 | PRES0A | BT | 4.8 | 0.10544 | west | N | -0.023369 | 0.28434 | -0.0098112 | 0.14366 | 0.0098112 | west | N | 0.0098112 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.1189 | west | Y | -0.0099091 | 0.2978 | 0.0036488 | 0.15712 | 0.0036488 | west | N | 0.0036488 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.1189 | west | Y | -0.0099091 | 0.2978 | 0.0036488 | 0.15712 | 0.0036488 | west | N | 0.0036488 | 0
71057 | L_SWEETW | W1 | 135 | 0.1189 | west | Y | -0.0099091 | 0.2978 | 0.0036488 | 0.15712 | 0.0036488 | west | N | 0.0036488 | 0
71059 | L_SWEETW | W1 | 119 | 0.1189 | west | Y | -0.0099091 | 0.2978 | 0.0036488 | 0.15712 | 0.0036488 | west | N | 0.0036488 | 0
71060 | L_SWEETW | W1 | 105 | 0.1189 | west | Y | -0.0099091 | 0.2978 | 0.0036488 | 0.15712 | 0.0036488 | west | N | 0.0036488 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.1189 | west | Y | -0.0099091 | 0.2978 | 0.0036488 | 0.15712 | 0.0036488 | west | N | 0.0036488 | 0
76031 | L_GASCCR | W1 | 150 | 0.115 | west | Y | -0.013811 | 0.2939 | -0.00025318 | 0.15322 | 0.00025318 | west | N | 0.00025318 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.11449 | west | Y | -0.014322 | 0.29339 | -0.00076418 | 0.1527 | 0.00076418 | west | N | 0.00076418 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.11449 | west | Y | -0.014322 | 0.29339 | -0.00076418 | 0.1527 | 0.00076418 | west | N | 0.00076418 | 0
76096 | L_CAPRSI | W1 | 186 | 0.11449 | west | Y | -0.014322 | 0.29339 | -0.00076418 | 0.1527 | 0.00076418 | west | N | 0.00076418 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.11449 | west | Y | -0.014322 | 0.29339 | -0.00076418 | 0.1527 | 0.00076418 | west | N | 0.00076418 | 0
80003 | MILHWYS | F | 0 | -0.14239 | south | N | -0.2712 | 0.036512 | -0.25764 | -0.10417 | 0.036512 | south | N | 0.036512 | 0
80010 | EPLVT1 | F | 0 | -0.10883 | south | N | -0.23764 | 0.07007 | -0.22408 | -0.070611 | 0.07007 | south | N | 0.07007 | 0
80012 | LAR | F | 0 | -0.15025 | south | N | -0.27906 | 0.028646 | -0.2655 | -0.11204 | 0.028646 | south | N | 0.028646 | 0
80051 | FORPVCM0 | 8 | 28 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
80053 | FOR69CG0 | 10 | 74 | -0.12943 | south | N | -0.25824 | 0.04947 | -0.24468 | -0.091211 | 0.04947 | south | N | 0.04947 | 0
80080 | GWINDT11 | 1 | 94 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80080 | GWINDT11 | 2 | 41 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80080 | GWINDT11 | 3 | 38 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80080 | GWINDT11 | 4 | 19 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80081 | GWINDT21 | 1 | 94 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80081 | GWINDT21 | 2 | 36 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80081 | GWINDT21 | 3 | 43 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80081 | GWINDT21 | 4 | 22 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80137 | CSDR89 | 8 | 39 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
80137 | CSDR89 | 9 | 15 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
80138 | CSDR7 | 7 | 7 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
80139 | CSDR56 | 5 | 15 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
80139 | CSDR56 | 6 | 39 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
80140 | CSDR11 | 11 | 39 | -0.13433 | south | N | -0.26313 | 0.044574 | -0.24958 | -0.096107 | 0.044574 | south | N | 0.044574 | 0
80180 | PNSCALT1 | 1 | 148 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80180 | PNSCALT1 | 2 | 50 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80181 | PNSCALT2 | 1 | 55 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80181 | PNSCALT2 | 2 | 50 | -0.14229 | south | Y | -0.2711 | 0.036611 | -0.25754 | -0.10407 | 0.036611 | south | N | 0.036611 | 0
80223 | REYSHR G | 1 | 12 | -0.13937 | south | N | -0.26818 | 0.039529 | -0.25462 | -0.10115 | 0.039529 | south | N | 0.039529 | 0
80224 | VISTRONG | 1 | 15 | -0.13589 | south | N | -0.2647 | 0.043006 | -0.25114 | -0.097675 | 0.043006 | south | N | 0.043006 | 0
80225 | VISTRONG | 2 | 23 | -0.13589 | south | N | -0.2647 | 0.043006 | -0.25114 | -0.097675 | 0.043006 | south | N | 0.043006 | 0
80226 | ALCOA G | 1 | 48 | -0.13058 | south | N | -0.25939 | 0.048317 | -0.24583 | -0.092364 | 0.048317 | south | N | 0.048317 | 0
80227 | AIRCO G | 1 | 8 | -0.13488 | south | N | -0.26369 | 0.044017 | -0.25013 | -0.096664 | 0.044017 | south | N | 0.044017 | 0
80261 | NBEC81A | 1 | 180 | -0.14089 | south | Y | -0.2697 | 0.038009 | -0.25614 | -0.10267 | 0.038009 | south | N | 0.038009 | 0
80262 | NBEC91A | 1 | 180 | -0.14085 | south | Y | -0.26965 | 0.038054 | -0.2561 | -0.10263 | 0.038054 | south | N | 0.038054 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.14117 | south | Y | -0.26998 | 0.037726 | -0.25642 | -0.10296 | 0.037726 | south | N | 0.037726 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.14117 | south | Y | -0.26998 | 0.037726 | -0.25642 | -0.10296 | 0.037726 | south | N | 0.037726 | 0
80265 | LARECU40 | 4 | 100 | -0.15027 | south | Y | -0.27908 | 0.028633 | -0.26552 | -0.11205 | 0.028633 | south | N | 0.028633 | 0
80266 | LARECU50 | 5 | 100 | -0.15027 | south | Y | -0.27908 | 0.028633 | -0.26552 | -0.11205 | 0.028633 | south | N | 0.028633 | 0
80291 | PAPALOTE | 1 | 25 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
80291 | PAPALOTE | 2 | 25 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
80291 | PAPALOTE | 3 | 25 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
80291 | PAPALOTE | 4 | 16 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
80294 | PAPALOTE | 5 | 25 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
80294 | PAPALOTE | 6 | 25 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
80294 | PAPALOTE | 7 | 25 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
80294 | PAPALOTE | 8 | 15 | -0.13995 | south | Y | -0.26876 | 0.038947 | -0.2552 | -0.10173 | 0.038947 | south | N | 0.038947 | 0
86104 | CID-138 | EQ | 0 | -0.15027 | south | N | -0.27908 | 0.028633 | -0.26552 | -0.11205 | 0.028633 | south | N | 0.028633 | 0
86105 | CID-230 | EQ | 500 | -0.15027 | south | N | -0.27908 | 0.028633 | -0.26552 | -0.11205 | 0.028633 | south | N | 0.028633 | 0
86106 | CUF-230 | EQ | 500 | -0.15027 | south | N | -0.27908 | 0.028633 | -0.26552 | -0.11205 | 0.028633 | south | N | 0.028633 | 0
86107 | CUF-138 | EQ | 0 | -0.15027 | south | N | -0.27908 | 0.028633 | -0.26552 | -0.11205 | 0.028633 | south | N | 0.028633 | 0
88198 | BEEVILLE | F | 0 | -0.14897 | south | N | -0.27777 | 0.029934 | -0.26422 | -0.11075 | 0.029934 | south | N | 0.029934 | 0
88253 | HAMILTON | F | 0 | -0.082417 | south | N | -0.21122 | 0.096484 | -0.19767 | -0.044197 | 0.044197 | houston | Y | 0.096484 | 0
88299 | ZAPATA | F | 0 | -0.14642 | south | N | -0.27523 | 0.032477 | -0.26167 | -0.1082 | 0.032477 | south | N | 0.032477 | 0
88508 | FALFURRI | F | 0 | -0.14475 | south | N | -0.27356 | 0.034153 | -0.26 | -0.10653 | 0.034153 | south | N | 0.034153 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0 | Weighted Shift Factors
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0 | South | -0.1789
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0 | North | 0.13885
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0 |  | -0.31775
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.1789 | 0 | 0 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8829 | 0 | 0.16224 | 0 | 0 | 0 | Line Rating | 1239.6
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5996 | 0 | 0.16224 | 0 | 0 | 0 | Conc Gen | 2023
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5663 | 0 | 0.16224 | 0 | 0 | 0 | Weighted Imp. | 312.9647
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5663 | 0 | 0.16224 | 0 | 0 | 0 | PTDF | 0.1547
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016664 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6996 | 0 | 0.16224 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501 | 56 | 8.7501 | Concentration | -0.48687
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3363 | 59 | 0.15625 | 9.2189 | 115 | 17.969
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501 | 171 | 26.7191
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501 | 227 | 35.4692
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3363 | 59 | 0.15625 | 9.2189 | 286 | 44.6881
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501 | 342 | 53.4382
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.023267 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.2603 | 398 | 0.15563 | 61.9423 | 740 | 115.3805
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8452 | 0 | 0.15528 | 0 | 740 | 115.3805
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8121 | 0 | 0.15528 | 0 | 740 | 115.3805
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7531 | 0 | 0.15528 | 0 | 740 | 115.3805
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3582 | 0 | 0.15528 | 0 | 740 | 115.3805
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.237 | 172 | 0.15427 | 26.5339 | 912 | 141.9144
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.237 | 172 | 0.15427 | 26.5339 | 1084 | 168.4483
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.237 | 172 | 0.15427 | 26.5339 | 1256 | 194.9822
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.024805 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8944 | 0 | 0.1541 | 0 | 1256 | 194.9822
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.025067 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -18.6248 | 743 | 0.15383 | 114.2986 | 1999 | 309.2808
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.025107 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.30128 | 12 | 0.15379 | 1.8455 | 2011 | 311.1264
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6337 | 0 | 0.15377 | 0 | 2011 | 311.1264
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6588 | 0 | 0.15377 | 0 | 2011 | 311.1264
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7594 | 0 | 0.15377 | 0 | 2011 | 311.1264
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5834 | 0 | 0.15377 | 0 | 2011 | 311.1264
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5583 | 0 | 0.15377 | 0 | 2011 | 311.1264
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6139 | 0 | 0.15377 | 0 | 2011 | 311.1264
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4829 | 0 | 0.15377 | 0 | 2011 | 311.1264
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.025143 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12571 | 0 | 0.15376 | 0 | 2011 | 311.1264
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.025143 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.528 | 0 | 0.15376 | 0 | 2011 | 311.1264
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.025709 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30851 | 12 | 0.15319 | 1.8383 | 2023 | 312.9647
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88924 | 0 | 0.15275 | 0 | 2023 | 312.9647
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90754 | 0 | 0.15275 | 0 | 2023 | 312.9647
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85524 | 0 | 0.15275 | 0 | 2023 | 312.9647
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2005 | 0 | 0.15275 | 0 | 2023 | 312.9647
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46293 | 0 | 0.15275 | 0 | 2023 | 312.9647
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53354 | 0 | 0.15275 | 0 | 2023 | 312.9647
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52046 | 0 | 0.15275 | 0 | 2023 | 312.9647
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.91539 | 0 | 0.15275 | 0 | 2023 | 312.9647
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47077 | 0 | 0.15275 | 0 | 2023 | 312.9647
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2336 | 0 | 0.15275 | 0 | 2023 | 312.9647
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8708 | 0 | 0.15275 | 0 | 2023 | 312.9647
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.026503 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -19.4797 | 735 | 0.1524 | 112.0125
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8109 | 104 | 0.15187 | 15.7948
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8109 | 104 | 0.15187 | 15.7948
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4325 | 53 | 0.15187 | 8.0493
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5406 | 57 | 0.15187 | 8.6568
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5676 | 58 | 0.15187 | 8.8086
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5676 | 58 | 0.15187 | 8.8086
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.028389 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9113 | 0 | 0.15051 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.028389 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8325 | 0 | 0.15051 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2015 | 42 | 0.15029 | 6.3123
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2015 | 42 | 0.15029 | 6.3123
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0871 | 38 | 0.15029 | 5.7112
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0871 | 38 | 0.15029 | 5.7112
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.028675 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8998 | 0 | 0.15023 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0961 | 0 | 0.14938 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1257 | 0 | 0.14938 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1514 | 0 | 0.14938 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88569 | 0 | 0.14938 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.4103 | 0 | 0.14884 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.767 | 0 | 0.14884 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7189 | 0 | 0.14884 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.03007 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.856 | 228 | 0.14883 | 33.9335
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9254 | 0 | 0.14882 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9013 | 0 | 0.14882 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4849 | 0 | 0.14882 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2142 | 0 | 0.14882 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.030091 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48747 | 0 | 0.14881 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.0301 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.4113 | 213 | 0.1488 | 31.6946
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.030178 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4965 | 0 | 0.14872 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.030178 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9646 | 0 | 0.14872 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.030201 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9832 | 165 | 0.1487 | 24.5355
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.030231 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.109 | 169 | 0.14867 | 25.1252
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.030252 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36302 | 12 | 0.14865 | 1.7838
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.030252 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14865 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.030631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0721 | 0 | 0.14827 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0566 | 0 | 0.14792 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8676 | 0 | 0.14792 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.88 | 0 | 0.14792 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8645 | 0 | 0.14792 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.3347 | 0 | 0.14792 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03142 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4508 | 0 | 0.14748 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03142 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5136 | 0 | 0.14748 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4599 | 46 | 0.14716 | 6.7696
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4599 | 46 | 0.14716 | 6.7696
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4599 | 46 | 0.14716 | 6.7696
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7455 | 55 | 0.14716 | 8.0941
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7455 | 55 | 0.14716 | 8.0941
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7137 | 54 | 0.14716 | 7.9469
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1449 | 0 | 0.1459 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9799 | 0 | 0.1459 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1449 | 0 | 0.1459 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1449 | 0 | 0.1459 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0803 | 0 | 0.14505 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9652 | 0 | 0.14505 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9449 | 0 | 0.14505 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8448 | 0 | 0.14505 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41296 | 0 | 0.14505 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.036016 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14288 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.037875 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8938 | 50 | 0.14103 | 7.0513
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8501 | 0 | 0.13864 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6851 | 0 | 0.13864 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1336 | 0 | 0.13864 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1672 | 0 | 0.13864 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1793 | 0 | 0.13864 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.131 | 0 | 0.13864 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8646 | 0 | 0.13864 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.8225 | 0 | 0.13864 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6102 | 0 | 0.13864 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.040286 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2892 | 0 | 0.13861 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.040286 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2086 | 0 | 0.13861 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0408 | 0 | 0.13861 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7427 | 0 | 0.13861 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1375 | 0 | 0.13861 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1093 | 0 | 0.13861 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.4218 | 161 | 0.1328 | 21.3813
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.6523 | 166 | 0.1328 | 22.0453
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.4323 | 248 | 0.1328 | 32.9351
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.046098 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -25.1695 | 546 | 0.1328 | 72.5104
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.046098 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -29.641 | 0 | 0.1328 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.046098 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59927 | 13 | 0.1328 | 1.7264
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.046593 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5376 | 0 | 0.13231 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.7844 | 0 | 0.13114 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.7844 | 0 | 0.13114 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.7005 | 0 | 0.13114 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -31.1503 | 651 | 0.13105 | 85.3142
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -26.9874 | 564 | 0.13105 | 73.9127
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -28.71 | 600 | 0.13105 | 78.6306
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.048242 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.224 | 0 | 0.13066 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.58 | 0 | 0.11962 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.58 | 0 | 0.11962 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0542 | 0 | 0.11962 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.4911 | 0 | 0.11962 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.062332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4256 | 0 | 0.11657 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.062332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62332 | 0 | 0.11657 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.104 | 0 | 0.11271 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7263 | 0 | 0.11271 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9787 | 0 | 0.11271 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6856 | 0 | 0.11271 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6927 | 0 | 0.11271 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8251 | 0 | 0.11271 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3097 | 0 | 0.11271 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1915 | 0 | 0.11271 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2222 | 0 | 0.11271 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6336 | 0 | 0.11271 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1702 | 0 | 0.11271 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.766 | 0 | 0.11271 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2894 | 0 | 0.11271 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6856 | 0 | 0.11271 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4208 | 0 | 0.11271 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.818 | 0 | 0.11271 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0307 | 0 | 0.11271 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2955 | 0 | 0.11271 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2955 | 0 | 0.11271 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3192 | 0 | 0.11271 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.0821 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.4186 | 66 | 0.096801 | 6.3889
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.082417 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.7198 | 0 | 0.096484 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.082417 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0604 | 0 | 0.096484 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.082417 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.096484 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6242 | 76 | 0.091741 | 6.9723
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6242 | 76 | 0.091741 | 6.9723
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1518 | 105 | 0.091741 | 9.6328
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4498 | 74 | 0.091741 | 6.7888
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4498 | 74 | 0.091741 | 6.7888
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.8903 | 102 | 0.091741 | 9.3576
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.087766 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -116.9921 | 0 | 0.091135 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.087766 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -116.5532 | 0 | 0.091135 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.2147 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.075846 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.2147 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 168.9673 | 787 | 0.075846 | 59.6911
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.10385 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62308 | 0 | 0.075054 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.10883 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.07007 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.225 | 0 | 0.04947 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.4839 | 0 | 0.04947 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.225 | 0 | 0.04947 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.3545 | 0 | 0.04947 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.1474 | 0 | 0.04947 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2358 | 0 | 0.04947 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9538 | 0 | 0.04947 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6241 | 0 | 0.04947 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6432 | 0 | 0.04947 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.5779 | 0 | 0.04947 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13058 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.268 | 0 | 0.048317 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.18641 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.047557 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.18641 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.047557 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.18349 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 46.7897 | 255 | 0.044637 | 11.3825
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.18349 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 27.3399 | 149 | 0.044637 | 6.651
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.18349 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 28.0738 | 153 | 0.044637 | 6.8295
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7612 | 0 | 0.044574 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.94029 | 0 | 0.044574 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2388 | 0 | 0.044574 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0149 | 0 | 0.044574 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.94029 | 0 | 0.044574 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0149 | 0 | 0.044574 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2388 | 0 | 0.044574 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2388 | 0 | 0.044574 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.13488 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0791 | 0 | 0.044017 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.13589 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0384 | 0 | 0.043006 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.13589 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1256 | 0 | 0.043006 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.1371 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.0162 | 22 | 0.0418 | 0.9196
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5081 | 11 | 0.0418 | 0.4598
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5081 | 11 | 0.0418 | 0.4598
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6001 | 47.7 | 0.040534 | 1.9335
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1611 | 37.3 | 0.040534 | 1.5119
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3649 | 46 | 0.040534 | 1.8646
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6416 | 48 | 0.040534 | 1.9456
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.13866 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.122 | 0 | 0.040244 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.0208 | 0 | 0.039529 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.3239 | 0 | 0.039529 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -13.9372 | 0 | 0.039529 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.2089 | 0 | 0.039529 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.4877 | 0 | 0.039529 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -17.7002 | 0 | 0.039529 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.13937 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6725 | 0 | 0.039529 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 25 | 0.038947 | 0.97367
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 25 | 0.038947 | 0.97367
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 25 | 0.038947 | 0.97367
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2393 | 16 | 0.038947 | 0.62315
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 25 | 0.038947 | 0.97367
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 25 | 0.038947 | 0.97367
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 25 | 0.038947 | 0.97367
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0993 | 15 | 0.038947 | 0.5842
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14023 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.1938 | 144 | 0.038666 | 5.5679
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14023 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.3642 | 188 | 0.038666 | 7.2692
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.14085 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -47.3246 | 336 | 0.038054 | 12.7861
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14085 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.3525 | 180 | 0.038054 | 6.8497
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.8901 | 0 | 0.038037 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.9324 | 0 | 0.038037 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.5522 | 0 | 0.038037 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14089 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.3606 | 180 | 0.038009 | 6.8416
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.14117 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.1525 | 334 | 0.037726 | 12.6005
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.14117 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.9995 | 340 | 0.037726 | 12.8268
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.14117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.4115 | 180 | 0.037726 | 6.7907
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.14117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.4115 | 180 | 0.037726 | 6.7907
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.14123 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5307 | 0 | 0.037675 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.14123 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5307 | 0 | 0.037675 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.14137 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.372 | 0 | 0.037533 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.14138 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3723 | 0 | 0.037524 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.14206 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.1198 | 0 | 0.036839 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.3753 | 94 | 0.036611 | 3.4414
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8339 | 41 | 0.036611 | 1.501
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.407 | 38 | 0.036611 | 1.3912
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7035 | 19 | 0.036611 | 0.69561
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.3753 | 94 | 0.036611 | 3.4414
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.1224 | 36 | 0.036611 | 1.318
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.1185 | 43 | 0.036611 | 1.5743
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1304 | 22 | 0.036611 | 0.80544
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.0589 | 148 | 0.036611 | 5.4184
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1145 | 50 | 0.036611 | 1.8305
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.8259 | 55 | 0.036611 | 2.0136
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1145 | 50 | 0.036611 | 1.8305
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.4107 | 38 | 0.036513 | 1.3875
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7481 | 19.3 | 0.036513 | 0.7047
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1358 | 15 | 0.036513 | 0.54769
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.14239 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6922 | 47 | 0.036513 | 1.7161
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.14239 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.036512 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.5438 | 144 | 0.036236 | 5.218
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.5438 | 144 | 0.036236 | 5.218
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.3957 | 171 | 0.036236 | 6.1963
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.5325 | 207 | 0.036232 | 7.5
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -30.9164 | 216.7 | 0.036232 | 7.8515
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5259 | 242 | 0.036232 | 8.7681
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.9428 | 146.5 | 0.035947 | 5.2662
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.1429 | 147.9 | 0.035947 | 5.3166
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.731 | 173 | 0.035947 | 6.2188
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7367 | 0 | 0.034174 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.592 | 0 | 0.034174 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7367 | 0 | 0.034174 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.14475 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.034153 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.14642 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.032477 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -92.4643 | 629 | 0.031899 | 20.0644
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.14897 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.029934 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.15025 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028646 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.15027 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.0268 | 100 | 0.028633 | 2.8633
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.15027 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.0268 | 100 | 0.028633 | 2.8633
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15134 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.6321 | 24 | 0.027564 | 0.66153
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15134 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.6321 | 24 | 0.027564 | 0.66153
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.15134 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.4808 | 23 | 0.027564 | 0.63397
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.16155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2329 | 150 | 0.022701 | 3.4052
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.16155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9242 | 80 | 0.022701 | 1.8161
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.16051 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -63.5628 | 396 | 0.018389 | 7.282
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.15659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3489 | 0 | 0.017742 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.15659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3489 | 0 | 0.017742 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.16911 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0293 | 0 | 0.0097929 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.16971 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -92.6617 | 546 | 0.0091909 | 5.0183
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.16971 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -127.2825 | 750 | 0.0091909 | 6.8932
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.16991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.8548 | 58 | 0.0089909 | 0.52147
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.16991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.122 | 89 | 0.0089909 | 0.80019
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.476 | 44 | 0.0089909 | 0.3956
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.476 | 44 | 0.0089909 | 0.3956
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3061 | 43 | 0.0089909 | 0.38661
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.646 | 45 | 0.0089909 | 0.40459
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.4352 | 155 | 0.0083509 | 1.2944
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.9935 | 170 | 0.0083509 | 1.4197
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.4352 | 155 | 0.0083509 | 1.2944
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.17087 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -69.5461 | 407 | 0.0080259 | 3.2666
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.17095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.7296 | 209 | 0.0079459 | 1.6607
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.17095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.9263 | 216 | 0.0079459 | 1.7163
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8639 | 46 | 0.0079459 | 0.36551
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.0349 | 47 | 0.0079459 | 0.37346
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8639 | 46 | 0.0079459 | 0.36551
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8639 | 46 | 0.0079459 | 0.36551
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.17115 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.5134 | 412 | 0.0077519 | 3.1938
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.17115 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -68.4596 | 400 | 0.0077519 | 3.1008
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.17128 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -72.6223 | 424 | 0.0076219 | 3.2317
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.17128 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -72.7936 | 425 | 0.0076219 | 3.2393
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0071119 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0071119 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0071119 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.3477 | 216.4 | 0.0060084 | 1.3002
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.3042 | 216.1 | 0.0060084 | 1.2984
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.4025 | 224 | 0.0058024 | 1.2997
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.6918 | 226 | 0.0058024 | 1.3113
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.6666 | 212 | 0.0058024 | 1.2301
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.522 | 211 | 0.0058024 | 1.2243
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.8364 | 147 | 0.0031429 | 0.46201
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2546 | 138 | 0.0031429 | 0.43373
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6061 | 140 | 0.0031429 | 0.44001
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.8364 | 147 | 0.0031429 | 0.46201
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.988 | 182 | 0.0031429 | 0.57202
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.8001 | 198 | 0.0031429 | 0.6223
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.14092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6744 | 168 | 0.0020674 | 0.34732
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.14092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.6827 | 90 | 0.0020674 | 0.18606
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.17815 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.4406 | 0 | 0.00075495 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.3741 | 114 | 0.00018095 | 0.020628
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -39.6758 | 222 | 0.00018095 | 0.04017
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -32.8845 | 184 | 0.00018095 | 0.033294
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -40.0333 | 224 | 0.00018095 | 0.040532
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.5528 | 115 | 0.00018095 | 0.020809
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.8311 | 395 | -3.8623e-05 | -0.015256
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13881 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.3837 | 435 | -3.8623e-05 | -0.016801
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.13858 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.2827 | 435 | -0.00027062 | -0.11772
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2367 | 0 | -0.00091805 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2367 | 0 | -0.00091805 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.6973 | 0 | -0.00091805 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.1801 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43223 | 0 | -0.0011941 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.1801 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43223 | 0 | -0.0011941 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.18013 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.72051 | 0 | -0.0012271 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.6151 | 70 | -0.0014926 | -0.10448
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4778 | 69 | -0.0014926 | -0.10299
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4778 | 69 | -0.0014926 | -0.10299
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.3404 | 68 | -0.0014926 | -0.1015
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13718 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016736 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7073 | 217.3 | -0.0021406 | -0.46516
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0258 | 205 | -0.0021406 | -0.43883
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 37.2401 | 272.4 | -0.0021406 | -0.58311
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13629 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.713 | 196 | -0.0025606 | -0.50188
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13629 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.1283 | 111 | -0.0025606 | -0.28423
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13617 | north | 3 | N | N | Nnorth | Nnorth | 1 | 157.5452 | 0 | -0.0026846 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13617 | north | 3 | N | N | Nnorth | Nnorth | 1 | 157.6814 | 0 | -0.0026846 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13616 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0026916 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13616 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0026916 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13616 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0026916 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.13583 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.0278 | 118 | -0.0030226 | -0.35667
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.13583 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.6203 | 115 | -0.0030226 | -0.3476
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.13583 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.5209 | 556 | -0.0030226 | -1.6806
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.8859 | 142 | -0.0033941 | -0.48196
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.4328 | 145 | -0.0033941 | -0.49214
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5265 | 151 | -0.0033941 | -0.5125
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -52.8655 | 290 | -0.0033941 | -0.98428
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43848 | 0 | -0.0037971 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43848 | 0 | -0.0037971 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.51155 | 0 | -0.0037971 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13477 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.086 | 60 | -0.0040856 | -0.24514
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13477 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4903 | 63 | -0.0040856 | -0.25739
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.13459 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0042656 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.1345 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0043506 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4204 | 18 | -0.0043836 | -0.078905
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4204 | 18 | -0.0043836 | -0.078905
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.1098 | 38 | -0.0043836 | -0.16658
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 38.7046 | 288 | -0.0044606 | -1.2847
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7555 | 147 | -0.0044606 | -0.65571
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7555 | 147 | -0.0044606 | -0.65571
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13409 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0047596 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13409 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0047596 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.13408 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.084 | 112.5 | -0.0047716 | -0.53681
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.13395 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3578 | 0 | -0.0049066 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.13395 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3578 | 0 | -0.0049066 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.13386 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 22.7555 | 170 | -0.0049956 | -0.84926
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.13386 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.6051 | 520 | -0.0049956 | -2.5977
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.13377 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 49.4938 | 370 | -0.0050846 | -1.8813
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.7274 | 0 | -0.0050846 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.8611 | 0 | -0.0050846 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.334 | 0 | -0.0050846 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.1287 | 0 | -0.0050846 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.2624 | 0 | -0.0050846 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.4678 | 0 | -0.0050846 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3898 | 160 | -0.0051656 | -0.8265
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.855 | 156 | -0.0051656 | -0.80584
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.2025 | 196 | -0.0051656 | -1.0125
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.855 | 156 | -0.0051656 | -0.80584
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9887 | 157 | -0.0051656 | -0.811
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.4698 | 198 | -0.0051656 | -1.0228
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.13363 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 51.8488 | 388 | -0.0052206 | -2.0256
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.13363 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 68.82 | 515 | -0.0052206 | -2.6886
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.13363 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.3451 | 40 | -0.0052236 | -0.20894
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.5548 | 79 | -0.0052466 | -0.41448
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.1621 | 106 | -0.0052466 | -0.55614
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.5063 | 146 | -0.0052466 | -0.76601
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.13361 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.154 | 76 | -0.0052466 | -0.39874
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.0201 | 0 | -0.0052506 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6346 | 0 | -0.0052506 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.8103 | 0 | -0.0052506 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 74.5293 | 558 | -0.0052866 | -2.9499
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.3341 | 579 | -0.0052866 | -3.061
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 107.9205 | 808 | -0.0052866 | -4.2716
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6691 | 20 | -0.0053986 | -0.10797
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.3363 | 25 | -0.0053986 | -0.13497
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.4716 | 41 | -0.0053986 | -0.22134
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.13343 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.7406 | 73 | -0.0054186 | -0.39556
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.13343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.8785 | 119 | -0.0054186 | -0.64482
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.13343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.3538 | 205 | -0.0054186 | -1.1108
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.13343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.6102 | 102 | -0.0054186 | -0.5527
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.13343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.8096 | 96 | -0.0054186 | -0.52019
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.18463 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -77.9117 | 422 | -0.0057241 | -2.4156
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.0845 | 204 | -0.0060846 | -1.2413
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.6862 | 201 | -0.0060846 | -1.223
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.1296 | 242 | -0.0060846 | -1.4725
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3549 | 161 | -0.0062126 | -1.0002
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7528 | 164 | -0.0062126 | -1.0189
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7528 | 164 | -0.0062126 | -1.0189
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 54.9125 | 414 | -0.0062126 | -2.572
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.4875 | 162 | -0.0062126 | -1.0064
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3549 | 161 | -0.0062126 | -1.0002
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6202 | 163 | -0.0062126 | -1.0127
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 54.2494 | 409 | -0.0062126 | -2.541
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.18593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.2059 | 0 | -0.0070251 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.18593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.3919 | 0 | -0.0070251 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5793 | 0 | -0.0072396 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5793 | 0 | -0.0072396 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13152 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.4607 | 224 | -0.0073306 | -1.6421
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13148 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.7777 | 120 | -0.0073706 | -0.88447
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5895 | 20 | -0.0093776 | -0.18755
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5895 | 20 | -0.0093776 | -0.18755
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5895 | 20 | -0.0093776 | -0.18755
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2011 | 17 | -0.0093776 | -0.15942
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.12934 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 47.3384 | 366 | -0.0095116 | -3.4813
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.12882 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.1732 | 242 | -0.010037 | -2.4289
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 100.9808 | 785 | -0.010214 | -8.0177
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 102.2672 | 795 | -0.010214 | -8.1198
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 100.3376 | 780 | -0.010214 | -7.9666
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.3617 | 223.9 | -0.010298 | -2.3057
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.5698 | 225 | -0.010298 | -2.3171
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.4941 | 224.6 | -0.010298 | -2.3129
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.8914 | 226.7 | -0.010298 | -2.3346
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12842 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7051 | 60 | -0.010434 | -0.62602
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.9649 | 0 | -0.010711 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.6583 | 0 | -0.010711 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.5804 | 0 | -0.010711 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 51.1283 | 0 | -0.010711 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.12746 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.011389 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.12742 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.3712 | 50 | -0.011428 | -0.57138
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.12683 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.0834 | 182 | -0.01202 | -2.1876
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.12683 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 61.3867 | 484 | -0.01202 | -5.8175
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.12587 | west | 4 | Y | N | Ywest | Nwest | 1 | 81.7797 | 649.7 | -0.012979 | -8.4322
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.19272 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4689 | 0 | -0.013815 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.19272 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4689 | 0 | -0.013815 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.19291 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1575 | 0 | -0.01401 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5859 | 165 | -0.014089 | -2.3246
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.19398 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -83.9942 | 433 | -0.015081 | -6.5301
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.19418 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -113.4017 | 584 | -0.01528 | -8.9236
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.19418 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -115.5377 | 595 | -0.01528 | -9.0916
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.12332 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.103 | 236 | -0.015534 | -3.6659
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.12331 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.324 | 400 | -0.015542 | -6.2166
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5718 | 151.5 | -0.016266 | -2.4642
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6698 | 152.3 | -0.016266 | -2.4773
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.759 | 177.5 | -0.016266 | -2.8871
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.4445 | 150.7 | -0.01646 | -2.4805
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.4812 | 151 | -0.01646 | -2.4854
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7123 | 177.4 | -0.01646 | -2.9199
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 74.4827 | 615 | -0.017742 | -10.9111
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 71.0916 | 587 | -0.017742 | -10.4143
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2597 | 60 | -0.017857 | -1.0714
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.11929 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8932 | 150 | -0.019564 | -2.9345
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9005 | 209 | -0.019711 | -4.1195
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0713 | 126.5 | -0.019711 | -2.4934
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.6661 | 249 | -0.019711 | -4.9079
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.4708 | 197 | -0.019711 | -3.883
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4587 | 37.5 | -0.019954 | -0.74826
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7815 | 107.5 | -0.019954 | -2.145
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0512 | 135 | -0.019954 | -2.6937
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1489 | 119 | -0.019954 | -2.3745
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4843 | 105 | -0.019954 | -2.0951
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5713 | 80.5 | -0.019954 | -1.6063
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11828 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7855 | 125 | -0.020568 | -2.571
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11828 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7855 | 125 | -0.020568 | -2.571
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.11807 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.71 | 150 | -0.020785 | -3.1177
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.11807 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9248 | 101 | -0.020785 | -2.0992
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.11793 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9065 | 84 | -0.020918 | -1.7571
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6449 | 99 | -0.021227 | -2.1014
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1751 | 61 | -0.021227 | -1.2948
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9406 | 0 | -0.021227 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3755 | 0 | -0.021227 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3755 | 0 | -0.021227 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.11759 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5803 | 141 | -0.021261 | -2.9977
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.11759 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1109 | 120 | -0.021261 | -2.5513
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.11749 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4019 | 63 | -0.021361 | -1.3457
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7473 | 66 | -0.021468 | -1.4169
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0995 | 69 | -0.021468 | -1.4813
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0995 | 69 | -0.021468 | -1.4813
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8647 | 67 | -0.021468 | -1.4383
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8647 | 67 | -0.021468 | -1.4383
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.63 | 65 | -0.021468 | -1.3954
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.568 | 150 | -0.021732 | -3.2597
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.7664 | 220 | -0.021732 | -4.781
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.424 | 200 | -0.021732 | -4.3463
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.2769 | 121.9 | -0.021732 | -2.6491
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11679 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0217 | 180 | -0.022065 | -3.9716
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11679 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0217 | 180 | -0.022065 | -3.9716
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 1 | 8.1745 | 0 | -0.022074 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 1 | 8.5715 | 0 | -0.022074 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 1 | 8.2212 | 0 | -0.022074 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.11668 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.2519 | 225 | -0.022177 | -4.9897
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.11643 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9716 | 120 | -0.022422 | -2.6906
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.11638 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9656 | 120 | -0.022472 | -2.6966
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9585 | 120 | -0.022531 | -2.7037
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.1028 | 233 | -0.022531 | -5.2496
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.7978 | 170.2 | -0.022531 | -3.8347
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.11564 | west | 8 | N | N | Nwest | Nwest | 1 | 2.9836 | 0 | -0.02321 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.11562 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.7654 | 214.2 | -0.023234 | -4.9766
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.11535 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5928 | 100.5 | -0.023501 | -2.3618
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.11533 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6892 | 58 | -0.023521 | -1.3642
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.0692 | 70 | -0.023578 | -1.6504
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.0692 | 70 | -0.023578 | -1.6504
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.6974 | 92.8 | -0.023578 | -2.188
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2219 | 80 | -0.023578 | -1.8862
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2219 | 80 | -0.023578 | -1.8862
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.2565 | 115 | -0.023578 | -2.7114
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.9959 | 208.2 | -0.023598 | -4.913
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.3776 | 142.1 | -0.023598 | -3.3532
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.2596 | 132.4 | -0.023598 | -3.1243
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.6745 | 136 | -0.023598 | -3.2093
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.9423 | 147 | -0.023598 | -3.4689
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 24.2033 | 210 | -0.023598 | -4.9555
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.115 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2494 | 150 | -0.023856 | -3.5783
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8796 | 112.5 | -0.024367 | -2.7412
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.1155 | 149.5 | -0.024367 | -3.6428
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.2942 | 186 | -0.024367 | -4.5322
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.557 | 214.5 | -0.024367 | -5.2266
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.11392 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.75189 | 6.6 | -0.02493 | -0.16454
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.11392 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9075 | 34.3 | -0.02493 | -0.85509
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.11362 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.9291 | 149 | -0.025234 | -3.7598
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.11326 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.964 | 35 | -0.025594 | -0.89578
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.11326 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3977 | 30 | -0.025594 | -0.76781
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.4681 | 66 | -0.025699 | -1.6961
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.3549 | 65 | -0.025699 | -1.6704
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5813 | 67 | -0.025699 | -1.7218
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5813 | 67 | -0.025699 | -1.7218
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5813 | 67 | -0.025699 | -1.7218
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.11315 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.025699 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.11315 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.025699 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1127 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1018 | 169.5 | -0.026157 | -4.4335
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.3873 | 0 | -0.032165 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.1762 | 0 | -0.032165 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.3873 | 0 | -0.032165 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.10544 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.5061 | 0 | -0.033414 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -28.1989 | 132 | -0.034727 | -4.584
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -28.6262 | 134 | -0.034727 | -4.6534
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -69.0018 | 323 | -0.034727 | -11.2168
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10224 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1794 | 80 | -0.03661 | -2.9288
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10224 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1794 | 80 | -0.03661 | -2.9288
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10203 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 84.3755 | 827 | -0.036826 | -30.4548
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10203 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.5593 | 819 | -0.036826 | -30.1602
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6038 | 75 | -0.037468 | -2.8101
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1107 | 80 | -0.037468 | -2.9974
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0554 | 40 | -0.037468 | -1.4987
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.1012 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0958 | 80 | -0.037654 | -3.0123
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10117 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0938 | 80 | -0.037679 | -3.0143
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10106 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1596 | 150 | -0.037788 | -5.6681
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10106 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1596 | 150 | -0.037788 | -5.6681
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5845 | 158 | -0.039988 | -6.3181
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0222 | 160 | -0.039988 | -6.3981
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -38.3056 | 175 | -0.039988 | -6.9979
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7689 | 49 | -0.040872 | -2.0027
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.1096 | 46 | -0.040872 | -1.8801
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.1096 | 46 | -0.040872 | -1.8801
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3293 | 47 | -0.040872 | -1.921
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.21977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.845 | 154 | -0.040872 | -6.2943
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.21977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.5264 | 148 | -0.040872 | -6.0491
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5491 | 48 | -0.040872 | -1.9619
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5491 | 48 | -0.040872 | -1.9619
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.5387 | 152.5 | -0.041025 | -6.2563
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.8789 | 149.5 | -0.041025 | -6.1332
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -51.1548 | 232.6 | -0.041025 | -9.5424
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.22048 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7639 | 0 | -0.041583 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.22048 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7639 | 0 | -0.041583 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.096776 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7421 | 80 | -0.042076 | -3.366
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.096032 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3464 | 76.5 | -0.04282 | -3.2757
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.22188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -68.7819 | 310 | -0.042976 | -13.3226
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.22188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -91.6352 | 413 | -0.042976 | -17.7491
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.095329 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0076 | 84 | -0.043523 | -3.6559
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.4256 | 42 | -0.045517 | -1.9117
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8744 | 44 | -0.045517 | -2.0028
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8744 | 44 | -0.045517 | -2.0028
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5476 | 47 | -0.045517 | -2.1393
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.8805 | 855 | -0.052442 | -44.8376
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.8805 | 855 | -0.052442 | -44.8376
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1602 | 152.3 | -0.052442 | -7.9869
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.2207 | 153 | -0.052442 | -8.0236
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.072271 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.066581 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.2644 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -150.4453 | 569 | -0.085502 | -48.6507
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.2644 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -153.6181 | 581 | -0.085502 | -49.6767
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.051171 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6757 | 150 | -0.087681 | -13.1521
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.05008 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.187 | 463 | -0.088772 | -41.1013
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.042306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.7192 | 17 | -0.096546 | -1.6413
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.042217 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.3509 | 0 | -0.096635 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.0958 | 0 | -0.09932 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.167 | 0 | -0.09932 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.167 | 0 | -0.09932 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.0222 | 0 | -0.09932 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.038598 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8527 | 48 | -0.10025 | -4.8122
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.038598 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7755 | 46 | -0.10025 | -4.6117
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.038598 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.0528 | 105 | -0.10025 | -10.5266
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.13885 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.13885 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.091897 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.23075 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -17.872 | 100 | -0.31757 | -31.7572

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:3409 LAKE_CRK - 3414 TEMP_SS_ C:3412 TEMP_PEC - 3414 TEMP_SS_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -17.872 | 0 | -0.31757 | 0 | 0 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.091897 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.23075 | 0 | 0 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.13885 | 0 | 0 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.13885 | 0 | 0 | 0 | Weighted Shift Factors
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.038598 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8527 | 48 | -0.10025 | -4.8122 | 48 | 4.8122 | South | -0.1789
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.038598 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7755 | 46 | -0.10025 | -4.6117 | 94 | 9.4238 | North | 0.13885
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.038598 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.0528 | 105 | -0.10025 | -10.5266 | 199 | 19.9505 |  | -0.31775
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.0958 | 0 | -0.09932 | 0 | 199 | 19.9505
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.167 | 0 | -0.09932 | 0 | 199 | 19.9505 | Line Rating | 1239.6
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.167 | 0 | -0.09932 | 0 | 199 | 19.9505 | Conc Gen | 2394.6
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.039532 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.0222 | 0 | -0.09932 | 0 | 199 | 19.9505 | Weighted Imp. | 112.9211
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.042217 | north | 7 | N | N | Nnorth | Nnorth | 1 | 1.3509 | 0 | -0.096635 | 0 | 199 | 19.9505 | PTDF | 0.047157
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0 | 199 | 19.9505
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0 | 199 | 19.9505 | Concentration | -0.14841
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.042306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.7192 | 17 | -0.096546 | -1.6413 | 216 | 21.5917
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0 | 216 | 21.5917
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.042306 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.096546 | 0 | 216 | 21.5917
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.05008 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.187 | 0 | -0.088772 | 0 | 216 | 21.5917
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.051171 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6757 | 0 | -0.087681 | 0 | 216 | 21.5917
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.2644 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -150.4453 | 0 | -0.085502 | 0 | 216 | 21.5917
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.2644 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -153.6181 | 0 | -0.085502 | 0 | 216 | 21.5917
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.072271 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.066581 | 0 | 216 | 21.5917
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.8805 | 0 | -0.052442 | 0 | 216 | 21.5917
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 73.8805 | 0 | -0.052442 | 0 | 216 | 21.5917
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1602 | 0 | -0.052442 | 0 | 216 | 21.5917
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.08641 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.2207 | 0 | -0.052442 | 0 | 216 | 21.5917
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.4256 | 42 | -0.045517 | -1.9117 | 258 | 23.5035
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8744 | 44 | -0.045517 | -2.0028 | 302 | 25.5062
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.8744 | 44 | -0.045517 | -2.0028 | 346 | 27.509
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.22442 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5476 | 47 | -0.045517 | -2.1393 | 393 | 29.6483
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.095329 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0076 | 0 | -0.043523 | 0 | 393 | 29.6483
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.22188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -68.7819 | 310 | -0.042976 | -13.3226 | 703 | 42.9708
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.22188 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -91.6352 | 413 | -0.042976 | -17.7491 | 1116 | 60.72
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.096032 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3464 | 0 | -0.04282 | 0 | 1116 | 60.72
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.096776 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7421 | 0 | -0.042076 | 0 | 1116 | 60.72
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.22048 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7639 | 0 | -0.041583 | 0 | 1116 | 60.72
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.22048 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7639 | 0 | -0.041583 | 0 | 1116 | 60.72
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.5387 | 152.5 | -0.041025 | -6.2563 | 1268.5 | 66.9763
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.8789 | 149.5 | -0.041025 | -6.1332 | 1418 | 73.1095
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.21993 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -51.1548 | 232.6 | -0.041025 | -9.5424 | 1650.6 | 82.6519
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.7689 | 49 | -0.040872 | -2.0027 | 1699.6 | 84.6547
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.1096 | 46 | -0.040872 | -1.8801 | 1745.6 | 86.5348
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.1096 | 46 | -0.040872 | -1.8801 | 1791.6 | 88.4149
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.3293 | 47 | -0.040872 | -1.921 | 1838.6 | 90.3359
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.21977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -33.845 | 154 | -0.040872 | -6.2943 | 1992.6 | 96.6302
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.21977 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.5264 | 148 | -0.040872 | -6.0491 | 2140.6 | 102.6793
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5491 | 48 | -0.040872 | -1.9619 | 2188.6 | 104.6411
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.21977 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -10.5491 | 48 | -0.040872 | -1.9619 | 2236.6 | 106.603
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5845 | 158 | -0.039988 | -6.3181 | 2394.6 | 112.9211
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -35.0222 | 160 | -0.039988 | -6.3981
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21889 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -38.3056 | 175 | -0.039988 | -6.9979
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.10106 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1596 | 0 | -0.037788 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.10106 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.1596 | 0 | -0.037788 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.10117 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0938 | 0 | -0.037679 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.1012 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0958 | 0 | -0.037654 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6038 | 0 | -0.037468 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1107 | 0 | -0.037468 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.10138 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0554 | 0 | -0.037468 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.10203 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 84.3755 | 0 | -0.036826 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.10203 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 83.5593 | 0 | -0.036826 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10224 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1794 | 0 | -0.03661 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.10224 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1794 | 0 | -0.03661 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -28.1989 | 132 | -0.034727 | -4.584
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -28.6262 | 134 | -0.034727 | -4.6534
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.21363 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -69.0018 | 323 | -0.034727 | -11.2168
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.10544 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.5061 | 0 | -0.033414 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.3873 | 0 | -0.032165 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.1762 | 0 | -0.032165 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.21107 | south | 5 | N | N | Nsouth | Nsouth | -1 | -7.3873 | 0 | -0.032165 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1127 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1018 | 0 | -0.026157 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.4681 | 66 | -0.025699 | -1.6961
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.3549 | 65 | -0.025699 | -1.6704
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5813 | 67 | -0.025699 | -1.7218
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5813 | 67 | -0.025699 | -1.7218
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.11315 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.5813 | 67 | -0.025699 | -1.7218
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.11315 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.025699 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.11315 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.025699 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.11326 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.964 | 0 | -0.025594 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.11326 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3977 | 0 | -0.025594 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.11362 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.9291 | 0 | -0.025234 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.11392 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.75189 | 0 | -0.02493 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.11392 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9075 | 0 | -0.02493 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8796 | 0 | -0.024367 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.1155 | 0 | -0.024367 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.2942 | 0 | -0.024367 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.11449 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.557 | 0 | -0.024367 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.115 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.2494 | 0 | -0.023856 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 23.9959 | 208.2 | -0.023598 | -4.913
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.3776 | 142.1 | -0.023598 | -3.3532
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.2596 | 132.4 | -0.023598 | -3.1243
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.6745 | 136 | -0.023598 | -3.2093
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 16.9423 | 147 | -0.023598 | -3.4689
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.11525 | west | 9 | Y | Y | Ywest | Ywest | 1 | 24.2033 | 210 | -0.023598 | -4.9555
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.0692 | 70 | -0.023578 | -1.6504
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.0692 | 70 | -0.023578 | -1.6504
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.6974 | 92.8 | -0.023578 | -2.188
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2219 | 80 | -0.023578 | -1.8862
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.2219 | 80 | -0.023578 | -1.8862
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.11527 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.2565 | 115 | -0.023578 | -2.7114
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.11533 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6892 | 0 | -0.023521 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.11535 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5928 | 0 | -0.023501 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.11562 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.7654 | 0 | -0.023234 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.11564 | west | 8 | N | N | Nwest | Nwest | 1 | 2.9836 | 0 | -0.02321 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9585 | 0 | -0.022531 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 1 | 27.1028 | 0 | -0.022531 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.11632 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.7978 | 0 | -0.022531 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.11638 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9656 | 0 | -0.022472 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.11643 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.9716 | 0 | -0.022422 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.11668 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.2519 | 0 | -0.022177 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 1 | 8.1745 | 0 | -0.022074 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 1 | 8.5715 | 0 | -0.022074 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.11678 | west | 8 | N | N | Nwest | Nwest | 1 | 8.2212 | 0 | -0.022074 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11679 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0217 | 0 | -0.022065 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.11679 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.0217 | 0 | -0.022065 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.568 | 0 | -0.021732 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.7664 | 0 | -0.021732 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.424 | 0 | -0.021732 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.11712 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.2769 | 0 | -0.021732 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.7473 | 66 | -0.021468 | -1.4169
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0995 | 69 | -0.021468 | -1.4813
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 8.0995 | 69 | -0.021468 | -1.4813
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8647 | 67 | -0.021468 | -1.4383
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.8647 | 67 | -0.021468 | -1.4383
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.11738 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.63 | 65 | -0.021468 | -1.3954
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.11749 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4019 | 0 | -0.021361 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.11759 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5803 | 0 | -0.021261 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.11759 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1109 | 0 | -0.021261 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6449 | 0 | -0.021227 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.11762 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1751 | 0 | -0.021227 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 1 | 2.9406 | 0 | -0.021227 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3755 | 0 | -0.021227 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.11762 | west | 7 | N | N | Nwest | Nwest | 1 | 5.3755 | 0 | -0.021227 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.11793 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9065 | 0 | -0.020918 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.11807 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.71 | 0 | -0.020785 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.11807 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9248 | 0 | -0.020785 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11828 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7855 | 0 | -0.020568 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.11828 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7855 | 0 | -0.020568 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4587 | 0 | -0.019954 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7815 | 0 | -0.019954 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0512 | 0 | -0.019954 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1489 | 0 | -0.019954 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4843 | 0 | -0.019954 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.1189 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.5713 | 0 | -0.019954 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.9005 | 0 | -0.019711 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0713 | 0 | -0.019711 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.6661 | 0 | -0.019711 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.11914 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.4708 | 0 | -0.019711 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.11929 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8932 | 0 | -0.019564 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.121 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.2597 | 0 | -0.017857 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.12111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 74.4827 | 0 | -0.017742 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.12111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 71.0916 | 0 | -0.017742 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.4445 | 150.7 | -0.01646 | -2.4805
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.4812 | 151 | -0.01646 | -2.4854
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.12239 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7123 | 177.4 | -0.01646 | -2.9199
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.5718 | 151.5 | -0.016266 | -2.4642
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.6698 | 152.3 | -0.016266 | -2.4773
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.12259 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.759 | 177.5 | -0.016266 | -2.8871
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.19506 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -9.7528 | 50 | -0.016155 | -0.80775
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.12331 | west | 6 | Y | N | Ywest | Nwest | 1 | 49.324 | 0 | -0.015542 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.12332 | west | 6 | Y | N | Ywest | Nwest | 1 | 29.103 | 0 | -0.015534 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.19418 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -113.4017 | 0 | -0.01528 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.19418 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -115.5377 | 0 | -0.01528 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.19398 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -83.9942 | 0 | -0.015081 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.12476 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5859 | 0 | -0.014089 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.19291 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1575 | 0 | -0.01401 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.19272 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4689 | 0 | -0.013815 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.19272 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.4689 | 0 | -0.013815 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.12587 | west | 4 | Y | N | Ywest | Nwest | 1 | 81.7797 | 0 | -0.012979 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.12683 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.0834 | 182 | -0.01202 | -2.1876
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.12683 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 61.3867 | 484 | -0.01202 | -5.8175
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.12742 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.3712 | 0 | -0.011428 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.12746 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.011389 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.9649 | 0 | -0.010711 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.6583 | 0 | -0.010711 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.5804 | 0 | -0.010711 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.12814 | north | 1 | N | N | Nnorth | Nnorth | 1 | 51.1283 | 0 | -0.010711 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.12842 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.7051 | 0 | -0.010434 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.3617 | 223.9 | -0.010298 | -2.3057
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.5698 | 225 | -0.010298 | -2.3171
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.4941 | 224.6 | -0.010298 | -2.3129
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.1892 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -42.8914 | 226.7 | -0.010298 | -2.3346
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 100.9808 | 0 | -0.010214 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 102.2672 | 0 | -0.010214 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.12864 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 100.3376 | 0 | -0.010214 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.12882 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.1732 | 242 | -0.010037 | -2.4289
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.12934 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 47.3384 | 366 | -0.0095116 | -3.4813
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5895 | 20 | -0.0093776 | -0.18755
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5895 | 20 | -0.0093776 | -0.18755
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.5895 | 20 | -0.0093776 | -0.18755
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.12947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2011 | 17 | -0.0093776 | -0.15942
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.13148 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.7777 | 0 | -0.0073706 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.13152 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.4607 | 224 | -0.0073306 | -1.6421
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5793 | 0 | -0.0072396 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13161 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.5793 | 0 | -0.0072396 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.18593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.2059 | 0 | -0.0070251 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.18593 | south | 5 | N | N | Nsouth | Nsouth | -1 | -5.3919 | 0 | -0.0070251 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3549 | 161 | -0.0062126 | -1.0002
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7528 | 164 | -0.0062126 | -1.0189
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7528 | 164 | -0.0062126 | -1.0189
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 54.9125 | 414 | -0.0062126 | -2.572
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.4875 | 162 | -0.0062126 | -1.0064
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3549 | 161 | -0.0062126 | -1.0002
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.6202 | 163 | -0.0062126 | -1.0127
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.13264 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 54.2494 | 409 | -0.0062126 | -2.541
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.0845 | 204 | -0.0060846 | -1.2413
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.6862 | 201 | -0.0060846 | -1.223
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.13277 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.1296 | 242 | -0.0060846 | -1.4725
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.18463 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -77.9117 | 422 | -0.0057241 | -2.4156
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.13343 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.7406 | 73 | -0.0054186 | -0.39556
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.13343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 15.8785 | 119 | -0.0054186 | -0.64482
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.13343 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.3538 | 205 | -0.0054186 | -1.1108
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.13343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.6102 | 102 | -0.0054186 | -0.5527
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.13343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 12.8096 | 96 | -0.0054186 | -0.52019
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6691 | 20 | -0.0053986 | -0.10797
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.3363 | 25 | -0.0053986 | -0.13497
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.13345 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.4716 | 41 | -0.0053986 | -0.22134
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 74.5293 | 0 | -0.0052866 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.3341 | 0 | -0.0052866 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.13356 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 107.9205 | 0 | -0.0052866 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.0201 | 0 | -0.0052506 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6346 | 0 | -0.0052506 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.1336 | north | 8 | N | N | Nnorth | Nnorth | 1 | 11.8103 | 0 | -0.0052506 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 10.5548 | 79 | -0.0052466 | -0.41448
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 14.1621 | 106 | -0.0052466 | -0.55614
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.13361 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 19.5063 | 146 | -0.0052466 | -0.76601
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.13361 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.154 | 76 | -0.0052466 | -0.39874
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.13363 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 5.3451 | 40 | -0.0052236 | -0.20894
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.13363 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 51.8488 | 388 | -0.0052206 | -2.0256
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.13363 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 68.82 | 515 | -0.0052206 | -2.6886
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.3898 | 160 | -0.0051656 | -0.8265
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.855 | 156 | -0.0051656 | -0.80584
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.2025 | 196 | -0.0051656 | -1.0125
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.855 | 156 | -0.0051656 | -0.80584
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9887 | 157 | -0.0051656 | -0.811
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.13369 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.4698 | 198 | -0.0051656 | -1.0228
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.13377 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 49.4938 | 370 | -0.0050846 | -1.8813
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.7274 | 0 | -0.0050846 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.8611 | 0 | -0.0050846 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.334 | 0 | -0.0050846 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.1287 | 0 | -0.0050846 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 19.2624 | 0 | -0.0050846 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.13377 | north | 1 | N | N | Nnorth | Nnorth | 1 | 41.4678 | 0 | -0.0050846 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.13386 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 22.7555 | 170 | -0.0049956 | -0.84926
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.13386 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.6051 | 520 | -0.0049956 | -2.5977
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.13395 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3578 | 0 | -0.0049066 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.13395 | north | 5 | N | N | Nnorth | Nnorth | 1 | 5.3578 | 0 | -0.0049066 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.13408 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 15.084 | 0 | -0.0047716 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13409 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0047596 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.13409 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0047596 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 38.7046 | 288 | -0.0044606 | -1.2847
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7555 | 147 | -0.0044606 | -0.65571
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.13439 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7555 | 147 | -0.0044606 | -0.65571
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4204 | 18 | -0.0043836 | -0.078905
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.4204 | 18 | -0.0043836 | -0.078905
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.13447 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 5.1098 | 38 | -0.0043836 | -0.16658
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.1345 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0043506 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.13459 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0042656 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.13477 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.086 | 60 | -0.0040856 | -0.24514
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.13477 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4903 | 63 | -0.0040856 | -0.25739
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43848 | 0 | -0.0037971 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43848 | 0 | -0.0037971 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.1827 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.51155 | 0 | -0.0037971 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.8859 | 142 | -0.0033941 | -0.48196
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.4328 | 145 | -0.0033941 | -0.49214
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.5265 | 151 | -0.0033941 | -0.5125
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.1823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -52.8655 | 290 | -0.0033941 | -0.98428
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.13583 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 16.0278 | 118 | -0.0030226 | -0.35667
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.13583 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.6203 | 115 | -0.0030226 | -0.3476
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.13583 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.5209 | 556 | -0.0030226 | -1.6806
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.13616 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0026916 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.13616 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0026916 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.13616 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0026916 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.13617 | north | 3 | N | N | Nnorth | Nnorth | 1 | 157.5452 | 0 | -0.0026846 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.13617 | north | 3 | N | N | Nnorth | Nnorth | 1 | 157.6814 | 0 | -0.0026846 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.13629 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.713 | 196 | -0.0025606 | -0.50188
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.13629 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 15.1283 | 111 | -0.0025606 | -0.28423
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 29.7073 | 217.3 | -0.0021406 | -0.46516
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 28.0258 | 205 | -0.0021406 | -0.43883
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.13671 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 37.2401 | 272.4 | -0.0021406 | -0.58311
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.13718 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016736 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.6151 | 70 | -0.0014926 | -0.10448
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4778 | 69 | -0.0014926 | -0.10299
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.4778 | 69 | -0.0014926 | -0.10299
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.13736 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.3404 | 68 | -0.0014926 | -0.1015
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.18013 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.72051 | 0 | -0.0012271 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.1801 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43223 | 0 | -0.0011941 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.1801 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.43223 | 0 | -0.0011941 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2367 | 0 | -0.00091805 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -1 | -3.2367 | 0 | -0.00091805 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.17982 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.6973 | 0 | -0.00091805 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.13858 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.2827 | 435 | -0.00027062 | -0.11772
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.13881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.8311 | 395 | -3.8623e-05 | -0.015256
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.13881 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 60.3837 | 435 | -3.8623e-05 | -0.016801
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.3741 | 0 | 0.00018095 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -39.6758 | 0 | 0.00018095 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -32.8845 | 0 | 0.00018095 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -40.0333 | 0 | 0.00018095 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.17872 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -20.5528 | 0 | 0.00018095 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.17815 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.4406 | 0 | 0.00075495 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.14092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6744 | 168 | 0.0020674 | 0.34732
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.14092 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.6827 | 90 | 0.0020674 | 0.18606
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.8364 | 147 | 0.0031429 | 0.46201
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2546 | 138 | 0.0031429 | 0.43373
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6061 | 140 | 0.0031429 | 0.44001
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.8364 | 147 | 0.0031429 | 0.46201
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.988 | 182 | 0.0031429 | 0.57202
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.17576 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.8001 | 198 | 0.0031429 | 0.6223
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.4025 | 224 | 0.0058024 | 1.2997
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.6918 | 226 | 0.0058024 | 1.3113
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.6666 | 212 | 0.0058024 | 1.2301
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.14465 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.522 | 211 | 0.0058024 | 1.2243
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.3477 | 216.4 | 0.0060084 | 1.3002
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.14486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.3042 | 216.1 | 0.0060084 | 1.2984
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0071119 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0071119 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.17179 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0071119 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.17128 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -72.6223 | 0 | 0.0076219 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.17128 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -72.7936 | 0 | 0.0076219 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.17115 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -70.5134 | 412 | 0.0077519 | 3.1938
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.17115 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -68.4596 | 400 | 0.0077519 | 3.1008
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.17095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.7296 | 209 | 0.0079459 | 1.6607
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.17095 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -36.9263 | 216 | 0.0079459 | 1.7163
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8639 | 46 | 0.0079459 | 0.36551
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.0349 | 47 | 0.0079459 | 0.37346
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8639 | 46 | 0.0079459 | 0.36551
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.17095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8639 | 46 | 0.0079459 | 0.36551
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.17087 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -69.5461 | 407 | 0.0080259 | 3.2666
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.4352 | 155 | 0.0083509 | 1.2944
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.9935 | 170 | 0.0083509 | 1.4197
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.17055 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.4352 | 155 | 0.0083509 | 1.2944
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.16991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.8548 | 58 | 0.0089909 | 0.52147
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.16991 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.122 | 89 | 0.0089909 | 0.80019
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.476 | 44 | 0.0089909 | 0.3956
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.476 | 44 | 0.0089909 | 0.3956
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3061 | 43 | 0.0089909 | 0.38661
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.16991 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.646 | 45 | 0.0089909 | 0.40459
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.16971 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -92.6617 | 0 | 0.0091909 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.16971 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -127.2825 | 0 | 0.0091909 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.16911 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0293 | 0 | 0.0097929 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.15659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3489 | 0 | 0.017742 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.15659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3489 | 0 | 0.017742 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.16051 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -63.5628 | 0 | 0.018389 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.16155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2329 | 150 | 0.022701 | 3.4052
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.16155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.9242 | 80 | 0.022701 | 1.8161
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15134 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.6321 | 24 | 0.027564 | 0.66153
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.15134 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.6321 | 24 | 0.027564 | 0.66153
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.15134 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.4808 | 23 | 0.027564 | 0.63397
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.15027 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.0268 | 100 | 0.028633 | 2.8633
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.15027 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -15.0268 | 100 | 0.028633 | 2.8633
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.15027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028633 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.15025 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028646 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.14962 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.2568 | 8.4 | 0.029279 | 0.24594
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.14897 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.029934 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -92.4643 | 0 | 0.031899 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.14642 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.032477 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.14475 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.034153 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7367 | 0 | 0.034174 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.592 | 0 | 0.034174 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.14473 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.7367 | 0 | 0.034174 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.9428 | 146.5 | 0.035947 | 5.2662
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.1429 | 147.9 | 0.035947 | 5.3166
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.14295 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.731 | 173 | 0.035947 | 6.2188
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.5325 | 207 | 0.036232 | 7.5
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -30.9164 | 216.7 | 0.036232 | 7.8515
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.14267 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.5259 | 242 | 0.036232 | 8.7681
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.5438 | 144 | 0.036236 | 5.218
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.5438 | 144 | 0.036236 | 5.218
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.14266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.3957 | 171 | 0.036236 | 6.1963
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.14239 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.036512 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.4107 | 38 | 0.036513 | 1.3875
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7481 | 19.3 | 0.036513 | 0.7047
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.14239 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1358 | 15 | 0.036513 | 0.54769
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.14239 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6922 | 47 | 0.036513 | 1.7161
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.3753 | 0 | 0.036611 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.8339 | 0 | 0.036611 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.407 | 0 | 0.036611 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.7035 | 0 | 0.036611 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -13.3753 | 0 | 0.036611 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.1224 | 0 | 0.036611 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.1185 | 0 | 0.036611 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1304 | 0 | 0.036611 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -21.0589 | 0 | 0.036611 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1145 | 0 | 0.036611 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.8259 | 0 | 0.036611 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.14229 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.1145 | 0 | 0.036611 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.14206 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.1198 | 0 | 0.036839 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.14138 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3723 | 0 | 0.037524 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.14137 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.372 | 0 | 0.037533 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.14123 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5307 | 0 | 0.037675 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.14123 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5307 | 0 | 0.037675 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.14117 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.1525 | 334 | 0.037726 | 12.6005
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.14117 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.9995 | 340 | 0.037726 | 12.8268
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.14117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.4115 | 180 | 0.037726 | 6.7907
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.14117 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.4115 | 180 | 0.037726 | 6.7907
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14089 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.3606 | 180 | 0.038009 | 6.8416
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.8901 | 0 | 0.038037 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.9324 | 0 | 0.038037 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.14086 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.5522 | 0 | 0.038037 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.14085 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -47.3246 | 336 | 0.038054 | 12.7861
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.14085 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.3525 | 180 | 0.038054 | 6.8497
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.14023 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.1938 | 144 | 0.038666 | 5.5679
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.14023 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.3642 | 188 | 0.038666 | 7.2692
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 0 | 0.038947 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 0 | 0.038947 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 0 | 0.038947 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2393 | 0 | 0.038947 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 0 | 0.038947 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 0 | 0.038947 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.4989 | 0 | 0.038947 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.13995 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0993 | 0 | 0.038947 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -22.0208 | 0 | 0.039529 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -21.3239 | 0 | 0.039529 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -13.9372 | 0 | 0.039529 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.2089 | 0 | 0.039529 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.4877 | 0 | 0.039529 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.13937 | south | 8 | N | N | Nsouth | Nsouth | -1 | -17.7002 | 0 | 0.039529 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.13937 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6725 | 0 | 0.039529 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.13866 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.122 | 0 | 0.040244 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6001 | 47.7 | 0.040534 | 1.9335
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.1611 | 37.3 | 0.040534 | 1.5119
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.3649 | 46 | 0.040534 | 1.8646
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.13837 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.6416 | 48 | 0.040534 | 1.9456
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.1371 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.0162 | 22 | 0.0418 | 0.9196
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5081 | 11 | 0.0418 | 0.4598
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5081 | 11 | 0.0418 | 0.4598
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.13589 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0384 | 0 | 0.043006 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.13589 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1256 | 0 | 0.043006 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.13488 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0791 | 0 | 0.044017 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.7612 | 0 | 0.044574 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.94029 | 0 | 0.044574 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2388 | 0 | 0.044574 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0149 | 0 | 0.044574 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.94029 | 0 | 0.044574 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.0149 | 0 | 0.044574 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2388 | 0 | 0.044574 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.13433 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2388 | 0 | 0.044574 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.18349 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 46.7897 | 255 | 0.044637 | 11.3825
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.18349 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 27.3399 | 149 | 0.044637 | 6.651
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.18349 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 28.0738 | 153 | 0.044637 | 6.8295
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.18641 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.047557 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.18641 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.047557 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.13058 | south | 7 | N | N | Nsouth | Nsouth | -1 | -6.268 | 0 | 0.048317 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.225 | 0 | 0.04947 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.4839 | 0 | 0.04947 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.225 | 0 | 0.04947 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.3545 | 0 | 0.04947 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -10.1474 | 0 | 0.04947 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2358 | 0 | 0.04947 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9538 | 0 | 0.04947 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.6241 | 0 | 0.04947 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6432 | 0 | 0.04947 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.12943 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.5779 | 0 | 0.04947 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.10883 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.07007 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.10385 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62308 | 0 | 0.075054 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.2147 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.075846 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.2147 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 168.9673 | 787 | 0.075846 | 59.6911
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.087766 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -116.9921 | 0 | 0.091135 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.087766 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -116.5532 | 0 | 0.091135 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6242 | 76 | 0.091741 | 6.9723
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6242 | 76 | 0.091741 | 6.9723
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.1518 | 105 | 0.091741 | 9.6328
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4498 | 74 | 0.091741 | 6.7888
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4498 | 74 | 0.091741 | 6.7888
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.08716 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.8903 | 102 | 0.091741 | 9.3576
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.082417 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.7198 | 0 | 0.096484 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.082417 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.0604 | 0 | 0.096484 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.082417 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.096484 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.0821 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.4186 | 66 | 0.096801 | 6.3889
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.104 | 0 | 0.11271 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7263 | 0 | 0.11271 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9787 | 0 | 0.11271 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6856 | 0 | 0.11271 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6927 | 0 | 0.11271 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8251 | 0 | 0.11271 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3097 | 0 | 0.11271 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1915 | 0 | 0.11271 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.2222 | 0 | 0.11271 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.6336 | 0 | 0.11271 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1702 | 0 | 0.11271 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.766 | 0 | 0.11271 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.2894 | 0 | 0.11271 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6856 | 0 | 0.11271 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.4208 | 0 | 0.11271 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.818 | 0 | 0.11271 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0307 | 0 | 0.11271 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2955 | 0 | 0.11271 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.2955 | 0 | 0.11271 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.066194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.3192 | 0 | 0.11271 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.062332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4256 | 0 | 0.11657 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.062332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.62332 | 0 | 0.11657 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.58 | 0 | 0.11962 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.58 | 0 | 0.11962 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0542 | 0 | 0.11962 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.059279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.4911 | 0 | 0.11962 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.048242 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.224 | 0 | 0.13066 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -31.1503 | 0 | 0.13105 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -26.9874 | 0 | 0.13105 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.04785 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -28.71 | 0 | 0.13105 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.7844 | 0 | 0.13114 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.7844 | 0 | 0.13114 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.047757 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.7005 | 0 | 0.13114 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.046593 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5376 | 0 | 0.13231 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.4218 | 161 | 0.1328 | 21.3813
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.6523 | 166 | 0.1328 | 22.0453
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.046098 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -11.4323 | 248 | 0.1328 | 32.9351
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.046098 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -25.1695 | 546 | 0.1328 | 72.5104
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.046098 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -29.641 | 0 | 0.1328 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.046098 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.59927 | 13 | 0.1328 | 1.7264
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0408 | 0 | 0.13861 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7427 | 0 | 0.13861 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1375 | 0 | 0.13861 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.040287 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1093 | 0 | 0.13861 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.040286 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2892 | 0 | 0.13861 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.040286 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2086 | 0 | 0.13861 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8501 | 0 | 0.13864 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6851 | 0 | 0.13864 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1336 | 0 | 0.13864 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1672 | 0 | 0.13864 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1793 | 0 | 0.13864 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.131 | 0 | 0.13864 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8646 | 0 | 0.13864 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.040256 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.8225 | 0 | 0.13864 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.040256 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6102 | 0 | 0.13864 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.037875 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.8938 | 50 | 0.14103 | 7.0513
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.036016 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14288 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0803 | 0 | 0.14505 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9652 | 0 | 0.14505 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9449 | 0 | 0.14505 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8448 | 0 | 0.14505 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.033849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.41296 | 0 | 0.14505 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1449 | 0 | 0.1459 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9799 | 0 | 0.1459 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1449 | 0 | 0.1459 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.032999 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.1449 | 0 | 0.1459 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4599 | 46 | 0.14716 | 6.7696
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4599 | 46 | 0.14716 | 6.7696
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4599 | 46 | 0.14716 | 6.7696
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7455 | 55 | 0.14716 | 8.0941
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7455 | 55 | 0.14716 | 8.0941
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.031736 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7137 | 54 | 0.14716 | 7.9469
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03142 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.4508 | 0 | 0.14748 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03142 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5136 | 0 | 0.14748 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.0566 | 0 | 0.14792 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8676 | 0 | 0.14792 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.88 | 0 | 0.14792 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8645 | 0 | 0.14792 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.030984 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.3347 | 0 | 0.14792 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.030631 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0721 | 0 | 0.14827 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.030252 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.36302 | 12 | 0.14865 | 1.7838
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.030252 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.14865 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.030231 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.109 | 169 | 0.14867 | 25.1252
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.030201 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9832 | 165 | 0.1487 | 24.5355
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.030178 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4965 | 0 | 0.14872 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.030178 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9646 | 0 | 0.14872 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.0301 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.4113 | 213 | 0.1488 | 31.6946
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.030091 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.48747 | 0 | 0.14881 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9254 | 0 | 0.14882 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9013 | 0 | 0.14882 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4849 | 0 | 0.14882 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.030084 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2142 | 0 | 0.14882 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.03007 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.856 | 228 | 0.14883 | 33.9335
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.4103 | 0 | 0.14884 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.767 | 0 | 0.14884 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.030057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.7189 | 0 | 0.14884 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0961 | 0 | 0.14938 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1257 | 0 | 0.14938 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1514 | 0 | 0.14938 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.029523 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88569 | 0 | 0.14938 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.028675 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8998 | 0 | 0.15023 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2015 | 42 | 0.15029 | 6.3123
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2015 | 42 | 0.15029 | 6.3123
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0871 | 38 | 0.15029 | 5.7112
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.028607 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0871 | 38 | 0.15029 | 5.7112
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.028389 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9113 | 0 | 0.15051 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.028389 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8325 | 0 | 0.15051 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8109 | 104 | 0.15187 | 15.7948
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.8109 | 104 | 0.15187 | 15.7948
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4325 | 53 | 0.15187 | 8.0493
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5406 | 57 | 0.15187 | 8.6568
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.4595 | 54 | 0.15187 | 8.2011
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5676 | 58 | 0.15187 | 8.8086
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.027028 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.5676 | 58 | 0.15187 | 8.8086
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.026503 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -19.4797 | 735 | 0.1524 | 112.0125
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88924 | 0 | 0.15275 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.90754 | 0 | 0.15275 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.85524 | 0 | 0.15275 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2005 | 0 | 0.15275 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46293 | 0 | 0.15275 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.53354 | 0 | 0.15275 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.52046 | 0 | 0.15275 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.91539 | 0 | 0.15275 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47077 | 0 | 0.15275 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2336 | 0 | 0.15275 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.026154 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8708 | 0 | 0.15275 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.025709 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.30851 | 12 | 0.15319 | 1.8383
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.025143 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12571 | 0 | 0.15376 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.025143 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.528 | 0 | 0.15376 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6337 | 0 | 0.15377 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6588 | 0 | 0.15377 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7594 | 0 | 0.15377 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5834 | 0 | 0.15377 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5583 | 0 | 0.15377 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6139 | 0 | 0.15377 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.025134 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4829 | 0 | 0.15377 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.025107 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.30128 | 0 | 0.15379 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.025067 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -18.6248 | 743 | 0.15383 | 114.2986
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.024805 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8944 | 0 | 0.1541 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.237 | 172 | 0.15427 | 26.5339
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.237 | 172 | 0.15427 | 26.5339
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.024634 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -4.237 | 172 | 0.15427 | 26.5339
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8452 | 0 | 0.15528 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8121 | 0 | 0.15528 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7531 | 0 | 0.15528 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.023619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3582 | 0 | 0.15528 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.023267 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -9.2603 | 398 | 0.15563 | 61.9423
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3363 | 59 | 0.15625 | 9.2189
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3363 | 59 | 0.15625 | 9.2189
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.022649 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2683 | 56 | 0.15625 | 8.7501
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8829 | 0 | 0.16224 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5996 | 0 | 0.16224 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5663 | 0 | 0.16224 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016664 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5663 | 0 | 0.16224 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016664 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6996 | 0 | 0.16224 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.1789 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.1789 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.1789 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1239.6