## test results
CRE test for: |  | 1430 GRHAMES - 1435 LONGCREK | [5 empty] | PASS
Line Rating: |  | 1239.6
Direction |  | West | → | North |  | W-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1430 GRHAMES - 1435 LONGCREK
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.017715
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0027611
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.22098
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0088707
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1430 GRHAMES - 1435 LONGCREK
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.0187
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.0024197
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.22468
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.008974
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 1430 GRHAMES - 1435 LONGCREK
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.015295
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.24239
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.0087409
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.22744
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.0061096
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.22996
PTDF tests
West | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | -0.23968 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.23968 | 0.015295
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.2304
[6 empty] | Concentration |  | -0.96125 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.23257
[6 empty] | Concentration |  | -0.97034 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 73.2433
| Percent of line rating => | [6 empty] | 5.909% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -3.3909
[7 empty] | B1(N-S) | 0.011737 | -0.040127 | -0.051864 | 0.011737
[7 empty] | B2 (N-W) | 0.0071501 | -0.81477 | -0.82192 | 0.0071501
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.010665 | -0.018975 | -0.029639 | 0.010665
[7 empty] | B4 (S-W) | -0.0045575 | -0.77577 | -0.77121 | -0.0045575
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.00069267 | 0.020024 | 0.020717 | -0.00069267
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.013185 | 0.79294 | 0.77975 | 0.013185
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | 1.444%
Deployment Error Percent | [6 empty] | B2 | 0.8798%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 1.312%
[7 empty] | B4 | -0.5608%
[7 empty] | B5 | -0.08523%
[7 empty] | B6 | 1.622%
[7 empty] | Max Abs Error | 1.622% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011059 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 2.82
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011059 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.6478
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.010637 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.15956
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.010637 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.15956
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011059 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.692
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.0103 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.545
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.0103 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.824
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.00685 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.50005
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.00685 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 0.81515
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.00685 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 1.4042
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.00685 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 0.6987
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.00685 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 0.6576
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.007809 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.093708
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.007809 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.093708
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.012483 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 2.0971
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.012483 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 1.1235
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.25144
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.25144
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.53082
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 4.9406
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 2.5218
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 2.5218
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.019393 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.1817
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.019615 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.7846
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.5564
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 2.0883
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 2.8763
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.019701 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.4973
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.023358 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.4015
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.023358 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.4716
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.39238
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.49047
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.80438
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.012257 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 5.675
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -15.1981
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -14.9678
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -15.4284
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -15.4284
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -15.4284
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.23027 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -26.2512
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.23027 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -118.5911
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -15.2951
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -15.9903
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -15.9903
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -15.5268
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -15.5268
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -15.0634
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -16.5535
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -17.3576
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -16.6481
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -35.5795
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -52.1833
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.22131 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -21.9101
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.22131 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -13.5002
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.22159 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -31.2438
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -5.5328
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -10.114
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -10.114
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.22159 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -26.5904
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.2267 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -5.849
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.23069 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -23.184
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.22795 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -27.3536
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.23071 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -13.3814
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.23086 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -49.4498
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.21306 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -31.9595
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.22187 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -1.4643
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.22187 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -7.6101
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.21306 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -21.5194
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.2272 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -27.2634
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.067053 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 24.5414
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.017813 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 4.3107
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.31678 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -126.7124
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.31529 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -74.4091
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.22354 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -36.8833
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 7.4729
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 7.363
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 8.8649
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.28924
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.28924
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.28924
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.24585
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.014237 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 1.7084
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.022852 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.3711
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.5053
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 1.5977
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 1.7743
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 3.2195
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.139
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 3.9439
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.139
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 3.1592
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 3.9842
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.02028 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 3.4476
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.02028 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 10.5456
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020186 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 7.4688
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 11.1673
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 11.5875
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 16.1705
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.023153 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 2.5931
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.023153 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 2.3153
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.023153 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 8.7518
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 2.5255
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 2.3825
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 3.1658
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.015217 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 11.7171
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.82082
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.80909
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.80909
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.79737
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.010497 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 12.145
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.010497 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 12.1555
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 3.7265
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 3.7597
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.017509 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 3.7889
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.017509 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 3.7837
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 3.5268
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 3.5102
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019778 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 7.8123
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.019739 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 8.5865
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.019778 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 8.6034
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.020923 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 2.8874
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.018791 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.2173
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.018791 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.161
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.018791 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 10.4478
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.019244 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 7.4667
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.019244 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 9.9107
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 14.0727
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 14.252
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 13.9831
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.017576 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 3.1988
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.017576 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 8.5068
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.016896 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 3.7847
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.017605 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.88025
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.017621 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.74008
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.01586 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 9.7539
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.01586 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 9.3098
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.01203 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 6.4601
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.01203 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 9.4676
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.011449 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.85867
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.011449 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 2.5417
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.007042 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 4.0069
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001582 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.33064
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001582 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.34171
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.001455 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 0.59218
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.072772
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.074354
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.072772
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.072772
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.00165 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 0.6996
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.00165 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 0.70125
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.001082 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.062756
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.001082 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.096298
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.047608
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.047608
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.046526
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.04869
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.001584 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 0.65261
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.001584 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 0.6336
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002129 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 1.1624
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002129 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 1.5967
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.1173
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.18268
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.29037
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.31093
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.34102
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.31093
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003216 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.070752
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003216 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.035376
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003216 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.035376
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.16061
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.12559
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.15488
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.16162
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.004176
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.003828
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.006179 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.1483
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.006179 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.1483
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.006179 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.14212
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.001523 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.60311
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.006794 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 9.0564
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.006794 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 9.0224
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.092112
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.046783
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.03636
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002424 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.11393
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -16.147
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.18967 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -28.4499
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.21158 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -35.8625
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.15504 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -23.2566
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.22371 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -14.094
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.081789 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -53.1383
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.020362 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.81448
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.020362 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.81448
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.004902 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -2.0686
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.62674
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.63623
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 1.5336
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.81639
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.82672
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 0.90422
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.00521 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 3.0426
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.00521 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 3.1
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.005208 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 2.2551
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.7026
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.70605
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.70479
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.71138
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.003972 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.031776
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.003972 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.031776
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.093744
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.093744
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.07812
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.007637 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.10463
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.002832 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.050976
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.002832 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.050976
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.065135
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.063274
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.065135
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.004377 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.12256
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.004377 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.12693
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.23004 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -8.0515
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.23004 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -6.9013
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2516
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2516
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2516
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2516
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.002647 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.015882
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.00702
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.00702
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.00819
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.002585 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.01034
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003272 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0078528
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003272 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0078528
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.39925
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.37481
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.38024
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.39925
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.49431
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.53777
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.72697
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.71267
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 1.1088
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.41606
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.42485
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.44243
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.8497
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.05878 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -1.9397
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.05878 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.4695
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.004176
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.003515 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.2566
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.32248
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.33064
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.1038
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.025949
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.32248
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.32656
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.32003
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.10205
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.18777
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.002736 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 1.7209
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.003434 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.4945
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.003434 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.64559
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.003279 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.039348
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.042062 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.25237
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.002722 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 0.91459
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002691 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 0.89879
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002691 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 0.91494
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.002651 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.10074
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.002671 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.066775
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.002671 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.066775
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.002669 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.10142
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.002567 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.074443
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.40338
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.40419
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.41616
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.45567
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.44125
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.2884
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.41818
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.42395
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.36627
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.2911
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.29388
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.34375
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.46782
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.48974
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.54692
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.32558
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.32558
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.38663
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004171 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 1.293
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004171 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 1.7226
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.18228
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.19096
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.19096
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.20398
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.20183
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.18947
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.18947
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.19359
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.63433
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.60961
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.19771
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.19771
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -16.3758
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -16.3758
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -21.7096
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -18.7152
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -18.7152
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -26.9031
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -48.6988
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -33.2378
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -30.9689
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -31.8109
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -34.3839
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -49.1198
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -49.7573
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -30.1162
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -59.2802
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -46.9004
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -47.4394
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -28.9143
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.2297 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -34.2252
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.22509 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -40.5162
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.22509 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -40.5162
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.22529 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -50.6893
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.24712 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -30.8897
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.24712 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -30.8897
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 2.826
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 2.8462
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 6.2375
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 2.8866
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 2.9068
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 6.2577
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.017072 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 3.3461
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.017072 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 1.895
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.020469 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.0827
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.1401
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.1401
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 7.9269
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 3.1018
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.0827
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 3.121
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 7.8311
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.019127 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.019127 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 2.6286
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 2.3089
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 2.5753
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 7.0866
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 2.4323
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 2.4371
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 2.8632
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 2.454
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 2.467
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 2.8751
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.007042 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 4.0914
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 11.7058
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 11.7058
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.012238 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.39162
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.012208 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.58598
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.012208 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.56157
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.14696
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.6246
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.012247 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.2082
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.26943
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.30617
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.012208 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 1.2818
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.21544 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -18.0968
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.21506 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -17.205
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.21492 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -32.2385
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.21492 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -32.2385
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.62177
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.58576
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.46545
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 1.3454
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 1.348
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 1.3375
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.84307
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 2.1428
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.35128
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.88073
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.81575
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.90181
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.89566
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.008781 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.28099
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.008781 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.26343
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.88922
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.88922
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 0.95331
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 0.8772
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 2.0851
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 2.0947
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.009242 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 1.2569
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.008526 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.28136
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.38812
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.38812
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.35116
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.35116
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.007872 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.55891
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.007872 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.07872
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.3865
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.3865
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 2.084
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.58949
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.54414
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.58949
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.58949
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.00918 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 1.3678
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.00918 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.59762
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.82228
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.79155
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.78613
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.49246
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.11024
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.009378 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 6.9679
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.009322 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 6.8517
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6158
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6158
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.6158
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 1.6788
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.009253 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 1.6008
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 1.2492
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 1.5357
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 1.5225
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 1.4989
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 2.5394
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.58778
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.58043
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.7586
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.67594
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 1.4923
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 1.4365
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 1.4402
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 1.4356
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 2.4597
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.009376 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.04688
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.009376 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.1969
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 1.823
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.8442
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.8442
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 4.4924
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.009451 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 3.7615
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.41984
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.41984
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.41984
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.50199
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.50199
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.49286
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.014266 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 11.798
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.014266 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 11.6839
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.008459 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.38996
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.52577
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.52577
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.72639
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.51193
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.51193
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.70564
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 1.6533
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 1.4567
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 1.442
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.009163 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.32071
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.008949 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 4.1076
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.60957
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.61895
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.65646
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.59081
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.58144
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.97531
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.5533
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 1.5138
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.4944
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.4944
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.009704 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 1.572
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.00939 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 1.4742
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.65363
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.66283
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.35903
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.27618
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.009131 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.71222
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.009131 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.73048
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.009183 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.14876
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.009179 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 1.5145
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.009178 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 1.5511
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.009183 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 1.956
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.009184 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 2.094
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.009177 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.11012
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.009177 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.16519
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.00889 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.4445
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.96845
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.96845
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50285
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.49354
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50285
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.53078
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50285
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.50285
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.5401
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.5401
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.009362 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.11234
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53066
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.55908
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53066
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53066
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.55908
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.53066
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.007024 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.46358
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.383
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.4259
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 2.1303
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00859 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 4.6901
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00859 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 5.5234
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 5.5355
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 4.7957
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 5.1018
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00859 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.11167
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.009377 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.11252
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.31742
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.32396
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.30529
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.42852
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.16525
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.19045
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.18579
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.32676
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.16805
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.79729
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 1.3817
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.4779
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.55035
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.34686
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.77851
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.66289
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.6783
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.3854
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.13874
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.72455
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.53956
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.4856
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.55498
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.49948
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.77851
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.74768
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.79392
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.58581
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.61664
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.61664
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 1.3181
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.065285
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.20831 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -15.9354
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -17.2234
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -8.6117
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.21628 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -17.3026
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.21509 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -17.2075
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.20981 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -16.7851
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.20809 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -17.4796
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.21628 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -17.3026
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.095304
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -26.4895
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -51.4338
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -37.571
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.18559
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.15382
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.18726
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.09614
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.0836
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.15875 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -9.5251
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.060928 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.18095 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.22048 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -1.0583
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -9.1289
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -26.1695
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -32.864
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -28.969
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -25.5609
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -19.5967
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.21992 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -32.9883
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -24.3433
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -32.3496
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -40.2476
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -46.4146
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.002424 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.038174 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.003023 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.1143
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.17798
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.30207
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.23397
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.10205
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.094582
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.047291
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.23397
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.089604
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.10703
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.054758
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.14457
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.055605
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.025949
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.055605
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.14457
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.14457
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.36837
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.12445
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.13689
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.12445
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002884 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.034608
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.003625 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.054375
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.003625 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.083375
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.004002 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.1921
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.003649 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.029192
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.002717 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.48906
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.002722 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.48996
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002691 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.48438
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002691 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.48438
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.00302 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.302
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.00302 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.302
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.070375
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.070375
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.070375
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.04504
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.070375
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.070375
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.070375
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.042225
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.00302 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.00302 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -1.51
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.00302 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -1.51
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.00302 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.001791 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.05878 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.001221 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.001642 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES | [7 empty] | 73.2433
Number of Bus | Name of Bus | ID | Max MW | L:1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.011059 | north | Y | -0.0066559 | 0.0082979 | 0.23204 | 0.0021883 | 0.0021883 | houston | Y | 0.0066559 | 1.1392
239 | BOSQUESW | 1 | 149 | 0.011059 | north | Y | -0.0066559 | 0.0082979 | 0.23204 | 0.0021883 | 0.0021883 | houston | Y | 0.0066559 | 0.66567
244 | WHITNYDM | 1 | 15 | 0.010637 | north | N | -0.0070779 | 0.0078759 | 0.23162 | 0.0017663 | 0.0017663 | houston | Y | 0.0070779 | 0
245 | WHITNYDM | 2 | 15 | 0.010637 | north | N | -0.0070779 | 0.0078759 | 0.23162 | 0.0017663 | 0.0017663 | houston | Y | 0.0070779 | 0
247 | BOSQUESW | 2 | 153 | 0.011059 | north | Y | -0.0066559 | 0.0082979 | 0.23204 | 0.0021883 | 0.0021883 | houston | Y | 0.0066559 | 0.68354
251 | BOSQUESW | 2 | 150 | 0.0103 | north | Y | -0.0074149 | 0.0075389 | 0.23128 | 0.0014293 | 0.0014293 | houston | Y | 0.0074149 | 0.89783
253 | BOSQUESW | 2 | 80 | 0.0103 | north | Y | -0.0074149 | 0.0075389 | 0.23128 | 0.0014293 | 0.0014293 | houston | Y | 0.0074149 | 0.47884
332 | RWMILLER | 1 | 73 | 0.00685 | north | Y | -0.010865 | 0.0040889 | 0.22783 | -0.0020207 | 0.0020207 | houston | Y | 0.010865 | 0.64563
333 | RWMILLER | 2 | 119 | 0.00685 | north | Y | -0.010865 | 0.0040889 | 0.22783 | -0.0020207 | 0.0020207 | houston | Y | 0.010865 | 1.0525
334 | RWMILLER | 3 | 205 | 0.00685 | north | Y | -0.010865 | 0.0040889 | 0.22783 | -0.0020207 | 0.0020207 | houston | Y | 0.010865 | 1.8131
335 | RWMILLER | 4 | 102 | 0.00685 | north | Y | -0.010865 | 0.0040889 | 0.22783 | -0.0020207 | 0.0020207 | houston | Y | 0.010865 | 0.90211
336 | RWMILLER | 5 | 96 | 0.00685 | north | Y | -0.010865 | 0.0040889 | 0.22783 | -0.0020207 | 0.0020207 | houston | Y | 0.010865 | 0.84904
344 | MRSSHPRD | 1 | 12 | 0.007809 | north | N | -0.0099059 | 0.0050479 | 0.22879 | -0.0010617 | 0.0010617 | houston | Y | 0.0099059 | 0
345 | MRSSHPRD | 2 | 12 | 0.007809 | north | N | -0.0099059 | 0.0050479 | 0.22879 | -0.0010617 | 0.0010617 | houston | Y | 0.0099059 | 0
366 | JNSNCNTY | 1 | 168 | 0.012483 | north | Y | -0.0052319 | 0.0097219 | 0.23347 | 0.0036123 | 0.0036123 | houston | Y | 0.0052319 | 0.27209
367 | JNSNCNTY | 2 | 90 | 0.012483 | north | Y | -0.0052319 | 0.0097219 | 0.23347 | 0.0036123 | 0.0036123 | houston | Y | 0.0052319 | 0.14576
503 | NTHTEXAS | 1 | 18 | 0.013969 | north | Y | -0.0037459 | 0.011208 | 0.23495 | 0.0050983 | 0.0037459 | North | N | 0.0037459 | 0
504 | NTHTEXAS | 2 | 18 | 0.013969 | north | Y | -0.0037459 | 0.011208 | 0.23495 | 0.0050983 | 0.0037459 | North | N | 0.0037459 | 0
505 | NTHTEXAS | 3 | 38 | 0.013969 | north | Y | -0.0037459 | 0.011208 | 0.23495 | 0.0050983 | 0.0037459 | North | N | 0.0037459 | 0
580 | JCKCNTY8 | 1 | 288 | 0.017155 | north | Y | -0.00055987 | 0.014394 | 0.23814 | 0.0082843 | 0.00055987 | North | N | 0.00055987 | 0
581 | JCKCNTY8 | 2 | 147 | 0.017155 | north | Y | -0.00055987 | 0.014394 | 0.23814 | 0.0082843 | 0.00055987 | North | N | 0.00055987 | 0
582 | JCKCNTY8 | 3 | 147 | 0.017155 | north | Y | -0.00055987 | 0.014394 | 0.23814 | 0.0082843 | 0.00055987 | North | N | 0.00055987 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.019393 | north | Y | 0.0016781 | 0.016632 | 0.24038 | 0.010522 | 0.0016781 | North | N | 0.0016781 | 0
837 | NEWMAN_G | 1 | 40 | 0.019615 | north | Y | 0.0019001 | 0.016854 | 0.2406 | 0.010744 | 0.0019001 | North | N | 0.0019001 | 0
842 | OLINGER_ | 1 | 79 | 0.019701 | north | Y | 0.0019861 | 0.01694 | 0.24068 | 0.01083 | 0.0019861 | North | N | 0.0019861 | 0
843 | OLINGER_ | 1 | 106 | 0.019701 | north | Y | 0.0019861 | 0.01694 | 0.24068 | 0.01083 | 0.0019861 | North | N | 0.0019861 | 0
844 | OLINGER_ | 1 | 146 | 0.019701 | north | Y | 0.0019861 | 0.01694 | 0.24068 | 0.01083 | 0.0019861 | North | N | 0.0019861 | 0
845 | OLINGER_ | 1 | 76 | 0.019701 | north | Y | 0.0019861 | 0.01694 | 0.24068 | 0.01083 | 0.0019861 | North | N | 0.0019861 | 0
923 | SPENCER_ | 1 | 60 | 0.023358 | north | Y | 0.0056431 | 0.020597 | 0.24434 | 0.014487 | 0.0056431 | North | N | 0.0056431 | 0
924 | SPENCER_ | 1 | 63 | 0.023358 | north | Y | 0.0056431 | 0.020597 | 0.24434 | 0.014487 | 0.0056431 | North | N | 0.0056431 | 0
948 | STEAM1 | 1 | 20 | 0.019619 | north | Y | 0.0019041 | 0.016858 | 0.2406 | 0.010748 | 0.0019041 | North | N | 0.0019041 | 0
949 | STEAM2 | 1 | 25 | 0.019619 | north | Y | 0.0019041 | 0.016858 | 0.2406 | 0.010748 | 0.0019041 | North | N | 0.0019041 | 0
950 | STEAM3 | 1 | 41 | 0.019619 | north | Y | 0.0019041 | 0.016858 | 0.2406 | 0.010748 | 0.0019041 | North | N | 0.0019041 | 0
990 | GIBN_CRE | 1 | 463 | 0.012257 | north | Y | -0.0054579 | 0.0094959 | 0.23324 | 0.0033863 | 0.0033863 | houston | Y | 0.0054579 | 0.95913
1002 | PBCTAGE_ | A | 66 | -0.23027 | west | Y | -0.24799 | -0.23304 | -0.0092916 | -0.23914 | 0.0092916 | west | N | 0.0092916 | 0
1003 | PBCTBGE_ | B | 65 | -0.23027 | west | Y | -0.24799 | -0.23304 | -0.0092916 | -0.23914 | 0.0092916 | west | N | 0.0092916 | 0
1004 | PBCTCGE_ | C | 67 | -0.23027 | west | Y | -0.24799 | -0.23304 | -0.0092916 | -0.23914 | 0.0092916 | west | N | 0.0092916 | 0
1005 | PBCTDGE_ | D | 67 | -0.23027 | west | Y | -0.24799 | -0.23304 | -0.0092916 | -0.23914 | 0.0092916 | west | N | 0.0092916 | 0
1006 | PBCTEGE_ | E | 67 | -0.23027 | west | Y | -0.24799 | -0.23304 | -0.0092916 | -0.23914 | 0.0092916 | west | N | 0.0092916 | 0
1007 | PB5GEN_6 | MB | 114 | -0.23027 | west | Y | -0.24799 | -0.23304 | -0.0092916 | -0.23914 | 0.0092916 | west | N | 0.0092916 | 0
1008 | PB6GEN_7 | MB | 515 | -0.23027 | west | Y | -0.24799 | -0.23304 | -0.0092916 | -0.23914 | 0.0092916 | west | N | 0.0092916 | 0
1039 | MRGNAG_1 | A | 66 | -0.23174 | west | Y | -0.24946 | -0.23451 | -0.010762 | -0.24061 | 0.010762 | west | N | 0.010762 | 0
1040 | MRGNBG_2 | B | 69 | -0.23174 | west | Y | -0.24946 | -0.23451 | -0.010762 | -0.24061 | 0.010762 | west | N | 0.010762 | 0
1041 | MRGNCG_3 | C | 69 | -0.23174 | west | Y | -0.24946 | -0.23451 | -0.010762 | -0.24061 | 0.010762 | west | N | 0.010762 | 0
1042 | MRGNDG_4 | D | 67 | -0.23174 | west | Y | -0.24946 | -0.23451 | -0.010762 | -0.24061 | 0.010762 | west | N | 0.010762 | 0
1043 | MRGNEG_5 | E | 67 | -0.23174 | west | Y | -0.24946 | -0.23451 | -0.010762 | -0.24061 | 0.010762 | west | N | 0.010762 | 0
1044 | MRGNFG_6 | F | 65 | -0.23174 | west | Y | -0.24946 | -0.23451 | -0.010762 | -0.24061 | 0.010762 | west | N | 0.010762 | 0
1045 | CALENG1G | 1 | 70 | -0.23648 | west | N | -0.25419 | -0.23924 | -0.015497 | -0.24535 | 0.015497 | west | N | 0.015497 | 0
1046 | CALENG2G | 2 | 73.4 | -0.23648 | west | N | -0.25419 | -0.23924 | -0.015497 | -0.24535 | 0.015497 | west | N | 0.015497 | 0
1047 | CALENG3G | 3 | 70.4 | -0.23648 | west | N | -0.25419 | -0.23924 | -0.015497 | -0.24535 | 0.015497 | west | N | 0.015497 | 0
1058 | LONGSHOR | 1 | 150 | -0.2372 | west | Y | -0.25491 | -0.23996 | -0.016215 | -0.24607 | 0.016215 | west | N | 0.016215 | 0
1058 | LONGSHOR | 2 | 220 | -0.2372 | west | Y | -0.25491 | -0.23996 | -0.016215 | -0.24607 | 0.016215 | west | N | 0.016215 | 0
1061 | CIELOGEN | 1 | 99 | -0.22131 | west | Y | -0.23903 | -0.22408 | -0.00033162 | -0.23018 | 0.00033162 | west | N | 0.00033162 | 0
1062 | CIELOGEN | 1 | 61 | -0.22131 | west | Y | -0.23903 | -0.22408 | -0.00033162 | -0.23018 | 0.00033162 | west | N | 0.00033162 | 0
1068 | SCURRYCW | 1 | 141 | -0.22159 | west | Y | -0.2393 | -0.22435 | -0.00060462 | -0.23046 | 0.00060462 | west | N | 0.00060462 | 0
1069 | KINDERMG | 1 | 25 | -0.22131 | west | N | -0.23903 | -0.22408 | -0.00033162 | -0.23018 | 0.00033162 | west | N | 0.00033162 | 0
1070 | KINDERMG | 1 | 45.7 | -0.22131 | west | N | -0.23903 | -0.22408 | -0.00033162 | -0.23018 | 0.00033162 | west | N | 0.00033162 | 0
1071 | KINDERMG | 1 | 45.7 | -0.22131 | west | N | -0.23903 | -0.22408 | -0.00033162 | -0.23018 | 0.00033162 | west | N | 0.00033162 | 0
1073 | SCURRYCW | 2 | 120 | -0.22159 | west | Y | -0.2393 | -0.22435 | -0.00060462 | -0.23046 | 0.00060462 | west | N | 0.00060462 | 0
1320 | BSP 1 | 1 | 25.8 | -0.2267 | west | N | -0.24442 | -0.22947 | -0.0057216 | -0.23557 | 0.0057216 | west | N | 0.0057216 | 0
1326 | STANTONW | 1 | 100.5 | -0.23069 | west | Y | -0.2484 | -0.23345 | -0.0097046 | -0.23956 | 0.0097046 | west | N | 0.0097046 | 0
1327 | WILDHRSE | 1 | 120 | -0.22795 | west | Y | -0.24566 | -0.23071 | -0.0069646 | -0.23682 | 0.0069646 | west | N | 0.0069646 | 0
1328 | OCOTILLO | 1 | 58 | -0.23071 | west | Y | -0.24843 | -0.23348 | -0.0097316 | -0.23958 | 0.0097316 | west | N | 0.0097316 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.23086 | west | Y | -0.24857 | -0.23362 | -0.0098756 | -0.23973 | 0.0098756 | west | N | 0.0098756 | 0
1343 | TRENTIPP | 1 | 150 | -0.21306 | west | Y | -0.23078 | -0.21582 | 0.0079194 | -0.22193 | 0.0079194 | west | N | 0.0079194 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.22187 | west | Y | -0.23958 | -0.22463 | -0.00088662 | -0.23074 | 0.00088662 | west | N | 0.00088662 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.22187 | west | Y | -0.23958 | -0.22463 | -0.00088662 | -0.23074 | 0.00088662 | west | N | 0.00088662 | 0
1354 | AEPWIND_ | 1 | 101 | -0.21306 | west | Y | -0.23078 | -0.21582 | 0.0079194 | -0.22193 | 0.0079194 | west | N | 0.0079194 | 0
1360 | GUNSIGHT | 1 | 120 | -0.2272 | west | Y | -0.24491 | -0.22996 | -0.0062126 | -0.23607 | 0.0062126 | west | N | 0.0062126 | 0
1432 | GRHAMSES | 2 | 366 | 0.067053 | north | Y | 0.049338 | 0.064292 | 0.28804 | 0.058182 | 0.049338 | North | N | 0.049338 | 0
1433 | GRHAMSES | 1 | 242 | 0.017813 | north | Y | 9.8133e-05 | 0.015052 | 0.2388 | 0.0089423 | 9.8133e-05 | North | N | 9.8133e-05 | 0
1437 | MESQUITW | 1 | 400 | -0.31678 | west | Y | -0.3345 | -0.31954 | -0.095799 | -0.32565 | 0.095799 | west | N | 0.095799 | 0
1438 | MESQUITW | 1 | 236 | -0.31529 | west | Y | -0.33301 | -0.31805 | -0.094311 | -0.32416 | 0.094311 | west | N | 0.094311 | 0
1442 | COKFIELD | 1 | 165 | -0.22354 | west | Y | -0.24125 | -0.2263 | -0.0025526 | -0.23241 | 0.0025526 | west | N | 0.0025526 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.036632 | north | Y | 0.018917 | 0.033871 | 0.25761 | 0.027761 | 0.018917 | North | N | 0.018917 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.036632 | north | Y | 0.018917 | 0.033871 | 0.25761 | 0.027761 | 0.018917 | North | N | 0.018917 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.036632 | north | Y | 0.018917 | 0.033871 | 0.25761 | 0.027761 | 0.018917 | North | N | 0.018917 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.014462 | west | Y | -0.0032529 | 0.011701 | 0.23544 | 0.0055913 | 0.0032529 | North | Y | 0.23544 | 4.6438
1479 | WFCOGEN_ | 2 | 20 | 0.014462 | west | Y | -0.0032529 | 0.011701 | 0.23544 | 0.0055913 | 0.0032529 | North | Y | 0.23544 | 4.6438
1482 | WFCOGEN_ | 1 | 20 | 0.014462 | west | Y | -0.0032529 | 0.011701 | 0.23544 | 0.0055913 | 0.0032529 | North | Y | 0.23544 | 4.6438
1482 | WFCOGEN_ | 2 | 17 | 0.014462 | west | Y | -0.0032529 | 0.011701 | 0.23544 | 0.0055913 | 0.0032529 | North | Y | 0.23544 | 3.9473
1600 | BARTNWND | 1 | 120 | 0.014237 | north | Y | -0.0034779 | 0.011476 | 0.23522 | 0.0053663 | 0.0034779 | North | N | 0.0034779 | 0
1643 | SLSTR1PP | 1 | 60 | -0.022852 | north | Y | -0.040567 | -0.025613 | 0.19813 | -0.031723 | 0.025613 | south | Y | 0.040567 | 0.89723
1675 | PEC_1G | 1 | 75 | 0.020071 | north | N | 0.0023561 | 0.01731 | 0.24105 | 0.0112 | 0.0023561 | North | N | 0.0023561 | 0
1676 | PEC_2G | 2 | 79.6 | 0.020071 | north | N | 0.0023561 | 0.01731 | 0.24105 | 0.0112 | 0.0023561 | North | N | 0.0023561 | 0
1677 | PEC_3G | 3 | 88.4 | 0.020071 | north | N | 0.0023561 | 0.01731 | 0.24105 | 0.0112 | 0.0023561 | North | N | 0.0023561 | 0
1678 | LAMARPWR | 1 | 160 | 0.020122 | north | Y | 0.0024071 | 0.017361 | 0.2411 | 0.011251 | 0.0024071 | North | N | 0.0024071 | 0
1679 | LAMARPWR | 2 | 156 | 0.020122 | north | Y | 0.0024071 | 0.017361 | 0.2411 | 0.011251 | 0.0024071 | North | N | 0.0024071 | 0
1680 | LAMARPWR | 3 | 196 | 0.020122 | north | Y | 0.0024071 | 0.017361 | 0.2411 | 0.011251 | 0.0024071 | North | N | 0.0024071 | 0
1681 | LAMARPWR | 4 | 156 | 0.020122 | north | Y | 0.0024071 | 0.017361 | 0.2411 | 0.011251 | 0.0024071 | North | N | 0.0024071 | 0
1682 | LAMARPWR | 5 | 157 | 0.020122 | north | Y | 0.0024071 | 0.017361 | 0.2411 | 0.011251 | 0.0024071 | North | N | 0.0024071 | 0
1683 | LAMARPWR | 6 | 198 | 0.020122 | north | Y | 0.0024071 | 0.017361 | 0.2411 | 0.011251 | 0.0024071 | North | N | 0.0024071 | 0
1687 | VALLEY_1 | 1 | 170 | 0.02028 | north | Y | 0.0025651 | 0.017519 | 0.24126 | 0.011409 | 0.0025651 | North | N | 0.0025651 | 0
1688 | VALLEY_2 | 2 | 520 | 0.02028 | north | Y | 0.0025651 | 0.017519 | 0.24126 | 0.011409 | 0.0025651 | North | N | 0.0025651 | 0
1689 | VALLEY_3 | 3 | 370 | 0.020186 | north | Y | 0.0024711 | 0.017425 | 0.24117 | 0.011315 | 0.0024711 | North | N | 0.0024711 | 0
1701 | MOSES_1G | 1 | 558 | 0.020013 | north | Y | 0.0022981 | 0.017252 | 0.241 | 0.011142 | 0.0022981 | North | N | 0.0022981 | 0
1702 | MOSES_2G | 2 | 579 | 0.020013 | north | Y | 0.0022981 | 0.017252 | 0.241 | 0.011142 | 0.0022981 | North | N | 0.0022981 | 0
1703 | MOSES_3G | 3 | 808 | 0.020013 | north | Y | 0.0022981 | 0.017252 | 0.241 | 0.011142 | 0.0022981 | North | N | 0.0022981 | 0
1861 | EAGLEMNT | MB | 112 | 0.023153 | north | Y | 0.0054381 | 0.020392 | 0.24414 | 0.014282 | 0.0054381 | North | N | 0.0054381 | 0
1862 | EAGLEMNT | MB | 100 | 0.023153 | north | Y | 0.0054381 | 0.020392 | 0.24414 | 0.014282 | 0.0054381 | North | N | 0.0054381 | 0
1863 | EAGLEMNT | MB | 378 | 0.023153 | north | Y | 0.0054381 | 0.020392 | 0.24414 | 0.014282 | 0.0054381 | North | N | 0.0054381 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.011622 | north | Y | -0.0060929 | 0.0088609 | 0.2326 | 0.0027513 | 0.0027513 | houston | Y | 0.0060929 | 0.72612
1878 | WLFHOLW_ | 2 | 205 | 0.011622 | north | Y | -0.0060929 | 0.0088609 | 0.2326 | 0.0027513 | 0.0027513 | houston | Y | 0.0060929 | 0.68502
1879 | WLFHOLW_ | 3 | 272.4 | 0.011622 | north | Y | -0.0060929 | 0.0088609 | 0.2326 | 0.0027513 | 0.0027513 | houston | Y | 0.0060929 | 0.91024
1889 | DECRDOVA | MB | 770 | 0.015217 | north | Y | -0.0024979 | 0.012456 | 0.2362 | 0.0063463 | 0.0024979 | North | N | 0.0024979 | 0
1892 | DECRDOVA | A | 70 | 0.011726 | north | Y | -0.0059889 | 0.0089649 | 0.23271 | 0.0028553 | 0.0028553 | houston | Y | 0.0059889 | 0.21935
1893 | DECRDOVA | B | 69 | 0.011726 | north | Y | -0.0059889 | 0.0089649 | 0.23271 | 0.0028553 | 0.0028553 | houston | Y | 0.0059889 | 0.21622
1894 | DECRDOVA | C | 69 | 0.011726 | north | Y | -0.0059889 | 0.0089649 | 0.23271 | 0.0028553 | 0.0028553 | houston | Y | 0.0059889 | 0.21622
1895 | DECRDOVA | D | 68 | 0.011726 | north | Y | -0.0059889 | 0.0089649 | 0.23271 | 0.0028553 | 0.0028553 | houston | Y | 0.0059889 | 0.21308
1898 | COMCHEPK | 1 | 1157 | 0.010497 | north | N | -0.0072179 | 0.0077359 | 0.23148 | 0.0016263 | 0.0016263 | houston | Y | 0.0072179 | 0
1899 | COMCHEPK | 2 | 1158 | 0.010497 | north | N | -0.0072179 | 0.0077359 | 0.23148 | 0.0016263 | 0.0016263 | houston | Y | 0.0072179 | 0
1937 | MDLTHELP | 5 | 224 | 0.016636 | north | Y | -0.0010789 | 0.013875 | 0.23762 | 0.0077653 | 0.0010789 | North | N | 0.0010789 | 0
1938 | MDLTHELP | 6 | 226 | 0.016636 | north | Y | -0.0010789 | 0.013875 | 0.23762 | 0.0077653 | 0.0010789 | North | N | 0.0010789 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.017509 | north | Y | -0.00020587 | 0.014748 | 0.23849 | 0.0086383 | 0.00020587 | North | N | 0.00020587 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.017509 | north | Y | -0.00020587 | 0.014748 | 0.23849 | 0.0086383 | 0.00020587 | North | N | 0.00020587 | 0
1943 | MDLTHELP | 3 | 212 | 0.016636 | north | Y | -0.0010789 | 0.013875 | 0.23762 | 0.0077653 | 0.0010789 | North | N | 0.0010789 | 0
1944 | MDLTHELP | 4 | 211 | 0.016636 | north | Y | -0.0010789 | 0.013875 | 0.23762 | 0.0077653 | 0.0010789 | North | N | 0.0010789 | 0
1947 | HANDLEY_ | 3 | 395 | 0.019778 | north | Y | 0.0020631 | 0.017017 | 0.24076 | 0.010907 | 0.0020631 | North | N | 0.0020631 | 0
1948 | HANDLEY_ | 4 | 435 | 0.019739 | north | Y | 0.0020241 | 0.016978 | 0.24072 | 0.010868 | 0.0020241 | North | N | 0.0020241 | 0
1949 | HANDLEY_ | 5 | 435 | 0.019778 | north | Y | 0.0020631 | 0.017017 | 0.24076 | 0.010907 | 0.0020631 | North | N | 0.0020631 | 0
2371 | COLLIN_1 | MB | 138 | 0.020923 | north | Y | 0.0032081 | 0.018162 | 0.24191 | 0.012052 | 0.0032081 | North | N | 0.0032081 | 0
2413 | MTCK6_G | 6 | 118 | 0.018791 | north | Y | 0.0010761 | 0.01603 | 0.23977 | 0.0099203 | 0.0010761 | North | N | 0.0010761 | 0
2414 | MTCK7_G | 7 | 115 | 0.018791 | north | Y | 0.0010761 | 0.01603 | 0.23977 | 0.0099203 | 0.0010761 | North | N | 0.0010761 | 0
2417 | MTCK8_G | 8 | 556 | 0.018791 | north | Y | 0.0010761 | 0.01603 | 0.23977 | 0.0099203 | 0.0010761 | North | N | 0.0010761 | 0
2451 | LKHB1_G | 1 | 388 | 0.019244 | north | Y | 0.0015291 | 0.016483 | 0.24023 | 0.010373 | 0.0015291 | North | N | 0.0015291 | 0
2452 | LKHB2_G | 2 | 515 | 0.019244 | north | Y | 0.0015291 | 0.016483 | 0.24023 | 0.010373 | 0.0015291 | North | N | 0.0015291 | 0
3097 | MARTLAKE | 1 | 785 | 0.017927 | north | Y | 0.00021213 | 0.015166 | 0.23891 | 0.0090563 | 0.00021213 | North | N | 0.00021213 | 0
3098 | MARTLAKE | 2 | 795 | 0.017927 | north | Y | 0.00021213 | 0.015166 | 0.23891 | 0.0090563 | 0.00021213 | North | N | 0.00021213 | 0
3099 | MARTLAKE | 3 | 780 | 0.017927 | north | Y | 0.00021213 | 0.015166 | 0.23891 | 0.0090563 | 0.00021213 | North | N | 0.00021213 | 0
3107 | STRYKER_ | 1 | 182 | 0.017576 | north | Y | -0.00013887 | 0.014815 | 0.23856 | 0.0087053 | 0.00013887 | North | N | 0.00013887 | 0
3108 | STRYKER_ | 2 | 484 | 0.017576 | north | Y | -0.00013887 | 0.014815 | 0.23856 | 0.0087053 | 0.00013887 | North | N | 0.00013887 | 0
3126 | TRINIDAD | 1 | 224 | 0.016896 | north | Y | -0.00081887 | 0.014135 | 0.23788 | 0.0080253 | 0.00081887 | North | N | 0.00081887 | 0
3309 | ASPN_G | 1 | 50 | 0.017605 | north | Y | -0.00010987 | 0.014844 | 0.23859 | 0.0087343 | 0.00010987 | North | N | 0.00010987 | 0
3348 | CHAMPION | MB | 42 | 0.017621 | north | N | -9.3867e-05 | 0.01486 | 0.2386 | 0.0087503 | 9.3867e-05 | North | N | 9.3867e-05 | 0
3381 | BBRN_1G | 1 | 615 | 0.01586 | north | Y | -0.0018549 | 0.013099 | 0.23684 | 0.0069893 | 0.0018549 | North | N | 0.0018549 | 0
3382 | BBRN_2G | 2 | 587 | 0.01586 | north | Y | -0.0018549 | 0.013099 | 0.23684 | 0.0069893 | 0.0018549 | North | N | 0.0018549 | 0
3403 | THOUSE_1 | MB | 537 | 0.01203 | north | Y | -0.0056849 | 0.0092689 | 0.23301 | 0.0031593 | 0.0031593 | houston | Y | 0.0056849 | 0
3404 | THOUSE_2 | 2 | 787 | 0.01203 | north | Y | -0.0056849 | 0.0092689 | 0.23301 | 0.0031593 | 0.0031593 | houston | Y | 0.0056849 | 1.9876
3416 | LAKE_CRK | MB | 75 | 0.011449 | north | Y | -0.0062659 | 0.0086879 | 0.23243 | 0.0025783 | 0.0025783 | houston | Y | 0.0062659 | 0
3417 | LAKE_CRK | MB | 222 | 0.011449 | north | Y | -0.0062659 | 0.0086879 | 0.23243 | 0.0025783 | 0.0025783 | houston | Y | 0.0062659 | 0
3432 | SANDOW_4 | 4 | 569 | 0.007042 | south | Y | -0.010673 | 0.0042809 | 0.22802 | -0.0018287 | 0.0018287 | houston | Y | 0.0042809 | 1.3953
5026 | BRAUNIG_ | 1 | 209 | 0.001582 | south | Y | -0.016133 | -0.0011791 | 0.22256 | -0.0072887 | 0.0011791 | south | N | 0.0011791 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.001582 | south | Y | -0.016133 | -0.0011791 | 0.22256 | -0.0072887 | 0.0011791 | south | N | 0.0011791 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.001455 | south | Y | -0.01626 | -0.0013061 | 0.22244 | -0.0074157 | 0.0013061 | south | N | 0.0013061 | 0
5031 | BRA_VHBC | 1 | 46 | 0.001582 | south | Y | -0.016133 | -0.0011791 | 0.22256 | -0.0072887 | 0.0011791 | south | N | 0.0011791 | 0
5032 | BRA_VHBC | 2 | 47 | 0.001582 | south | Y | -0.016133 | -0.0011791 | 0.22256 | -0.0072887 | 0.0011791 | south | N | 0.0011791 | 0
5033 | BRA_VHBC | 3 | 46 | 0.001582 | south | Y | -0.016133 | -0.0011791 | 0.22256 | -0.0072887 | 0.0011791 | south | N | 0.0011791 | 0
5034 | BRA_VHBC | 4 | 46 | 0.001582 | south | Y | -0.016133 | -0.0011791 | 0.22256 | -0.0072887 | 0.0011791 | south | N | 0.0011791 | 0
5111 | CALAVER_ | 1 | 424 | 0.00165 | south | Y | -0.016065 | -0.0011111 | 0.22263 | -0.0072207 | 0.0011111 | south | N | 0.0011111 | 0
5112 | CALAVER_ | 2 | 425 | 0.00165 | south | Y | -0.016065 | -0.0011111 | 0.22263 | -0.0072207 | 0.0011111 | south | N | 0.0011111 | 0
5264 | LEON_LCP | 3 | 58 | 0.001082 | south | Y | -0.016633 | -0.0016791 | 0.22206 | -0.0077887 | 0.0016791 | south | N | 0.0016791 | 0
5265 | LEON_LCP | 4 | 89 | 0.001082 | south | Y | -0.016633 | -0.0016791 | 0.22206 | -0.0077887 | 0.0016791 | south | N | 0.0016791 | 0
5266 | LEON_LCP | 1 | 44 | 0.001082 | south | Y | -0.016633 | -0.0016791 | 0.22206 | -0.0077887 | 0.0016791 | south | N | 0.0016791 | 0
5267 | LEON_LCP | 2 | 44 | 0.001082 | south | Y | -0.016633 | -0.0016791 | 0.22206 | -0.0077887 | 0.0016791 | south | N | 0.0016791 | 0
5268 | LEON_LCP | 3 | 43 | 0.001082 | south | Y | -0.016633 | -0.0016791 | 0.22206 | -0.0077887 | 0.0016791 | south | N | 0.0016791 | 0
5269 | LEON_LCP | 4 | 45 | 0.001082 | south | Y | -0.016633 | -0.0016791 | 0.22206 | -0.0077887 | 0.0016791 | south | N | 0.0016791 | 0
5396 | CALAVER_ | 1 | 412 | 0.001584 | south | Y | -0.016131 | -0.0011771 | 0.22257 | -0.0072867 | 0.0011771 | south | N | 0.0011771 | 0
5397 | CALAVER_ | 2 | 400 | 0.001584 | south | Y | -0.016131 | -0.0011771 | 0.22257 | -0.0072867 | 0.0011771 | south | N | 0.0011771 | 0
5401 | CALAVER_ | 1 | 546 | 0.002129 | south | Y | -0.015586 | -0.00063211 | 0.22311 | -0.0067417 | 0.00063211 | south | N | 0.00063211 | 0
5402 | CALAVER_ | 2 | 750 | 0.002129 | south | Y | -0.015586 | -0.00063211 | 0.22311 | -0.0067417 | 0.00063211 | south | N | 0.00063211 | 0
5436 | TUTTL_WB | MB | 61 | 0.001923 | south | Y | -0.015792 | -0.00083811 | 0.22291 | -0.0069477 | 0.00083811 | south | N | 0.00083811 | 0
5438 | TUTTL_WB | MB | 95 | 0.001923 | south | Y | -0.015792 | -0.00083811 | 0.22291 | -0.0069477 | 0.00083811 | south | N | 0.00083811 | 0
5439 | TUTTL_WB | MB | 151 | 0.001923 | south | Y | -0.015792 | -0.00083811 | 0.22291 | -0.0069477 | 0.00083811 | south | N | 0.00083811 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.002006 | south | Y | -0.015709 | -0.00075511 | 0.22299 | -0.0068647 | 0.00075511 | south | N | 0.00075511 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.002006 | south | Y | -0.015709 | -0.00075511 | 0.22299 | -0.0068647 | 0.00075511 | south | N | 0.00075511 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.002006 | south | Y | -0.015709 | -0.00075511 | 0.22299 | -0.0068647 | 0.00075511 | south | N | 0.00075511 | 0
5503 | RAYBURNG | 1 | 22 | 0.003216 | south | Y | -0.014499 | 0.00045489 | 0.2242 | -0.0056547 | 0.00045489 | south | N | 0.00045489 | 0
5505 | RAYBURNG | 1 | 11 | 0.003216 | south | Y | -0.014499 | 0.00045489 | 0.2242 | -0.0056547 | 0.00045489 | south | N | 0.00045489 | 0
5506 | RAYBURNG | 1 | 11 | 0.003216 | south | Y | -0.014499 | 0.00045489 | 0.2242 | -0.0056547 | 0.00045489 | south | N | 0.00045489 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.003367 | south | Y | -0.014348 | 0.00060589 | 0.22435 | -0.0055037 | 0.00060589 | south | N | 0.00060589 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.003367 | south | Y | -0.014348 | 0.00060589 | 0.22435 | -0.0055037 | 0.00060589 | south | N | 0.00060589 | 0
5511 | RAYBURNC | 1 | 46 | 0.003367 | south | Y | -0.014348 | 0.00060589 | 0.22435 | -0.0055037 | 0.00060589 | south | N | 0.00060589 | 0
5512 | RAYBURNC | 1 | 48 | 0.003367 | south | Y | -0.014348 | 0.00060589 | 0.22435 | -0.0055037 | 0.00060589 | south | N | 0.00060589 | 0
5728 | FALCONHY | 2 | 12 | 0.000348 | south | N | -0.017367 | -0.0024131 | 0.22133 | -0.0085227 | 0.0024131 | south | N | 0.0024131 | 0
5729 | FALCONHY | 3 | 11 | 0.000348 | south | N | -0.017367 | -0.0024131 | 0.22133 | -0.0085227 | 0.0024131 | south | N | 0.0024131 | 0
5890 | PEARSALL | 1 | 24 | -0.006179 | south | Y | -0.023894 | -0.0089401 | 0.2148 | -0.01505 | 0.0089401 | south | N | 0.0089401 | 0
5891 | PEARSALL | 1 | 24 | -0.006179 | south | Y | -0.023894 | -0.0089401 | 0.2148 | -0.01505 | 0.0089401 | south | N | 0.0089401 | 0
5892 | PEARSALL | 1 | 23 | -0.006179 | south | Y | -0.023894 | -0.0089401 | 0.2148 | -0.01505 | 0.0089401 | south | N | 0.0089401 | 0
5903 | SANMIGUE | 1 | 396 | 0.001523 | south | Y | -0.016192 | -0.0012381 | 0.22251 | -0.0073477 | 0.0012381 | south | N | 0.0012381 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.006794 | houston | N | -0.010921 | 0.0040329 | 0.22778 | -0.0020767 | 0.0020767 | houston | N | 0.0020767 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.006794 | houston | N | -0.010921 | 0.0040329 | 0.22778 | -0.0020767 | 0.0020767 | houston | N | 0.0020767 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | Y | 0.017715 | 0
5932 | SI_RAY9 | 9 | 38 | 0.002424 | south | Y | -0.015291 | -0.00033711 | 0.22341 | -0.0064467 | 0.00033711 | south | N | 0.00033711 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.002424 | south | Y | -0.015291 | -0.00033711 | 0.22341 | -0.0064467 | 0.00033711 | south | N | 0.00033711 | 0
5934 | SI_RAY5 | 5 | 15 | 0.002424 | south | Y | -0.015291 | -0.00033711 | 0.22341 | -0.0064467 | 0.00033711 | south | N | 0.00033711 | 0
5935 | SI_RAY10 | 10 | 47 | 0.002424 | south | Y | -0.015291 | -0.00033711 | 0.22341 | -0.0064467 | 0.00033711 | south | N | 0.00033711 | 0
6016 | SWMESA | 1 | 75 | -0.21529 | west | Y | -0.23301 | -0.21805 | 0.0056894 | -0.22416 | 0.0056894 | west | N | 0.0056894 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | Y | 0.22098 | 0
6144 | MCADOO1A | 1 | 150 | -0.18967 | west | Y | -0.20738 | -0.19243 | 0.031316 | -0.19854 | 0.031316 | west | N | 0.031316 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.21158 | west | Y | -0.22929 | -0.21434 | 0.0094044 | -0.22045 | 0.0094044 | west | N | 0.0094044 | 0
6476 | LANGFORD | 1 | 150 | -0.15504 | west | Y | -0.17276 | -0.15781 | 0.065938 | -0.16391 | 0.065938 | west | N | 0.065938 | 0
6637 | SNYDERW1 | 1 | 63 | -0.22371 | west | Y | -0.24143 | -0.22648 | -0.0027316 | -0.23258 | 0.0027316 | west | N | 0.0027316 | 0
6752 | OKLA0A | 1 | 649.7 | -0.081789 | west | Y | -0.099504 | -0.08455 | 0.13919 | -0.09066 | 0.08455 | south | Y | 0.13919 | 35.5017
6948 | DENISNDM | 1 | 40 | 0.020362 | north | N | 0.0026471 | 0.017601 | 0.24134 | 0.011491 | 0.0026471 | North | N | 0.0026471 | 0
6948 | DENISNDM | 2 | 40 | 0.020362 | north | N | 0.0026471 | 0.017601 | 0.24134 | 0.011491 | 0.0026471 | North | N | 0.0026471 | 0
7000 | L_FERGUS | 1 | 422 | -0.004902 | south | Y | -0.022617 | -0.0076631 | 0.21608 | -0.013773 | 0.0076631 | south | N | 0.0076631 | 0
7004 | L_SIMGID | 1 | 132 | 0.004748 | south | Y | -0.012967 | 0.0019869 | 0.22573 | -0.0041227 | 0.0019869 | south | N | 0.0019869 | 0
7005 | L_SIMGID | 2 | 134 | 0.004748 | south | Y | -0.012967 | 0.0019869 | 0.22573 | -0.0041227 | 0.0019869 | south | N | 0.0019869 | 0
7006 | L_SIMGID | 3 | 323 | 0.004748 | south | Y | -0.012967 | 0.0019869 | 0.22573 | -0.0041227 | 0.0019869 | south | N | 0.0019869 | 0
7007 | L_LOSTPI | 1 | 158 | 0.005167 | south | Y | -0.012548 | 0.0024059 | 0.22615 | -0.0037037 | 0.0024059 | south | N | 0.0024059 | 0
7008 | L_LOSTPI | 2 | 160 | 0.005167 | south | Y | -0.012548 | 0.0024059 | 0.22615 | -0.0037037 | 0.0024059 | south | N | 0.0024059 | 0
7009 | L_LOSTPI | 3 | 175 | 0.005167 | south | Y | -0.012548 | 0.0024059 | 0.22615 | -0.0037037 | 0.0024059 | south | N | 0.0024059 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.00521 | south | Y | -0.012505 | 0.0024489 | 0.22619 | -0.0036607 | 0.0024489 | south | N | 0.0024489 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.00521 | south | Y | -0.012505 | 0.0024489 | 0.22619 | -0.0036607 | 0.0024489 | south | N | 0.0024489 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.005208 | south | Y | -0.012507 | 0.0024469 | 0.22619 | -0.0036627 | 0.0024469 | south | N | 0.0024469 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.003138 | south | Y | -0.014577 | 0.00037689 | 0.22412 | -0.0057327 | 0.00037689 | south | N | 0.00037689 | 0
7015 | L_HAYSEN | 2 | 225 | 0.003138 | south | Y | -0.014577 | 0.00037689 | 0.22412 | -0.0057327 | 0.00037689 | south | N | 0.00037689 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.003138 | south | Y | -0.014577 | 0.00037689 | 0.22412 | -0.0057327 | 0.00037689 | south | N | 0.00037689 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.003138 | south | Y | -0.014577 | 0.00037689 | 0.22412 | -0.0057327 | 0.00037689 | south | N | 0.00037689 | 0
7020 | L_AUSTPL | 1 | 8 | 0.003972 | south | N | -0.013743 | 0.0012109 | 0.22495 | -0.0048987 | 0.0012109 | south | N | 0.0012109 | 0
7020 | L_AUSTPL | 2 | 8 | 0.003972 | south | N | -0.013743 | 0.0012109 | 0.22495 | -0.0048987 | 0.0012109 | south | N | 0.0012109 | 0
7022 | L_BUCHAN | 1 | 18 | -0.005208 | south | N | -0.022923 | -0.0079691 | 0.21577 | -0.014079 | 0.0079691 | south | N | 0.0079691 | 0
7023 | L_BUCHAN | 2 | 18 | -0.005208 | south | N | -0.022923 | -0.0079691 | 0.21577 | -0.014079 | 0.0079691 | south | N | 0.0079691 | 0
7024 | L_BUCHAN | 3 | 15 | -0.005208 | south | N | -0.022923 | -0.0079691 | 0.21577 | -0.014079 | 0.0079691 | south | N | 0.0079691 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.007637 | south | N | -0.025352 | -0.010398 | 0.21335 | -0.016508 | 0.010398 | south | N | 0.010398 | 0
7028 | L_MARBFA | 1 | 18 | -0.002832 | south | N | -0.020547 | -0.0055931 | 0.21815 | -0.011703 | 0.0055931 | south | N | 0.0055931 | 0
7029 | L_MARBFA | 2 | 18 | -0.002832 | south | N | -0.020547 | -0.0055931 | 0.21815 | -0.011703 | 0.0055931 | south | N | 0.0055931 | 0
7031 | L_MARSFO | 1 | 35 | 0.001861 | south | N | -0.015854 | -0.00090011 | 0.22284 | -0.0070097 | 0.00090011 | south | N | 0.00090011 | 0
7032 | L_MARSFO | 2 | 34 | 0.001861 | south | N | -0.015854 | -0.00090011 | 0.22284 | -0.0070097 | 0.00090011 | south | N | 0.00090011 | 0
7033 | L_MARSFO | 3 | 35 | 0.001861 | south | N | -0.015854 | -0.00090011 | 0.22284 | -0.0070097 | 0.00090011 | south | N | 0.00090011 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.004377 | south | N | -0.022092 | -0.0071381 | 0.21661 | -0.013248 | 0.0071381 | south | N | 0.0071381 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.004377 | south | N | -0.022092 | -0.0071381 | 0.21661 | -0.013248 | 0.0071381 | south | N | 0.0071381 | 0
7038 | L_DELAWA | 1 | 35 | -0.23004 | west | Y | -0.24776 | -0.23281 | -0.0090616 | -0.23891 | 0.0090616 | west | N | 0.0090616 | 0
7038 | L_DELAWA | 2 | 30 | -0.23004 | west | Y | -0.24776 | -0.23281 | -0.0090616 | -0.23891 | 0.0090616 | west | N | 0.0090616 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.005032 | south | Y | -0.012683 | 0.0022709 | 0.22601 | -0.0038387 | 0.0022709 | south | N | 0.0022709 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.005032 | south | Y | -0.012683 | 0.0022709 | 0.22601 | -0.0038387 | 0.0022709 | south | N | 0.0022709 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.005032 | south | Y | -0.012683 | 0.0022709 | 0.22601 | -0.0038387 | 0.0022709 | south | N | 0.0022709 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.005032 | south | Y | -0.012683 | 0.0022709 | 0.22601 | -0.0038387 | 0.0022709 | south | N | 0.0022709 | 0
7487 | L_CANYHY | 1 | 6 | 0.002647 | south | N | -0.015068 | -0.00011411 | 0.22363 | -0.0062237 | 0.00011411 | south | N | 0.00011411 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.002925 | south | N | -0.01479 | 0.00016389 | 0.22391 | -0.0059457 | 0.00016389 | south | N | 0.00016389 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.002925 | south | N | -0.01479 | 0.00016389 | 0.22391 | -0.0059457 | 0.00016389 | south | N | 0.00016389 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.002925 | south | N | -0.01479 | 0.00016389 | 0.22391 | -0.0059457 | 0.00016389 | south | N | 0.00016389 | 0
7609 | L_SCHUMA | 1 | 4 | 0.002585 | south | N | -0.01513 | -0.00017611 | 0.22357 | -0.0062857 | 0.00017611 | south | N | 0.00017611 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.003272 | south | N | -0.014443 | 0.00051089 | 0.22425 | -0.0055987 | 0.00051089 | south | N | 0.00051089 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.003272 | south | N | -0.014443 | 0.00051089 | 0.22425 | -0.0055987 | 0.00051089 | south | N | 0.00051089 | 0
7800 | L_GUADGE | 1 | 147 | 0.002716 | south | Y | -0.014999 | -4.5111e-05 | 0.2237 | -0.0061547 | 4.5111e-05 | south | N | 4.5111e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.002716 | south | Y | -0.014999 | -4.5111e-05 | 0.2237 | -0.0061547 | 4.5111e-05 | south | N | 4.5111e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.002716 | south | Y | -0.014999 | -4.5111e-05 | 0.2237 | -0.0061547 | 4.5111e-05 | south | N | 4.5111e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.002716 | south | Y | -0.014999 | -4.5111e-05 | 0.2237 | -0.0061547 | 4.5111e-05 | south | N | 4.5111e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.002716 | south | Y | -0.014999 | -4.5111e-05 | 0.2237 | -0.0061547 | 4.5111e-05 | south | N | 4.5111e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.002716 | south | Y | -0.014999 | -4.5111e-05 | 0.2237 | -0.0061547 | 4.5111e-05 | south | N | 4.5111e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.004767 | south | Y | -0.012948 | 0.0020059 | 0.22575 | -0.0041037 | 0.0020059 | south | N | 0.0020059 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.004767 | south | Y | -0.012948 | 0.0020059 | 0.22575 | -0.0041037 | 0.0020059 | south | N | 0.0020059 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.004767 | south | Y | -0.012948 | 0.0020059 | 0.22575 | -0.0041037 | 0.0020059 | south | N | 0.0020059 | 0
7810 | L_RIONOG | 1 | 142 | 0.00293 | south | Y | -0.014785 | 0.00016889 | 0.22391 | -0.0059407 | 0.00016889 | south | N | 0.00016889 | 0
7811 | L_RIONOG | 2 | 145 | 0.00293 | south | Y | -0.014785 | 0.00016889 | 0.22391 | -0.0059407 | 0.00016889 | south | N | 0.00016889 | 0
7812 | L_RIONOG | 3 | 151 | 0.00293 | south | Y | -0.014785 | 0.00016889 | 0.22391 | -0.0059407 | 0.00016889 | south | N | 0.00016889 | 0
7813 | L_RIONOG | 4 | 290 | 0.00293 | south | Y | -0.014785 | 0.00016889 | 0.22391 | -0.0059407 | 0.00016889 | south | N | 0.00016889 | 0
8032 | AMISTADH | 1 | 33 | -0.05878 | south | N | -0.076495 | -0.061541 | 0.1622 | -0.067651 | 0.061541 | south | N | 0.061541 | 0
8033 | AMISTADH | 2 | 25 | -0.05878 | south | N | -0.076495 | -0.061541 | 0.1622 | -0.067651 | 0.061541 | south | N | 0.061541 | 0
8048 | FALCONHY | 1 | 12 | 0.000348 | south | N | -0.017367 | -0.0024131 | 0.22133 | -0.0085227 | 0.0024131 | south | N | 0.0024131 | 0
8066 | DUP1V#1 | 1 | 73 | 0.003515 | south | N | -0.0142 | 0.00075389 | 0.2245 | -0.0053557 | 0.00075389 | south | N | 0.00075389 | 0
8134 | FOR69CG0 | 1 | 79 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
8138 | FOR69CG0 | 2 | 81 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8147 | UCAR #2 | 10 | 28 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
8148 | UCAR #1 | 2 | 7 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
8153 | FOR69CG0 | 3 | 79 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
8154 | FOR69CG0 | 4 | 80 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
8156 | FOR69CG0 | 6 | 25 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
8157 | FOR69CG0 | 7 | 46 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
8161 | COLETOU1 | 1 | 629 | 0.002736 | south | Y | -0.014979 | -2.5111e-05 | 0.22372 | -0.0061347 | 2.5111e-05 | south | N | 2.5111e-05 | 0
8173 | VICEC51A | 5 | 144 | 0.003434 | south | Y | -0.014281 | 0.00067289 | 0.22442 | -0.0054367 | 0.00067289 | south | N | 0.00067289 | 0
8174 | VICEC61A | 6 | 188 | 0.003434 | south | Y | -0.014281 | 0.00067289 | 0.22442 | -0.0054367 | 0.00067289 | south | N | 0.00067289 | 0
8189 | CUERO 2 | 1 | 12 | 0.003279 | south | N | -0.014436 | 0.00051789 | 0.22426 | -0.0055917 | 0.00051789 | south | N | 0.00051789 | 0
8262 | ELPS | 1 | 6 | -0.042062 | south | N | -0.059777 | -0.044823 | 0.17892 | -0.050933 | 0.044823 | south | N | 0.044823 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8442 | NBEC71A | 1 | 336 | 0.002722 | south | Y | -0.014993 | -3.9111e-05 | 0.2237 | -0.0061487 | 3.9111e-05 | south | N | 3.9111e-05 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.017715 | -0.0027611 | 0.22098 | -0.0088707 | 0.0027611 | south | N | 0.0027611 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.002691 | south | Y | -0.015024 | -7.0111e-05 | 0.22367 | -0.0061797 | 7.0111e-05 | south | N | 7.0111e-05 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.002691 | south | Y | -0.015024 | -7.0111e-05 | 0.22367 | -0.0061797 | 7.0111e-05 | south | N | 7.0111e-05 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.002651 | south | N | -0.015064 | -0.00011011 | 0.22363 | -0.0062197 | 0.00011011 | south | N | 0.00011011 | 0
8506 | VAL #1 | 1 | 25 | 0.002671 | south | N | -0.015044 | -9.0111e-05 | 0.22365 | -0.0061997 | 9.0111e-05 | south | N | 9.0111e-05 | 0
8507 | VAL #2 | 2 | 25 | 0.002671 | south | N | -0.015044 | -9.0111e-05 | 0.22365 | -0.0061997 | 9.0111e-05 | south | N | 9.0111e-05 | 0
8511 | OXY_CC0A | 1 | 38 | 0.002669 | south | N | -0.015046 | -9.2111e-05 | 0.22365 | -0.0062017 | 9.2111e-05 | south | N | 9.2111e-05 | 0
8517 | CELANEBI | 1 | 29 | 0.002567 | south | N | -0.015148 | -0.00019411 | 0.22355 | -0.0063037 | 0.00019411 | south | N | 0.00019411 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.00272 | south | N | -0.014995 | -4.1111e-05 | 0.2237 | -0.0061507 | 4.1111e-05 | south | N | 4.1111e-05 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.00272 | south | N | -0.014995 | -4.1111e-05 | 0.2237 | -0.0061507 | 4.1111e-05 | south | N | 4.1111e-05 | 0
8562 | CNOPST1 | 3 | 153 | 0.00272 | south | N | -0.014995 | -4.1111e-05 | 0.2237 | -0.0061507 | 4.1111e-05 | south | N | 4.1111e-05 | 0
8926 | LGE_GT10 | 1 | 158 | 0.002884 | south | N | -0.014831 | 0.00012289 | 0.22387 | -0.0059867 | 0.00012289 | south | N | 0.00012289 | 0
8927 | LGE_GT20 | 2 | 153 | 0.002884 | south | N | -0.014831 | 0.00012289 | 0.22387 | -0.0059867 | 0.00012289 | south | N | 0.00012289 | 0
8928 | LGE_STG0 | 3 | 100 | 0.002884 | south | N | -0.014831 | 0.00012289 | 0.22387 | -0.0059867 | 0.00012289 | south | N | 0.00012289 | 0
8930 | ICPGN10A | 1 | 145 | 0.002884 | south | N | -0.014831 | 0.00012289 | 0.22387 | -0.0059867 | 0.00012289 | south | N | 0.00012289 | 0
8931 | ICPGN20A | 2 | 147 | 0.002884 | south | N | -0.014831 | 0.00012289 | 0.22387 | -0.0059867 | 0.00012289 | south | N | 0.00012289 | 0
8932 | ICPGN30A | 3 | 127 | 0.002884 | south | N | -0.014831 | 0.00012289 | 0.22387 | -0.0059867 | 0.00012289 | south | N | 0.00012289 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.001987 | south | Y | -0.015728 | -0.00077411 | 0.22297 | -0.0068837 | 0.00077411 | south | N | 0.00077411 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.001987 | south | Y | -0.015728 | -0.00077411 | 0.22297 | -0.0068837 | 0.00077411 | south | N | 0.00077411 | 0
8935 | FGNTS201 | 3 | 173 | 0.001987 | south | Y | -0.015728 | -0.00077411 | 0.22297 | -0.0068837 | 0.00077411 | south | N | 0.00077411 | 0
8936 | MVGN#1 | 1 | 207 | 0.00226 | south | Y | -0.015455 | -0.00050111 | 0.22324 | -0.0066107 | 0.00050111 | south | N | 0.00050111 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.00226 | south | Y | -0.015455 | -0.00050111 | 0.22324 | -0.0066107 | 0.00050111 | south | N | 0.00050111 | 0
8938 | MVGN#3 | 3 | 242 | 0.00226 | south | Y | -0.015455 | -0.00050111 | 0.22324 | -0.0066107 | 0.00050111 | south | N | 0.00050111 | 0
8981 | HECN1 | 1 | 144 | 0.002261 | south | Y | -0.015454 | -0.00050011 | 0.22324 | -0.0066097 | 0.00050011 | south | N | 0.00050011 | 0
8982 | HECN2 | 2 | 144 | 0.002261 | south | Y | -0.015454 | -0.00050011 | 0.22324 | -0.0066097 | 0.00050011 | south | N | 0.00050011 | 0
8983 | HECN3 | 3 | 171 | 0.002261 | south | Y | -0.015454 | -0.00050011 | 0.22324 | -0.0066097 | 0.00050011 | south | N | 0.00050011 | 0
9000 | DECKR_G1 | 1 | 310 | 0.004171 | south | Y | -0.013544 | 0.0014099 | 0.22515 | -0.0046997 | 0.0014099 | south | N | 0.0014099 | 0
9001 | DECKR_G2 | 2 | 413 | 0.004171 | south | Y | -0.013544 | 0.0014099 | 0.22515 | -0.0046997 | 0.0014099 | south | N | 0.0014099 | 0
9002 | DECKR_G3 | 3 | 42 | 0.00434 | south | Y | -0.013375 | 0.0015789 | 0.22532 | -0.0045307 | 0.0015789 | south | N | 0.0015789 | 0
9003 | DECKR_G4 | 4 | 44 | 0.00434 | south | Y | -0.013375 | 0.0015789 | 0.22532 | -0.0045307 | 0.0015789 | south | N | 0.0015789 | 0
9004 | DECKR_G5 | 5 | 44 | 0.00434 | south | Y | -0.013375 | 0.0015789 | 0.22532 | -0.0045307 | 0.0015789 | south | N | 0.0015789 | 0
9005 | DECKR_G6 | 6 | 47 | 0.00434 | south | Y | -0.013375 | 0.0015789 | 0.22532 | -0.0045307 | 0.0015789 | south | N | 0.0015789 | 0
9016 | SANDH_G1 | 1 | 49 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
9017 | SANDH_G2 | 2 | 46 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
9018 | SANDH_G3 | 3 | 46 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
9019 | SANDH_G4 | 4 | 47 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
9020 | SANDHG5A | 5A | 154 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
9021 | SANDHG5C | 5C | 148 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
9022 | SANDH_G6 | 6 | 48 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
9023 | SANDH_G7 | 7 | 48 | 0.004119 | south | Y | -0.013596 | 0.0013579 | 0.2251 | -0.0047517 | 0.0013579 | south | N | 0.0013579 | 0
11001 | NAV1CT | 1 | 70 | -0.23394 | west | Y | -0.25165 | -0.2367 | -0.012958 | -0.24281 | 0.012958 | west | N | 0.012958 | 0
11009 | NAV2CT | 1 | 70 | -0.23394 | west | Y | -0.25165 | -0.2367 | -0.012958 | -0.24281 | 0.012958 | west | N | 0.012958 | 0
11011 | NAV3ST | 1 | 92.8 | -0.23394 | west | Y | -0.25165 | -0.2367 | -0.012958 | -0.24281 | 0.012958 | west | N | 0.012958 | 0
11012 | NAV4CT | 1 | 80 | -0.23394 | west | Y | -0.25165 | -0.2367 | -0.012958 | -0.24281 | 0.012958 | west | N | 0.012958 | 0
11013 | NAV5CT | 1 | 80 | -0.23394 | west | Y | -0.25165 | -0.2367 | -0.012958 | -0.24281 | 0.012958 | west | N | 0.012958 | 0
11014 | NAV6ST | 1 | 115 | -0.23394 | west | Y | -0.25165 | -0.2367 | -0.012958 | -0.24281 | 0.012958 | west | N | 0.012958 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.2339 | west | Y | -0.25162 | -0.23667 | -0.012922 | -0.24277 | 0.012922 | west | N | 0.012922 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.2339 | west | Y | -0.25162 | -0.23667 | -0.012922 | -0.24277 | 0.012922 | west | N | 0.012922 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.2339 | west | Y | -0.25162 | -0.23667 | -0.012922 | -0.24277 | 0.012922 | west | N | 0.012922 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.2339 | west | Y | -0.25162 | -0.23667 | -0.012922 | -0.24277 | 0.012922 | west | N | 0.012922 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.2339 | west | Y | -0.25162 | -0.23667 | -0.012922 | -0.24277 | 0.012922 | west | N | 0.012922 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.2339 | west | Y | -0.25162 | -0.23667 | -0.012922 | -0.24277 | 0.012922 | west | N | 0.012922 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.23807 | west | Y | -0.25579 | -0.24083 | -0.017091 | -0.24694 | 0.017091 | west | N | 0.017091 | 0
11057 | CHAMPION | 1 | 126.5 | -0.23807 | west | Y | -0.25579 | -0.24083 | -0.017091 | -0.24694 | 0.017091 | west | N | 0.017091 | 0
11058 | PYRON_1G | 1 | 249 | -0.23807 | west | Y | -0.25579 | -0.24083 | -0.017091 | -0.24694 | 0.017091 | west | N | 0.017091 | 0
11059 | INADALE_ | 1 | 197 | -0.23807 | west | Y | -0.25579 | -0.24083 | -0.017091 | -0.24694 | 0.017091 | west | N | 0.017091 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.2372 | west | Y | -0.25491 | -0.23996 | -0.016215 | -0.24607 | 0.016215 | west | N | 0.016215 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.2372 | west | Y | -0.25491 | -0.23996 | -0.016215 | -0.24607 | 0.016215 | west | N | 0.016215 | 0
11147 | NOTREES_ | 1 | 149 | -0.2297 | west | Y | -0.24741 | -0.23246 | -0.0087166 | -0.23857 | 0.0087166 | west | N | 0.0087166 | 0
11309 | BULLCREK | 1 | 180 | -0.22509 | west | Y | -0.2428 | -0.22785 | -0.0041076 | -0.23396 | 0.0041076 | west | N | 0.0041076 | 0
11310 | BULLCREK | 1 | 180 | -0.22509 | west | Y | -0.2428 | -0.22785 | -0.0041076 | -0.23396 | 0.0041076 | west | N | 0.0041076 | 0
11320 | COYOTE_1 | 1 | 225 | -0.22529 | west | Y | -0.243 | -0.22805 | -0.0043036 | -0.23416 | 0.0043036 | west | N | 0.0043036 | 0
11415 | LORAINE_ | 1 | 125 | -0.24712 | west | Y | -0.26483 | -0.24988 | -0.026136 | -0.25599 | 0.026136 | west | N | 0.026136 | 0
11416 | LORAINE_ | 1 | 125 | -0.24712 | west | Y | -0.26483 | -0.24988 | -0.026136 | -0.25599 | 0.026136 | west | N | 0.026136 | 0
11691 | KMICHICT | 1 | 140 | 0.020186 | north | N | 0.0024711 | 0.017425 | 0.24117 | 0.011315 | 0.0024711 | North | N | 0.0024711 | 0
11692 | KMICHICT | 2 | 141 | 0.020186 | north | N | 0.0024711 | 0.017425 | 0.24117 | 0.011315 | 0.0024711 | North | N | 0.0024711 | 0
11693 | KMICHIST | 3 | 309 | 0.020186 | north | N | 0.0024711 | 0.017425 | 0.24117 | 0.011315 | 0.0024711 | North | N | 0.0024711 | 0
11694 | KMICHICT | 4 | 143 | 0.020186 | north | N | 0.0024711 | 0.017425 | 0.24117 | 0.011315 | 0.0024711 | North | N | 0.0024711 | 0
11695 | KMICHICT | 5 | 144 | 0.020186 | north | N | 0.0024711 | 0.017425 | 0.24117 | 0.011315 | 0.0024711 | North | N | 0.0024711 | 0
11696 | KMICHIST | 6 | 310 | 0.020186 | north | N | 0.0024711 | 0.017425 | 0.24117 | 0.011315 | 0.0024711 | North | N | 0.0024711 | 0
12322 | ENNSTRAC | 1 | 196 | 0.017072 | north | Y | -0.00064287 | 0.014311 | 0.23805 | 0.0082013 | 0.00064287 | North | N | 0.00064287 | 0
12323 | ENNSTRAC | 2 | 111 | 0.017072 | north | Y | -0.00064287 | 0.014311 | 0.23805 | 0.0082013 | 0.00064287 | North | N | 0.00064287 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.020469 | north | N | 0.0027541 | 0.017708 | 0.24145 | 0.011598 | 0.0027541 | North | N | 0.0027541 | 0
12411 | FPLEFR1A | 1 | 161 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12412 | FPLEFR1B | 2 | 164 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12413 | FPLEFR1C | 3 | 164 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12414 | FPLEFR1S | 4 | 414 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12421 | FPLEFR2A | 1 | 162 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12422 | FPLEFR2B | 2 | 161 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12423 | FPLEFR2C | 3 | 163 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12424 | FPLEFR2S | 4 | 409 | 0.019147 | north | Y | 0.0014321 | 0.016386 | 0.24013 | 0.010276 | 0.0014321 | North | N | 0.0014321 | 0
12440 | PARKD_1S | 1 | 0 | 0.019127 | north | N | 0.0014121 | 0.016366 | 0.24011 | 0.010256 | 0.0014121 | North | N | 0.0014121 | 0
12449 | PARKD_2S | 1 | 0 | 0.019127 | north | N | 0.0014121 | 0.016366 | 0.24011 | 0.010256 | 0.0014121 | North | N | 0.0014121 | 0
13116 | TGATEWAY | 1 | 148 | 0.017761 | north | N | 4.6133e-05 | 0.015 | 0.23874 | 0.0088903 | 4.6133e-05 | North | N | 4.6133e-05 | 0
13117 | TGATEWAY | 2 | 130 | 0.017761 | north | N | 4.6133e-05 | 0.015 | 0.23874 | 0.0088903 | 4.6133e-05 | North | N | 4.6133e-05 | 0
13118 | TGATEWAY | 3 | 145 | 0.017761 | north | N | 4.6133e-05 | 0.015 | 0.23874 | 0.0088903 | 4.6133e-05 | North | N | 4.6133e-05 | 0
13119 | TGATEWAY | 4 | 399 | 0.017761 | north | N | 4.6133e-05 | 0.015 | 0.23874 | 0.0088903 | 4.6133e-05 | North | N | 4.6133e-05 | 0
13131 | CALFREST | 1 | 150.7 | 0.01614 | north | Y | -0.0015749 | 0.013379 | 0.23712 | 0.0072693 | 0.0015749 | North | N | 0.0015749 | 0
13132 | CALFREST | 2 | 151 | 0.01614 | north | Y | -0.0015749 | 0.013379 | 0.23712 | 0.0072693 | 0.0015749 | North | N | 0.0015749 | 0
13133 | CALFREST | 3 | 177.4 | 0.01614 | north | Y | -0.0015749 | 0.013379 | 0.23712 | 0.0072693 | 0.0015749 | North | N | 0.0015749 | 0
13134 | CALFREST | 4 | 151.5 | 0.016198 | north | Y | -0.0015169 | 0.013437 | 0.23718 | 0.0073273 | 0.0015169 | North | N | 0.0015169 | 0
13135 | CALFREST | 5 | 152.3 | 0.016198 | north | Y | -0.0015169 | 0.013437 | 0.23718 | 0.0073273 | 0.0015169 | North | N | 0.0015169 | 0
13136 | CALFREST | 6 | 177.5 | 0.016198 | north | Y | -0.0015169 | 0.013437 | 0.23718 | 0.0073273 | 0.0015169 | North | N | 0.0015169 | 0
13432 | SANDOW_5 | 5 | 581 | 0.007042 | south | Y | -0.010673 | 0.0042809 | 0.22802 | -0.0018287 | 0.0018287 | houston | Y | 0.0042809 | 1.4247
13691 | OAKGROVE | 1 | 855 | 0.013691 | north | Y | -0.0040239 | 0.01093 | 0.23467 | 0.0048203 | 0.0040239 | North | N | 0.0040239 | 0
13692 | OAKGROVE | 2 | 855 | 0.013691 | north | Y | -0.0040239 | 0.01093 | 0.23467 | 0.0048203 | 0.0040239 | North | N | 0.0040239 | 0
32798 | BRYN_TAM | 1 | 32 | 0.012238 | north | N | -0.0054769 | 0.0094769 | 0.23322 | 0.0033673 | 0.0033673 | houston | Y | 0.0054769 | 0
32883 | BRYN_DNS | 1 | 48 | 0.012208 | north | Y | -0.0055069 | 0.0094469 | 0.23319 | 0.0033373 | 0.0033373 | houston | Y | 0.0055069 | 0.10414
32884 | BRYN_DNS | 1 | 46 | 0.012208 | north | Y | -0.0055069 | 0.0094469 | 0.23319 | 0.0033373 | 0.0033373 | houston | Y | 0.0055069 | 0.099799
32886 | BRYN_ATK | MB | 12 | 0.012247 | north | Y | -0.0054679 | 0.0094859 | 0.23323 | 0.0033763 | 0.0033763 | houston | Y | 0.0054679 | 0
32887 | BRYN_ATK | MB | 51 | 0.012247 | north | Y | -0.0054679 | 0.0094859 | 0.23323 | 0.0033763 | 0.0033763 | houston | Y | 0.0054679 | 0
32888 | BRYN_ATK | 1 | 17 | 0.012247 | north | Y | -0.0054679 | 0.0094859 | 0.23323 | 0.0033763 | 0.0033763 | houston | Y | 0.0054679 | 0.035556
32890 | BRYN_ATK | MB | 22 | 0.012247 | north | Y | -0.0054679 | 0.0094859 | 0.23323 | 0.0033763 | 0.0033763 | houston | Y | 0.0054679 | 0
32891 | BRYN_ATK | MB | 25 | 0.012247 | north | Y | -0.0054679 | 0.0094859 | 0.23323 | 0.0033763 | 0.0033763 | houston | Y | 0.0054679 | 0
32892 | BRYN_DNS | 1 | 105 | 0.012208 | north | Y | -0.0055069 | 0.0094469 | 0.23319 | 0.0033373 | 0.0033373 | houston | Y | 0.0055069 | 0.2278
36998 | RDCNYNG1 | 1 | 84 | -0.21544 | west | Y | -0.23315 | -0.2182 | 0.0055444 | -0.22431 | 0.0055444 | west | N | 0.0055444 | 0
38332 | WDWRDU2 | 1 | 80 | -0.21506 | west | Y | -0.23278 | -0.21782 | 0.0059204 | -0.22393 | 0.0059204 | west | N | 0.0059204 | 0
38437 | TNSRBNMS | 1 | 150 | -0.21492 | west | Y | -0.23264 | -0.21768 | 0.0060594 | -0.22379 | 0.0060594 | west | N | 0.0060594 | 0
38438 | TNSRBNMS | 1 | 150 | -0.21492 | west | Y | -0.23264 | -0.21768 | 0.0060594 | -0.22379 | 0.0060594 | west | N | 0.0060594 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38600 | TNBP_CGN | 5 | 53 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38614 | TNBPAMCG | 4 | 96 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38615 | TNBPAMCG | 1 | 244 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38690 | TNBP_CGN | 3 | 40 | 0.008782 | houston | N | -0.0089329 | 0.0060209 | 0.22976 | -8.8687e-05 | 8.8687e-05 | houston | N | 8.8687e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.008781 | houston | N | -0.0089339 | 0.0060199 | 0.22976 | -8.9687e-05 | 8.9687e-05 | houston | N | 8.9687e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.008781 | houston | N | -0.0089339 | 0.0060199 | 0.22976 | -8.9687e-05 | 8.9687e-05 | houston | N | 8.9687e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.008781 | houston | N | -0.0089339 | 0.0060199 | 0.22976 | -8.9687e-05 | 8.9687e-05 | houston | N | 8.9687e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.008781 | houston | N | -0.0089339 | 0.0060199 | 0.22976 | -8.9687e-05 | 8.9687e-05 | houston | N | 8.9687e-05 | 0
39470 | TNDOWCGN | 1 | 32 | 0.008781 | houston | N | -0.0089339 | 0.0060199 | 0.22976 | -8.9687e-05 | 8.9687e-05 | houston | N | 8.9687e-05 | 0
39480 | TNDOWCGN | 1 | 30 | 0.008781 | houston | N | -0.0089339 | 0.0060199 | 0.22976 | -8.9687e-05 | 8.9687e-05 | houston | N | 8.9687e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.008011 | houston | N | -0.0097039 | 0.0052499 | 0.22899 | -0.00085969 | 0.00085969 | houston | N | 0.00085969 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.008011 | houston | N | -0.0097039 | 0.0052499 | 0.22899 | -0.00085969 | 0.00085969 | houston | N | 0.00085969 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.008011 | houston | N | -0.0097039 | 0.0052499 | 0.22899 | -0.00085969 | 0.00085969 | houston | N | 0.00085969 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.008011 | houston | N | -0.0097039 | 0.0052499 | 0.22899 | -0.00085969 | 0.00085969 | houston | N | 0.00085969 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.013691 | north | Y | -0.0040239 | 0.01093 | 0.23467 | 0.0048203 | 0.0040239 | North | N | 0.0040239 | 0
39970 | TNTNPONE | 1 | 153 | 0.013691 | north | Y | -0.0040239 | 0.01093 | 0.23467 | 0.0048203 | 0.0040239 | North | N | 0.0040239 | 0
48500 | APD_GT1_ | 1 | 136 | 0.009242 | houston | N | -0.0084729 | 0.0064809 | 0.23022 | 0.00037131 | 0.00037131 | houston | N | 0.00037131 | 0
48510 | AK_GT1__ | 1 | 33 | 0.008526 | houston | N | -0.0091889 | 0.0057649 | 0.22951 | -0.00034469 | 0.00034469 | houston | N | 0.00034469 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.009241 | houston | Y | -0.0084739 | 0.0064799 | 0.23022 | 0.00037031 | 0.00037031 | houston | N | 0.00037031 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.009241 | houston | Y | -0.0084739 | 0.0064799 | 0.23022 | 0.00037031 | 0.00037031 | houston | N | 0.00037031 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.009241 | houston | Y | -0.0084739 | 0.0064799 | 0.23022 | 0.00037031 | 0.00037031 | houston | N | 0.00037031 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.009241 | houston | Y | -0.0084739 | 0.0064799 | 0.23022 | 0.00037031 | 0.00037031 | houston | N | 0.00037031 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.007872 | houston | N | -0.0098429 | 0.0051109 | 0.22885 | -0.00099869 | 0.00099869 | houston | N | 0.00099869 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.007872 | houston | N | -0.0098429 | 0.0051109 | 0.22885 | -0.00099869 | 0.00099869 | houston | N | 0.00099869 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.008506 | houston | N | -0.0092089 | 0.0057449 | 0.22949 | -0.00036469 | 0.00036469 | houston | N | 0.00036469 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.008506 | houston | N | -0.0092089 | 0.0057449 | 0.22949 | -0.00036469 | 0.00036469 | houston | N | 0.00036469 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.008506 | houston | N | -0.0092089 | 0.0057449 | 0.22949 | -0.00036469 | 0.00036469 | houston | N | 0.00036469 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.009069 | houston | N | -0.0086459 | 0.0063079 | 0.23005 | 0.00019831 | 0.00019831 | houston | N | 0.00019831 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.009069 | houston | N | -0.0086459 | 0.0063079 | 0.23005 | 0.00019831 | 0.00019831 | houston | N | 0.00019831 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.009069 | houston | N | -0.0086459 | 0.0063079 | 0.23005 | 0.00019831 | 0.00019831 | houston | N | 0.00019831 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.009069 | houston | N | -0.0086459 | 0.0063079 | 0.23005 | 0.00019831 | 0.00019831 | houston | N | 0.00019831 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.00918 | houston | N | -0.0085349 | 0.0064189 | 0.23016 | 0.00030931 | 0.00030931 | houston | N | 0.00030931 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.00918 | houston | N | -0.0085349 | 0.0064189 | 0.23016 | 0.00030931 | 0.00030931 | houston | N | 0.00030931 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.009036 | houston | N | -0.0086789 | 0.0062749 | 0.23002 | 0.00016531 | 0.00016531 | houston | N | 0.00016531 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.009036 | houston | N | -0.0086789 | 0.0062749 | 0.23002 | 0.00016531 | 0.00016531 | houston | N | 0.00016531 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.009036 | houston | N | -0.0086789 | 0.0062749 | 0.23002 | 0.00016531 | 0.00016531 | houston | N | 0.00016531 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.009036 | houston | N | -0.0086789 | 0.0062749 | 0.23002 | 0.00016531 | 0.00016531 | houston | N | 0.00016531 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.009036 | houston | N | -0.0086789 | 0.0062749 | 0.23002 | 0.00016531 | 0.00016531 | houston | N | 0.00016531 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.009378 | houston | Y | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.009322 | houston | Y | -0.0083929 | 0.0065609 | 0.2303 | 0.00045131 | 0.00045131 | houston | N | 0.00045131 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.009394 | houston | Y | -0.0083209 | 0.0066329 | 0.23038 | 0.00052331 | 0.00052331 | houston | N | 0.00052331 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.009394 | houston | Y | -0.0083209 | 0.0066329 | 0.23038 | 0.00052331 | 0.00052331 | houston | N | 0.00052331 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.009394 | houston | Y | -0.0083209 | 0.0066329 | 0.23038 | 0.00052331 | 0.00052331 | houston | N | 0.00052331 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.009704 | houston | N | -0.0080109 | 0.0069429 | 0.23069 | 0.00083331 | 0.00083331 | houston | N | 0.00083331 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.009253 | houston | N | -0.0084619 | 0.0064919 | 0.23024 | 0.00038231 | 0.00038231 | houston | N | 0.00038231 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.009253 | houston | N | -0.0084619 | 0.0064919 | 0.23024 | 0.00038231 | 0.00038231 | houston | N | 0.00038231 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.009433 | houston | N | -0.0082819 | 0.0066719 | 0.23042 | 0.00056231 | 0.00056231 | houston | N | 0.00056231 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.009433 | houston | N | -0.0082819 | 0.0066719 | 0.23042 | 0.00056231 | 0.00056231 | houston | N | 0.00056231 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.009433 | houston | N | -0.0082819 | 0.0066719 | 0.23042 | 0.00056231 | 0.00056231 | houston | N | 0.00056231 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.009433 | houston | N | -0.0082819 | 0.0066719 | 0.23042 | 0.00056231 | 0.00056231 | houston | N | 0.00056231 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.009184 | houston | N | -0.0085309 | 0.0064229 | 0.23017 | 0.00031331 | 0.00031331 | houston | N | 0.00031331 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.009184 | houston | N | -0.0085309 | 0.0064229 | 0.23017 | 0.00031331 | 0.00031331 | houston | N | 0.00031331 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.009184 | houston | N | -0.0085309 | 0.0064229 | 0.23017 | 0.00031331 | 0.00031331 | houston | N | 0.00031331 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.009184 | houston | N | -0.0085309 | 0.0064229 | 0.23017 | 0.00031331 | 0.00031331 | houston | N | 0.00031331 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.009144 | houston | N | -0.0085709 | 0.0063829 | 0.23013 | 0.00027331 | 0.00027331 | houston | N | 0.00027331 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.009144 | houston | N | -0.0085709 | 0.0063829 | 0.23013 | 0.00027331 | 0.00027331 | houston | N | 0.00027331 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.009144 | houston | N | -0.0085709 | 0.0063829 | 0.23013 | 0.00027331 | 0.00027331 | houston | N | 0.00027331 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.009144 | houston | N | -0.0085709 | 0.0063829 | 0.23013 | 0.00027331 | 0.00027331 | houston | N | 0.00027331 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.009144 | houston | N | -0.0085709 | 0.0063829 | 0.23013 | 0.00027331 | 0.00027331 | houston | N | 0.00027331 | 0
48651 | EP_1_2 | 1 | 5 | 0.009376 | houston | N | -0.0083389 | 0.0066149 | 0.23036 | 0.00050531 | 0.00050531 | houston | N | 0.00050531 | 0
48651 | EP_1_2 | 2 | 21 | 0.009376 | houston | N | -0.0083389 | 0.0066149 | 0.23036 | 0.00050531 | 0.00050531 | houston | N | 0.00050531 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.011822 | north | N | -0.0058929 | 0.0090609 | 0.2328 | 0.0029513 | 0.0029513 | houston | Y | 0.0058929 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.011822 | north | N | -0.0058929 | 0.0090609 | 0.2328 | 0.0029513 | 0.0029513 | houston | Y | 0.0058929 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.011822 | north | N | -0.0058929 | 0.0090609 | 0.2328 | 0.0029513 | 0.0029513 | houston | Y | 0.0058929 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.011822 | north | N | -0.0058929 | 0.0090609 | 0.2328 | 0.0029513 | 0.0029513 | houston | Y | 0.0058929 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.009451 | houston | Y | -0.0082639 | 0.0066899 | 0.23043 | 0.00058031 | 0.00058031 | houston | N | 0.00058031 | 0
48691 | GBY_7374 | A | 46 | 0.009127 | houston | Y | -0.0085879 | 0.0063659 | 0.23011 | 0.00025631 | 0.00025631 | houston | N | 0.00025631 | 0
48691 | GBY_7374 | B | 46 | 0.009127 | houston | Y | -0.0085879 | 0.0063659 | 0.23011 | 0.00025631 | 0.00025631 | houston | N | 0.00025631 | 0
48692 | GBY_8182 | C | 46 | 0.009127 | houston | Y | -0.0085879 | 0.0063659 | 0.23011 | 0.00025631 | 0.00025631 | houston | N | 0.00025631 | 0
48692 | GBY_8182 | D | 55 | 0.009127 | houston | Y | -0.0085879 | 0.0063659 | 0.23011 | 0.00025631 | 0.00025631 | houston | N | 0.00025631 | 0
48693 | GBY_8384 | E | 55 | 0.009127 | houston | Y | -0.0085879 | 0.0063659 | 0.23011 | 0.00025631 | 0.00025631 | houston | N | 0.00025631 | 0
48693 | GBY_8384 | F | 54 | 0.009127 | houston | Y | -0.0085879 | 0.0063659 | 0.23011 | 0.00025631 | 0.00025631 | houston | N | 0.00025631 | 0
48721 | LEG_1___ | 1 | 827 | 0.014266 | north | Y | -0.0034489 | 0.011505 | 0.23525 | 0.0053953 | 0.0034489 | North | N | 0.0034489 | 0
48722 | LEG_2___ | 2 | 819 | 0.014266 | north | Y | -0.0034489 | 0.011505 | 0.23525 | 0.0053953 | 0.0034489 | North | N | 0.0034489 | 0
48730 | MNS_GT | 1 | 46.1 | 0.008459 | houston | N | -0.0092559 | 0.0056979 | 0.22944 | -0.00041169 | 0.00041169 | houston | N | 0.00041169 | 0
48731 | CBE_GT1 | 1 | 76 | 0.006918 | houston | Y | -0.010797 | 0.0041569 | 0.2279 | -0.0019527 | 0.0019527 | houston | N | 0.0019527 | 0
48732 | CBE_GT2 | 1 | 76 | 0.006918 | houston | Y | -0.010797 | 0.0041569 | 0.2279 | -0.0019527 | 0.0019527 | houston | N | 0.0019527 | 0
48733 | CBE_ST12 | 1 | 105 | 0.006918 | houston | Y | -0.010797 | 0.0041569 | 0.2279 | -0.0019527 | 0.0019527 | houston | N | 0.0019527 | 0
48734 | CBE_GT3 | 1 | 74 | 0.006918 | houston | Y | -0.010797 | 0.0041569 | 0.2279 | -0.0019527 | 0.0019527 | houston | N | 0.0019527 | 0
48735 | CBE_GT4 | 1 | 74 | 0.006918 | houston | Y | -0.010797 | 0.0041569 | 0.2279 | -0.0019527 | 0.0019527 | houston | N | 0.0019527 | 0
48736 | CBE_ST34 | 1 | 102 | 0.006918 | houston | Y | -0.010797 | 0.0041569 | 0.2279 | -0.0019527 | 0.0019527 | houston | N | 0.0019527 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.009185 | houston | N | -0.0085299 | 0.0064239 | 0.23017 | 0.00031431 | 0.00031431 | houston | N | 0.00031431 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.009185 | houston | N | -0.0085299 | 0.0064239 | 0.23017 | 0.00031431 | 0.00031431 | houston | N | 0.00031431 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.009185 | houston | N | -0.0085299 | 0.0064239 | 0.23017 | 0.00031431 | 0.00031431 | houston | N | 0.00031431 | 0
48761 | PR_GT1__ | 1 | 35 | 0.009163 | houston | N | -0.0085519 | 0.0064019 | 0.23015 | 0.00029231 | 0.00029231 | houston | N | 0.00029231 | 0
48772 | PHR_GN2_ | MB | 459 | 0.008949 | houston | Y | -0.0087659 | 0.0061879 | 0.22993 | 7.8313e-05 | 7.8313e-05 | houston | N | 7.8313e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.009378 | houston | N | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.009378 | houston | N | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.009378 | houston | N | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.009378 | houston | N | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.009378 | houston | N | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.009378 | houston | N | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.009378 | houston | N | -0.0083369 | 0.0066169 | 0.23036 | 0.00050731 | 0.00050731 | houston | N | 0.00050731 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.009704 | houston | N | -0.0080109 | 0.0069429 | 0.23069 | 0.00083331 | 0.00083331 | houston | N | 0.00083331 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.009704 | houston | N | -0.0080109 | 0.0069429 | 0.23069 | 0.00083331 | 0.00083331 | houston | N | 0.00083331 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.009704 | houston | N | -0.0080109 | 0.0069429 | 0.23069 | 0.00083331 | 0.00083331 | houston | N | 0.00083331 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.009704 | houston | N | -0.0080109 | 0.0069429 | 0.23069 | 0.00083331 | 0.00083331 | houston | N | 0.00083331 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.00939 | houston | N | -0.0083249 | 0.0066289 | 0.23037 | 0.00051931 | 0.00051931 | houston | N | 0.00051931 | 0
48820 | SHELLG1_ | 1 | 71 | 0.009206 | houston | N | -0.0085089 | 0.0064449 | 0.23019 | 0.00033531 | 0.00033531 | houston | N | 0.00033531 | 0
48821 | SHELLG2 | 2 | 72 | 0.009206 | houston | N | -0.0085089 | 0.0064449 | 0.23019 | 0.00033531 | 0.00033531 | houston | N | 0.00033531 | 0
48822 | SHELLG3_ | 1 | 39 | 0.009206 | houston | N | -0.0085089 | 0.0064449 | 0.23019 | 0.00033531 | 0.00033531 | houston | N | 0.00033531 | 0
48822 | SHELLG3_ | 2 | 30 | 0.009206 | houston | N | -0.0085089 | 0.0064449 | 0.23019 | 0.00033531 | 0.00033531 | houston | N | 0.00033531 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.009131 | houston | N | -0.0085839 | 0.0063699 | 0.23011 | 0.00026031 | 0.00026031 | houston | N | 0.00026031 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.009131 | houston | N | -0.0085839 | 0.0063699 | 0.23011 | 0.00026031 | 0.00026031 | houston | N | 0.00026031 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.009183 | houston | N | -0.0085319 | 0.0064219 | 0.23017 | 0.00031231 | 0.00031231 | houston | N | 0.00031231 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.009179 | houston | Y | -0.0085359 | 0.0064179 | 0.23016 | 0.00030831 | 0.00030831 | houston | N | 0.00030831 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.009178 | houston | Y | -0.0085369 | 0.0064169 | 0.23016 | 0.00030731 | 0.00030731 | houston | N | 0.00030731 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.009183 | houston | Y | -0.0085319 | 0.0064219 | 0.23017 | 0.00031231 | 0.00031231 | houston | N | 0.00031231 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.009184 | houston | Y | -0.0085309 | 0.0064229 | 0.23017 | 0.00031331 | 0.00031331 | houston | N | 0.00031331 | 0
48855 | SRB_GT21 | B2 | 12 | 0.009177 | houston | Y | -0.0085379 | 0.0064159 | 0.23016 | 0.00030631 | 0.00030631 | houston | N | 0.00030631 | 0
48855 | SRB_GT21 | MB | 18 | 0.009177 | houston | Y | -0.0085379 | 0.0064159 | 0.23016 | 0.00030631 | 0.00030631 | houston | N | 0.00030631 | 0
48865 | TECO_GT1 | 1 | 50 | 0.00889 | houston | Y | -0.0088249 | 0.0061289 | 0.22987 | 1.9313e-05 | 1.9313e-05 | houston | N | 1.9313e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48874 | THW_ST4_ | 4 | 104 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48875 | THW_3132 | A | 54 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48875 | THW_3132 | B | 53 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48877 | THW_3334 | C | 54 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48877 | THW_3334 | D | 57 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48879 | THW_4142 | E | 54 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48879 | THW_4142 | F | 54 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48881 | THW_4344 | G | 58 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48881 | THW_4344 | H | 58 | 0.009312 | houston | Y | -0.0084029 | 0.0065509 | 0.23029 | 0.00044131 | 0.00044131 | houston | N | 0.00044131 | 0
48883 | THW_GT1_ | B2 | 12 | 0.009362 | houston | Y | -0.0083529 | 0.0066009 | 0.23034 | 0.00049131 | 0.00049131 | houston | N | 0.00049131 | 0
48885 | THW_5152 | A | 56 | 0.009476 | houston | Y | -0.0082389 | 0.0067149 | 0.23046 | 0.00060531 | 0.00060531 | houston | N | 0.00060531 | 0
48885 | THW_5152 | B | 59 | 0.009476 | houston | Y | -0.0082389 | 0.0067149 | 0.23046 | 0.00060531 | 0.00060531 | houston | N | 0.00060531 | 0
48886 | THW_5354 | C | 56 | 0.009476 | houston | Y | -0.0082389 | 0.0067149 | 0.23046 | 0.00060531 | 0.00060531 | houston | N | 0.00060531 | 0
48886 | THW_5354 | D | 56 | 0.009476 | houston | Y | -0.0082389 | 0.0067149 | 0.23046 | 0.00060531 | 0.00060531 | houston | N | 0.00060531 | 0
48887 | THW_5556 | E | 59 | 0.009476 | houston | Y | -0.0082389 | 0.0067149 | 0.23046 | 0.00060531 | 0.00060531 | houston | N | 0.00060531 | 0
48887 | THW_5556 | F | 56 | 0.009476 | houston | Y | -0.0082389 | 0.0067149 | 0.23046 | 0.00060531 | 0.00060531 | houston | N | 0.00060531 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.007024 | houston | Y | -0.010691 | 0.0042629 | 0.22801 | -0.0018467 | 0.0018467 | houston | N | 0.0018467 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.00859 | houston | Y | -0.0091249 | 0.0058289 | 0.22957 | -0.00028069 | 0.00028069 | houston | N | 0.00028069 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.00859 | houston | Y | -0.0091249 | 0.0058289 | 0.22957 | -0.00028069 | 0.00028069 | houston | N | 0.00028069 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.00859 | houston | Y | -0.0091249 | 0.0058289 | 0.22957 | -0.00028069 | 0.00028069 | houston | N | 0.00028069 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.00859 | houston | Y | -0.0091249 | 0.0058289 | 0.22957 | -0.00028069 | 0.00028069 | houston | N | 0.00028069 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.00859 | houston | N | -0.0091249 | 0.0058289 | 0.22957 | -0.00028069 | 0.00028069 | houston | N | 0.00028069 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.008503 | houston | Y | -0.0092119 | 0.0057419 | 0.22949 | -0.00036769 | 0.00036769 | houston | N | 0.00036769 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.008503 | houston | Y | -0.0092119 | 0.0057419 | 0.22949 | -0.00036769 | 0.00036769 | houston | N | 0.00036769 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.008503 | houston | Y | -0.0092119 | 0.0057419 | 0.22949 | -0.00036769 | 0.00036769 | houston | N | 0.00036769 | 0
48929 | WAPGT21_ | B1 | 13 | 0.00859 | houston | Y | -0.0091249 | 0.0058289 | 0.22957 | -0.00028069 | 0.00028069 | houston | N | 0.00028069 | 0
48940 | WARVUE_G | G1 | 12 | 0.009377 | houston | Y | -0.0083379 | 0.0066159 | 0.23036 | 0.00050631 | 0.00050631 | houston | N | 0.00050631 | 0
49803 | EXN_15GT | 1 | 34 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49826 | EXN938GT | 5 | 45.9 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49828 | EXN941GT | 10 | 17.7 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49829 | EXN942GT | 11 | 20.4 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49830 | EXN943GT | 12 | 19.9 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49831 | EXN944GT | 13 | 35 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49832 | EXN945GT | 9 | 18 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49837 | EXN_GT | 4 | 85.4 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49838 | EXN_14GT | 14 | 148 | 0.009336 | houston | N | -0.0083789 | 0.0065749 | 0.23032 | 0.00046531 | 0.00046531 | houston | N | 0.00046531 | 0
49851 | DOW17000 | 37 | 62 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49858 | DOW38100 | 31 | 71.4 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49859 | DOW38200 | 33 | 45 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49860 | DOW38300 | 32 | 101 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49862 | DOW39100 | 36 | 86 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49863 | DOW39200 | 35 | 88 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49865 | DOW41000 | 41 | 50 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49866 | DOW42000 | 42 | 18 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49869 | DOW49000 | 45 | 94 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49870 | DOW61000 | 61 | 70 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49871 | DOW62000 | 62 | 63 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49872 | DOW63000 | 63 | 72 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49873 | DOW64000 | 64 | 64.8 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49876 | DOW65000 | 65 | 101 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49877 | DOW66000 | 66 | 97 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49878 | DOW67000 | 67 | 103 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49882 | DOW81000 | 81 | 76 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49884 | DOW82000 | 82 | 80 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49885 | DOW83000 | 83 | 80 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
49886 | DOW84000 | 84 | 171 | 0.007708 | houston | N | -0.010007 | 0.0049469 | 0.22869 | -0.0011627 | 0.0011627 | houston | N | 0.0011627 | 0
58909 | PEARSALL | 1 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58909 | PEARSALL | 2 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58909 | PEARSALL | 3 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58909 | PEARSALL | 4 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58909 | PEARSALL | 5 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58909 | PEARSALL | 6 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58919 | PEARSALL | 1 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58919 | PEARSALL | 2 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58919 | PEARSALL | 3 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58919 | PEARSALL | 4 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58919 | PEARSALL | 5 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58919 | PEARSALL | 6 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58929 | PEARSALL | 1 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58929 | PEARSALL | 2 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58929 | PEARSALL | 3 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58929 | PEARSALL | 4 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58929 | PEARSALL | 5 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58929 | PEARSALL | 6 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58949 | PEARSALL | 1 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58949 | PEARSALL | 2 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58949 | PEARSALL | 3 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58949 | PEARSALL | 4 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58949 | PEARSALL | 5 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
58949 | PEARSALL | 6 | 8.4 | -0.007772 | south | Y | -0.025487 | -0.010533 | 0.21321 | -0.016643 | 0.010533 | south | N | 0.010533 | 0
60000 | DSKY2 | 1 | 76.5 | -0.20831 | west | Y | -0.22602 | -0.21107 | 0.012676 | -0.21718 | 0.012676 | west | N | 0.012676 | 0
60003 | KING_NE1 | 1 | 80 | -0.21529 | west | Y | -0.23301 | -0.21805 | 0.0056894 | -0.22416 | 0.0056894 | west | N | 0.0056894 | 0
60005 | KING_SE1 | 1 | 40 | -0.21529 | west | Y | -0.23301 | -0.21805 | 0.0056894 | -0.22416 | 0.0056894 | west | N | 0.0056894 | 0
60007 | KING_SW1 | 1 | 80 | -0.21628 | west | Y | -0.234 | -0.21904 | 0.0047004 | -0.22515 | 0.0047004 | west | N | 0.0047004 | 0
60016 | WOODWRD1 | 1 | 80 | -0.21509 | west | Y | -0.23281 | -0.21786 | 0.0058884 | -0.22396 | 0.0058884 | west | N | 0.0058884 | 0
60017 | ORNNWP1 | 1 | 80 | -0.20981 | west | Y | -0.22753 | -0.21258 | 0.011168 | -0.21868 | 0.011168 | west | N | 0.011168 | 0
60018 | DSKY1 | 1 | 84 | -0.20809 | west | Y | -0.2258 | -0.21085 | 0.012892 | -0.21696 | 0.012892 | west | N | 0.012892 | 0
60019 | KING_NW1 | 1 | 80 | -0.21628 | west | Y | -0.234 | -0.21904 | 0.0047004 | -0.22515 | 0.0047004 | west | N | 0.0047004 | 0
60057 | CALLAHAN | 1 | 114 | 0.000836 | south | Y | -0.016879 | -0.0019251 | 0.22182 | -0.0080347 | 0.0019251 | south | N | 0.0019251 | 0
60058 | BUFF_GAP | 1 | 120 | -0.22075 | west | Y | -0.23846 | -0.22351 | 0.00023638 | -0.22962 | 0.00023638 | west | N | 0.00023638 | 0
60060 | CIRELLO | 1 | 233 | -0.22075 | west | Y | -0.23846 | -0.22351 | 0.00023638 | -0.22962 | 0.00023638 | west | N | 0.00023638 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.22075 | west | Y | -0.23846 | -0.22351 | 0.00023638 | -0.22962 | 0.00023638 | west | N | 0.00023638 | 0
60066 | H_HOLLOW | 1 | 222 | 0.000836 | south | Y | -0.016879 | -0.0019251 | 0.22182 | -0.0080347 | 0.0019251 | south | N | 0.0019251 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.000836 | south | Y | -0.016879 | -0.0019251 | 0.22182 | -0.0080347 | 0.0019251 | south | N | 0.0019251 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.000836 | south | Y | -0.016879 | -0.0019251 | 0.22182 | -0.0080347 | 0.0019251 | south | N | 0.0019251 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.000836 | south | Y | -0.016879 | -0.0019251 | 0.22182 | -0.0080347 | 0.0019251 | south | N | 0.0019251 | 0
60074 | HORSH5 | 1 | 100 | 0.000836 | south | Y | -0.016879 | -0.0019251 | 0.22182 | -0.0080347 | 0.0019251 | south | N | 0.0019251 | 0
60081 | WHRLWIND | 1 | 60 | -0.15875 | west | Y | -0.17647 | -0.16151 | 0.062231 | -0.16762 | 0.062231 | west | N | 0.062231 | 0
60201 | RIO DRCS | F | 0 | -0.060928 | south | N | -0.078643 | -0.063689 | 0.16005 | -0.069799 | 0.063689 | south | N | 0.063689 | 0
60202 | FRIEND_R | F | 0 | -0.18095 | west | N | -0.19866 | -0.18371 | 0.040035 | -0.18982 | 0.040035 | west | N | 0.040035 | 0
60203 | PRES0A | BT | 4.8 | -0.22048 | west | N | -0.23819 | -0.22324 | 0.00050438 | -0.22935 | 0.00050438 | west | N | 0.00050438 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.24344 | west | Y | -0.26115 | -0.2462 | -0.022455 | -0.25231 | 0.022455 | west | N | 0.022455 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.24344 | west | Y | -0.26115 | -0.2462 | -0.022455 | -0.25231 | 0.022455 | west | N | 0.022455 | 0
71057 | L_SWEETW | W1 | 135 | -0.24344 | west | Y | -0.26115 | -0.2462 | -0.022455 | -0.25231 | 0.022455 | west | N | 0.022455 | 0
71059 | L_SWEETW | W1 | 119 | -0.24344 | west | Y | -0.26115 | -0.2462 | -0.022455 | -0.25231 | 0.022455 | west | N | 0.022455 | 0
71060 | L_SWEETW | W1 | 105 | -0.24344 | west | Y | -0.26115 | -0.2462 | -0.022455 | -0.25231 | 0.022455 | west | N | 0.022455 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.24344 | west | Y | -0.26115 | -0.2462 | -0.022455 | -0.25231 | 0.022455 | west | N | 0.022455 | 0
76031 | L_GASCCR | W1 | 150 | -0.21992 | west | Y | -0.23764 | -0.22268 | 0.0010604 | -0.22879 | 0.0010604 | west | N | 0.0010604 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.21638 | west | Y | -0.2341 | -0.21915 | 0.0045974 | -0.22526 | 0.0045974 | west | N | 0.0045974 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.21638 | west | Y | -0.2341 | -0.21915 | 0.0045974 | -0.22526 | 0.0045974 | west | N | 0.0045974 | 0
76096 | L_CAPRSI | W1 | 186 | -0.21638 | west | Y | -0.2341 | -0.21915 | 0.0045974 | -0.22526 | 0.0045974 | west | N | 0.0045974 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.21638 | west | Y | -0.2341 | -0.21915 | 0.0045974 | -0.22526 | 0.0045974 | west | N | 0.0045974 | 0
80003 | MILHWYS | F | 0 | 0.002424 | south | N | -0.015291 | -0.00033711 | 0.22341 | -0.0064467 | 0.00033711 | south | N | 0.00033711 | 0
80010 | EPLVT1 | F | 0 | -0.038174 | south | N | -0.055889 | -0.040935 | 0.18281 | -0.047045 | 0.040935 | south | N | 0.040935 | 0
80012 | LAR | F | 0 | -0.003023 | south | N | -0.020738 | -0.0057841 | 0.21796 | -0.011894 | 0.0057841 | south | N | 0.0057841 | 0
80051 | FORPVCM0 | 8 | 28 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
80053 | FOR69CG0 | 10 | 74 | 0.004082 | south | N | -0.013633 | 0.0013209 | 0.22506 | -0.0047887 | 0.0013209 | south | N | 0.0013209 | 0
80080 | GWINDT11 | 1 | 94 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80080 | GWINDT11 | 2 | 41 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80080 | GWINDT11 | 3 | 38 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80080 | GWINDT11 | 4 | 19 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80081 | GWINDT21 | 1 | 94 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80081 | GWINDT21 | 2 | 36 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80081 | GWINDT21 | 3 | 43 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80081 | GWINDT21 | 4 | 22 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80137 | CSDR89 | 8 | 39 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
80137 | CSDR89 | 9 | 15 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
80138 | CSDR7 | 7 | 7 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
80139 | CSDR56 | 5 | 15 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
80139 | CSDR56 | 6 | 39 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
80140 | CSDR11 | 11 | 39 | 0.003707 | south | N | -0.014008 | 0.00094589 | 0.22469 | -0.0051637 | 0.00094589 | south | N | 0.00094589 | 0
80180 | PNSCALT1 | 1 | 148 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80180 | PNSCALT1 | 2 | 50 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80181 | PNSCALT2 | 1 | 55 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80181 | PNSCALT2 | 2 | 50 | 0.002489 | south | Y | -0.015226 | -0.00027211 | 0.22347 | -0.0063817 | 0.00027211 | south | N | 0.00027211 | 0
80223 | REYSHR G | 1 | 12 | 0.002884 | south | N | -0.014831 | 0.00012289 | 0.22387 | -0.0059867 | 0.00012289 | south | N | 0.00012289 | 0
80224 | VISTRONG | 1 | 15 | 0.003625 | south | N | -0.01409 | 0.00086389 | 0.22461 | -0.0052457 | 0.00086389 | south | N | 0.00086389 | 0
80225 | VISTRONG | 2 | 23 | 0.003625 | south | N | -0.01409 | 0.00086389 | 0.22461 | -0.0052457 | 0.00086389 | south | N | 0.00086389 | 0
80226 | ALCOA G | 1 | 48 | 0.004002 | south | N | -0.013713 | 0.0012409 | 0.22498 | -0.0048687 | 0.0012409 | south | N | 0.0012409 | 0
80227 | AIRCO G | 1 | 8 | 0.003649 | south | N | -0.014066 | 0.00088789 | 0.22463 | -0.0052217 | 0.00088789 | south | N | 0.00088789 | 0
80261 | NBEC81A | 1 | 180 | 0.002717 | south | Y | -0.014998 | -4.4111e-05 | 0.2237 | -0.0061537 | 4.4111e-05 | south | N | 4.4111e-05 | 0
80262 | NBEC91A | 1 | 180 | 0.002722 | south | Y | -0.014993 | -3.9111e-05 | 0.2237 | -0.0061487 | 3.9111e-05 | south | N | 3.9111e-05 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.002691 | south | Y | -0.015024 | -7.0111e-05 | 0.22367 | -0.0061797 | 7.0111e-05 | south | N | 7.0111e-05 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.002691 | south | Y | -0.015024 | -7.0111e-05 | 0.22367 | -0.0061797 | 7.0111e-05 | south | N | 7.0111e-05 | 0
80265 | LARECU40 | 4 | 100 | -0.00302 | south | Y | -0.020735 | -0.0057811 | 0.21796 | -0.011891 | 0.0057811 | south | N | 0.0057811 | 0
80266 | LARECU50 | 5 | 100 | -0.00302 | south | Y | -0.020735 | -0.0057811 | 0.21796 | -0.011891 | 0.0057811 | south | N | 0.0057811 | 0
80291 | PAPALOTE | 1 | 25 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
80291 | PAPALOTE | 2 | 25 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
80291 | PAPALOTE | 3 | 25 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
80291 | PAPALOTE | 4 | 16 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
80294 | PAPALOTE | 5 | 25 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
80294 | PAPALOTE | 6 | 25 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
80294 | PAPALOTE | 7 | 25 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
80294 | PAPALOTE | 8 | 15 | 0.002815 | south | Y | -0.0149 | 5.3889e-05 | 0.2238 | -0.0060557 | 5.3889e-05 | south | N | 5.3889e-05 | 0
86104 | CID-138 | EQ | 0 | -0.00302 | south | N | -0.020735 | -0.0057811 | 0.21796 | -0.011891 | 0.0057811 | south | N | 0.0057811 | 0
86105 | CID-230 | EQ | 500 | -0.00302 | south | N | -0.020735 | -0.0057811 | 0.21796 | -0.011891 | 0.0057811 | south | N | 0.0057811 | 0
86106 | CUF-230 | EQ | 500 | -0.00302 | south | N | -0.020735 | -0.0057811 | 0.21796 | -0.011891 | 0.0057811 | south | N | 0.0057811 | 0
86107 | CUF-138 | EQ | 0 | -0.00302 | south | N | -0.020735 | -0.0057811 | 0.21796 | -0.011891 | 0.0057811 | south | N | 0.0057811 | 0
88198 | BEEVILLE | F | 0 | 0.001791 | south | N | -0.015924 | -0.00097011 | 0.22277 | -0.0070797 | 0.00097011 | south | N | 0.00097011 | 0
88253 | HAMILTON | F | 0 | -0.05878 | south | N | -0.076495 | -0.061541 | 0.1622 | -0.067651 | 0.061541 | south | N | 0.061541 | 0
88299 | ZAPATA | F | 0 | -0.001221 | south | N | -0.018936 | -0.0039821 | 0.21976 | -0.010092 | 0.0039821 | south | N | 0.0039821 | 0
88508 | FALFURRI | F | 0 | 0.001642 | south | N | -0.016073 | -0.0011191 | 0.22262 | -0.0072287 | 0.0011191 | south | N | 0.0011191 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6788 | 0 | 0.23069 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5138 | 0 | 0.23069 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4944 | 0 | 0.23069 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4944 | 0 | 0.23069 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.009704 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.572 | 0 | 0.23069 | 0 | 0 | 0 | West | -0.22098
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057 | 56 | 12.9057 | North | 0.0187
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.55908 | 59 | 0.23046 | 13.597 | 115 | 26.5027 |  | -0.23968
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057 | 171 | 39.4084
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057 | 227 | 52.3141 | Line Rating | 1239.6
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.55908 | 59 | 0.23046 | 13.597 | 286 | 65.9111 | Conc Gen | 2023
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057 | 342 | 78.8168 | Weighted Imp. | 466.0897
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.009451 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.7615 | 398 | 0.23043 | 91.7125 | 740 | 170.5293 | PTDF | 0.2304
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5357 | 0 | 0.23042 | 0 | 740 | 170.5293
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5225 | 0 | 0.23042 | 0 | 740 | 170.5293 | Concentration | -0.96125
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4989 | 0 | 0.23042 | 0 | 740 | 170.5293
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5394 | 0 | 0.23042 | 0 | 740 | 170.5293
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6158 | 172 | 0.23038 | 39.6247 | 912 | 210.154
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6158 | 172 | 0.23038 | 39.6247 | 1084 | 249.7787
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6158 | 172 | 0.23038 | 39.6247 | 1256 | 289.4035
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.00939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4742 | 0 | 0.23037 | 0 | 1256 | 289.4035
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.009378 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.9679 | 743 | 0.23036 | 171.1578 | 1999 | 460.5612
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60957 | 0 | 0.23036 | 0 | 1999 | 460.5612
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61895 | 0 | 0.23036 | 0 | 1999 | 460.5612
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65646 | 0 | 0.23036 | 0 | 1999 | 460.5612
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59081 | 0 | 0.23036 | 0 | 1999 | 460.5612
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58144 | 0 | 0.23036 | 0 | 1999 | 460.5612
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97531 | 0 | 0.23036 | 0 | 1999 | 460.5612
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5533 | 0 | 0.23036 | 0 | 1999 | 460.5612
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.009377 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.11252 | 12 | 0.23036 | 2.7643 | 2011 | 463.3255
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.009376 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.04688 | 0 | 0.23036 | 0 | 2011 | 463.3255
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.009376 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1969 | 0 | 0.23036 | 0 | 2011 | 463.3255
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009362 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11234 | 12 | 0.23034 | 2.7641 | 2023 | 466.0897
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31742 | 0 | 0.23032 | 0 | 2023 | 466.0897
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32396 | 0 | 0.23032 | 0 | 2023 | 466.0897
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30529 | 0 | 0.23032 | 0 | 2023 | 466.0897
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42852 | 0 | 0.23032 | 0 | 2023 | 466.0897
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16525 | 0 | 0.23032 | 0 | 2023 | 466.0897
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19045 | 0 | 0.23032 | 0 | 2023 | 466.0897
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18579 | 0 | 0.23032 | 0 | 2023 | 466.0897
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32676 | 0 | 0.23032 | 0 | 2023 | 466.0897
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16805 | 0 | 0.23032 | 0 | 2023 | 466.0897
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79729 | 0 | 0.23032 | 0 | 2023 | 466.0897
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3817 | 0 | 0.23032 | 0 | 2023 | 466.0897
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.009322 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.8517 | 735 | 0.2303 | 169.2737
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.96845 | 104 | 0.23029 | 23.9506
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.96845 | 104 | 0.23029 | 23.9506
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49354 | 53 | 0.23029 | 12.2056
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53078 | 57 | 0.23029 | 13.1268
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.5401 | 58 | 0.23029 | 13.3571
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.5401 | 58 | 0.23029 | 13.3571
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.009253 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6008 | 0 | 0.23024 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2492 | 0 | 0.23024 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.009242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2569 | 0 | 0.23022 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.38812 | 42 | 0.23022 | 9.6694
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.38812 | 42 | 0.23022 | 9.6694
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35116 | 38 | 0.23022 | 8.7485
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35116 | 38 | 0.23022 | 8.7485
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65363 | 0 | 0.23019 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66283 | 0 | 0.23019 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35903 | 0 | 0.23019 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27618 | 0 | 0.23019 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6533 | 0 | 0.23017 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4567 | 0 | 0.23017 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.442 | 0 | 0.23017 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.009184 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.094 | 228 | 0.23017 | 52.4779
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58778 | 0 | 0.23017 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58043 | 0 | 0.23017 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7586 | 0 | 0.23017 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67594 | 0 | 0.23017 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.009183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14876 | 0 | 0.23017 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.009183 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.956 | 213 | 0.23017 | 49.0252
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.00918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3678 | 0 | 0.23016 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.00918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59762 | 0 | 0.23016 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.009179 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5145 | 165 | 0.23016 | 37.9766
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.009178 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5511 | 169 | 0.23016 | 38.8971
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009177 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11012 | 12 | 0.23016 | 2.7619
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.009177 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.23016 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.009163 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32071 | 0 | 0.23015 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4923 | 0 | 0.23013 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4365 | 0 | 0.23013 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4402 | 0 | 0.23013 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4356 | 0 | 0.23013 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4597 | 0 | 0.23013 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.009131 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.71222 | 0 | 0.23011 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.009131 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73048 | 0 | 0.23011 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41984 | 46 | 0.23011 | 10.585
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41984 | 46 | 0.23011 | 10.585
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41984 | 46 | 0.23011 | 10.585
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50199 | 55 | 0.23011 | 12.656
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50199 | 55 | 0.23011 | 12.656
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.49286 | 54 | 0.23011 | 12.4259
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.58949 | 0 | 0.23005 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54414 | 0 | 0.23005 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.58949 | 0 | 0.23005 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.58949 | 0 | 0.23005 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82228 | 0 | 0.23002 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79155 | 0 | 0.23002 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.78613 | 0 | 0.23002 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49246 | 0 | 0.23002 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11024 | 0 | 0.23002 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.008949 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22993 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.00889 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.4445 | 50 | 0.22987 | 11.4936
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.62177 | 0 | 0.22976 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58576 | 0 | 0.22976 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.46545 | 0 | 0.22976 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3454 | 0 | 0.22976 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.348 | 0 | 0.22976 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3375 | 0 | 0.22976 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.84307 | 0 | 0.22976 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.1428 | 0 | 0.22976 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35128 | 0 | 0.22976 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.008781 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28099 | 0 | 0.22976 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.008781 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26343 | 0 | 0.22976 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88073 | 0 | 0.22976 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.81575 | 0 | 0.22976 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90181 | 0 | 0.22976 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89566 | 0 | 0.22976 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.383 | 161 | 0.22957 | 36.9612
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4259 | 166 | 0.22957 | 38.109
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.1303 | 248 | 0.22957 | 56.934
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.00859 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.6901 | 546 | 0.22957 | 125.3465
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.00859 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.5234 | 0 | 0.22957 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.00859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11167 | 13 | 0.22957 | 2.9844
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28136 | 0 | 0.22951 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3865 | 0 | 0.22949 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3865 | 0 | 0.22949 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.084 | 0 | 0.22949 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.5355 | 651 | 0.22949 | 149.395
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.7957 | 564 | 0.22949 | 129.4298
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.1018 | 600 | 0.22949 | 137.6912
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008459 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38996 | 0 | 0.22944 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88922 | 0 | 0.22899 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88922 | 0 | 0.22899 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.95331 | 0 | 0.22899 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.8772 | 0 | 0.22899 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.007872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55891 | 0 | 0.22885 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.007872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07872 | 0 | 0.22885 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4779 | 0 | 0.22869 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55035 | 0 | 0.22869 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34686 | 0 | 0.22869 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77851 | 0 | 0.22869 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66289 | 0 | 0.22869 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6783 | 0 | 0.22869 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3854 | 0 | 0.22869 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13874 | 0 | 0.22869 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72455 | 0 | 0.22869 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53956 | 0 | 0.22869 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4856 | 0 | 0.22869 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55498 | 0 | 0.22869 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49948 | 0 | 0.22869 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77851 | 0 | 0.22869 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74768 | 0 | 0.22869 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79392 | 0 | 0.22869 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58581 | 0 | 0.22869 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61664 | 0 | 0.22869 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61664 | 0 | 0.22869 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3181 | 0 | 0.22869 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.007042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.0069 | 569 | 0.22802 | 129.7459
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.007042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.0914 | 581 | 0.22802 | 132.4822
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.007024 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.46358 | 66 | 0.22801 | 15.0484
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52577 | 76 | 0.2279 | 17.3204
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52577 | 76 | 0.2279 | 17.3204
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.72639 | 105 | 0.2279 | 23.9295
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.51193 | 74 | 0.2279 | 16.8646
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.51193 | 74 | 0.2279 | 16.8646
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.70564 | 102 | 0.2279 | 23.2458
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.006794 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.0564 | 0 | 0.22778 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.006794 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.0224 | 0 | 0.22778 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.00521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.0426 | 584 | 0.22619 | 132.0964
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.00521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.1 | 595 | 0.22619 | 134.5845
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.005208 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.2551 | 433 | 0.22619 | 97.9404
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.81639 | 158 | 0.22615 | 35.7316
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.82672 | 160 | 0.22615 | 36.1839
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.90422 | 175 | 0.22615 | 39.5761
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.72697 | 152.5 | 0.22575 | 34.4268
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71267 | 149.5 | 0.22575 | 33.7495
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.1088 | 232.6 | 0.22575 | 52.5093
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.62674 | 132 | 0.22573 | 29.7964
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.63623 | 134 | 0.22573 | 30.2479
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5336 | 323 | 0.22573 | 72.9109
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18228 | 42 | 0.22532 | 9.4635
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19096 | 44 | 0.22532 | 9.9142
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19096 | 44 | 0.22532 | 9.9142
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20398 | 47 | 0.22532 | 10.5902
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004171 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.293 | 310 | 0.22515 | 69.7975
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004171 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7226 | 413 | 0.22515 | 92.9883
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20183 | 49 | 0.2251 | 11.03
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18947 | 46 | 0.2251 | 10.3547
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18947 | 46 | 0.2251 | 10.3547
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19359 | 47 | 0.2251 | 10.5798
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004119 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.63433 | 154 | 0.2251 | 34.6656
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004119 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60961 | 148 | 0.2251 | 33.315
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19771 | 48 | 0.2251 | 10.8049
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19771 | 48 | 0.2251 | 10.8049
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32248 | 0 | 0.22506 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33064 | 0 | 0.22506 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32248 | 0 | 0.22506 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32656 | 0 | 0.22506 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32003 | 0 | 0.22506 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10205 | 0 | 0.22506 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18777 | 0 | 0.22506 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1143 | 0 | 0.22506 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17798 | 0 | 0.22506 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.30207 | 0 | 0.22506 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.004002 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1921 | 0 | 0.22498 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.003972 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031776 | 0 | 0.22495 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.003972 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031776 | 0 | 0.22495 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1038 | 0 | 0.22469 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025949 | 0 | 0.22469 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14457 | 0 | 0.22469 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.055605 | 0 | 0.22469 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025949 | 0 | 0.22469 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.055605 | 0 | 0.22469 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14457 | 0 | 0.22469 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14457 | 0 | 0.22469 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.003649 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.029192 | 0 | 0.22463 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.003625 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.054375 | 0 | 0.22461 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.003625 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.083375 | 0 | 0.22461 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.003515 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2566 | 0 | 0.2245 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.003434 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4945 | 144 | 0.22442 | 32.316
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.003434 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64559 | 188 | 0.22442 | 42.1903
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.16061 | 47.7 | 0.22435 | 10.7015
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12559 | 37.3 | 0.22435 | 8.3682
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15488 | 46 | 0.22435 | 10.3201
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.16162 | 48 | 0.22435 | 10.7688
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003279 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.039348 | 0 | 0.22426 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0078528 | 0 | 0.22425 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0078528 | 0 | 0.22425 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003216 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.070752 | 22 | 0.2242 | 4.9324
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003216 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035376 | 11 | 0.2242 | 2.4662
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003216 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035376 | 11 | 0.2242 | 2.4662
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7026 | 223.9 | 0.22412 | 50.1806
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70605 | 225 | 0.22412 | 50.4271
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70479 | 224.6 | 0.22412 | 50.3374
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71138 | 226.7 | 0.22412 | 50.8081
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.41606 | 142 | 0.22391 | 31.7956
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42485 | 145 | 0.22391 | 32.4673
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44243 | 151 | 0.22391 | 33.8108
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.8497 | 290 | 0.22391 | 64.9346
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00702 | 0 | 0.22391 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00702 | 0 | 0.22391 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00819 | 0 | 0.22391 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45567 | 0 | 0.22387 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.44125 | 0 | 0.22387 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.2884 | 0 | 0.22387 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41818 | 0 | 0.22387 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.42395 | 0 | 0.22387 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.36627 | 0 | 0.22387 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.002884 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.034608 | 0 | 0.22387 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 25 | 0.2238 | 5.5949
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 25 | 0.2238 | 5.5949
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 25 | 0.2238 | 5.5949
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04504 | 16 | 0.2238 | 3.5808
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 25 | 0.2238 | 5.5949
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 25 | 0.2238 | 5.5949
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 25 | 0.2238 | 5.5949
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.042225 | 15 | 0.2238 | 3.357
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.002736 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.7209 | 629 | 0.22372 | 140.7189
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.002722 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.91459 | 336 | 0.2237 | 75.1647
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002722 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48996 | 180 | 0.2237 | 40.2668
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.40338 | 0 | 0.2237 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.40419 | 0 | 0.2237 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41616 | 0 | 0.2237 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002717 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48906 | 180 | 0.2237 | 40.2659
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39925 | 147 | 0.2237 | 32.8837
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37481 | 138 | 0.2237 | 30.8704
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38024 | 140 | 0.2237 | 31.3178
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39925 | 147 | 0.2237 | 32.8837
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.49431 | 182 | 0.2237 | 40.7131
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53777 | 198 | 0.2237 | 44.2923
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.002691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.89879 | 334 | 0.22367 | 74.7069
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.002691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.91494 | 340 | 0.22367 | 76.0489
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.002691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48438 | 180 | 0.22367 | 40.2612
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.002691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48438 | 180 | 0.22367 | 40.2612
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.002671 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.066775 | 0 | 0.22365 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.002671 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.066775 | 0 | 0.22365 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.002669 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10142 | 0 | 0.22365 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.002651 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10074 | 0 | 0.22363 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002647 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.015882 | 0 | 0.22363 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002585 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01034 | 0 | 0.22357 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002567 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.074443 | 0 | 0.22355 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.23397 | 94 | 0.22347 | 21.0063
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10205 | 41 | 0.22347 | 9.1623
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.094582 | 38 | 0.22347 | 8.4919
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.047291 | 19 | 0.22347 | 4.246
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.23397 | 94 | 0.22347 | 21.0063
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.089604 | 36 | 0.22347 | 8.045
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10703 | 43 | 0.22347 | 9.6093
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.054758 | 22 | 0.22347 | 4.9164
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.36837 | 148 | 0.22347 | 33.0738
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12445 | 50 | 0.22347 | 11.1736
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13689 | 55 | 0.22347 | 12.2909
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12445 | 50 | 0.22347 | 11.1736
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.002424 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22341 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.092112 | 38 | 0.22341 | 8.4894
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.046783 | 19.3 | 0.22341 | 4.3117
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.03636 | 15 | 0.22341 | 3.3511
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.002424 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11393 | 47 | 0.22341 | 10.5001
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.32558 | 144 | 0.22324 | 32.147
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.32558 | 144 | 0.22324 | 32.147
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38663 | 171 | 0.22324 | 38.1746
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.46782 | 207 | 0.22324 | 46.2112
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48974 | 216.7 | 0.22324 | 48.3766
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54692 | 242 | 0.22324 | 54.0247
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1624 | 546 | 0.22311 | 121.8188
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.5967 | 750 | 0.22311 | 167.3335
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31093 | 155 | 0.22299 | 34.5632
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.34102 | 170 | 0.22299 | 37.908
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31093 | 155 | 0.22299 | 34.5632
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2911 | 146.5 | 0.22297 | 32.665
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29388 | 147.9 | 0.22297 | 32.9772
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.34375 | 173 | 0.22297 | 38.5737
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22291 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22291 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22291 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065135 | 0 | 0.22284 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.063274 | 0 | 0.22284 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065135 | 0 | 0.22284 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001791 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22277 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.00165 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.6996 | 424 | 0.22263 | 94.3961
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.00165 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.70125 | 425 | 0.22263 | 94.6188
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001642 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22262 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.001584 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.65261 | 412 | 0.22257 | 91.6973
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.001584 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.6336 | 400 | 0.22257 | 89.0266
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.33064 | 209 | 0.22256 | 46.516
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34171 | 216 | 0.22256 | 48.0739
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.072772 | 46 | 0.22256 | 10.238
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074354 | 47 | 0.22256 | 10.4605
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.072772 | 46 | 0.22256 | 10.238
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.072772 | 46 | 0.22256 | 10.238
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001523 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.60311 | 396 | 0.22251 | 88.1121
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.001455 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.59218 | 407 | 0.22244 | 90.532
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.001082 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.062756 | 58 | 0.22206 | 12.8797
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.001082 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.096298 | 89 | 0.22206 | 19.7637
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.047608 | 44 | 0.22206 | 9.7708
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.047608 | 44 | 0.22206 | 9.7708
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.046526 | 43 | 0.22206 | 9.5488
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04869 | 45 | 0.22206 | 9.9929
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.095304 | 114 | 0.22182 | 25.2873
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.18559 | 222 | 0.22182 | 49.2437
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15382 | 184 | 0.22182 | 40.8146
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.18726 | 224 | 0.22182 | 49.6873
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09614 | 115 | 0.22182 | 25.5091
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004176 | 0 | 0.22133 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003828 | 0 | 0.22133 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004176 | 0 | 0.22133 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22098 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22098 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001221 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21976 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002832 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050976 | 0 | 0.21815 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002832 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050976 | 0 | 0.21815 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.00302 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.302 | 100 | 0.21796 | 21.7962
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.00302 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.302 | 100 | 0.21796 | 21.7962
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.003023 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.004377 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12256 | 0 | 0.21661 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.004377 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12693 | 0 | 0.21661 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.004902 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0686 | 422 | 0.21608 | 91.1859
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.093744 | 0 | 0.21577 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.093744 | 0 | 0.21577 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07812 | 0 | 0.21577 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006179 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1483 | 24 | 0.2148 | 5.1553
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006179 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.1483 | 24 | 0.2148 | 5.1553
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.006179 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.14212 | 23 | 0.2148 | 4.9405
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.007637 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10463 | 0 | 0.21335 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.038174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.18281 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.042062 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25237 | 0 | 0.17892 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.05878 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9397 | 0 | 0.1622 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.05878 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4695 | 0 | 0.1622 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.05878 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.1622 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.067053 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.5414 | 366 | 0.048353 | 17.6971
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4729 | 204 | 0.017932 | 3.6581
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.363 | 201 | 0.017932 | 3.6043
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.8649 | 242 | 0.017932 | 4.3395
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.023358 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4015 | 60 | 0.0046578 | 0.27947
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.023358 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4716 | 63 | 0.0046578 | 0.29344
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.023153 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0044528 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.023153 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0044528 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.023153 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0044528 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.020923 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0022228 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.020469 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0017688 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.020362 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81448 | 0 | 0.0016618 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.020362 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81448 | 0 | 0.0016618 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.02028 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.4476 | 170 | 0.0015798 | 0.26856
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.02028 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.5456 | 520 | 0.0015798 | 0.82148
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.020186 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.4688 | 370 | 0.0014858 | 0.54974
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.826 | 0 | 0.0014858 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8462 | 0 | 0.0014858 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.2375 | 0 | 0.0014858 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8866 | 0 | 0.0014858 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9068 | 0 | 0.0014858 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.2577 | 0 | 0.0014858 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2195 | 160 | 0.0014218 | 0.22748
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.139 | 156 | 0.0014218 | 0.2218
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9439 | 196 | 0.0014218 | 0.27867
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.139 | 156 | 0.0014218 | 0.2218
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1592 | 157 | 0.0014218 | 0.22322
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9842 | 198 | 0.0014218 | 0.28151
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5053 | 0 | 0.0013708 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5977 | 0 | 0.0013708 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.7743 | 0 | 0.0013708 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.1673 | 558 | 0.0013128 | 0.73253
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.5875 | 579 | 0.0013128 | 0.7601
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.1705 | 808 | 0.0013128 | 1.0607
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019778 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.8123 | 395 | 0.0010778 | 0.42572
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019778 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.6034 | 435 | 0.0010778 | 0.46883
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019739 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.5865 | 435 | 0.0010388 | 0.45187
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5564 | 79 | 0.0010008 | 0.079061
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0883 | 106 | 0.0010008 | 0.10608
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8763 | 146 | 0.0010008 | 0.14611
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.019701 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4973 | 76 | 0.0010008 | 0.076059
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.39238 | 20 | 0.00091878 | 0.018376
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49047 | 25 | 0.00091878 | 0.022969
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.80438 | 41 | 0.00091878 | 0.03767
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.019615 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.7846 | 40 | 0.00091478 | 0.036591
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.019393 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.1817 | 112.5 | 0.00069278 | 0.077938
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.019244 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.4667 | 388 | 0.00054378 | 0.21099
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.019244 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.9107 | 515 | 0.00054378 | 0.28005
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0827 | 161 | 0.00044678 | 0.071931
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1401 | 164 | 0.00044678 | 0.073272
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1401 | 164 | 0.00044678 | 0.073272
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.9269 | 414 | 0.00044678 | 0.18497
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1018 | 162 | 0.00044678 | 0.072378
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0827 | 161 | 0.00044678 | 0.071931
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.121 | 163 | 0.00044678 | 0.072825
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.8311 | 409 | 0.00044678 | 0.18273
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019127 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00042678 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019127 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00042678 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.018791 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.2173 | 118 | 9.0778e-05 | 0.010712
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.018791 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.161 | 115 | 9.0778e-05 | 0.010439
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.018791 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.4478 | 556 | 9.0778e-05 | 0.050473
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0727 | 785 | -0.00077322 | -0.60698
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.252 | 795 | -0.00077322 | -0.61471
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.9831 | 780 | -0.00077322 | -0.60311
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.017813 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.3107 | 242 | -0.00088722 | -0.21471
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6286 | 0 | -0.00093922 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.3089 | 0 | -0.00093922 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5753 | 0 | -0.00093922 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0866 | 0 | -0.00093922 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.017621 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0010792 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.017605 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.88025 | 50 | -0.0010952 | -0.054761
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.017576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.1988 | 182 | -0.0011242 | -0.20461
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.017576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.5068 | 484 | -0.0011242 | -0.54412
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.017509 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7889 | 216.4 | -0.0011912 | -0.25778
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.017509 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7837 | 216.1 | -0.0011912 | -0.25742
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9406 | 288 | -0.0015452 | -0.44502
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5218 | 147 | -0.0015452 | -0.22715
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5218 | 147 | -0.0015452 | -0.22715
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.017072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3461 | 196 | -0.0016282 | -0.31913
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.017072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.895 | 111 | -0.0016282 | -0.18073
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.016896 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.7847 | 224 | -0.0018042 | -0.40415
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7265 | 224 | -0.0020642 | -0.46239
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7597 | 226 | -0.0020642 | -0.46651
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5268 | 212 | -0.0020642 | -0.43762
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5102 | 211 | -0.0020642 | -0.43555
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.454 | 151.5 | -0.0025022 | -0.37909
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.467 | 152.3 | -0.0025022 | -0.38109
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8751 | 177.5 | -0.0025022 | -0.44414
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4323 | 150.7 | -0.0025602 | -0.38583
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4371 | 151 | -0.0025602 | -0.38659
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8632 | 177.4 | -0.0025602 | -0.45418
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.01586 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.7539 | 615 | -0.0028402 | -1.7467
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.01586 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.3098 | 587 | -0.0028402 | -1.6672
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.015217 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034832 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.28924 | 20 | -0.0042382 | -0.084764
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.28924 | 20 | -0.0042382 | -0.084764
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.28924 | 20 | -0.0042382 | -0.084764
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24585 | 17 | -0.0042382 | -0.07205
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.014266 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.798 | 827 | -0.0044342 | -3.6671
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.014266 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.6839 | 819 | -0.0044342 | -3.6316
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.014237 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.7084 | 120 | -0.0044632 | -0.53559
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.25144 | 18 | -0.0047312 | -0.085162
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.25144 | 18 | -0.0047312 | -0.085162
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.53082 | 38 | -0.0047312 | -0.17979
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.7058 | 855 | -0.0050092 | -4.2829
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.7058 | 855 | -0.0050092 | -4.2829
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0851 | 152.3 | -0.0050092 | -0.7629
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0947 | 153 | -0.0050092 | -0.76641
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.012483 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0971 | 168 | -0.0062172 | -1.0445
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.012483 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1235 | 90 | -0.0062172 | -0.55955
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.012257 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.675 | 463 | -0.0064432 | -2.9832
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.012247 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.2082 | 17 | -0.0064532 | -0.1097
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.012238 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.39162 | 0 | -0.0064622 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.012208 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.58598 | 48 | -0.0064922 | -0.31163
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.012208 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.56157 | 46 | -0.0064922 | -0.29864
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.012208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2818 | 105 | -0.0064922 | -0.68168
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.01203 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0066702 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.01203 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.4676 | 787 | -0.0066702 | -5.2495
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.823 | 0 | -0.0068782 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.8442 | 0 | -0.0068782 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.8442 | 0 | -0.0068782 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.4924 | 0 | -0.0068782 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.82082 | 70 | -0.0069742 | -0.4882
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.80909 | 69 | -0.0069742 | -0.48122
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.80909 | 69 | -0.0069742 | -0.48122
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.79737 | 68 | -0.0069742 | -0.47425
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5255 | 217.3 | -0.0070782 | -1.5381
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3825 | 205 | -0.0070782 | -1.451
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1658 | 272.4 | -0.0070782 | -1.9281
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.011449 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0072512 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.011449 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0072512 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.82 | 255 | -0.0076412 | -1.9485
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011059 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6478 | 149 | -0.0076412 | -1.1385
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011059 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.692 | 153 | -0.0076412 | -1.1691
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.010637 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.15956 | 0 | -0.0080632 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.010637 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.15956 | 0 | -0.0080632 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.010497 | north | 3 | N | N | Nnorth | Nnorth | 1 | 12.145 | 0 | -0.0082032 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.010497 | north | 3 | N | N | Nnorth | Nnorth | 1 | 12.1555 | 0 | -0.0082032 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.0103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.545 | 150 | -0.0084002 | -1.26
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.0103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.824 | 80 | -0.0084002 | -0.67202
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.007809 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.093708 | 0 | -0.010891 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.007809 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.093708 | 0 | -0.010891 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00685 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.50005 | 73 | -0.01185 | -0.86507
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00685 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.81515 | 119 | -0.01185 | -1.4102
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00685 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.4042 | 205 | -0.01185 | -2.4293
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6987 | 102 | -0.01185 | -1.2087
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6576 | 96 | -0.01185 | -1.1376
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0836 | 100 | -0.017864 | -1.7864
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0187 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0187 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.022852 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.3711 | 60 | -0.041552 | -2.4931
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.060928 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.079628 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.081789 | west | 4 | Y | N | Ywest | Nwest | 1 | -53.1383 | 649.7 | -0.10049 | -65.2878
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.15504 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2566 | 150 | -0.17374 | -26.0616
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.15875 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.5251 | 60 | -0.17745 | -10.6471
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.18095 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.19965 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.18967 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.4499 | 150 | -0.20837 | -31.2549
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.20809 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.4796 | 84 | -0.22679 | -19.0504
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.20831 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.9354 | 76.5 | -0.22701 | -17.366
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.20981 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.7851 | 80 | -0.22851 | -18.2811
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.21158 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.8625 | 169.5 | -0.23028 | -39.0322
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.21306 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.9595 | 150 | -0.23176 | -34.7645
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.21306 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.5194 | 101 | -0.23176 | -23.4081
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.21492 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.2385 | 150 | -0.23362 | -35.0435
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.21492 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.2385 | 150 | -0.23362 | -35.0435
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.21506 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.205 | 80 | -0.23376 | -18.701
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21509 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.2075 | 80 | -0.23379 | -18.7035
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.147 | 75 | -0.23399 | -17.5495
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.2234 | 80 | -0.23399 | -18.7195
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6117 | 40 | -0.23399 | -9.3597
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.21544 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.0968 | 84 | -0.23414 | -19.6676
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21628 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.3026 | 80 | -0.23498 | -18.7986
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21628 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.3026 | 80 | -0.23498 | -18.7986
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.3433 | 112.5 | -0.23509 | -26.4471
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.3496 | 149.5 | -0.23509 | -35.1452
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.2476 | 186 | -0.23509 | -43.7259
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.4146 | 214.5 | -0.23509 | -50.4258
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.21992 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.9883 | 150 | -0.23862 | -35.7933
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.22048 | west | #N/A | N | N | Nwest | Nwest | 1 | -1.0583 | 0 | -0.23918 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.4895 | 120 | -0.23945 | -28.7335
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 1 | -51.4338 | 233 | -0.23945 | -55.791
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.571 | 170.2 | -0.23945 | -40.7537
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.22131 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.9101 | 99 | -0.24001 | -23.7614
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.22131 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.5002 | 61 | -0.24001 | -14.6409
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 1 | -5.5328 | 0 | -0.24001 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 1 | -10.114 | 0 | -0.24001 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 1 | -10.114 | 0 | -0.24001 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.22159 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.2438 | 141 | -0.24029 | -33.8805
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.22159 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.5904 | 120 | -0.24029 | -28.8345
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.22187 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4643 | 6.6 | -0.24057 | -1.5878
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.22187 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.6101 | 34.3 | -0.24057 | -8.2515
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.22354 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.8833 | 165 | -0.24224 | -39.9688
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.22371 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.094 | 63 | -0.24241 | -15.2721
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.22509 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.5162 | 180 | -0.24379 | -43.8822
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.22509 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.5162 | 180 | -0.24379 | -43.8822
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.22529 | west | 6 | Y | N | Ywest | Nwest | 1 | -50.6893 | 225 | -0.24399 | -54.8969
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.2267 | west | 8 | N | N | Nwest | Nwest | 1 | -5.849 | 0 | -0.2454 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.2272 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.2634 | 120 | -0.2459 | -29.5074
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.22795 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.3536 | 120 | -0.24665 | -29.5977
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.2297 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.2252 | 149 | -0.2484 | -37.0115
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.23004 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.0515 | 35 | -0.24874 | -8.706
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.23004 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9013 | 30 | -0.24874 | -7.4623
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.1981 | 66 | -0.24897 | -16.4323
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -14.9678 | 65 | -0.24897 | -16.1833
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.4284 | 67 | -0.24897 | -16.6813
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.4284 | 67 | -0.24897 | -16.6813
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.4284 | 67 | -0.24897 | -16.6813
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.23027 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24897 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.23027 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24897 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.23069 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.184 | 100.5 | -0.24939 | -25.0634
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.23071 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.3814 | 58 | -0.24941 | -14.466
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.23086 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.4498 | 214.2 | -0.24956 | -53.4554
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.2951 | 66 | -0.25044 | -16.5293
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.9903 | 69 | -0.25044 | -17.2807
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.9903 | 69 | -0.25044 | -17.2807
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.5268 | 67 | -0.25044 | -16.7798
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.5268 | 67 | -0.25044 | -16.7798
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.0634 | 65 | -0.25044 | -16.2789
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -48.6988 | 208.2 | -0.2526 | -52.5922
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -33.2378 | 142.1 | -0.2526 | -35.8951
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -30.9689 | 132.4 | -0.2526 | -33.4448
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -31.8109 | 136 | -0.2526 | -34.3542
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -34.3839 | 147 | -0.2526 | -37.1328
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -49.1198 | 210 | -0.2526 | -53.0469
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.3758 | 70 | -0.25264 | -17.6848
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.3758 | 70 | -0.25264 | -17.6848
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -21.7096 | 92.8 | -0.25264 | -23.445
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -18.7152 | 80 | -0.25264 | -20.2112
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -18.7152 | 80 | -0.25264 | -20.2112
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -26.9031 | 115 | -0.25264 | -29.0536
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 1 | -16.5535 | 0 | -0.25518 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 1 | -17.3576 | 0 | -0.25518 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 1 | -16.6481 | 0 | -0.25518 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.5795 | 150 | -0.2559 | -38.3846
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -52.1833 | 220 | -0.2559 | -56.2974
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -47.4394 | 200 | -0.2559 | -51.1794
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.9143 | 121.9 | -0.2559 | -31.1939
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.7573 | 209 | -0.25677 | -53.6656
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.1162 | 126.5 | -0.25677 | -32.4818
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -59.2802 | 249 | -0.25677 | -63.9365
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.9004 | 197 | -0.25677 | -50.5843
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.1289 | 37.5 | -0.26214 | -9.8301
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.1695 | 107.5 | -0.26214 | -28.1798
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.864 | 135 | -0.26214 | -35.3885
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.969 | 119 | -0.26214 | -31.1943
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.5609 | 105 | -0.26214 | -27.5244
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.5967 | 80.5 | -0.26214 | -21.102
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.24712 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.8897 | 125 | -0.26582 | -33.2273
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.24712 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.8897 | 125 | -0.26582 | -33.2273
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.31529 | west | 6 | Y | N | Ywest | Nwest | 1 | -74.4091 | 236 | -0.33399 | -78.8224
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.31678 | west | 6 | Y | N | Ywest | Nwest | 1 | -126.7124 | 400 | -0.33548 | -134.1925

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1430 GRHAMES - 1435 LONGCREK C: 1048 TONKAWA - 1430 GRHAMSES | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.31678 | west | 6 | Y | N | Ywest | Nwest | 1 | -126.7124 | 0 | -0.33548 | 0 | 0 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.31529 | west | 6 | Y | N | Ywest | Nwest | 1 | -74.4091 | 0 | -0.33399 | 0 | 0 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.24712 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.8897 | 0 | -0.26582 | 0 | 0 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.24712 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.8897 | 0 | -0.26582 | 0 | 0 | 0 | Weighted Shift Factors
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.1289 | 0 | -0.26214 | 0 | 0 | 0 | West | -0.22098
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.1695 | 0 | -0.26214 | 0 | 0 | 0 | North | 0.0187
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.864 | 0 | -0.26214 | 0 | 0 | 0 |  | -0.23968
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.969 | 0 | -0.26214 | 0 | 0 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.5609 | 0 | -0.26214 | 0 | 0 | 0 | Line Rating | 1239.6
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.24344 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.5967 | 0 | -0.26214 | 0 | 0 | 0 | Conc Gen | 2410.5
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.7573 | 0 | -0.25677 | 0 | 0 | 0 | Weighted Imp. | 560.6204
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.1162 | 0 | -0.25677 | 0 | 0 | 0 | PTDF | 0.23257
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -59.2802 | 0 | -0.25677 | 0 | 0 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.23807 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.9004 | 0 | -0.25677 | 0 | 0 | 0 | Concentration | -0.97034
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.5795 | 0 | -0.2559 | 0 | 0 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -52.1833 | 0 | -0.2559 | 0 | 0 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -47.4394 | 0 | -0.2559 | 0 | 0 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.2372 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.9143 | 0 | -0.2559 | 0 | 0 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 1 | -16.5535 | 0 | -0.25518 | 0 | 0 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 1 | -17.3576 | 0 | -0.25518 | 0 | 0 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.23648 | west | 8 | N | N | Nwest | Nwest | 1 | -16.6481 | 0 | -0.25518 | 0 | 0 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.3758 | 70 | -0.25264 | -17.6848 | 70 | 17.6848
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.3758 | 70 | -0.25264 | -17.6848 | 140 | 35.3696
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -21.7096 | 92.8 | -0.25264 | -23.445 | 232.8 | 58.8146
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -18.7152 | 80 | -0.25264 | -20.2112 | 312.8 | 79.0259
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -18.7152 | 80 | -0.25264 | -20.2112 | 392.8 | 99.2371
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.23394 | west | 9 | Y | Y | Ywest | Ywest | 1 | -26.9031 | 115 | -0.25264 | -29.0536 | 507.8 | 128.2907
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -48.6988 | 208.2 | -0.2526 | -52.5922 | 716 | 180.8829
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -33.2378 | 142.1 | -0.2526 | -35.8951 | 858.1 | 216.778
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -30.9689 | 132.4 | -0.2526 | -33.4448 | 990.5 | 250.2228
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -31.8109 | 136 | -0.2526 | -34.3542 | 1126.5 | 284.5769
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -34.3839 | 147 | -0.2526 | -37.1328 | 1273.5 | 321.7098
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.2339 | west | 9 | Y | Y | Ywest | Ywest | 1 | -49.1198 | 210 | -0.2526 | -53.0469 | 1483.5 | 374.7566
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.2951 | 66 | -0.25044 | -16.5293 | 1549.5 | 391.286
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.9903 | 69 | -0.25044 | -17.2807 | 1618.5 | 408.5666
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.9903 | 69 | -0.25044 | -17.2807 | 1687.5 | 425.8473
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.5268 | 67 | -0.25044 | -16.7798 | 1754.5 | 442.627
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.5268 | 67 | -0.25044 | -16.7798 | 1821.5 | 459.4068
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.23174 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.0634 | 65 | -0.25044 | -16.2789 | 1886.5 | 475.6857
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.23086 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.4498 | 0 | -0.24956 | 0 | 1886.5 | 475.6857
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.23071 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.3814 | 0 | -0.24941 | 0 | 1886.5 | 475.6857
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.23069 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.184 | 0 | -0.24939 | 0 | 1886.5 | 475.6857
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.1981 | 66 | -0.24897 | -16.4323 | 1952.5 | 492.118
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -14.9678 | 65 | -0.24897 | -16.1833 | 2017.5 | 508.3013
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.4284 | 67 | -0.24897 | -16.6813 | 2084.5 | 524.9826
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.4284 | 67 | -0.24897 | -16.6813 | 2151.5 | 541.6638
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.23027 | west | 13 | Y | Y | Ywest | Ywest | 1 | -15.4284 | 67 | -0.24897 | -16.6813 | 2218.5 | 558.3451
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.23027 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24897 | 0 | 2218.5 | 558.3451
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.23027 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.24897 | 0 | 2218.5 | 558.3451
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.23004 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.0515 | 0 | -0.24874 | 0 | 2218.5 | 558.3451
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.23004 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.9013 | 0 | -0.24874 | 0 | 2218.5 | 558.3451
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.2297 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.2252 | 0 | -0.2484 | 0 | 2218.5 | 558.3451
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.22795 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.3536 | 0 | -0.24665 | 0 | 2218.5 | 558.3451
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.2272 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.2634 | 0 | -0.2459 | 0 | 2218.5 | 558.3451
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.2267 | west | 8 | N | N | Nwest | Nwest | 1 | -5.849 | 0 | -0.2454 | 0 | 2218.5 | 558.3451
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.22529 | west | 6 | Y | N | Ywest | Nwest | 1 | -50.6893 | 0 | -0.24399 | 0 | 2218.5 | 558.3451
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.22509 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.5162 | 0 | -0.24379 | 0 | 2218.5 | 558.3451
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.22509 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.5162 | 0 | -0.24379 | 0 | 2218.5 | 558.3451
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.22371 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.094 | 0 | -0.24241 | 0 | 2218.5 | 558.3451
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.22354 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.8833 | 0 | -0.24224 | 0 | 2218.5 | 558.3451
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.22187 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4643 | 0 | -0.24057 | 0 | 2218.5 | 558.3451
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.22187 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.6101 | 0 | -0.24057 | 0 | 2218.5 | 558.3451
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.22159 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.2438 | 0 | -0.24029 | 0 | 2218.5 | 558.3451
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.22159 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.5904 | 0 | -0.24029 | 0 | 2218.5 | 558.3451
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.22131 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.9101 | 0 | -0.24001 | 0 | 2218.5 | 558.3451
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.22131 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.5002 | 0 | -0.24001 | 0 | 2218.5 | 558.3451
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 1 | -5.5328 | 0 | -0.24001 | 0 | 2218.5 | 558.3451
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 1 | -10.114 | 0 | -0.24001 | 0 | 2218.5 | 558.3451
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.22131 | west | 7 | N | N | Nwest | Nwest | 1 | -10.114 | 0 | -0.24001 | 0 | 2218.5 | 558.3451
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.4895 | 0 | -0.23945 | 0 | 2218.5 | 558.3451
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 1 | -51.4338 | 0 | -0.23945 | 0 | 2218.5 | 558.3451
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.22075 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.571 | 0 | -0.23945 | 0 | 2218.5 | 558.3451
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.22048 | west | #N/A | N | N | Nwest | Nwest | 1 | -1.0583 | 0 | -0.23918 | 0 | 2218.5 | 558.3451
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.21992 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.9883 | 0 | -0.23862 | 0 | 2218.5 | 558.3451
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.3433 | 0 | -0.23509 | 0 | 2218.5 | 558.3451
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.3496 | 0 | -0.23509 | 0 | 2218.5 | 558.3451
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.2476 | 0 | -0.23509 | 0 | 2218.5 | 558.3451
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.21638 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.4146 | 0 | -0.23509 | 0 | 2218.5 | 558.3451
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21628 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.3026 | 0 | -0.23498 | 0 | 2218.5 | 558.3451
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21628 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.3026 | 0 | -0.23498 | 0 | 2218.5 | 558.3451
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.21544 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.0968 | 0 | -0.23414 | 0 | 2218.5 | 558.3451
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.147 | 0 | -0.23399 | 0 | 2218.5 | 558.3451
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.2234 | 0 | -0.23399 | 0 | 2218.5 | 558.3451
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.21529 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.6117 | 0 | -0.23399 | 0 | 2218.5 | 558.3451
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.21509 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.2075 | 0 | -0.23379 | 0 | 2218.5 | 558.3451
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.21506 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.205 | 0 | -0.23376 | 0 | 2218.5 | 558.3451
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.21492 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.2385 | 0 | -0.23362 | 0 | 2218.5 | 558.3451
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.21492 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.2385 | 0 | -0.23362 | 0 | 2218.5 | 558.3451
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.21306 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.9595 | 0 | -0.23176 | 0 | 2218.5 | 558.3451
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.21306 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.5194 | 0 | -0.23176 | 0 | 2218.5 | 558.3451
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.21158 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.8625 | 0 | -0.23028 | 0 | 2218.5 | 558.3451
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.20981 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.7851 | 0 | -0.22851 | 0 | 2218.5 | 558.3451
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.20831 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.9354 | 0 | -0.22701 | 0 | 2218.5 | 558.3451
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.20809 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.4796 | 0 | -0.22679 | 0 | 2218.5 | 558.3451
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.18967 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.4499 | 0 | -0.20837 | 0 | 2218.5 | 558.3451
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.18095 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.19965 | 0 | 2218.5 | 558.3451
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.15875 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.5251 | 0 | -0.17745 | 0 | 2218.5 | 558.3451
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.15504 | west | 6 | Y | N | Ywest | Nwest | 1 | -23.2566 | 0 | -0.17374 | 0 | 2218.5 | 558.3451
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.081789 | west | 4 | Y | N | Ywest | Nwest | 1 | -53.1383 | 0 | -0.10049 | 0 | 2218.5 | 558.3451
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.060928 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.079628 | 0 | 2218.5 | 558.3451
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.022852 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.3711 | 0 | -0.041552 | 0 | 2218.5 | 558.3451
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0187 | 0 | 2218.5 | 558.3451
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0187 | 0 | 2218.5 | 558.3451
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0836 | 0 | -0.017864 | 0 | 2218.5 | 558.3451
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00685 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.50005 | 73 | -0.01185 | -0.86507 | 2291.5 | 559.2102
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00685 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.81515 | 119 | -0.01185 | -1.4102 | 2410.5 | 560.6204
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00685 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.4042 | 205 | -0.01185 | -2.4293
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6987 | 102 | -0.01185 | -1.2087
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00685 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.6576 | 96 | -0.01185 | -1.1376
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.007809 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.093708 | 0 | -0.010891 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.007809 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.093708 | 0 | -0.010891 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.0103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.545 | 150 | -0.0084002 | -1.26
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.0103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.824 | 80 | -0.0084002 | -0.67202
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.010497 | north | 3 | N | N | Nnorth | Nnorth | 1 | 12.145 | 0 | -0.0082032 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.010497 | north | 3 | N | N | Nnorth | Nnorth | 1 | 12.1555 | 0 | -0.0082032 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.010637 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.15956 | 0 | -0.0080632 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.010637 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.15956 | 0 | -0.0080632 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.82 | 255 | -0.0076412 | -1.9485
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011059 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6478 | 149 | -0.0076412 | -1.1385
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011059 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.692 | 153 | -0.0076412 | -1.1691
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.011449 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0072512 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.011449 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0072512 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5255 | 217.3 | -0.0070782 | -1.5381
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3825 | 205 | -0.0070782 | -1.451
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.011622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1658 | 272.4 | -0.0070782 | -1.9281
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.82082 | 70 | -0.0069742 | -0.4882
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.80909 | 69 | -0.0069742 | -0.48122
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.80909 | 69 | -0.0069742 | -0.48122
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.011726 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.79737 | 68 | -0.0069742 | -0.47425
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.823 | 0 | -0.0068782 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.8442 | 0 | -0.0068782 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.8442 | 0 | -0.0068782 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.011822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.4924 | 0 | -0.0068782 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.01203 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0066702 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.01203 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.4676 | 787 | -0.0066702 | -5.2495
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.012208 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.58598 | 48 | -0.0064922 | -0.31163
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.012208 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.56157 | 46 | -0.0064922 | -0.29864
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.012208 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.2818 | 105 | -0.0064922 | -0.68168
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.012238 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.39162 | 0 | -0.0064622 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.012247 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.2082 | 17 | -0.0064532 | -0.1097
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.012247 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0064532 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.012257 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.675 | 0 | -0.0064432 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.012483 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.0971 | 168 | -0.0062172 | -1.0445
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.012483 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.1235 | 90 | -0.0062172 | -0.55955
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.7058 | 0 | -0.0050092 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.7058 | 0 | -0.0050092 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0851 | 0 | -0.0050092 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.013691 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.0947 | 0 | -0.0050092 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.25144 | 18 | -0.0047312 | -0.085162
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.25144 | 18 | -0.0047312 | -0.085162
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.013969 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.53082 | 38 | -0.0047312 | -0.17979
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.014237 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.7084 | 0 | -0.0044632 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.014266 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.798 | 0 | -0.0044342 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.014266 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.6839 | 0 | -0.0044342 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.28924 | 20 | -0.0042382 | -0.084764
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.28924 | 20 | -0.0042382 | -0.084764
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.28924 | 20 | -0.0042382 | -0.084764
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.014462 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.24585 | 17 | -0.0042382 | -0.07205
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.015217 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034832 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.01586 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.7539 | 0 | -0.0028402 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.01586 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.3098 | 0 | -0.0028402 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4323 | 150.7 | -0.0025602 | -0.38583
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.4371 | 151 | -0.0025602 | -0.38659
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.01614 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8632 | 177.4 | -0.0025602 | -0.45418
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.454 | 151.5 | -0.0025022 | -0.37909
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.467 | 152.3 | -0.0025022 | -0.38109
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.016198 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8751 | 177.5 | -0.0025022 | -0.44414
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7265 | 224 | -0.0020642 | -0.46239
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7597 | 226 | -0.0020642 | -0.46651
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5268 | 212 | -0.0020642 | -0.43762
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.016636 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5102 | 211 | -0.0020642 | -0.43555
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.016896 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.7847 | 224 | -0.0018042 | -0.40415
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.017072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.3461 | 196 | -0.0016282 | -0.31913
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.017072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.895 | 111 | -0.0016282 | -0.18073
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9406 | 288 | -0.0015452 | -0.44502
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5218 | 147 | -0.0015452 | -0.22715
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.017155 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5218 | 147 | -0.0015452 | -0.22715
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.017509 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7889 | 216.4 | -0.0011912 | -0.25778
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.017509 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7837 | 216.1 | -0.0011912 | -0.25742
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.017576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.1988 | 182 | -0.0011242 | -0.20461
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.017576 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.5068 | 484 | -0.0011242 | -0.54412
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.017605 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.88025 | 0 | -0.0010952 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.017621 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0010792 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6286 | 0 | -0.00093922 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.3089 | 0 | -0.00093922 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.5753 | 0 | -0.00093922 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.017761 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0866 | 0 | -0.00093922 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.017813 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.3107 | 242 | -0.00088722 | -0.21471
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0727 | 0 | -0.00077322 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.252 | 0 | -0.00077322 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.017927 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.9831 | 0 | -0.00077322 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.018791 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.2173 | 118 | 9.0778e-05 | 0.010712
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.018791 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.161 | 115 | 9.0778e-05 | 0.010439
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.018791 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.4478 | 556 | 9.0778e-05 | 0.050473
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019127 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00042678 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.019127 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00042678 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0827 | 161 | 0.00044678 | 0.071931
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1401 | 164 | 0.00044678 | 0.073272
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1401 | 164 | 0.00044678 | 0.073272
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.9269 | 414 | 0.00044678 | 0.18497
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1018 | 162 | 0.00044678 | 0.072378
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0827 | 161 | 0.00044678 | 0.071931
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.121 | 163 | 0.00044678 | 0.072825
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.019147 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.8311 | 409 | 0.00044678 | 0.18273
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.019244 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.4667 | 388 | 0.00054378 | 0.21099
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.019244 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.9107 | 515 | 0.00054378 | 0.28005
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.019393 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.1817 | 0 | 0.00069278 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.019615 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.7846 | 40 | 0.00091478 | 0.036591
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.39238 | 20 | 0.00091878 | 0.018376
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49047 | 25 | 0.00091878 | 0.022969
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.019619 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.80438 | 41 | 0.00091878 | 0.03767
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5564 | 79 | 0.0010008 | 0.079061
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0883 | 106 | 0.0010008 | 0.10608
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.019701 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.8763 | 146 | 0.0010008 | 0.14611
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.019701 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4973 | 76 | 0.0010008 | 0.076059
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.019739 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.5865 | 435 | 0.0010388 | 0.45187
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.019778 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.8123 | 395 | 0.0010778 | 0.42572
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.019778 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.6034 | 435 | 0.0010778 | 0.46883
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.1673 | 0 | 0.0013128 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.5875 | 0 | 0.0013128 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.020013 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 16.1705 | 0 | 0.0013128 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5053 | 0 | 0.0013708 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5977 | 0 | 0.0013708 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.020071 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.7743 | 0 | 0.0013708 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2195 | 160 | 0.0014218 | 0.22748
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.139 | 156 | 0.0014218 | 0.2218
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9439 | 196 | 0.0014218 | 0.27867
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.139 | 156 | 0.0014218 | 0.2218
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1592 | 157 | 0.0014218 | 0.22322
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.020122 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9842 | 198 | 0.0014218 | 0.28151
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.020186 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.4688 | 370 | 0.0014858 | 0.54974
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.826 | 0 | 0.0014858 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8462 | 0 | 0.0014858 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.2375 | 0 | 0.0014858 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8866 | 0 | 0.0014858 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.9068 | 0 | 0.0014858 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.020186 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.2577 | 0 | 0.0014858 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.02028 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.4476 | 170 | 0.0015798 | 0.26856
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.02028 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.5456 | 520 | 0.0015798 | 0.82148
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.020362 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81448 | 0 | 0.0016618 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.020362 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.81448 | 0 | 0.0016618 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.020469 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0017688 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.020923 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0022228 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.023153 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0044528 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.023153 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0044528 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.023153 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0044528 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.023358 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4015 | 60 | 0.0046578 | 0.27947
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.023358 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4716 | 63 | 0.0046578 | 0.29344
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4729 | 204 | 0.017932 | 3.6581
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.363 | 201 | 0.017932 | 3.6043
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.036632 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.8649 | 242 | 0.017932 | 4.3395
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.067053 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.5414 | 366 | 0.048353 | 17.6971
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.05878 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9397 | 0 | 0.1622 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.05878 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4695 | 0 | 0.1622 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.05878 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.1622 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.042062 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25237 | 0 | 0.17892 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.038174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.18281 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007772 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.065285 | 8.4 | 0.21321 | 1.791
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.007637 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10463 | 0 | 0.21335 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006179 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1483 | 24 | 0.2148 | 5.1553
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006179 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.1483 | 24 | 0.2148 | 5.1553
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.006179 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.14212 | 23 | 0.2148 | 4.9405
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.093744 | 0 | 0.21577 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.093744 | 0 | 0.21577 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.005208 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.07812 | 0 | 0.21577 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.004902 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0686 | 422 | 0.21608 | 91.1859
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.004377 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12256 | 0 | 0.21661 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.004377 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.12693 | 0 | 0.21661 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.003023 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.00302 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.302 | 100 | 0.21796 | 21.7962
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.00302 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.302 | 100 | 0.21796 | 21.7962
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.00302 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21796 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002832 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050976 | 0 | 0.21815 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002832 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.050976 | 0 | 0.21815 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001221 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21976 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22098 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22098 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22098 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004176 | 0 | 0.22133 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.003828 | 0 | 0.22133 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000348 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.004176 | 0 | 0.22133 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.095304 | 0 | 0.22182 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.18559 | 0 | 0.22182 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15382 | 0 | 0.22182 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.18726 | 0 | 0.22182 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000836 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09614 | 0 | 0.22182 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.001082 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.062756 | 58 | 0.22206 | 12.8797
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.001082 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.096298 | 89 | 0.22206 | 19.7637
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.047608 | 44 | 0.22206 | 9.7708
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.047608 | 44 | 0.22206 | 9.7708
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.046526 | 43 | 0.22206 | 9.5488
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.001082 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.04869 | 45 | 0.22206 | 9.9929
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.001455 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.59218 | 407 | 0.22244 | 90.532
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001523 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.60311 | 0 | 0.22251 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.33064 | 209 | 0.22256 | 46.516
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001582 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34171 | 216 | 0.22256 | 48.0739
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.072772 | 46 | 0.22256 | 10.238
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074354 | 47 | 0.22256 | 10.4605
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.072772 | 46 | 0.22256 | 10.238
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001582 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.072772 | 46 | 0.22256 | 10.238
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.001584 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.65261 | 412 | 0.22257 | 91.6973
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.001584 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.6336 | 400 | 0.22257 | 89.0266
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001642 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22262 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.00165 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.6996 | 0 | 0.22263 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.00165 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.70125 | 0 | 0.22263 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001791 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22277 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065135 | 0 | 0.22284 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.063274 | 0 | 0.22284 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001861 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.065135 | 0 | 0.22284 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22291 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22291 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.001923 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22291 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2911 | 146.5 | 0.22297 | 32.665
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29388 | 147.9 | 0.22297 | 32.9772
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.001987 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.34375 | 173 | 0.22297 | 38.5737
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31093 | 155 | 0.22299 | 34.5632
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.34102 | 170 | 0.22299 | 37.908
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002006 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31093 | 155 | 0.22299 | 34.5632
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1624 | 0 | 0.22311 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002129 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.5967 | 0 | 0.22311 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.46782 | 207 | 0.22324 | 46.2112
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48974 | 216.7 | 0.22324 | 48.3766
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.00226 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54692 | 242 | 0.22324 | 54.0247
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.32558 | 144 | 0.22324 | 32.147
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.32558 | 144 | 0.22324 | 32.147
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.002261 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38663 | 171 | 0.22324 | 38.1746
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.092112 | 38 | 0.22341 | 8.4894
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.046783 | 19.3 | 0.22341 | 4.3117
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.002424 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.03636 | 15 | 0.22341 | 3.3511
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.002424 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.11393 | 47 | 0.22341 | 10.5001
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.002424 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.22341 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.23397 | 0 | 0.22347 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10205 | 0 | 0.22347 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.094582 | 0 | 0.22347 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.047291 | 0 | 0.22347 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.23397 | 0 | 0.22347 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.089604 | 0 | 0.22347 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10703 | 0 | 0.22347 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.054758 | 0 | 0.22347 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.36837 | 0 | 0.22347 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12445 | 0 | 0.22347 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13689 | 0 | 0.22347 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.002489 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12445 | 0 | 0.22347 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002567 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.074443 | 0 | 0.22355 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002585 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01034 | 0 | 0.22357 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002647 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.015882 | 0 | 0.22363 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.002651 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10074 | 0 | 0.22363 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.002669 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10142 | 0 | 0.22365 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.002671 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.066775 | 0 | 0.22365 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.002671 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.066775 | 0 | 0.22365 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.002691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.89879 | 334 | 0.22367 | 74.7069
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.002691 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.91494 | 340 | 0.22367 | 76.0489
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.002691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48438 | 180 | 0.22367 | 40.2612
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.002691 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48438 | 180 | 0.22367 | 40.2612
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39925 | 147 | 0.2237 | 32.8837
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37481 | 138 | 0.2237 | 30.8704
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38024 | 140 | 0.2237 | 31.3178
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39925 | 147 | 0.2237 | 32.8837
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.49431 | 182 | 0.2237 | 40.7131
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.002716 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53777 | 198 | 0.2237 | 44.2923
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002717 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48906 | 180 | 0.2237 | 40.2659
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.40338 | 0 | 0.2237 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.40419 | 0 | 0.2237 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.00272 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41616 | 0 | 0.2237 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.002722 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.91459 | 336 | 0.2237 | 75.1647
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002722 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48996 | 180 | 0.2237 | 40.2668
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.002736 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.7209 | 0 | 0.22372 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 0 | 0.2238 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 0 | 0.2238 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 0 | 0.2238 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04504 | 0 | 0.2238 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 0 | 0.2238 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 0 | 0.2238 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070375 | 0 | 0.2238 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.002815 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.042225 | 0 | 0.2238 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45567 | 0 | 0.22387 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.44125 | 0 | 0.22387 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.2884 | 0 | 0.22387 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41818 | 0 | 0.22387 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.42395 | 0 | 0.22387 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.002884 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.36627 | 0 | 0.22387 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.002884 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.034608 | 0 | 0.22387 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00702 | 0 | 0.22391 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00702 | 0 | 0.22391 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.002925 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.00819 | 0 | 0.22391 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.41606 | 142 | 0.22391 | 31.7956
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42485 | 145 | 0.22391 | 32.4673
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44243 | 151 | 0.22391 | 33.8108
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.00293 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.8497 | 290 | 0.22391 | 64.9346
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7026 | 223.9 | 0.22412 | 50.1806
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70605 | 225 | 0.22412 | 50.4271
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70479 | 224.6 | 0.22412 | 50.3374
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003138 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71138 | 226.7 | 0.22412 | 50.8081
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003216 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.070752 | 22 | 0.2242 | 4.9324
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003216 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035376 | 11 | 0.2242 | 2.4662
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003216 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035376 | 11 | 0.2242 | 2.4662
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0078528 | 0 | 0.22425 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003272 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0078528 | 0 | 0.22425 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003279 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.039348 | 0 | 0.22426 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.16061 | 47.7 | 0.22435 | 10.7015
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12559 | 37.3 | 0.22435 | 8.3682
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15488 | 46 | 0.22435 | 10.3201
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003367 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.16162 | 48 | 0.22435 | 10.7688
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.003434 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4945 | 144 | 0.22442 | 32.316
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.003434 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64559 | 188 | 0.22442 | 42.1903
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.003515 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2566 | 0 | 0.2245 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.003625 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.054375 | 0 | 0.22461 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.003625 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.083375 | 0 | 0.22461 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.003649 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.029192 | 0 | 0.22463 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1038 | 0 | 0.22469 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025949 | 0 | 0.22469 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14457 | 0 | 0.22469 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.055605 | 0 | 0.22469 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.025949 | 0 | 0.22469 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.055605 | 0 | 0.22469 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14457 | 0 | 0.22469 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.003707 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14457 | 0 | 0.22469 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.003972 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031776 | 0 | 0.22495 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.003972 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.031776 | 0 | 0.22495 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.004002 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1921 | 0 | 0.22498 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32248 | 0 | 0.22506 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.33064 | 0 | 0.22506 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32248 | 0 | 0.22506 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32656 | 0 | 0.22506 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.32003 | 0 | 0.22506 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.10205 | 0 | 0.22506 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.18777 | 0 | 0.22506 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1143 | 0 | 0.22506 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.17798 | 0 | 0.22506 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.004082 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.30207 | 0 | 0.22506 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20183 | 49 | 0.2251 | 11.03
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18947 | 46 | 0.2251 | 10.3547
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18947 | 46 | 0.2251 | 10.3547
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19359 | 47 | 0.2251 | 10.5798
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004119 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.63433 | 154 | 0.2251 | 34.6656
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004119 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60961 | 148 | 0.2251 | 33.315
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19771 | 48 | 0.2251 | 10.8049
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004119 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19771 | 48 | 0.2251 | 10.8049
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004171 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.293 | 310 | 0.22515 | 69.7975
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004171 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7226 | 413 | 0.22515 | 92.9883
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18228 | 42 | 0.22532 | 9.4635
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19096 | 44 | 0.22532 | 9.9142
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19096 | 44 | 0.22532 | 9.9142
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00434 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20398 | 47 | 0.22532 | 10.5902
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.62674 | 132 | 0.22573 | 29.7964
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.63623 | 134 | 0.22573 | 30.2479
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.004748 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5336 | 323 | 0.22573 | 72.9109
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.72697 | 152.5 | 0.22575 | 34.4268
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71267 | 149.5 | 0.22575 | 33.7495
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.004767 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.1088 | 232.6 | 0.22575 | 52.5093
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005032 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2516 | 50 | 0.22601 | 11.3007
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.81639 | 158 | 0.22615 | 35.7316
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.82672 | 160 | 0.22615 | 36.1839
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.005167 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.90422 | 175 | 0.22615 | 39.5761
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.005208 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.2551 | 0 | 0.22619 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.00521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.0426 | 0 | 0.22619 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.00521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.1 | 0 | 0.22619 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.006794 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.0564 | 0 | 0.22778 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.006794 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 9.0224 | 0 | 0.22778 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52577 | 76 | 0.2279 | 17.3204
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.52577 | 76 | 0.2279 | 17.3204
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.72639 | 105 | 0.2279 | 23.9295
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.51193 | 74 | 0.2279 | 16.8646
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.51193 | 74 | 0.2279 | 16.8646
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.006918 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.70564 | 102 | 0.2279 | 23.2458
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.007024 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.46358 | 66 | 0.22801 | 15.0484
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.007042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.0069 | 0 | 0.22802 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.007042 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.0914 | 0 | 0.22802 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4779 | 0 | 0.22869 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55035 | 0 | 0.22869 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34686 | 0 | 0.22869 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77851 | 0 | 0.22869 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66289 | 0 | 0.22869 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6783 | 0 | 0.22869 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3854 | 0 | 0.22869 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13874 | 0 | 0.22869 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72455 | 0 | 0.22869 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53956 | 0 | 0.22869 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4856 | 0 | 0.22869 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55498 | 0 | 0.22869 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49948 | 0 | 0.22869 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.77851 | 0 | 0.22869 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74768 | 0 | 0.22869 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79392 | 0 | 0.22869 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58581 | 0 | 0.22869 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61664 | 0 | 0.22869 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61664 | 0 | 0.22869 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.007708 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3181 | 0 | 0.22869 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.007872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55891 | 0 | 0.22885 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.007872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07872 | 0 | 0.22885 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88922 | 0 | 0.22899 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88922 | 0 | 0.22899 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.95331 | 0 | 0.22899 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.008011 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.8772 | 0 | 0.22899 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.008459 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38996 | 0 | 0.22944 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.5355 | 0 | 0.22949 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.7957 | 0 | 0.22949 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.008503 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.1018 | 0 | 0.22949 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3865 | 0 | 0.22949 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3865 | 0 | 0.22949 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.008506 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.084 | 0 | 0.22949 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.008526 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28136 | 0 | 0.22951 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.383 | 161 | 0.22957 | 36.9612
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4259 | 166 | 0.22957 | 38.109
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.00859 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.1303 | 248 | 0.22957 | 56.934
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.00859 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.6901 | 546 | 0.22957 | 125.3465
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.00859 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 5.5234 | 0 | 0.22957 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.00859 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11167 | 13 | 0.22957 | 2.9844
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.88073 | 0 | 0.22976 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.81575 | 0 | 0.22976 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.90181 | 0 | 0.22976 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.008781 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89566 | 0 | 0.22976 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.008781 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28099 | 0 | 0.22976 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.008781 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.26343 | 0 | 0.22976 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.62177 | 0 | 0.22976 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58576 | 0 | 0.22976 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.46545 | 0 | 0.22976 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3454 | 0 | 0.22976 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.348 | 0 | 0.22976 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3375 | 0 | 0.22976 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.84307 | 0 | 0.22976 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.008782 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.1428 | 0 | 0.22976 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.008782 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35128 | 0 | 0.22976 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.00889 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.4445 | 50 | 0.22987 | 11.4936
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.008949 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22993 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82228 | 0 | 0.23002 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79155 | 0 | 0.23002 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.78613 | 0 | 0.23002 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49246 | 0 | 0.23002 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.009036 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11024 | 0 | 0.23002 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.58949 | 0 | 0.23005 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54414 | 0 | 0.23005 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.58949 | 0 | 0.23005 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.009069 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.58949 | 0 | 0.23005 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41984 | 46 | 0.23011 | 10.585
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41984 | 46 | 0.23011 | 10.585
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41984 | 46 | 0.23011 | 10.585
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50199 | 55 | 0.23011 | 12.656
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50199 | 55 | 0.23011 | 12.656
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.009127 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.49286 | 54 | 0.23011 | 12.4259
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.009131 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.71222 | 0 | 0.23011 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.009131 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73048 | 0 | 0.23011 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4923 | 0 | 0.23013 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4365 | 0 | 0.23013 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4402 | 0 | 0.23013 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4356 | 0 | 0.23013 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.009144 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.4597 | 0 | 0.23013 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.009163 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32071 | 0 | 0.23015 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009177 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11012 | 12 | 0.23016 | 2.7619
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.009177 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.23016 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.009178 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5511 | 169 | 0.23016 | 38.8971
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.009179 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.5145 | 165 | 0.23016 | 37.9766
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.00918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3678 | 0 | 0.23016 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.00918 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59762 | 0 | 0.23016 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.009183 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.956 | 213 | 0.23017 | 49.0252
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.009183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14876 | 0 | 0.23017 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58778 | 0 | 0.23017 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58043 | 0 | 0.23017 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7586 | 0 | 0.23017 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.009184 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67594 | 0 | 0.23017 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.009184 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.094 | 228 | 0.23017 | 52.4779
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6533 | 0 | 0.23017 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4567 | 0 | 0.23017 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.009185 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.442 | 0 | 0.23017 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65363 | 0 | 0.23019 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.66283 | 0 | 0.23019 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35903 | 0 | 0.23019 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.009206 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27618 | 0 | 0.23019 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.38812 | 42 | 0.23022 | 9.6694
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.38812 | 42 | 0.23022 | 9.6694
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35116 | 38 | 0.23022 | 8.7485
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.009241 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35116 | 38 | 0.23022 | 8.7485
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.009242 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2569 | 0 | 0.23022 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.009253 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6008 | 0 | 0.23024 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.009253 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2492 | 0 | 0.23024 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.96845 | 104 | 0.23029 | 23.9506
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.96845 | 104 | 0.23029 | 23.9506
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.49354 | 53 | 0.23029 | 12.2056
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.53078 | 57 | 0.23029 | 13.1268
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.50285 | 54 | 0.23029 | 12.4359
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.5401 | 58 | 0.23029 | 13.3571
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.009312 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.5401 | 58 | 0.23029 | 13.3571
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.009322 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.8517 | 735 | 0.2303 | 169.2737
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31742 | 0 | 0.23032 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32396 | 0 | 0.23032 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30529 | 0 | 0.23032 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42852 | 0 | 0.23032 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16525 | 0 | 0.23032 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19045 | 0 | 0.23032 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18579 | 0 | 0.23032 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32676 | 0 | 0.23032 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16805 | 0 | 0.23032 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.79729 | 0 | 0.23032 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.009336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3817 | 0 | 0.23032 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.009362 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.11234 | 12 | 0.23034 | 2.7641
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.009376 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.04688 | 0 | 0.23036 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.009376 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1969 | 0 | 0.23036 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.009377 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.11252 | 0 | 0.23036 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60957 | 0 | 0.23036 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61895 | 0 | 0.23036 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65646 | 0 | 0.23036 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59081 | 0 | 0.23036 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58144 | 0 | 0.23036 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97531 | 0 | 0.23036 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.009378 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5533 | 0 | 0.23036 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.009378 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.9679 | 743 | 0.23036 | 171.1578
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.00939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4742 | 0 | 0.23037 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6158 | 172 | 0.23038 | 39.6247
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6158 | 172 | 0.23038 | 39.6247
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.009394 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.6158 | 172 | 0.23038 | 39.6247
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5357 | 0 | 0.23042 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.5225 | 0 | 0.23042 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4989 | 0 | 0.23042 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.009433 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.5394 | 0 | 0.23042 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.009451 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.7615 | 398 | 0.23043 | 91.7125
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.55908 | 59 | 0.23046 | 13.597
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.55908 | 59 | 0.23046 | 13.597
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.009476 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.53066 | 56 | 0.23046 | 12.9057
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6788 | 0 | 0.23069 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5138 | 0 | 0.23069 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4944 | 0 | 0.23069 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.009704 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4944 | 0 | 0.23069 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.009704 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.572 | 0 | 0.23069 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1239.6