## test results
CRE test for: |  | 1430 GRHAMES - 1442 COKFIELD | [5 empty] | PASS
Line Rating: |  | 1239.6
Direction |  | West | → | North |  | W-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1430 GRHAMES - 1442 COKFIELD
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.016565
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0021903
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.21401
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0080181
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 1430 GRHAMES - 1442 COKFIELD
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.017506
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.0018675
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.19667
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.0081167
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 1430 GRHAMES - 1442 COKFIELD
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.014697
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.21324
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.008448
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.19886
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.0058278
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.22212
PTDF tests
West | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | -0.23151 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.23151 | 0.014697
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.22254
[6 empty] | Concentration |  | -0.96125 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.2055
[6 empty] | Concentration |  | -0.88765 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 38.0979
| Percent of line rating => | [6 empty] | 3.073% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -3.5105
[7 empty] | B1(N-S) | 0.011468 | -0.040127 | -0.051595 | 0.011468
[7 empty] | B2 (N-W) | -0.066196 | -0.81477 | -0.74857 | -0.066196
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.010682 | -0.018975 | -0.029657 | 0.010682
[7 empty] | B4 (S-W) | -0.077659 | -0.77577 | -0.69811 | -0.077659
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.00043445 | 0.020024 | 0.020459 | -0.00043445
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.013165 | 0.79294 | 0.77977 | 0.013165
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | 1.411%
Deployment Error Percent | [6 empty] | B2 | -8.145%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 1.314%
[7 empty] | B4 | -9.555%
[7 empty] | B5 | -0.05346%
[7 empty] | B6 | 1.62%
[7 empty] | Max Abs Error | 9.555% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.009989 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 2.5472
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.4884
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.009568 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.14352
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.009568 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.14352
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.5283
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.3845
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 0.7384
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.006188 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.45172
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 0.73637
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 1.2685
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 0.63118
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 0.59405
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.098472
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.098472
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 1.8949
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 1.0151
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.2477
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.2477
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.52292
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 5.4138
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 2.7633
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 2.7633
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.021754 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.4473
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.018459 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.73836
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.4654
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 1.9662
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 2.7082
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.018549 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.4097
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.3588
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.4267
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.018466 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.36932
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.46168
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.75715
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.011251 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 5.2092
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -13.3814
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -13.1787
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -13.5842
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -13.5842
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -13.5842
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.20275 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -23.1134
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.20275 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -104.4157
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -13.5724
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -14.1893
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -14.1893
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -13.778
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -13.778
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -13.3667
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -14.4657
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -15.1683
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -14.5484
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -31.0598
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -45.5543
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.20142 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -19.9409
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.20142 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -12.2868
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.20152 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -28.4142
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -5.0356
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -9.205
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -9.205
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.20152 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -24.1823
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.20284 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -5.2332
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.204 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -20.5022
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.20355 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -24.4259
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.20414 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -11.8401
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.20435 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -43.7716
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.20738 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -31.1072
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.20008 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -1.3205
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.20008 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -6.8626
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.20738 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -20.9455
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.20327 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -24.3926
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.057392 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 21.0055
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.016465 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 3.9845
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.32331 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -129.322
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.32518 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -76.7427
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.47336 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -78.1036
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 7.5402
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 7.4294
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 8.9448
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.7522
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.7522
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.7522
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.63937
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.013587 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 1.6304
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.02441 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.4646
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.4227
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 1.5099
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 1.6769
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 3.0421
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.966
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 3.7265
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 2.966
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 2.985
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 3.7646
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.01925 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 3.2725
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.01925 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 10.01
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.019084 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 7.0611
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 10.5373
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 10.9338
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 15.2583
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.021865 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 2.4489
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.021865 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 2.1865
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.021865 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 8.265
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 2.2351
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 2.1086
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 2.8019
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.013748 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 10.586
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 0.73129
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.72084
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.72084
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.7104
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.009179 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 10.6201
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.009179 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 10.6293
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 3.4321
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 3.4628
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 3.5091
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 3.5043
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 3.2483
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 3.2329
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.018377 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 7.2589
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.018366 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 7.9892
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.018377 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 7.994
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.019856 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 2.7401
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.0717
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017557 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.0191
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 9.7617
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.018068 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 7.0104
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.018068 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 9.305
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 13.1535
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 13.321
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 13.0697
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 2.9861
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 7.941
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.015721 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 3.5215
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.016434 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.8217
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.01645 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.6909
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.014695 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 9.0374
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.014695 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 8.626
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.010958 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 5.8844
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.010958 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 8.6239
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.010406 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.78045
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.010406 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 2.3101
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 3.5386
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.22656
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.23414
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.000964 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 0.39235
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.049864
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.050948
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.049864
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.049864
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 0.48633
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 0.48747
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.035786
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.054913
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.027148
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.027148
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.026531
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.027765
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 0.44743
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 0.4344
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 0.87196
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 1.1978
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.085583
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.13328
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.21185
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.22925
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.25143
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.22925
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.002652 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.058344
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.029172
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.029172
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.13318
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.10414
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.12843
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.13402
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.00036
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.00033
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.006121 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.1469
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.1469
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.14078
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.001048 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.41501
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 8.0487
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 8.0185
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.072466
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.036805
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.028605
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.001907 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.089629
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -14.3906
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.1889 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -28.3358
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.21461 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -36.3764
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.14784 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -22.176
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.20257 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -12.762
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.24757 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -160.8469
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.019381 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.77524
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.019381 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.77524
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.0053 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -2.2366
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.53341
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.54149
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 1.3052
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.70278
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.71168
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 0.7784
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 2.6257
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 2.6751
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.004494 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 1.9459
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.56759
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.57037
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.56936
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.57468
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.003287 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.026296
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.003287 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.026296
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.10174
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.10174
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.08478
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.00796 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.10905
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.003298 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.059364
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.003298 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.059364
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.04347
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.042228
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.04347
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.004798 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.13434
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.004798 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.13914
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.20272 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -7.095
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.20272 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -6.0815
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2161
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2161
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2161
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.2161
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.002052 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.012312
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0056088
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0056088
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.0065436
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.002018 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.008072
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.00267 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.006408
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.00267 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.006408
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.31561
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.29629
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.30058
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.31561
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.39075
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.42511
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.62006
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.60787
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 0.94575
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.33285
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.33988
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.35394
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.67976
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.055041 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -1.8164
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.055041 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.376
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.00036
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.00293 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.21389
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.27397
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.28091
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.087164
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.021791
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.27397
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.27744
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.27189
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.0867
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.15953
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.002193 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 1.3794
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.41083
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.53636
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.002687 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.032244
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.039493 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.23696
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 0.7345
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 0.72044
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 0.73338
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.002119 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.080522
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.002139 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.053475
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.002139 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.053475
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.002137 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.081206
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.002041 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.059189
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.32404
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.32469
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.33431
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.3694
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.35771
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.2338
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.33901
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.34369
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.29693
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.2196
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.2217
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.25933
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.36308
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.38009
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.42447
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.25258
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.25258
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.29993
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 1.0785
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 1.4368
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.15288
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.16016
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.16016
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.17108
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.16817
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.15787
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.15787
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.1613
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.52853
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.50794
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.16474
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.16474
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -14.3534
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -14.3534
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -19.0285
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -16.4039
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -16.4039
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -23.5806
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -42.6866
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -29.1343
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -27.1456
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -27.8837
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -30.139
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -43.0557
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -36.1867
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -21.9025
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -43.1124
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -34.109
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -41.413
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -25.2412
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.20276 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -30.2109
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.20255 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -36.4585
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.20255 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -36.4585
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.20257 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -45.578
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.22138 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -27.6724
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.22138 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -27.6724
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 2.6718
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 2.6908
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 5.897
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 2.729
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 2.7481
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 5.916
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 3.1064
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 1.7592
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.019332 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.8951
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.949
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 2.949
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 7.4445
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 2.9131
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 2.8951
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 2.9311
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 7.3546
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 2.4553
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 2.1567
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 2.4055
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 6.6194
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 2.2561
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 2.2606
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 2.6559
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 2.2772
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 2.2892
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 2.668
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 3.6132
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 10.7927
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 10.7927
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.01123 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.35936
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.5376
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.5152
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.13487
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.57319
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011239 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.19106
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.24726
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.28097
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.0112 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 1.176
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.1991 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -16.7243
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.1917 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -15.3358
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.1916 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -28.7394
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.1916 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -28.7394
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.56173
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.5292
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.4205
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 1.2155
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 1.2179
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 1.2083
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.76166
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 1.9359
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.31736
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.79568
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.73698
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.81472
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.80917
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.25386
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.23799
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.79909
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.79909
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 0.85668
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 0.78829
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 1.9225
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 1.9313
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.008373 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 1.1387
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.007689 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.25374
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.35162
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.35162
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.31814
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.31814
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.50169
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.07066
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.2502
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.2502
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 1.8792
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.53346
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.49242
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.53346
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.53346
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 1.2386
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.54118
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.74392
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.71613
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.71122
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.44554
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.099735
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.008502 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 6.317
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.008449 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 6.21
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.4649
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.4649
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.4649
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 1.5248
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.008383 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 1.4503
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.008383 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 1.1317
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 1.3928
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 1.3808
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 1.3594
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 2.303
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.53229
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.52563
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.68698
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.61213
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 1.3511
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 1.3006
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 1.3039
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 1.2998
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 2.2271
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.0425
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.1785
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 1.6709
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.6904
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.6904
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 4.1177
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.008572 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 3.4117
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.3801
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.3801
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.3801
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.45447
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.45447
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.4462
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.013173 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 10.8941
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.013173 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 10.7887
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.007625 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.35151
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.46786
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.46786
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.64638
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.45554
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.45554
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.62791
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 1.4972
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 1.3192
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 1.3059
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.008297 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.2904
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.008093 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 3.7147
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.55263
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.56113
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.59514
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.53563
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.52712
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.88421
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.50162
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 1.375
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.3574
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.3574
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.008814 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 1.4279
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.008514 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 1.3367
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.592
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.60034
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.32518
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.25014
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.64475
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.66128
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.008316 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.13472
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.008312 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 1.3715
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.008311 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 1.4046
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.008316 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 1.7713
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.008317 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 1.8963
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.008311 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.099732
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.008311 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.1496
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.008037 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.40185
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.87766
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.87766
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.45571
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.44727
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.45571
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.48102
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.45571
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.45571
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.48946
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.48946
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.008487 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.10184
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.48138
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.50716
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.48138
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.48138
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.50716
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.48138
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.006258 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.41303
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.2477
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.2865
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 1.922
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00775 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 4.2315
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00775 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 4.9832
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 4.9912
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 4.3242
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 4.6002
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.00775 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.10075
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.008501 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.10201
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.28771
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.29363
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.27671
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.38841
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.14978
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.17262
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.16839
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.29617
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.15232
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.72265
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 1.2524
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.42836
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.4933
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.3109
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.69781
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.59417
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.60799
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.34545
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.12436
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.64945
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.48363
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.43527
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.49745
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.4477
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.69781
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.67017
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.71163
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.52508
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.55272
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.55272
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 1.1814
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.063865
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.18684 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -14.2935
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -15.35
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -7.675
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.19262 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -15.4098
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.19172 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -15.3376
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.18779 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -15.0229
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.1865 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -15.666
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.19262 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -15.4098
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.038418
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -27.1782
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -52.771
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -38.5477
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.074814
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.062008
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.075488
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.038755
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.0337
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.18556 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -11.1337
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.059084 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.16616 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.19563 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.93903
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -8.8034
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -25.2363
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -31.6921
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -27.936
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -24.6494
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -18.8979
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.19833 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -29.7498
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -22.109
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -29.3803
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -36.5535
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -42.1544
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.001907 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.035876 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.003177 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.097104
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.1512
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.25663
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.1849
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.080647
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.074746
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.037373
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.1849
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.070812
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.084581
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.043274
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.12141
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.046695
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.021791
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.046695
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.12141
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.12141
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.29112
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.09835
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.10819
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.09835
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.002338 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.028056
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.003035 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.045525
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.003035 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.069805
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.003392 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.16282
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.003059 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.024472
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.002182 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.39276
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.39348
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.38826
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.38826
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.3174
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.3174
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.05685
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.05685
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.05685
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.036384
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.05685
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.05685
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.05685
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.03411
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.003174 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.003174 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -1.587
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.003174 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -1.587
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.003174 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.001311 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.055041 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.001494 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.001176 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A | [7 empty] | 38.0979
Number of Bus | Name of Bus | ID | Max MW | L:1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.009989 | north | Y | -0.0065757 | 0.0077987 | 0.224 | 0.0019709 | 0.0019709 | houston | Y | 0.0065757 | 1.1742
239 | BOSQUESW | 1 | 149 | 0.009989 | north | Y | -0.0065757 | 0.0077987 | 0.224 | 0.0019709 | 0.0019709 | houston | Y | 0.0065757 | 0.68611
244 | WHITNYDM | 1 | 15 | 0.009568 | north | N | -0.0069967 | 0.0073777 | 0.22358 | 0.0015499 | 0.0015499 | houston | Y | 0.0069967 | 0
245 | WHITNYDM | 2 | 15 | 0.009568 | north | N | -0.0069967 | 0.0073777 | 0.22358 | 0.0015499 | 0.0015499 | houston | Y | 0.0069967 | 0
247 | BOSQUESW | 2 | 153 | 0.009989 | north | Y | -0.0065757 | 0.0077987 | 0.224 | 0.0019709 | 0.0019709 | houston | Y | 0.0065757 | 0.70453
251 | BOSQUESW | 2 | 150 | 0.00923 | north | Y | -0.0073347 | 0.0070397 | 0.22324 | 0.0012119 | 0.0012119 | houston | Y | 0.0073347 | 0.91842
253 | BOSQUESW | 2 | 80 | 0.00923 | north | Y | -0.0073347 | 0.0070397 | 0.22324 | 0.0012119 | 0.0012119 | houston | Y | 0.0073347 | 0.48982
332 | RWMILLER | 1 | 73 | 0.006188 | north | Y | -0.010377 | 0.0039977 | 0.2202 | -0.0018301 | 0.0018301 | houston | Y | 0.010377 | 0.6239
333 | RWMILLER | 2 | 119 | 0.006188 | north | Y | -0.010377 | 0.0039977 | 0.2202 | -0.0018301 | 0.0018301 | houston | Y | 0.010377 | 1.017
334 | RWMILLER | 3 | 205 | 0.006188 | north | Y | -0.010377 | 0.0039977 | 0.2202 | -0.0018301 | 0.0018301 | houston | Y | 0.010377 | 1.7521
335 | RWMILLER | 4 | 102 | 0.006188 | north | Y | -0.010377 | 0.0039977 | 0.2202 | -0.0018301 | 0.0018301 | houston | Y | 0.010377 | 0.87175
336 | RWMILLER | 5 | 96 | 0.006188 | north | Y | -0.010377 | 0.0039977 | 0.2202 | -0.0018301 | 0.0018301 | houston | Y | 0.010377 | 0.82047
344 | MRSSHPRD | 1 | 12 | 0.008206 | north | N | -0.0083587 | 0.0060157 | 0.22221 | 0.00018791 | 0.00018791 | houston | Y | 0.0083587 | 0
345 | MRSSHPRD | 2 | 12 | 0.008206 | north | N | -0.0083587 | 0.0060157 | 0.22221 | 0.00018791 | 0.00018791 | houston | Y | 0.0083587 | 0
366 | JNSNCNTY | 1 | 168 | 0.011279 | north | Y | -0.0052857 | 0.0090887 | 0.22529 | 0.0032609 | 0.0032609 | houston | Y | 0.0052857 | 0.34016
367 | JNSNCNTY | 2 | 90 | 0.011279 | north | Y | -0.0052857 | 0.0090887 | 0.22529 | 0.0032609 | 0.0032609 | houston | Y | 0.0052857 | 0.18223
503 | NTHTEXAS | 1 | 18 | 0.013761 | north | Y | -0.0028037 | 0.011571 | 0.22777 | 0.0057429 | 0.0028037 | North | N | 0.0028037 | 0
504 | NTHTEXAS | 2 | 18 | 0.013761 | north | Y | -0.0028037 | 0.011571 | 0.22777 | 0.0057429 | 0.0028037 | North | N | 0.0028037 | 0
505 | NTHTEXAS | 3 | 38 | 0.013761 | north | Y | -0.0028037 | 0.011571 | 0.22777 | 0.0057429 | 0.0028037 | North | N | 0.0028037 | 0
580 | JCKCNTY8 | 1 | 288 | 0.018798 | north | Y | 0.0022333 | 0.016608 | 0.23281 | 0.01078 | 0.0022333 | North | N | 0.0022333 | 0
581 | JCKCNTY8 | 2 | 147 | 0.018798 | north | Y | 0.0022333 | 0.016608 | 0.23281 | 0.01078 | 0.0022333 | North | N | 0.0022333 | 0
582 | JCKCNTY8 | 3 | 147 | 0.018798 | north | Y | 0.0022333 | 0.016608 | 0.23281 | 0.01078 | 0.0022333 | North | N | 0.0022333 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.021754 | north | Y | 0.0051893 | 0.019564 | 0.23576 | 0.013736 | 0.0051893 | North | N | 0.0051893 | 0
837 | NEWMAN_G | 1 | 40 | 0.018459 | north | Y | 0.0018943 | 0.016269 | 0.23247 | 0.010441 | 0.0018943 | North | N | 0.0018943 | 0
842 | OLINGER_ | 1 | 79 | 0.018549 | north | Y | 0.0019843 | 0.016359 | 0.23256 | 0.010531 | 0.0019843 | North | N | 0.0019843 | 0
843 | OLINGER_ | 1 | 106 | 0.018549 | north | Y | 0.0019843 | 0.016359 | 0.23256 | 0.010531 | 0.0019843 | North | N | 0.0019843 | 0
844 | OLINGER_ | 1 | 146 | 0.018549 | north | Y | 0.0019843 | 0.016359 | 0.23256 | 0.010531 | 0.0019843 | North | N | 0.0019843 | 0
845 | OLINGER_ | 1 | 76 | 0.018549 | north | Y | 0.0019843 | 0.016359 | 0.23256 | 0.010531 | 0.0019843 | North | N | 0.0019843 | 0
923 | SPENCER_ | 1 | 60 | 0.022646 | north | Y | 0.0060813 | 0.020456 | 0.23665 | 0.014628 | 0.0060813 | North | N | 0.0060813 | 0
924 | SPENCER_ | 1 | 63 | 0.022646 | north | Y | 0.0060813 | 0.020456 | 0.23665 | 0.014628 | 0.0060813 | North | N | 0.0060813 | 0
948 | STEAM1 | 1 | 20 | 0.018466 | north | Y | 0.0019013 | 0.016276 | 0.23247 | 0.010448 | 0.0019013 | North | N | 0.0019013 | 0
949 | STEAM2 | 1 | 25 | 0.018467 | north | Y | 0.0019023 | 0.016277 | 0.23247 | 0.010449 | 0.0019023 | North | N | 0.0019023 | 0
950 | STEAM3 | 1 | 41 | 0.018467 | north | Y | 0.0019023 | 0.016277 | 0.23247 | 0.010449 | 0.0019023 | North | N | 0.0019023 | 0
990 | GIBN_CRE | 1 | 463 | 0.011251 | north | Y | -0.0053137 | 0.0090607 | 0.22526 | 0.0032329 | 0.0032329 | houston | Y | 0.0053137 | 0.9634
1002 | PBCTAGE_ | A | 66 | -0.20275 | west | Y | -0.21931 | -0.20494 | 0.011258 | -0.21077 | 0.011258 | west | N | 0.011258 | 0
1003 | PBCTBGE_ | B | 65 | -0.20275 | west | Y | -0.21931 | -0.20494 | 0.011258 | -0.21077 | 0.011258 | west | N | 0.011258 | 0
1004 | PBCTCGE_ | C | 67 | -0.20275 | west | Y | -0.21931 | -0.20494 | 0.011258 | -0.21077 | 0.011258 | west | N | 0.011258 | 0
1005 | PBCTDGE_ | D | 67 | -0.20275 | west | Y | -0.21931 | -0.20494 | 0.011258 | -0.21077 | 0.011258 | west | N | 0.011258 | 0
1006 | PBCTEGE_ | E | 67 | -0.20275 | west | Y | -0.21931 | -0.20494 | 0.011258 | -0.21077 | 0.011258 | west | N | 0.011258 | 0
1007 | PB5GEN_6 | MB | 114 | -0.20275 | west | Y | -0.21931 | -0.20494 | 0.011258 | -0.21077 | 0.011258 | west | N | 0.011258 | 0
1008 | PB6GEN_7 | MB | 515 | -0.20275 | west | Y | -0.21931 | -0.20494 | 0.011258 | -0.21077 | 0.011258 | west | N | 0.011258 | 0
1039 | MRGNAG_1 | A | 66 | -0.20564 | west | Y | -0.22221 | -0.20783 | 0.0083651 | -0.21366 | 0.0083651 | west | N | 0.0083651 | 0
1040 | MRGNBG_2 | B | 69 | -0.20564 | west | Y | -0.22221 | -0.20783 | 0.0083651 | -0.21366 | 0.0083651 | west | N | 0.0083651 | 0
1041 | MRGNCG_3 | C | 69 | -0.20564 | west | Y | -0.22221 | -0.20783 | 0.0083651 | -0.21366 | 0.0083651 | west | N | 0.0083651 | 0
1042 | MRGNDG_4 | D | 67 | -0.20564 | west | Y | -0.22221 | -0.20783 | 0.0083651 | -0.21366 | 0.0083651 | west | N | 0.0083651 | 0
1043 | MRGNEG_5 | E | 67 | -0.20564 | west | Y | -0.22221 | -0.20783 | 0.0083651 | -0.21366 | 0.0083651 | west | N | 0.0083651 | 0
1044 | MRGNFG_6 | F | 65 | -0.20564 | west | Y | -0.22221 | -0.20783 | 0.0083651 | -0.21366 | 0.0083651 | west | N | 0.0083651 | 0
1045 | CALENG1G | 1 | 70 | -0.20665 | west | N | -0.22322 | -0.20884 | 0.0073541 | -0.21467 | 0.0073541 | west | N | 0.0073541 | 0
1046 | CALENG2G | 2 | 73.4 | -0.20665 | west | N | -0.22322 | -0.20884 | 0.0073541 | -0.21467 | 0.0073541 | west | N | 0.0073541 | 0
1047 | CALENG3G | 3 | 70.4 | -0.20665 | west | N | -0.22322 | -0.20884 | 0.0073541 | -0.21467 | 0.0073541 | west | N | 0.0073541 | 0
1058 | LONGSHOR | 1 | 150 | -0.20706 | west | Y | -0.22363 | -0.20926 | 0.0069421 | -0.21508 | 0.0069421 | west | N | 0.0069421 | 0
1058 | LONGSHOR | 2 | 220 | -0.20706 | west | Y | -0.22363 | -0.20926 | 0.0069421 | -0.21508 | 0.0069421 | west | N | 0.0069421 | 0
1061 | CIELOGEN | 1 | 99 | -0.20142 | west | Y | -0.21799 | -0.20361 | 0.012584 | -0.20944 | 0.012584 | west | N | 0.012584 | 0
1062 | CIELOGEN | 1 | 61 | -0.20142 | west | Y | -0.21799 | -0.20361 | 0.012584 | -0.20944 | 0.012584 | west | N | 0.012584 | 0
1068 | SCURRYCW | 1 | 141 | -0.20152 | west | Y | -0.21808 | -0.20371 | 0.012488 | -0.20954 | 0.012488 | west | N | 0.012488 | 0
1069 | KINDERMG | 1 | 25 | -0.20142 | west | N | -0.21799 | -0.20361 | 0.012584 | -0.20944 | 0.012584 | west | N | 0.012584 | 0
1070 | KINDERMG | 1 | 45.7 | -0.20142 | west | N | -0.21799 | -0.20361 | 0.012584 | -0.20944 | 0.012584 | west | N | 0.012584 | 0
1071 | KINDERMG | 1 | 45.7 | -0.20142 | west | N | -0.21799 | -0.20361 | 0.012584 | -0.20944 | 0.012584 | west | N | 0.012584 | 0
1073 | SCURRYCW | 2 | 120 | -0.20152 | west | Y | -0.21808 | -0.20371 | 0.012488 | -0.20954 | 0.012488 | west | N | 0.012488 | 0
1320 | BSP 1 | 1 | 25.8 | -0.20284 | west | N | -0.2194 | -0.20503 | 0.011169 | -0.21086 | 0.011169 | west | N | 0.011169 | 0
1326 | STANTONW | 1 | 100.5 | -0.204 | west | Y | -0.22057 | -0.20619 | 0.010005 | -0.21202 | 0.010005 | west | N | 0.010005 | 0
1327 | WILDHRSE | 1 | 120 | -0.20355 | west | Y | -0.22011 | -0.20574 | 0.010458 | -0.21157 | 0.010458 | west | N | 0.010458 | 0
1328 | OCOTILLO | 1 | 58 | -0.20414 | west | Y | -0.2207 | -0.20633 | 0.0098681 | -0.21216 | 0.0098681 | west | N | 0.0098681 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.20435 | west | Y | -0.22091 | -0.20654 | 0.0096581 | -0.21237 | 0.0096581 | west | N | 0.0096581 | 0
1343 | TRENTIPP | 1 | 150 | -0.20738 | west | Y | -0.22395 | -0.20957 | 0.0066261 | -0.2154 | 0.0066261 | west | N | 0.0066261 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.20008 | west | Y | -0.21664 | -0.20227 | 0.01393 | -0.2081 | 0.01393 | west | N | 0.01393 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.20008 | west | Y | -0.21664 | -0.20227 | 0.01393 | -0.2081 | 0.01393 | west | N | 0.01393 | 0
1354 | AEPWIND_ | 1 | 101 | -0.20738 | west | Y | -0.22395 | -0.20957 | 0.0066261 | -0.2154 | 0.0066261 | west | N | 0.0066261 | 0
1360 | GUNSIGHT | 1 | 120 | -0.20327 | west | Y | -0.21984 | -0.20546 | 0.010735 | -0.21129 | 0.010735 | west | N | 0.010735 | 0
1432 | GRHAMSES | 2 | 366 | 0.057392 | north | Y | 0.040827 | 0.055202 | 0.2714 | 0.049374 | 0.040827 | North | N | 0.040827 | 0
1433 | GRHAMSES | 1 | 242 | 0.016465 | north | Y | -9.9679e-05 | 0.014275 | 0.23047 | 0.0084469 | 9.9679e-05 | North | N | 9.9679e-05 | 0
1437 | MESQUITW | 1 | 400 | -0.32331 | west | Y | -0.33987 | -0.3255 | -0.1093 | -0.33132 | 0.1093 | west | N | 0.1093 | 0
1438 | MESQUITW | 1 | 236 | -0.32518 | west | Y | -0.34175 | -0.32737 | -0.11117 | -0.3332 | 0.11117 | west | N | 0.11117 | 0
1442 | COKFIELD | 1 | 165 | -0.47336 | west | Y | -0.48992 | -0.47555 | -0.25935 | -0.48137 | 0.25935 | west | N | 0.25935 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.036962 | north | Y | 0.020397 | 0.034772 | 0.25097 | 0.028944 | 0.020397 | North | N | 0.020397 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.036962 | north | Y | 0.020397 | 0.034772 | 0.25097 | 0.028944 | 0.020397 | North | N | 0.020397 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.036962 | north | Y | 0.020397 | 0.034772 | 0.25097 | 0.028944 | 0.020397 | North | N | 0.020397 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.03761 | west | Y | 0.021045 | 0.03542 | 0.25162 | 0.029592 | 0.021045 | North | Y | 0.25162 | 4.6114
1479 | WFCOGEN_ | 2 | 20 | 0.03761 | west | Y | 0.021045 | 0.03542 | 0.25162 | 0.029592 | 0.021045 | North | Y | 0.25162 | 4.6114
1482 | WFCOGEN_ | 1 | 20 | 0.03761 | west | Y | 0.021045 | 0.03542 | 0.25162 | 0.029592 | 0.021045 | North | Y | 0.25162 | 4.6114
1482 | WFCOGEN_ | 2 | 17 | 0.03761 | west | Y | 0.021045 | 0.03542 | 0.25162 | 0.029592 | 0.021045 | North | Y | 0.25162 | 3.9197
1600 | BARTNWND | 1 | 120 | 0.013587 | north | Y | -0.0029777 | 0.011397 | 0.22759 | 0.0055689 | 0.0029777 | North | N | 0.0029777 | 0
1643 | SLSTR1PP | 1 | 60 | -0.02441 | north | Y | -0.040975 | -0.0266 | 0.1896 | -0.032428 | 0.0266 | south | Y | 0.040975 | 0.86246
1675 | PEC_1G | 1 | 75 | 0.018969 | north | N | 0.0024043 | 0.016779 | 0.23298 | 0.010951 | 0.0024043 | North | N | 0.0024043 | 0
1676 | PEC_2G | 2 | 79.6 | 0.018969 | north | N | 0.0024043 | 0.016779 | 0.23298 | 0.010951 | 0.0024043 | North | N | 0.0024043 | 0
1677 | PEC_3G | 3 | 88.4 | 0.018969 | north | N | 0.0024043 | 0.016779 | 0.23298 | 0.010951 | 0.0024043 | North | N | 0.0024043 | 0
1678 | LAMARPWR | 1 | 160 | 0.019013 | north | Y | 0.0024483 | 0.016823 | 0.23302 | 0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1679 | LAMARPWR | 2 | 156 | 0.019013 | north | Y | 0.0024483 | 0.016823 | 0.23302 | 0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1680 | LAMARPWR | 3 | 196 | 0.019013 | north | Y | 0.0024483 | 0.016823 | 0.23302 | 0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1681 | LAMARPWR | 4 | 156 | 0.019013 | north | Y | 0.0024483 | 0.016823 | 0.23302 | 0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1682 | LAMARPWR | 5 | 157 | 0.019013 | north | Y | 0.0024483 | 0.016823 | 0.23302 | 0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1683 | LAMARPWR | 6 | 198 | 0.019013 | north | Y | 0.0024483 | 0.016823 | 0.23302 | 0.010995 | 0.0024483 | North | N | 0.0024483 | 0
1687 | VALLEY_1 | 1 | 170 | 0.01925 | north | Y | 0.0026853 | 0.01706 | 0.23326 | 0.011232 | 0.0026853 | North | N | 0.0026853 | 0
1688 | VALLEY_2 | 2 | 520 | 0.01925 | north | Y | 0.0026853 | 0.01706 | 0.23326 | 0.011232 | 0.0026853 | North | N | 0.0026853 | 0
1689 | VALLEY_3 | 3 | 370 | 0.019084 | north | Y | 0.0025193 | 0.016894 | 0.23309 | 0.011066 | 0.0025193 | North | N | 0.0025193 | 0
1701 | MOSES_1G | 1 | 558 | 0.018884 | north | Y | 0.0023193 | 0.016694 | 0.23289 | 0.010866 | 0.0023193 | North | N | 0.0023193 | 0
1702 | MOSES_2G | 2 | 579 | 0.018884 | north | Y | 0.0023193 | 0.016694 | 0.23289 | 0.010866 | 0.0023193 | North | N | 0.0023193 | 0
1703 | MOSES_3G | 3 | 808 | 0.018884 | north | Y | 0.0023193 | 0.016694 | 0.23289 | 0.010866 | 0.0023193 | North | N | 0.0023193 | 0
1861 | EAGLEMNT | MB | 112 | 0.021865 | north | Y | 0.0053003 | 0.019675 | 0.23587 | 0.013847 | 0.0053003 | North | N | 0.0053003 | 0
1862 | EAGLEMNT | MB | 100 | 0.021865 | north | Y | 0.0053003 | 0.019675 | 0.23587 | 0.013847 | 0.0053003 | North | N | 0.0053003 | 0
1863 | EAGLEMNT | MB | 378 | 0.021865 | north | Y | 0.0053003 | 0.019675 | 0.23587 | 0.013847 | 0.0053003 | North | N | 0.0053003 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.010286 | north | Y | -0.0062787 | 0.0080957 | 0.22429 | 0.0022679 | 0.0022679 | houston | Y | 0.0062787 | 0.87154
1878 | WLFHOLW_ | 2 | 205 | 0.010286 | north | Y | -0.0062787 | 0.0080957 | 0.22429 | 0.0022679 | 0.0022679 | houston | Y | 0.0062787 | 0.82221
1879 | WLFHOLW_ | 3 | 272.4 | 0.010286 | north | Y | -0.0062787 | 0.0080957 | 0.22429 | 0.0022679 | 0.0022679 | houston | Y | 0.0062787 | 1.0925
1889 | DECRDOVA | MB | 770 | 0.013748 | north | Y | -0.0028167 | 0.011558 | 0.22776 | 0.0057299 | 0.0028167 | North | N | 0.0028167 | 0
1892 | DECRDOVA | A | 70 | 0.010447 | north | Y | -0.0061177 | 0.0082567 | 0.22445 | 0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25821
1893 | DECRDOVA | B | 69 | 0.010447 | north | Y | -0.0061177 | 0.0082567 | 0.22445 | 0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25452
1894 | DECRDOVA | C | 69 | 0.010447 | north | Y | -0.0061177 | 0.0082567 | 0.22445 | 0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25452
1895 | DECRDOVA | D | 68 | 0.010447 | north | Y | -0.0061177 | 0.0082567 | 0.22445 | 0.0024289 | 0.0024289 | houston | Y | 0.0061177 | 0.25084
1898 | COMCHEPK | 1 | 1157 | 0.009179 | north | N | -0.0073857 | 0.0069887 | 0.22319 | 0.0011609 | 0.0011609 | houston | Y | 0.0073857 | 0
1899 | COMCHEPK | 2 | 1158 | 0.009179 | north | N | -0.0073857 | 0.0069887 | 0.22319 | 0.0011609 | 0.0011609 | houston | Y | 0.0073857 | 0
1937 | MDLTHELP | 5 | 224 | 0.015322 | north | Y | -0.0012427 | 0.013132 | 0.22933 | 0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1938 | MDLTHELP | 6 | 226 | 0.015322 | north | Y | -0.0012427 | 0.013132 | 0.22933 | 0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.016216 | north | Y | -0.00034868 | 0.014026 | 0.23022 | 0.0081979 | 0.00034868 | North | N | 0.00034868 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.016216 | north | Y | -0.00034868 | 0.014026 | 0.23022 | 0.0081979 | 0.00034868 | North | N | 0.00034868 | 0
1943 | MDLTHELP | 3 | 212 | 0.015322 | north | Y | -0.0012427 | 0.013132 | 0.22933 | 0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1944 | MDLTHELP | 4 | 211 | 0.015322 | north | Y | -0.0012427 | 0.013132 | 0.22933 | 0.0073039 | 0.0012427 | North | N | 0.0012427 | 0
1947 | HANDLEY_ | 3 | 395 | 0.018377 | north | Y | 0.0018123 | 0.016187 | 0.23238 | 0.010359 | 0.0018123 | North | N | 0.0018123 | 0
1948 | HANDLEY_ | 4 | 435 | 0.018366 | north | Y | 0.0018013 | 0.016176 | 0.23237 | 0.010348 | 0.0018013 | North | N | 0.0018013 | 0
1949 | HANDLEY_ | 5 | 435 | 0.018377 | north | Y | 0.0018123 | 0.016187 | 0.23238 | 0.010359 | 0.0018123 | North | N | 0.0018123 | 0
2371 | COLLIN_1 | MB | 138 | 0.019856 | north | Y | 0.0032913 | 0.017666 | 0.23386 | 0.011838 | 0.0032913 | North | N | 0.0032913 | 0
2413 | MTCK6_G | 6 | 118 | 0.017557 | north | Y | 0.00099232 | 0.015367 | 0.23156 | 0.0095389 | 0.00099232 | North | N | 0.00099232 | 0
2414 | MTCK7_G | 7 | 115 | 0.017557 | north | Y | 0.00099232 | 0.015367 | 0.23156 | 0.0095389 | 0.00099232 | North | N | 0.00099232 | 0
2417 | MTCK8_G | 8 | 556 | 0.017557 | north | Y | 0.00099232 | 0.015367 | 0.23156 | 0.0095389 | 0.00099232 | North | N | 0.00099232 | 0
2451 | LKHB1_G | 1 | 388 | 0.018068 | north | Y | 0.0015033 | 0.015878 | 0.23208 | 0.01005 | 0.0015033 | North | N | 0.0015033 | 0
2452 | LKHB2_G | 2 | 515 | 0.018068 | north | Y | 0.0015033 | 0.015878 | 0.23208 | 0.01005 | 0.0015033 | North | N | 0.0015033 | 0
3097 | MARTLAKE | 1 | 785 | 0.016756 | north | Y | 0.00019132 | 0.014566 | 0.23076 | 0.0087379 | 0.00019132 | North | N | 0.00019132 | 0
3098 | MARTLAKE | 2 | 795 | 0.016756 | north | Y | 0.00019132 | 0.014566 | 0.23076 | 0.0087379 | 0.00019132 | North | N | 0.00019132 | 0
3099 | MARTLAKE | 3 | 780 | 0.016756 | north | Y | 0.00019132 | 0.014566 | 0.23076 | 0.0087379 | 0.00019132 | North | N | 0.00019132 | 0
3107 | STRYKER_ | 1 | 182 | 0.016407 | north | Y | -0.00015768 | 0.014217 | 0.23041 | 0.0083889 | 0.00015768 | North | N | 0.00015768 | 0
3108 | STRYKER_ | 2 | 484 | 0.016407 | north | Y | -0.00015768 | 0.014217 | 0.23041 | 0.0083889 | 0.00015768 | North | N | 0.00015768 | 0
3126 | TRINIDAD | 1 | 224 | 0.015721 | north | Y | -0.00084368 | 0.013531 | 0.22973 | 0.0077029 | 0.00084368 | North | N | 0.00084368 | 0
3309 | ASPN_G | 1 | 50 | 0.016434 | north | Y | -0.00013068 | 0.014244 | 0.23044 | 0.0084159 | 0.00013068 | North | N | 0.00013068 | 0
3348 | CHAMPION | MB | 42 | 0.01645 | north | N | -0.00011468 | 0.01426 | 0.23046 | 0.0084319 | 0.00011468 | North | N | 0.00011468 | 0
3381 | BBRN_1G | 1 | 615 | 0.014695 | north | Y | -0.0018697 | 0.012505 | 0.2287 | 0.0066769 | 0.0018697 | North | N | 0.0018697 | 0
3382 | BBRN_2G | 2 | 587 | 0.014695 | north | Y | -0.0018697 | 0.012505 | 0.2287 | 0.0066769 | 0.0018697 | North | N | 0.0018697 | 0
3403 | THOUSE_1 | MB | 537 | 0.010958 | north | Y | -0.0056067 | 0.0087677 | 0.22497 | 0.0029399 | 0.0029399 | houston | Y | 0.0056067 | 0
3404 | THOUSE_2 | 2 | 787 | 0.010958 | north | Y | -0.0056067 | 0.0087677 | 0.22497 | 0.0029399 | 0.0029399 | houston | Y | 0.0056067 | 2.0987
3416 | LAKE_CRK | MB | 75 | 0.010406 | north | Y | -0.0061587 | 0.0082157 | 0.22441 | 0.0023879 | 0.0023879 | houston | Y | 0.0061587 | 0
3417 | LAKE_CRK | MB | 222 | 0.010406 | north | Y | -0.0061587 | 0.0082157 | 0.22441 | 0.0023879 | 0.0023879 | houston | Y | 0.0061587 | 0
3432 | SANDOW_4 | 4 | 569 | 0.006219 | south | Y | -0.010346 | 0.0040287 | 0.22023 | -0.0017991 | 0.0017991 | houston | Y | 0.0040287 | 1.2686
5026 | BRAUNIG_ | 1 | 209 | 0.001084 | south | Y | -0.015481 | -0.0011063 | 0.21509 | -0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.001084 | south | Y | -0.015481 | -0.0011063 | 0.21509 | -0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.000964 | south | Y | -0.015601 | -0.0012263 | 0.21497 | -0.0070541 | 0.0012263 | south | N | 0.0012263 | 0
5031 | BRA_VHBC | 1 | 46 | 0.001084 | south | Y | -0.015481 | -0.0011063 | 0.21509 | -0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5032 | BRA_VHBC | 2 | 47 | 0.001084 | south | Y | -0.015481 | -0.0011063 | 0.21509 | -0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5033 | BRA_VHBC | 3 | 46 | 0.001084 | south | Y | -0.015481 | -0.0011063 | 0.21509 | -0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5034 | BRA_VHBC | 4 | 46 | 0.001084 | south | Y | -0.015481 | -0.0011063 | 0.21509 | -0.0069341 | 0.0011063 | south | N | 0.0011063 | 0
5111 | CALAVER_ | 1 | 424 | 0.001147 | south | Y | -0.015418 | -0.0010433 | 0.21515 | -0.0068711 | 0.0010433 | south | N | 0.0010433 | 0
5112 | CALAVER_ | 2 | 425 | 0.001147 | south | Y | -0.015418 | -0.0010433 | 0.21515 | -0.0068711 | 0.0010433 | south | N | 0.0010433 | 0
5264 | LEON_LCP | 3 | 58 | 0.000617 | south | Y | -0.015948 | -0.0015733 | 0.21462 | -0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5265 | LEON_LCP | 4 | 89 | 0.000617 | south | Y | -0.015948 | -0.0015733 | 0.21462 | -0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5266 | LEON_LCP | 1 | 44 | 0.000617 | south | Y | -0.015948 | -0.0015733 | 0.21462 | -0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5267 | LEON_LCP | 2 | 44 | 0.000617 | south | Y | -0.015948 | -0.0015733 | 0.21462 | -0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5268 | LEON_LCP | 3 | 43 | 0.000617 | south | Y | -0.015948 | -0.0015733 | 0.21462 | -0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5269 | LEON_LCP | 4 | 45 | 0.000617 | south | Y | -0.015948 | -0.0015733 | 0.21462 | -0.0074011 | 0.0015733 | south | N | 0.0015733 | 0
5396 | CALAVER_ | 1 | 412 | 0.001086 | south | Y | -0.015479 | -0.0011043 | 0.21509 | -0.0069321 | 0.0011043 | south | N | 0.0011043 | 0
5397 | CALAVER_ | 2 | 400 | 0.001086 | south | Y | -0.015479 | -0.0011043 | 0.21509 | -0.0069321 | 0.0011043 | south | N | 0.0011043 | 0
5401 | CALAVER_ | 1 | 546 | 0.001597 | south | Y | -0.014968 | -0.00059332 | 0.2156 | -0.0064211 | 0.00059332 | south | N | 0.00059332 | 0
5402 | CALAVER_ | 2 | 750 | 0.001597 | south | Y | -0.014968 | -0.00059332 | 0.2156 | -0.0064211 | 0.00059332 | south | N | 0.00059332 | 0
5436 | TUTTL_WB | MB | 61 | 0.001403 | south | Y | -0.015162 | -0.00078732 | 0.21541 | -0.0066151 | 0.00078732 | south | N | 0.00078732 | 0
5438 | TUTTL_WB | MB | 95 | 0.001403 | south | Y | -0.015162 | -0.00078732 | 0.21541 | -0.0066151 | 0.00078732 | south | N | 0.00078732 | 0
5439 | TUTTL_WB | MB | 151 | 0.001403 | south | Y | -0.015162 | -0.00078732 | 0.21541 | -0.0066151 | 0.00078732 | south | N | 0.00078732 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.001479 | south | Y | -0.015086 | -0.00071132 | 0.21549 | -0.0065391 | 0.00071132 | south | N | 0.00071132 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.001479 | south | Y | -0.015086 | -0.00071132 | 0.21549 | -0.0065391 | 0.00071132 | south | N | 0.00071132 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.001479 | south | Y | -0.015086 | -0.00071132 | 0.21549 | -0.0065391 | 0.00071132 | south | N | 0.00071132 | 0
5503 | RAYBURNG | 1 | 22 | 0.002652 | south | Y | -0.013913 | 0.00046168 | 0.21666 | -0.0053661 | 0.00046168 | south | N | 0.00046168 | 0
5505 | RAYBURNG | 1 | 11 | 0.002652 | south | Y | -0.013913 | 0.00046168 | 0.21666 | -0.0053661 | 0.00046168 | south | N | 0.00046168 | 0
5506 | RAYBURNG | 1 | 11 | 0.002652 | south | Y | -0.013913 | 0.00046168 | 0.21666 | -0.0053661 | 0.00046168 | south | N | 0.00046168 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.002792 | south | Y | -0.013773 | 0.00060168 | 0.2168 | -0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.002792 | south | Y | -0.013773 | 0.00060168 | 0.2168 | -0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5511 | RAYBURNC | 1 | 46 | 0.002792 | south | Y | -0.013773 | 0.00060168 | 0.2168 | -0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5512 | RAYBURNC | 1 | 48 | 0.002792 | south | Y | -0.013773 | 0.00060168 | 0.2168 | -0.0052261 | 0.00060168 | south | N | 0.00060168 | 0
5728 | FALCONHY | 2 | 12 | -3e-05 | south | N | -0.016595 | -0.0022203 | 0.21398 | -0.0080481 | 0.0022203 | south | N | 0.0022203 | 0
5729 | FALCONHY | 3 | 11 | -3e-05 | south | N | -0.016595 | -0.0022203 | 0.21398 | -0.0080481 | 0.0022203 | south | N | 0.0022203 | 0
5890 | PEARSALL | 1 | 24 | -0.006121 | south | Y | -0.022686 | -0.0083113 | 0.20789 | -0.014139 | 0.0083113 | south | N | 0.0083113 | 0
5891 | PEARSALL | 1 | 24 | -0.006121 | south | Y | -0.022686 | -0.0083113 | 0.20789 | -0.014139 | 0.0083113 | south | N | 0.0083113 | 0
5892 | PEARSALL | 1 | 23 | -0.006121 | south | Y | -0.022686 | -0.0083113 | 0.20789 | -0.014139 | 0.0083113 | south | N | 0.0083113 | 0
5903 | SANMIGUE | 1 | 396 | 0.001048 | south | Y | -0.015517 | -0.0011423 | 0.21506 | -0.0069701 | 0.0011423 | south | N | 0.0011423 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.006038 | houston | N | -0.010527 | 0.0038477 | 0.22005 | -0.0019801 | 0.0019801 | houston | N | 0.0019801 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.006038 | houston | N | -0.010527 | 0.0038477 | 0.22005 | -0.0019801 | 0.0019801 | houston | N | 0.0019801 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | Y | 0.016565 | 0
5932 | SI_RAY9 | 9 | 38 | 0.001907 | south | Y | -0.014658 | -0.00028332 | 0.21591 | -0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.001907 | south | Y | -0.014658 | -0.00028332 | 0.21591 | -0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
5934 | SI_RAY5 | 5 | 15 | 0.001907 | south | Y | -0.014658 | -0.00028332 | 0.21591 | -0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
5935 | SI_RAY10 | 10 | 47 | 0.001907 | south | Y | -0.014658 | -0.00028332 | 0.21591 | -0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
6016 | SWMESA | 1 | 75 | -0.19187 | west | Y | -0.20844 | -0.19407 | 0.022132 | -0.19989 | 0.022132 | west | N | 0.022132 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | Y | 0.21401 | 0
6144 | MCADOO1A | 1 | 150 | -0.1889 | west | Y | -0.20547 | -0.1911 | 0.025102 | -0.19692 | 0.025102 | west | N | 0.025102 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.21461 | west | Y | -0.23117 | -0.2168 | -0.00060292 | -0.22263 | 0.00060292 | west | N | 0.00060292 | 0
6476 | LANGFORD | 1 | 150 | -0.14784 | west | Y | -0.1644 | -0.15003 | 0.066167 | -0.15586 | 0.066167 | west | N | 0.066167 | 0
6637 | SNYDERW1 | 1 | 63 | -0.20257 | west | Y | -0.21914 | -0.20476 | 0.011435 | -0.21059 | 0.011435 | west | N | 0.011435 | 0
6752 | OKLA0A | 1 | 649.7 | -0.24757 | west | Y | -0.26414 | -0.24976 | -0.033564 | -0.25559 | 0.033564 | west | N | 0.033564 | 0
6948 | DENISNDM | 1 | 40 | 0.019381 | north | N | 0.0028163 | 0.017191 | 0.23339 | 0.011363 | 0.0028163 | North | N | 0.0028163 | 0
6948 | DENISNDM | 2 | 40 | 0.019381 | north | N | 0.0028163 | 0.017191 | 0.23339 | 0.011363 | 0.0028163 | North | N | 0.0028163 | 0
7000 | L_FERGUS | 1 | 422 | -0.0053 | south | Y | -0.021865 | -0.0074903 | 0.20871 | -0.013318 | 0.0074903 | south | N | 0.0074903 | 0
7004 | L_SIMGID | 1 | 132 | 0.004041 | south | Y | -0.012524 | 0.0018507 | 0.21805 | -0.0039771 | 0.0018507 | south | N | 0.0018507 | 0
7005 | L_SIMGID | 2 | 134 | 0.004041 | south | Y | -0.012524 | 0.0018507 | 0.21805 | -0.0039771 | 0.0018507 | south | N | 0.0018507 | 0
7006 | L_SIMGID | 3 | 323 | 0.004041 | south | Y | -0.012524 | 0.0018507 | 0.21805 | -0.0039771 | 0.0018507 | south | N | 0.0018507 | 0
7007 | L_LOSTPI | 1 | 158 | 0.004448 | south | Y | -0.012117 | 0.0022577 | 0.21846 | -0.0035701 | 0.0022577 | south | N | 0.0022577 | 0
7008 | L_LOSTPI | 2 | 160 | 0.004448 | south | Y | -0.012117 | 0.0022577 | 0.21846 | -0.0035701 | 0.0022577 | south | N | 0.0022577 | 0
7009 | L_LOSTPI | 3 | 175 | 0.004448 | south | Y | -0.012117 | 0.0022577 | 0.21846 | -0.0035701 | 0.0022577 | south | N | 0.0022577 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.004496 | south | Y | -0.012069 | 0.0023057 | 0.2185 | -0.0035221 | 0.0023057 | south | N | 0.0023057 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.004496 | south | Y | -0.012069 | 0.0023057 | 0.2185 | -0.0035221 | 0.0023057 | south | N | 0.0023057 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.004494 | south | Y | -0.012071 | 0.0023037 | 0.2185 | -0.0035241 | 0.0023037 | south | N | 0.0023037 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.002535 | south | Y | -0.01403 | 0.00034468 | 0.21654 | -0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7015 | L_HAYSEN | 2 | 225 | 0.002535 | south | Y | -0.01403 | 0.00034468 | 0.21654 | -0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.002535 | south | Y | -0.01403 | 0.00034468 | 0.21654 | -0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.002535 | south | Y | -0.01403 | 0.00034468 | 0.21654 | -0.0054831 | 0.00034468 | south | N | 0.00034468 | 0
7020 | L_AUSTPL | 1 | 8 | 0.003287 | south | N | -0.013278 | 0.0010967 | 0.21729 | -0.0047311 | 0.0010967 | south | N | 0.0010967 | 0
7020 | L_AUSTPL | 2 | 8 | 0.003287 | south | N | -0.013278 | 0.0010967 | 0.21729 | -0.0047311 | 0.0010967 | south | N | 0.0010967 | 0
7022 | L_BUCHAN | 1 | 18 | -0.005652 | south | N | -0.022217 | -0.0078423 | 0.20836 | -0.01367 | 0.0078423 | south | N | 0.0078423 | 0
7023 | L_BUCHAN | 2 | 18 | -0.005652 | south | N | -0.022217 | -0.0078423 | 0.20836 | -0.01367 | 0.0078423 | south | N | 0.0078423 | 0
7024 | L_BUCHAN | 3 | 15 | -0.005652 | south | N | -0.022217 | -0.0078423 | 0.20836 | -0.01367 | 0.0078423 | south | N | 0.0078423 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.00796 | south | N | -0.024525 | -0.01015 | 0.20605 | -0.015978 | 0.01015 | south | N | 0.01015 | 0
7028 | L_MARBFA | 1 | 18 | -0.003298 | south | N | -0.019863 | -0.0054883 | 0.21071 | -0.011316 | 0.0054883 | south | N | 0.0054883 | 0
7029 | L_MARBFA | 2 | 18 | -0.003298 | south | N | -0.019863 | -0.0054883 | 0.21071 | -0.011316 | 0.0054883 | south | N | 0.0054883 | 0
7031 | L_MARSFO | 1 | 35 | 0.001242 | south | N | -0.015323 | -0.00094832 | 0.21525 | -0.0067761 | 0.00094832 | south | N | 0.00094832 | 0
7032 | L_MARSFO | 2 | 34 | 0.001242 | south | N | -0.015323 | -0.00094832 | 0.21525 | -0.0067761 | 0.00094832 | south | N | 0.00094832 | 0
7033 | L_MARSFO | 3 | 35 | 0.001242 | south | N | -0.015323 | -0.00094832 | 0.21525 | -0.0067761 | 0.00094832 | south | N | 0.00094832 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.004798 | south | N | -0.021363 | -0.0069883 | 0.20921 | -0.012816 | 0.0069883 | south | N | 0.0069883 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.004798 | south | N | -0.021363 | -0.0069883 | 0.20921 | -0.012816 | 0.0069883 | south | N | 0.0069883 | 0
7038 | L_DELAWA | 1 | 35 | -0.20272 | west | Y | -0.21928 | -0.20491 | 0.011292 | -0.21073 | 0.011292 | west | N | 0.011292 | 0
7038 | L_DELAWA | 2 | 30 | -0.20272 | west | Y | -0.21928 | -0.20491 | 0.011292 | -0.21073 | 0.011292 | west | N | 0.011292 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.004322 | south | Y | -0.012243 | 0.0021317 | 0.21833 | -0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.004322 | south | Y | -0.012243 | 0.0021317 | 0.21833 | -0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.004322 | south | Y | -0.012243 | 0.0021317 | 0.21833 | -0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.004322 | south | Y | -0.012243 | 0.0021317 | 0.21833 | -0.0036961 | 0.0021317 | south | N | 0.0021317 | 0
7487 | L_CANYHY | 1 | 6 | 0.002052 | south | N | -0.014513 | -0.00013832 | 0.21606 | -0.0059661 | 0.00013832 | south | N | 0.00013832 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.002337 | south | N | -0.014228 | 0.00014668 | 0.21634 | -0.0056811 | 0.00014668 | south | N | 0.00014668 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.002337 | south | N | -0.014228 | 0.00014668 | 0.21634 | -0.0056811 | 0.00014668 | south | N | 0.00014668 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.002337 | south | N | -0.014228 | 0.00014668 | 0.21634 | -0.0056811 | 0.00014668 | south | N | 0.00014668 | 0
7609 | L_SCHUMA | 1 | 4 | 0.002018 | south | N | -0.014547 | -0.00017232 | 0.21603 | -0.0060001 | 0.00017232 | south | N | 0.00017232 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.00267 | south | N | -0.013895 | 0.00047968 | 0.21668 | -0.0053481 | 0.00047968 | south | N | 0.00047968 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.00267 | south | N | -0.013895 | 0.00047968 | 0.21668 | -0.0053481 | 0.00047968 | south | N | 0.00047968 | 0
7800 | L_GUADGE | 1 | 147 | 0.002147 | south | Y | -0.014418 | -4.3315e-05 | 0.21615 | -0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.002147 | south | Y | -0.014418 | -4.3315e-05 | 0.21615 | -0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.002147 | south | Y | -0.014418 | -4.3315e-05 | 0.21615 | -0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.002147 | south | Y | -0.014418 | -4.3315e-05 | 0.21615 | -0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.002147 | south | Y | -0.014418 | -4.3315e-05 | 0.21615 | -0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.002147 | south | Y | -0.014418 | -4.3315e-05 | 0.21615 | -0.0058711 | 4.3315e-05 | south | N | 4.3315e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.004066 | south | Y | -0.012499 | 0.0018757 | 0.21807 | -0.0039521 | 0.0018757 | south | N | 0.0018757 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.004066 | south | Y | -0.012499 | 0.0018757 | 0.21807 | -0.0039521 | 0.0018757 | south | N | 0.0018757 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.004066 | south | Y | -0.012499 | 0.0018757 | 0.21807 | -0.0039521 | 0.0018757 | south | N | 0.0018757 | 0
7810 | L_RIONOG | 1 | 142 | 0.002344 | south | Y | -0.014221 | 0.00015368 | 0.21635 | -0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
7811 | L_RIONOG | 2 | 145 | 0.002344 | south | Y | -0.014221 | 0.00015368 | 0.21635 | -0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
7812 | L_RIONOG | 3 | 151 | 0.002344 | south | Y | -0.014221 | 0.00015368 | 0.21635 | -0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
7813 | L_RIONOG | 4 | 290 | 0.002344 | south | Y | -0.014221 | 0.00015368 | 0.21635 | -0.0056741 | 0.00015368 | south | N | 0.00015368 | 0
8032 | AMISTADH | 1 | 33 | -0.055041 | south | N | -0.071606 | -0.057231 | 0.15897 | -0.063059 | 0.057231 | south | N | 0.057231 | 0
8033 | AMISTADH | 2 | 25 | -0.055041 | south | N | -0.071606 | -0.057231 | 0.15897 | -0.063059 | 0.057231 | south | N | 0.057231 | 0
8048 | FALCONHY | 1 | 12 | -3e-05 | south | N | -0.016595 | -0.0022203 | 0.21398 | -0.0080481 | 0.0022203 | south | N | 0.0022203 | 0
8066 | DUP1V#1 | 1 | 73 | 0.00293 | south | N | -0.013635 | 0.00073968 | 0.21694 | -0.0050881 | 0.00073968 | south | N | 0.00073968 | 0
8134 | FOR69CG0 | 1 | 79 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8138 | FOR69CG0 | 2 | 81 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8147 | UCAR #2 | 10 | 28 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
8148 | UCAR #1 | 2 | 7 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
8153 | FOR69CG0 | 3 | 79 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8154 | FOR69CG0 | 4 | 80 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8156 | FOR69CG0 | 6 | 25 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8157 | FOR69CG0 | 7 | 46 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
8161 | COLETOU1 | 1 | 629 | 0.002193 | south | Y | -0.014372 | 2.6848e-06 | 0.2162 | -0.0058251 | 2.6848e-06 | south | N | 2.6848e-06 | 0
8173 | VICEC51A | 5 | 144 | 0.002853 | south | Y | -0.013712 | 0.00066268 | 0.21686 | -0.0051651 | 0.00066268 | south | N | 0.00066268 | 0
8174 | VICEC61A | 6 | 188 | 0.002853 | south | Y | -0.013712 | 0.00066268 | 0.21686 | -0.0051651 | 0.00066268 | south | N | 0.00066268 | 0
8189 | CUERO 2 | 1 | 12 | 0.002687 | south | N | -0.013878 | 0.00049668 | 0.21669 | -0.0053311 | 0.00049668 | south | N | 0.00049668 | 0
8262 | ELPS | 1 | 6 | -0.039493 | south | N | -0.056058 | -0.041683 | 0.17451 | -0.047511 | 0.041683 | south | N | 0.041683 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8442 | NBEC71A | 1 | 336 | 0.002186 | south | Y | -0.014379 | -4.3152e-06 | 0.21619 | -0.0058321 | 4.3152e-06 | south | N | 4.3152e-06 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.016565 | -0.0021903 | 0.21401 | -0.0080181 | 0.0021903 | south | N | 0.0021903 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.002157 | south | Y | -0.014408 | -3.3315e-05 | 0.21616 | -0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.002157 | south | Y | -0.014408 | -3.3315e-05 | 0.21616 | -0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.002119 | south | N | -0.014446 | -7.1315e-05 | 0.21613 | -0.0058991 | 7.1315e-05 | south | N | 7.1315e-05 | 0
8506 | VAL #1 | 1 | 25 | 0.002139 | south | N | -0.014426 | -5.1315e-05 | 0.21615 | -0.0058791 | 5.1315e-05 | south | N | 5.1315e-05 | 0
8507 | VAL #2 | 2 | 25 | 0.002139 | south | N | -0.014426 | -5.1315e-05 | 0.21615 | -0.0058791 | 5.1315e-05 | south | N | 5.1315e-05 | 0
8511 | OXY_CC0A | 1 | 38 | 0.002137 | south | N | -0.014428 | -5.3315e-05 | 0.21614 | -0.0058811 | 5.3315e-05 | south | N | 5.3315e-05 | 0
8517 | CELANEBI | 1 | 29 | 0.002041 | south | N | -0.014524 | -0.00014932 | 0.21605 | -0.0059771 | 0.00014932 | south | N | 0.00014932 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.002185 | south | N | -0.01438 | -5.3152e-06 | 0.21619 | -0.0058331 | 5.3152e-06 | south | N | 5.3152e-06 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.002185 | south | N | -0.01438 | -5.3152e-06 | 0.21619 | -0.0058331 | 5.3152e-06 | south | N | 5.3152e-06 | 0
8562 | CNOPST1 | 3 | 153 | 0.002185 | south | N | -0.01438 | -5.3152e-06 | 0.21619 | -0.0058331 | 5.3152e-06 | south | N | 5.3152e-06 | 0
8926 | LGE_GT10 | 1 | 158 | 0.002338 | south | N | -0.014227 | 0.00014768 | 0.21635 | -0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8927 | LGE_GT20 | 2 | 153 | 0.002338 | south | N | -0.014227 | 0.00014768 | 0.21635 | -0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8928 | LGE_STG0 | 3 | 100 | 0.002338 | south | N | -0.014227 | 0.00014768 | 0.21635 | -0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8930 | ICPGN10A | 1 | 145 | 0.002338 | south | N | -0.014227 | 0.00014768 | 0.21635 | -0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8931 | ICPGN20A | 2 | 147 | 0.002338 | south | N | -0.014227 | 0.00014768 | 0.21635 | -0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8932 | ICPGN30A | 3 | 127 | 0.002338 | south | N | -0.014227 | 0.00014768 | 0.21635 | -0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.001499 | south | Y | -0.015066 | -0.00069132 | 0.21551 | -0.0065191 | 0.00069132 | south | N | 0.00069132 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.001499 | south | Y | -0.015066 | -0.00069132 | 0.21551 | -0.0065191 | 0.00069132 | south | N | 0.00069132 | 0
8935 | FGNTS201 | 3 | 173 | 0.001499 | south | Y | -0.015066 | -0.00069132 | 0.21551 | -0.0065191 | 0.00069132 | south | N | 0.00069132 | 0
8936 | MVGN#1 | 1 | 207 | 0.001754 | south | Y | -0.014811 | -0.00043632 | 0.21576 | -0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.001754 | south | Y | -0.014811 | -0.00043632 | 0.21576 | -0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8938 | MVGN#3 | 3 | 242 | 0.001754 | south | Y | -0.014811 | -0.00043632 | 0.21576 | -0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8981 | HECN1 | 1 | 144 | 0.001754 | south | Y | -0.014811 | -0.00043632 | 0.21576 | -0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8982 | HECN2 | 2 | 144 | 0.001754 | south | Y | -0.014811 | -0.00043632 | 0.21576 | -0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
8983 | HECN3 | 3 | 171 | 0.001754 | south | Y | -0.014811 | -0.00043632 | 0.21576 | -0.0062641 | 0.00043632 | south | N | 0.00043632 | 0
9000 | DECKR_G1 | 1 | 310 | 0.003479 | south | Y | -0.013086 | 0.0012887 | 0.21749 | -0.0045391 | 0.0012887 | south | N | 0.0012887 | 0
9001 | DECKR_G2 | 2 | 413 | 0.003479 | south | Y | -0.013086 | 0.0012887 | 0.21749 | -0.0045391 | 0.0012887 | south | N | 0.0012887 | 0
9002 | DECKR_G3 | 3 | 42 | 0.00364 | south | Y | -0.012925 | 0.0014497 | 0.21765 | -0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9003 | DECKR_G4 | 4 | 44 | 0.00364 | south | Y | -0.012925 | 0.0014497 | 0.21765 | -0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9004 | DECKR_G5 | 5 | 44 | 0.00364 | south | Y | -0.012925 | 0.0014497 | 0.21765 | -0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9005 | DECKR_G6 | 6 | 47 | 0.00364 | south | Y | -0.012925 | 0.0014497 | 0.21765 | -0.0043781 | 0.0014497 | south | N | 0.0014497 | 0
9016 | SANDH_G1 | 1 | 49 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9017 | SANDH_G2 | 2 | 46 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9018 | SANDH_G3 | 3 | 46 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9019 | SANDH_G4 | 4 | 47 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9020 | SANDHG5A | 5A | 154 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9021 | SANDHG5C | 5C | 148 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9022 | SANDH_G6 | 6 | 48 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
9023 | SANDH_G7 | 7 | 48 | 0.003432 | south | Y | -0.013133 | 0.0012417 | 0.21744 | -0.0045861 | 0.0012417 | south | N | 0.0012417 | 0
11001 | NAV1CT | 1 | 70 | -0.20505 | west | Y | -0.22161 | -0.20724 | 0.0089581 | -0.21307 | 0.0089581 | west | N | 0.0089581 | 0
11009 | NAV2CT | 1 | 70 | -0.20505 | west | Y | -0.22161 | -0.20724 | 0.0089581 | -0.21307 | 0.0089581 | west | N | 0.0089581 | 0
11011 | NAV3ST | 1 | 92.8 | -0.20505 | west | Y | -0.22161 | -0.20724 | 0.0089581 | -0.21307 | 0.0089581 | west | N | 0.0089581 | 0
11012 | NAV4CT | 1 | 80 | -0.20505 | west | Y | -0.22161 | -0.20724 | 0.0089581 | -0.21307 | 0.0089581 | west | N | 0.0089581 | 0
11013 | NAV5CT | 1 | 80 | -0.20505 | west | Y | -0.22161 | -0.20724 | 0.0089581 | -0.21307 | 0.0089581 | west | N | 0.0089581 | 0
11014 | NAV6ST | 1 | 115 | -0.20505 | west | Y | -0.22161 | -0.20724 | 0.0089581 | -0.21307 | 0.0089581 | west | N | 0.0089581 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.20503 | west | Y | -0.22159 | -0.20722 | 0.0089801 | -0.21305 | 0.0089801 | west | N | 0.0089801 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.20503 | west | Y | -0.22159 | -0.20722 | 0.0089801 | -0.21305 | 0.0089801 | west | N | 0.0089801 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.20503 | west | Y | -0.22159 | -0.20722 | 0.0089801 | -0.21305 | 0.0089801 | west | N | 0.0089801 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.20503 | west | Y | -0.22159 | -0.20722 | 0.0089801 | -0.21305 | 0.0089801 | west | N | 0.0089801 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.20503 | west | Y | -0.22159 | -0.20722 | 0.0089801 | -0.21305 | 0.0089801 | west | N | 0.0089801 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.20503 | west | Y | -0.22159 | -0.20722 | 0.0089801 | -0.21305 | 0.0089801 | west | N | 0.0089801 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.17314 | west | Y | -0.18971 | -0.17533 | 0.040865 | -0.18116 | 0.040865 | west | N | 0.040865 | 0
11057 | CHAMPION | 1 | 126.5 | -0.17314 | west | Y | -0.18971 | -0.17533 | 0.040865 | -0.18116 | 0.040865 | west | N | 0.040865 | 0
11058 | PYRON_1G | 1 | 249 | -0.17314 | west | Y | -0.18971 | -0.17533 | 0.040865 | -0.18116 | 0.040865 | west | N | 0.040865 | 0
11059 | INADALE_ | 1 | 197 | -0.17314 | west | Y | -0.18971 | -0.17533 | 0.040865 | -0.18116 | 0.040865 | west | N | 0.040865 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.20706 | west | Y | -0.22363 | -0.20926 | 0.0069421 | -0.21508 | 0.0069421 | west | N | 0.0069421 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.20706 | west | Y | -0.22363 | -0.20926 | 0.0069421 | -0.21508 | 0.0069421 | west | N | 0.0069421 | 0
11147 | NOTREES_ | 1 | 149 | -0.20276 | west | Y | -0.21932 | -0.20495 | 0.011249 | -0.21078 | 0.011249 | west | N | 0.011249 | 0
11309 | BULLCREK | 1 | 180 | -0.20255 | west | Y | -0.21911 | -0.20474 | 0.01146 | -0.21057 | 0.01146 | west | N | 0.01146 | 0
11310 | BULLCREK | 1 | 180 | -0.20255 | west | Y | -0.21911 | -0.20474 | 0.01146 | -0.21057 | 0.01146 | west | N | 0.01146 | 0
11320 | COYOTE_1 | 1 | 225 | -0.20257 | west | Y | -0.21913 | -0.20476 | 0.011438 | -0.21059 | 0.011438 | west | N | 0.011438 | 0
11415 | LORAINE_ | 1 | 125 | -0.22138 | west | Y | -0.23794 | -0.22357 | -0.0073719 | -0.2294 | 0.0073719 | west | N | 0.0073719 | 0
11416 | LORAINE_ | 1 | 125 | -0.22138 | west | Y | -0.23794 | -0.22357 | -0.0073719 | -0.2294 | 0.0073719 | west | N | 0.0073719 | 0
11691 | KMICHICT | 1 | 140 | 0.019084 | north | N | 0.0025193 | 0.016894 | 0.23309 | 0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11692 | KMICHICT | 2 | 141 | 0.019084 | north | N | 0.0025193 | 0.016894 | 0.23309 | 0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11693 | KMICHIST | 3 | 309 | 0.019084 | north | N | 0.0025193 | 0.016894 | 0.23309 | 0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11694 | KMICHICT | 4 | 143 | 0.019084 | north | N | 0.0025193 | 0.016894 | 0.23309 | 0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11695 | KMICHICT | 5 | 144 | 0.019084 | north | N | 0.0025193 | 0.016894 | 0.23309 | 0.011066 | 0.0025193 | North | N | 0.0025193 | 0
11696 | KMICHIST | 6 | 310 | 0.019084 | north | N | 0.0025193 | 0.016894 | 0.23309 | 0.011066 | 0.0025193 | North | N | 0.0025193 | 0
12322 | ENNSTRAC | 1 | 196 | 0.015849 | north | Y | -0.00071568 | 0.013659 | 0.22986 | 0.0078309 | 0.00071568 | North | N | 0.00071568 | 0
12323 | ENNSTRAC | 2 | 111 | 0.015849 | north | Y | -0.00071568 | 0.013659 | 0.22986 | 0.0078309 | 0.00071568 | North | N | 0.00071568 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.019332 | north | N | 0.0027673 | 0.017142 | 0.23334 | 0.011314 | 0.0027673 | North | N | 0.0027673 | 0
12411 | FPLEFR1A | 1 | 161 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12412 | FPLEFR1B | 2 | 164 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12413 | FPLEFR1C | 3 | 164 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12414 | FPLEFR1S | 4 | 414 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12421 | FPLEFR2A | 1 | 162 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12422 | FPLEFR2B | 2 | 161 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12423 | FPLEFR2C | 3 | 163 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12424 | FPLEFR2S | 4 | 409 | 0.017982 | north | Y | 0.0014173 | 0.015792 | 0.23199 | 0.0099639 | 0.0014173 | North | N | 0.0014173 | 0
12440 | PARKD_1S | 1 | 0 | 0.017938 | north | N | 0.0013733 | 0.015748 | 0.23195 | 0.0099199 | 0.0013733 | North | N | 0.0013733 | 0
12449 | PARKD_2S | 1 | 0 | 0.017938 | north | N | 0.0013733 | 0.015748 | 0.23195 | 0.0099199 | 0.0013733 | North | N | 0.0013733 | 0
13116 | TGATEWAY | 1 | 148 | 0.01659 | north | N | 2.5321e-05 | 0.0144 | 0.2306 | 0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13117 | TGATEWAY | 2 | 130 | 0.01659 | north | N | 2.5321e-05 | 0.0144 | 0.2306 | 0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13118 | TGATEWAY | 3 | 145 | 0.01659 | north | N | 2.5321e-05 | 0.0144 | 0.2306 | 0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13119 | TGATEWAY | 4 | 399 | 0.01659 | north | N | 2.5321e-05 | 0.0144 | 0.2306 | 0.0085719 | 2.5321e-05 | North | N | 2.5321e-05 | 0
13131 | CALFREST | 1 | 150.7 | 0.014971 | north | Y | -0.0015937 | 0.012781 | 0.22898 | 0.0069529 | 0.0015937 | North | N | 0.0015937 | 0
13132 | CALFREST | 2 | 151 | 0.014971 | north | Y | -0.0015937 | 0.012781 | 0.22898 | 0.0069529 | 0.0015937 | North | N | 0.0015937 | 0
13133 | CALFREST | 3 | 177.4 | 0.014971 | north | Y | -0.0015937 | 0.012781 | 0.22898 | 0.0069529 | 0.0015937 | North | N | 0.0015937 | 0
13134 | CALFREST | 4 | 151.5 | 0.015031 | north | Y | -0.0015337 | 0.012841 | 0.22904 | 0.0070129 | 0.0015337 | North | N | 0.0015337 | 0
13135 | CALFREST | 5 | 152.3 | 0.015031 | north | Y | -0.0015337 | 0.012841 | 0.22904 | 0.0070129 | 0.0015337 | North | N | 0.0015337 | 0
13136 | CALFREST | 6 | 177.5 | 0.015031 | north | Y | -0.0015337 | 0.012841 | 0.22904 | 0.0070129 | 0.0015337 | North | N | 0.0015337 | 0
13432 | SANDOW_5 | 5 | 581 | 0.006219 | south | Y | -0.010346 | 0.0040287 | 0.22023 | -0.0017991 | 0.0017991 | houston | Y | 0.0040287 | 1.2954
13691 | OAKGROVE | 1 | 855 | 0.012623 | north | Y | -0.0039417 | 0.010433 | 0.22663 | 0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
13692 | OAKGROVE | 2 | 855 | 0.012623 | north | Y | -0.0039417 | 0.010433 | 0.22663 | 0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
32798 | BRYN_TAM | 1 | 32 | 0.01123 | north | N | -0.0053347 | 0.0090397 | 0.22524 | 0.0032119 | 0.0032119 | houston | Y | 0.0053347 | 0
32883 | BRYN_DNS | 1 | 48 | 0.0112 | north | Y | -0.0053647 | 0.0090097 | 0.22521 | 0.0031819 | 0.0031819 | houston | Y | 0.0053647 | 0.10477
32884 | BRYN_DNS | 1 | 46 | 0.0112 | north | Y | -0.0053647 | 0.0090097 | 0.22521 | 0.0031819 | 0.0031819 | houston | Y | 0.0053647 | 0.10041
32886 | BRYN_ATK | MB | 12 | 0.011239 | north | Y | -0.0053257 | 0.0090487 | 0.22525 | 0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0
32887 | BRYN_ATK | MB | 51 | 0.011239 | north | Y | -0.0053257 | 0.0090487 | 0.22525 | 0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0
32888 | BRYN_ATK | 1 | 17 | 0.011239 | north | Y | -0.0053257 | 0.0090487 | 0.22525 | 0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0.035781
32890 | BRYN_ATK | MB | 22 | 0.011239 | north | Y | -0.0053257 | 0.0090487 | 0.22525 | 0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0
32891 | BRYN_ATK | MB | 25 | 0.011239 | north | Y | -0.0053257 | 0.0090487 | 0.22525 | 0.0032209 | 0.0032209 | houston | Y | 0.0053257 | 0
32892 | BRYN_DNS | 1 | 105 | 0.0112 | north | Y | -0.0053647 | 0.0090097 | 0.22521 | 0.0031819 | 0.0031819 | houston | Y | 0.0053647 | 0.22919
36998 | RDCNYNG1 | 1 | 84 | -0.1991 | west | Y | -0.21566 | -0.20129 | 0.014908 | -0.20712 | 0.014908 | west | N | 0.014908 | 0
38332 | WDWRDU2 | 1 | 80 | -0.1917 | west | Y | -0.20826 | -0.19389 | 0.02231 | -0.19972 | 0.02231 | west | N | 0.02231 | 0
38437 | TNSRBNMS | 1 | 150 | -0.1916 | west | Y | -0.20816 | -0.19379 | 0.022411 | -0.19961 | 0.022411 | west | N | 0.022411 | 0
38438 | TNSRBNMS | 1 | 150 | -0.1916 | west | Y | -0.20816 | -0.19379 | 0.022411 | -0.19961 | 0.022411 | west | N | 0.022411 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38600 | TNBP_CGN | 5 | 53 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38614 | TNBPAMCG | 4 | 96 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38615 | TNBPAMCG | 1 | 244 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38690 | TNBP_CGN | 3 | 40 | 0.007934 | houston | N | -0.0086307 | 0.0057437 | 0.22194 | -8.4088e-05 | 8.4088e-05 | houston | N | 8.4088e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.007933 | houston | N | -0.0086317 | 0.0057427 | 0.22194 | -8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.007933 | houston | N | -0.0086317 | 0.0057427 | 0.22194 | -8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.007933 | houston | N | -0.0086317 | 0.0057427 | 0.22194 | -8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.007933 | houston | N | -0.0086317 | 0.0057427 | 0.22194 | -8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
39470 | TNDOWCGN | 1 | 32 | 0.007933 | houston | N | -0.0086317 | 0.0057427 | 0.22194 | -8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
39480 | TNDOWCGN | 1 | 30 | 0.007933 | houston | N | -0.0086317 | 0.0057427 | 0.22194 | -8.5088e-05 | 8.5088e-05 | houston | N | 8.5088e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.007199 | houston | N | -0.0093657 | 0.0050087 | 0.22121 | -0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.007199 | houston | N | -0.0093657 | 0.0050087 | 0.22121 | -0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.007199 | houston | N | -0.0093657 | 0.0050087 | 0.22121 | -0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.007199 | houston | N | -0.0093657 | 0.0050087 | 0.22121 | -0.00081909 | 0.00081909 | houston | N | 0.00081909 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.012623 | north | Y | -0.0039417 | 0.010433 | 0.22663 | 0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
39970 | TNTNPONE | 1 | 153 | 0.012623 | north | Y | -0.0039417 | 0.010433 | 0.22663 | 0.0046049 | 0.0039417 | North | N | 0.0039417 | 0
48500 | APD_GT1_ | 1 | 136 | 0.008373 | houston | N | -0.0081917 | 0.0061827 | 0.22238 | 0.00035491 | 0.00035491 | houston | N | 0.00035491 | 0
48510 | AK_GT1__ | 1 | 33 | 0.007689 | houston | N | -0.0088757 | 0.0054987 | 0.2217 | -0.00032909 | 0.00032909 | houston | N | 0.00032909 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.008372 | houston | Y | -0.0081927 | 0.0061817 | 0.22238 | 0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.008372 | houston | Y | -0.0081927 | 0.0061817 | 0.22238 | 0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.008372 | houston | Y | -0.0081927 | 0.0061817 | 0.22238 | 0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.008372 | houston | Y | -0.0081927 | 0.0061817 | 0.22238 | 0.00035391 | 0.00035391 | houston | N | 0.00035391 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.007066 | houston | N | -0.0094987 | 0.0048757 | 0.22107 | -0.00095209 | 0.00095209 | houston | N | 0.00095209 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.007066 | houston | N | -0.0094987 | 0.0048757 | 0.22107 | -0.00095209 | 0.00095209 | houston | N | 0.00095209 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.00767 | houston | N | -0.0088947 | 0.0054797 | 0.22168 | -0.00034809 | 0.00034809 | houston | N | 0.00034809 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.00767 | houston | N | -0.0088947 | 0.0054797 | 0.22168 | -0.00034809 | 0.00034809 | houston | N | 0.00034809 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.00767 | houston | N | -0.0088947 | 0.0054797 | 0.22168 | -0.00034809 | 0.00034809 | houston | N | 0.00034809 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.008207 | houston | N | -0.0083577 | 0.0060167 | 0.22221 | 0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.008207 | houston | N | -0.0083577 | 0.0060167 | 0.22221 | 0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.008207 | houston | N | -0.0083577 | 0.0060167 | 0.22221 | 0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.008207 | houston | N | -0.0083577 | 0.0060167 | 0.22221 | 0.00018891 | 0.00018891 | houston | N | 0.00018891 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.008313 | houston | N | -0.0082517 | 0.0061227 | 0.22232 | 0.00029491 | 0.00029491 | houston | N | 0.00029491 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.008313 | houston | N | -0.0082517 | 0.0061227 | 0.22232 | 0.00029491 | 0.00029491 | houston | N | 0.00029491 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.008175 | houston | N | -0.0083897 | 0.0059847 | 0.22218 | 0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.008175 | houston | N | -0.0083897 | 0.0059847 | 0.22218 | 0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.008175 | houston | N | -0.0083897 | 0.0059847 | 0.22218 | 0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.008175 | houston | N | -0.0083897 | 0.0059847 | 0.22218 | 0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.008175 | houston | N | -0.0083897 | 0.0059847 | 0.22218 | 0.00015691 | 0.00015691 | houston | N | 0.00015691 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.008502 | houston | Y | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.008449 | houston | Y | -0.0081157 | 0.0062587 | 0.22246 | 0.00043091 | 0.00043091 | houston | N | 0.00043091 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.008517 | houston | Y | -0.0080477 | 0.0063267 | 0.22252 | 0.00049891 | 0.00049891 | houston | N | 0.00049891 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.008517 | houston | Y | -0.0080477 | 0.0063267 | 0.22252 | 0.00049891 | 0.00049891 | houston | N | 0.00049891 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.008517 | houston | Y | -0.0080477 | 0.0063267 | 0.22252 | 0.00049891 | 0.00049891 | houston | N | 0.00049891 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.008814 | houston | N | -0.0077507 | 0.0066237 | 0.22282 | 0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.008383 | houston | N | -0.0081817 | 0.0061927 | 0.22239 | 0.00036491 | 0.00036491 | houston | N | 0.00036491 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.008383 | houston | N | -0.0081817 | 0.0061927 | 0.22239 | 0.00036491 | 0.00036491 | houston | N | 0.00036491 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.008555 | houston | N | -0.0080097 | 0.0063647 | 0.22256 | 0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.008555 | houston | N | -0.0080097 | 0.0063647 | 0.22256 | 0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.008555 | houston | N | -0.0080097 | 0.0063647 | 0.22256 | 0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.008555 | houston | N | -0.0080097 | 0.0063647 | 0.22256 | 0.00053691 | 0.00053691 | houston | N | 0.00053691 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.008317 | houston | N | -0.0082477 | 0.0061267 | 0.22232 | 0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.008317 | houston | N | -0.0082477 | 0.0061267 | 0.22232 | 0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.008317 | houston | N | -0.0082477 | 0.0061267 | 0.22232 | 0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.008317 | houston | N | -0.0082477 | 0.0061267 | 0.22232 | 0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.008279 | houston | N | -0.0082857 | 0.0060887 | 0.22229 | 0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.008279 | houston | N | -0.0082857 | 0.0060887 | 0.22229 | 0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.008279 | houston | N | -0.0082857 | 0.0060887 | 0.22229 | 0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.008279 | houston | N | -0.0082857 | 0.0060887 | 0.22229 | 0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.008279 | houston | N | -0.0082857 | 0.0060887 | 0.22229 | 0.00026091 | 0.00026091 | houston | N | 0.00026091 | 0
48651 | EP_1_2 | 1 | 5 | 0.0085 | houston | N | -0.0080647 | 0.0063097 | 0.22251 | 0.00048191 | 0.00048191 | houston | N | 0.00048191 | 0
48651 | EP_1_2 | 2 | 21 | 0.0085 | houston | N | -0.0080647 | 0.0063097 | 0.22251 | 0.00048191 | 0.00048191 | houston | N | 0.00048191 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.010836 | north | N | -0.0057287 | 0.0086457 | 0.22484 | 0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.010836 | north | N | -0.0057287 | 0.0086457 | 0.22484 | 0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.010836 | north | N | -0.0057287 | 0.0086457 | 0.22484 | 0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.010836 | north | N | -0.0057287 | 0.0086457 | 0.22484 | 0.0028179 | 0.0028179 | houston | Y | 0.0057287 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.008572 | houston | Y | -0.0079927 | 0.0063817 | 0.22258 | 0.00055391 | 0.00055391 | houston | N | 0.00055391 | 0
48691 | GBY_7374 | A | 46 | 0.008263 | houston | Y | -0.0083017 | 0.0060727 | 0.22227 | 0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48691 | GBY_7374 | B | 46 | 0.008263 | houston | Y | -0.0083017 | 0.0060727 | 0.22227 | 0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48692 | GBY_8182 | C | 46 | 0.008263 | houston | Y | -0.0083017 | 0.0060727 | 0.22227 | 0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48692 | GBY_8182 | D | 55 | 0.008263 | houston | Y | -0.0083017 | 0.0060727 | 0.22227 | 0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48693 | GBY_8384 | E | 55 | 0.008263 | houston | Y | -0.0083017 | 0.0060727 | 0.22227 | 0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48693 | GBY_8384 | F | 54 | 0.008263 | houston | Y | -0.0083017 | 0.0060727 | 0.22227 | 0.00024491 | 0.00024491 | houston | N | 0.00024491 | 0
48721 | LEG_1___ | 1 | 827 | 0.013173 | north | Y | -0.0033917 | 0.010983 | 0.22718 | 0.0051549 | 0.0033917 | North | N | 0.0033917 | 0
48722 | LEG_2___ | 2 | 819 | 0.013173 | north | Y | -0.0033917 | 0.010983 | 0.22718 | 0.0051549 | 0.0033917 | North | N | 0.0033917 | 0
48730 | MNS_GT | 1 | 46.1 | 0.007625 | houston | N | -0.0089397 | 0.0054347 | 0.22163 | -0.00039309 | 0.00039309 | houston | N | 0.00039309 | 0
48731 | CBE_GT1 | 1 | 76 | 0.006156 | houston | Y | -0.010409 | 0.0039657 | 0.22016 | -0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48732 | CBE_GT2 | 1 | 76 | 0.006156 | houston | Y | -0.010409 | 0.0039657 | 0.22016 | -0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48733 | CBE_ST12 | 1 | 105 | 0.006156 | houston | Y | -0.010409 | 0.0039657 | 0.22016 | -0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48734 | CBE_GT3 | 1 | 74 | 0.006156 | houston | Y | -0.010409 | 0.0039657 | 0.22016 | -0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48735 | CBE_GT4 | 1 | 74 | 0.006156 | houston | Y | -0.010409 | 0.0039657 | 0.22016 | -0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48736 | CBE_ST34 | 1 | 102 | 0.006156 | houston | Y | -0.010409 | 0.0039657 | 0.22016 | -0.0018621 | 0.0018621 | houston | N | 0.0018621 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.008318 | houston | N | -0.0082467 | 0.0061277 | 0.22233 | 0.00029991 | 0.00029991 | houston | N | 0.00029991 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.008318 | houston | N | -0.0082467 | 0.0061277 | 0.22233 | 0.00029991 | 0.00029991 | houston | N | 0.00029991 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.008318 | houston | N | -0.0082467 | 0.0061277 | 0.22233 | 0.00029991 | 0.00029991 | houston | N | 0.00029991 | 0
48761 | PR_GT1__ | 1 | 35 | 0.008297 | houston | N | -0.0082677 | 0.0061067 | 0.2223 | 0.00027891 | 0.00027891 | houston | N | 0.00027891 | 0
48772 | PHR_GN2_ | MB | 459 | 0.008093 | houston | Y | -0.0084717 | 0.0059027 | 0.2221 | 7.4912e-05 | 7.4912e-05 | houston | N | 7.4912e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.008502 | houston | N | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.008502 | houston | N | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.008502 | houston | N | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.008502 | houston | N | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.008502 | houston | N | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.008502 | houston | N | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.008502 | houston | N | -0.0080627 | 0.0063117 | 0.22251 | 0.00048391 | 0.00048391 | houston | N | 0.00048391 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.008814 | houston | N | -0.0077507 | 0.0066237 | 0.22282 | 0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.008814 | houston | N | -0.0077507 | 0.0066237 | 0.22282 | 0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.008814 | houston | N | -0.0077507 | 0.0066237 | 0.22282 | 0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.008814 | houston | N | -0.0077507 | 0.0066237 | 0.22282 | 0.00079591 | 0.00079591 | houston | N | 0.00079591 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.008514 | houston | N | -0.0080507 | 0.0063237 | 0.22252 | 0.00049591 | 0.00049591 | houston | N | 0.00049591 | 0
48820 | SHELLG1_ | 1 | 71 | 0.008338 | houston | N | -0.0082267 | 0.0061477 | 0.22235 | 0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48821 | SHELLG2 | 2 | 72 | 0.008338 | houston | N | -0.0082267 | 0.0061477 | 0.22235 | 0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48822 | SHELLG3_ | 1 | 39 | 0.008338 | houston | N | -0.0082267 | 0.0061477 | 0.22235 | 0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48822 | SHELLG3_ | 2 | 30 | 0.008338 | houston | N | -0.0082267 | 0.0061477 | 0.22235 | 0.00031991 | 0.00031991 | houston | N | 0.00031991 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.008266 | houston | N | -0.0082987 | 0.0060757 | 0.22227 | 0.00024791 | 0.00024791 | houston | N | 0.00024791 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.008266 | houston | N | -0.0082987 | 0.0060757 | 0.22227 | 0.00024791 | 0.00024791 | houston | N | 0.00024791 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.008316 | houston | N | -0.0082487 | 0.0061257 | 0.22232 | 0.00029791 | 0.00029791 | houston | N | 0.00029791 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.008312 | houston | Y | -0.0082527 | 0.0061217 | 0.22232 | 0.00029391 | 0.00029391 | houston | N | 0.00029391 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.008311 | houston | Y | -0.0082537 | 0.0061207 | 0.22232 | 0.00029291 | 0.00029291 | houston | N | 0.00029291 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.008316 | houston | Y | -0.0082487 | 0.0061257 | 0.22232 | 0.00029791 | 0.00029791 | houston | N | 0.00029791 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.008317 | houston | Y | -0.0082477 | 0.0061267 | 0.22232 | 0.00029891 | 0.00029891 | houston | N | 0.00029891 | 0
48855 | SRB_GT21 | B2 | 12 | 0.008311 | houston | Y | -0.0082537 | 0.0061207 | 0.22232 | 0.00029291 | 0.00029291 | houston | N | 0.00029291 | 0
48855 | SRB_GT21 | MB | 18 | 0.008311 | houston | Y | -0.0082537 | 0.0061207 | 0.22232 | 0.00029291 | 0.00029291 | houston | N | 0.00029291 | 0
48865 | TECO_GT1 | 1 | 50 | 0.008037 | houston | Y | -0.0085277 | 0.0058467 | 0.22204 | 1.8912e-05 | 1.8912e-05 | houston | N | 1.8912e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48874 | THW_ST4_ | 4 | 104 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48875 | THW_3132 | A | 54 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48875 | THW_3132 | B | 53 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48877 | THW_3334 | C | 54 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48877 | THW_3334 | D | 57 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48879 | THW_4142 | E | 54 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48879 | THW_4142 | F | 54 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48881 | THW_4344 | G | 58 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48881 | THW_4344 | H | 58 | 0.008439 | houston | Y | -0.0081257 | 0.0062487 | 0.22245 | 0.00042091 | 0.00042091 | houston | N | 0.00042091 | 0
48883 | THW_GT1_ | B2 | 12 | 0.008487 | houston | Y | -0.0080777 | 0.0062967 | 0.22249 | 0.00046891 | 0.00046891 | houston | N | 0.00046891 | 0
48885 | THW_5152 | A | 56 | 0.008596 | houston | Y | -0.0079687 | 0.0064057 | 0.2226 | 0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48885 | THW_5152 | B | 59 | 0.008596 | houston | Y | -0.0079687 | 0.0064057 | 0.2226 | 0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48886 | THW_5354 | C | 56 | 0.008596 | houston | Y | -0.0079687 | 0.0064057 | 0.2226 | 0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48886 | THW_5354 | D | 56 | 0.008596 | houston | Y | -0.0079687 | 0.0064057 | 0.2226 | 0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48887 | THW_5556 | E | 59 | 0.008596 | houston | Y | -0.0079687 | 0.0064057 | 0.2226 | 0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48887 | THW_5556 | F | 56 | 0.008596 | houston | Y | -0.0079687 | 0.0064057 | 0.2226 | 0.00057791 | 0.00057791 | houston | N | 0.00057791 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.006258 | houston | Y | -0.010307 | 0.0040677 | 0.22027 | -0.0017601 | 0.0017601 | houston | N | 0.0017601 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.00775 | houston | Y | -0.0088147 | 0.0055597 | 0.22176 | -0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.00775 | houston | Y | -0.0088147 | 0.0055597 | 0.22176 | -0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.00775 | houston | Y | -0.0088147 | 0.0055597 | 0.22176 | -0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.00775 | houston | Y | -0.0088147 | 0.0055597 | 0.22176 | -0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.00775 | houston | N | -0.0088147 | 0.0055597 | 0.22176 | -0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.007667 | houston | Y | -0.0088977 | 0.0054767 | 0.22167 | -0.00035109 | 0.00035109 | houston | N | 0.00035109 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.007667 | houston | Y | -0.0088977 | 0.0054767 | 0.22167 | -0.00035109 | 0.00035109 | houston | N | 0.00035109 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.007667 | houston | Y | -0.0088977 | 0.0054767 | 0.22167 | -0.00035109 | 0.00035109 | houston | N | 0.00035109 | 0
48929 | WAPGT21_ | B1 | 13 | 0.00775 | houston | Y | -0.0088147 | 0.0055597 | 0.22176 | -0.00026809 | 0.00026809 | houston | N | 0.00026809 | 0
48940 | WARVUE_G | G1 | 12 | 0.008501 | houston | Y | -0.0080637 | 0.0063107 | 0.22251 | 0.00048291 | 0.00048291 | houston | N | 0.00048291 | 0
49803 | EXN_15GT | 1 | 34 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49826 | EXN938GT | 5 | 45.9 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49828 | EXN941GT | 10 | 17.7 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49829 | EXN942GT | 11 | 20.4 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49830 | EXN943GT | 12 | 19.9 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49831 | EXN944GT | 13 | 35 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49832 | EXN945GT | 9 | 18 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49837 | EXN_GT | 4 | 85.4 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49838 | EXN_14GT | 14 | 148 | 0.008462 | houston | N | -0.0081027 | 0.0062717 | 0.22247 | 0.00044391 | 0.00044391 | houston | N | 0.00044391 | 0
49851 | DOW17000 | 37 | 62 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49858 | DOW38100 | 31 | 71.4 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49859 | DOW38200 | 33 | 45 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49860 | DOW38300 | 32 | 101 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49862 | DOW39100 | 36 | 86 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49863 | DOW39200 | 35 | 88 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49865 | DOW41000 | 41 | 50 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49866 | DOW42000 | 42 | 18 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49869 | DOW49000 | 45 | 94 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49870 | DOW61000 | 61 | 70 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49871 | DOW62000 | 62 | 63 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49872 | DOW63000 | 63 | 72 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49873 | DOW64000 | 64 | 64.8 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49876 | DOW65000 | 65 | 101 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49877 | DOW66000 | 66 | 97 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49878 | DOW67000 | 67 | 103 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49882 | DOW81000 | 81 | 76 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49884 | DOW82000 | 82 | 80 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49885 | DOW83000 | 83 | 80 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
49886 | DOW84000 | 84 | 171 | 0.006909 | houston | N | -0.0096557 | 0.0047187 | 0.22092 | -0.0011091 | 0.0011091 | houston | N | 0.0011091 | 0
58909 | PEARSALL | 1 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 2 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 3 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 4 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 5 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58909 | PEARSALL | 6 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 1 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 2 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 3 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 4 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 5 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58919 | PEARSALL | 6 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 1 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 2 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 3 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 4 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 5 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58929 | PEARSALL | 6 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 1 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 2 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 3 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 4 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 5 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
58949 | PEARSALL | 6 | 8.4 | -0.007603 | south | Y | -0.024168 | -0.0097933 | 0.2064 | -0.015621 | 0.0097933 | south | N | 0.0097933 | 0
60000 | DSKY2 | 1 | 76.5 | -0.18684 | west | Y | -0.20341 | -0.18903 | 0.027164 | -0.19486 | 0.027164 | west | N | 0.027164 | 0
60003 | KING_NE1 | 1 | 80 | -0.19187 | west | Y | -0.20844 | -0.19407 | 0.022132 | -0.19989 | 0.022132 | west | N | 0.022132 | 0
60005 | KING_SE1 | 1 | 40 | -0.19187 | west | Y | -0.20844 | -0.19407 | 0.022132 | -0.19989 | 0.022132 | west | N | 0.022132 | 0
60007 | KING_SW1 | 1 | 80 | -0.19262 | west | Y | -0.20919 | -0.19481 | 0.021384 | -0.20064 | 0.021384 | west | N | 0.021384 | 0
60016 | WOODWRD1 | 1 | 80 | -0.19172 | west | Y | -0.20828 | -0.19391 | 0.022287 | -0.19974 | 0.022287 | west | N | 0.022287 | 0
60017 | ORNNWP1 | 1 | 80 | -0.18779 | west | Y | -0.20435 | -0.18998 | 0.026221 | -0.1958 | 0.026221 | west | N | 0.026221 | 0
60018 | DSKY1 | 1 | 84 | -0.1865 | west | Y | -0.20306 | -0.18869 | 0.027507 | -0.19452 | 0.027507 | west | N | 0.027507 | 0
60019 | KING_NW1 | 1 | 80 | -0.19262 | west | Y | -0.20919 | -0.19481 | 0.021384 | -0.20064 | 0.021384 | west | N | 0.021384 | 0
60057 | CALLAHAN | 1 | 114 | 0.000337 | south | Y | -0.016228 | -0.0018533 | 0.21434 | -0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60058 | BUFF_GAP | 1 | 120 | -0.22648 | west | Y | -0.24305 | -0.22868 | -0.012478 | -0.2345 | 0.012478 | west | N | 0.012478 | 0
60060 | CIRELLO | 1 | 233 | -0.22648 | west | Y | -0.24305 | -0.22868 | -0.012478 | -0.2345 | 0.012478 | west | N | 0.012478 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.22648 | west | Y | -0.24305 | -0.22868 | -0.012478 | -0.2345 | 0.012478 | west | N | 0.012478 | 0
60066 | H_HOLLOW | 1 | 222 | 0.000337 | south | Y | -0.016228 | -0.0018533 | 0.21434 | -0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.000337 | south | Y | -0.016228 | -0.0018533 | 0.21434 | -0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.000337 | south | Y | -0.016228 | -0.0018533 | 0.21434 | -0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.000337 | south | Y | -0.016228 | -0.0018533 | 0.21434 | -0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60074 | HORSH5 | 1 | 100 | 0.000337 | south | Y | -0.016228 | -0.0018533 | 0.21434 | -0.0076811 | 0.0018533 | south | N | 0.0018533 | 0
60081 | WHRLWIND | 1 | 60 | -0.18556 | west | Y | -0.20213 | -0.18775 | 0.028446 | -0.19358 | 0.028446 | west | N | 0.028446 | 0
60201 | RIO DRCS | F | 0 | -0.059084 | south | N | -0.075649 | -0.061274 | 0.15492 | -0.067102 | 0.061274 | south | N | 0.061274 | 0
60202 | FRIEND_R | F | 0 | -0.16616 | west | N | -0.18273 | -0.16835 | 0.047845 | -0.17418 | 0.047845 | west | N | 0.047845 | 0
60203 | PRES0A | BT | 4.8 | -0.19563 | west | N | -0.2122 | -0.19782 | 0.018376 | -0.20365 | 0.018376 | west | N | 0.018376 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.23476 | west | Y | -0.25132 | -0.23695 | -0.020749 | -0.24277 | 0.020749 | west | N | 0.020749 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.23476 | west | Y | -0.25132 | -0.23695 | -0.020749 | -0.24277 | 0.020749 | west | N | 0.020749 | 0
71057 | L_SWEETW | W1 | 135 | -0.23476 | west | Y | -0.25132 | -0.23695 | -0.020749 | -0.24277 | 0.020749 | west | N | 0.020749 | 0
71059 | L_SWEETW | W1 | 119 | -0.23476 | west | Y | -0.25132 | -0.23695 | -0.020749 | -0.24277 | 0.020749 | west | N | 0.020749 | 0
71060 | L_SWEETW | W1 | 105 | -0.23476 | west | Y | -0.25132 | -0.23695 | -0.020749 | -0.24277 | 0.020749 | west | N | 0.020749 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.23476 | west | Y | -0.25132 | -0.23695 | -0.020749 | -0.24277 | 0.020749 | west | N | 0.020749 | 0
76031 | L_GASCCR | W1 | 150 | -0.19833 | west | Y | -0.2149 | -0.20052 | 0.015675 | -0.20635 | 0.015675 | west | N | 0.015675 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.19652 | west | Y | -0.21309 | -0.19871 | 0.017483 | -0.20454 | 0.017483 | west | N | 0.017483 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.19652 | west | Y | -0.21309 | -0.19871 | 0.017483 | -0.20454 | 0.017483 | west | N | 0.017483 | 0
76096 | L_CAPRSI | W1 | 186 | -0.19652 | west | Y | -0.21309 | -0.19871 | 0.017483 | -0.20454 | 0.017483 | west | N | 0.017483 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.19652 | west | Y | -0.21309 | -0.19871 | 0.017483 | -0.20454 | 0.017483 | west | N | 0.017483 | 0
80003 | MILHWYS | F | 0 | 0.001907 | south | N | -0.014658 | -0.00028332 | 0.21591 | -0.0061111 | 0.00028332 | south | N | 0.00028332 | 0
80010 | EPLVT1 | F | 0 | -0.035876 | south | N | -0.052441 | -0.038066 | 0.17813 | -0.043894 | 0.038066 | south | N | 0.038066 | 0
80012 | LAR | F | 0 | -0.003177 | south | N | -0.019742 | -0.0053673 | 0.21083 | -0.011195 | 0.0053673 | south | N | 0.0053673 | 0
80051 | FORPVCM0 | 8 | 28 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
80053 | FOR69CG0 | 10 | 74 | 0.003468 | south | N | -0.013097 | 0.0012777 | 0.21748 | -0.0045501 | 0.0012777 | south | N | 0.0012777 | 0
80080 | GWINDT11 | 1 | 94 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80080 | GWINDT11 | 2 | 41 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80080 | GWINDT11 | 3 | 38 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80080 | GWINDT11 | 4 | 19 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 1 | 94 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 2 | 36 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 3 | 43 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80081 | GWINDT21 | 4 | 22 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80137 | CSDR89 | 8 | 39 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80137 | CSDR89 | 9 | 15 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80138 | CSDR7 | 7 | 7 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80139 | CSDR56 | 5 | 15 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80139 | CSDR56 | 6 | 39 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80140 | CSDR11 | 11 | 39 | 0.003113 | south | N | -0.013452 | 0.00092268 | 0.21712 | -0.0049051 | 0.00092268 | south | N | 0.00092268 | 0
80180 | PNSCALT1 | 1 | 148 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80180 | PNSCALT1 | 2 | 50 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80181 | PNSCALT2 | 1 | 55 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80181 | PNSCALT2 | 2 | 50 | 0.001967 | south | Y | -0.014598 | -0.00022332 | 0.21597 | -0.0060511 | 0.00022332 | south | N | 0.00022332 | 0
80223 | REYSHR G | 1 | 12 | 0.002338 | south | N | -0.014227 | 0.00014768 | 0.21635 | -0.0056801 | 0.00014768 | south | N | 0.00014768 | 0
80224 | VISTRONG | 1 | 15 | 0.003035 | south | N | -0.01353 | 0.00084468 | 0.21704 | -0.0049831 | 0.00084468 | south | N | 0.00084468 | 0
80225 | VISTRONG | 2 | 23 | 0.003035 | south | N | -0.01353 | 0.00084468 | 0.21704 | -0.0049831 | 0.00084468 | south | N | 0.00084468 | 0
80226 | ALCOA G | 1 | 48 | 0.003392 | south | N | -0.013173 | 0.0012017 | 0.2174 | -0.0046261 | 0.0012017 | south | N | 0.0012017 | 0
80227 | AIRCO G | 1 | 8 | 0.003059 | south | N | -0.013506 | 0.00086868 | 0.21707 | -0.0049591 | 0.00086868 | south | N | 0.00086868 | 0
80261 | NBEC81A | 1 | 180 | 0.002182 | south | Y | -0.014383 | -8.3152e-06 | 0.21619 | -0.0058361 | 8.3152e-06 | south | N | 8.3152e-06 | 0
80262 | NBEC91A | 1 | 180 | 0.002186 | south | Y | -0.014379 | -4.3152e-06 | 0.21619 | -0.0058321 | 4.3152e-06 | south | N | 4.3152e-06 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.002157 | south | Y | -0.014408 | -3.3315e-05 | 0.21616 | -0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.002157 | south | Y | -0.014408 | -3.3315e-05 | 0.21616 | -0.0058611 | 3.3315e-05 | south | N | 3.3315e-05 | 0
80265 | LARECU40 | 4 | 100 | -0.003174 | south | Y | -0.019739 | -0.0053643 | 0.21083 | -0.011192 | 0.0053643 | south | N | 0.0053643 | 0
80266 | LARECU50 | 5 | 100 | -0.003174 | south | Y | -0.019739 | -0.0053643 | 0.21083 | -0.011192 | 0.0053643 | south | N | 0.0053643 | 0
80291 | PAPALOTE | 1 | 25 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80291 | PAPALOTE | 2 | 25 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80291 | PAPALOTE | 3 | 25 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80291 | PAPALOTE | 4 | 16 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 5 | 25 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 6 | 25 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 7 | 25 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
80294 | PAPALOTE | 8 | 15 | 0.002274 | south | Y | -0.014291 | 8.3685e-05 | 0.21628 | -0.0057441 | 8.3685e-05 | south | N | 8.3685e-05 | 0
86104 | CID-138 | EQ | 0 | -0.003174 | south | N | -0.019739 | -0.0053643 | 0.21083 | -0.011192 | 0.0053643 | south | N | 0.0053643 | 0
86105 | CID-230 | EQ | 500 | -0.003174 | south | N | -0.019739 | -0.0053643 | 0.21083 | -0.011192 | 0.0053643 | south | N | 0.0053643 | 0
86106 | CUF-230 | EQ | 500 | -0.003174 | south | N | -0.019739 | -0.0053643 | 0.21083 | -0.011192 | 0.0053643 | south | N | 0.0053643 | 0
86107 | CUF-138 | EQ | 0 | -0.003174 | south | N | -0.019739 | -0.0053643 | 0.21083 | -0.011192 | 0.0053643 | south | N | 0.0053643 | 0
88198 | BEEVILLE | F | 0 | 0.001311 | south | N | -0.015254 | -0.00087932 | 0.21532 | -0.0067071 | 0.00087932 | south | N | 0.00087932 | 0
88253 | HAMILTON | F | 0 | -0.055041 | south | N | -0.071606 | -0.057231 | 0.15897 | -0.063059 | 0.057231 | south | N | 0.057231 | 0
88299 | ZAPATA | F | 0 | -0.001494 | south | N | -0.018059 | -0.0036843 | 0.21251 | -0.0095121 | 0.0036843 | south | N | 0.0036843 | 0
88508 | FALFURRI | F | 0 | 0.001176 | south | N | -0.015389 | -0.0010143 | 0.21518 | -0.0068421 | 0.0010143 | south | N | 0.0010143 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5248 | 0 | 0.22282 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.375 | 0 | 0.22282 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3574 | 0 | 0.22282 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3574 | 0 | 0.22282 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.008814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4279 | 0 | 0.22282 | 0 | 0 | 0 | West | -0.21401
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658 | 56 | 12.4658 | North | 0.017506
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50716 | 59 | 0.2226 | 13.1336 | 115 | 25.5994 |  | -0.23151
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658 | 171 | 38.0651
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658 | 227 | 50.5309 | Line Rating | 1239.6
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50716 | 59 | 0.2226 | 13.1336 | 286 | 63.6645 | Conc Gen | 2023
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658 | 342 | 76.1303 | Weighted Imp. | 450.2034
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.008572 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.4117 | 398 | 0.22258 | 88.5865 | 740 | 164.7167 | PTDF | 0.22254
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3928 | 0 | 0.22256 | 0 | 740 | 164.7167
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3808 | 0 | 0.22256 | 0 | 740 | 164.7167 | Concentration | -0.96125
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3594 | 0 | 0.22256 | 0 | 740 | 164.7167
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.303 | 0 | 0.22256 | 0 | 740 | 164.7167
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4649 | 172 | 0.22252 | 38.2741 | 912 | 202.9909
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4649 | 172 | 0.22252 | 38.2741 | 1084 | 241.265
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4649 | 172 | 0.22252 | 38.2741 | 1256 | 279.5392
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.008514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3367 | 0 | 0.22252 | 0 | 1256 | 279.5392
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.008502 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.317 | 743 | 0.22251 | 165.3242 | 1999 | 444.8634
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55263 | 0 | 0.22251 | 0 | 1999 | 444.8634
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56113 | 0 | 0.22251 | 0 | 1999 | 444.8634
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59514 | 0 | 0.22251 | 0 | 1999 | 444.8634
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53563 | 0 | 0.22251 | 0 | 1999 | 444.8634
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52712 | 0 | 0.22251 | 0 | 1999 | 444.8634
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.88421 | 0 | 0.22251 | 0 | 1999 | 444.8634
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50162 | 0 | 0.22251 | 0 | 1999 | 444.8634
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.008501 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.10201 | 12 | 0.22251 | 2.6701 | 2011 | 447.5335
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0425 | 0 | 0.22251 | 0 | 2011 | 447.5335
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1785 | 0 | 0.22251 | 0 | 2011 | 447.5335
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.008487 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10184 | 12 | 0.22249 | 2.6699 | 2023 | 450.2034
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28771 | 0 | 0.22247 | 0 | 2023 | 450.2034
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29363 | 0 | 0.22247 | 0 | 2023 | 450.2034
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27671 | 0 | 0.22247 | 0 | 2023 | 450.2034
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38841 | 0 | 0.22247 | 0 | 2023 | 450.2034
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14978 | 0 | 0.22247 | 0 | 2023 | 450.2034
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17262 | 0 | 0.22247 | 0 | 2023 | 450.2034
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16839 | 0 | 0.22247 | 0 | 2023 | 450.2034
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29617 | 0 | 0.22247 | 0 | 2023 | 450.2034
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15232 | 0 | 0.22247 | 0 | 2023 | 450.2034
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72265 | 0 | 0.22247 | 0 | 2023 | 450.2034
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2524 | 0 | 0.22247 | 0 | 2023 | 450.2034
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.008449 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.21 | 735 | 0.22246 | 163.5052
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.87766 | 104 | 0.22245 | 23.1344
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.87766 | 104 | 0.22245 | 23.1344
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.44727 | 53 | 0.22245 | 11.7896
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.48102 | 57 | 0.22245 | 12.6794
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.48946 | 58 | 0.22245 | 12.9019
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.48946 | 58 | 0.22245 | 12.9019
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.008383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4503 | 0 | 0.22239 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.008383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1317 | 0 | 0.22239 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.008373 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1387 | 0 | 0.22238 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35162 | 42 | 0.22238 | 9.3399
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35162 | 42 | 0.22238 | 9.3399
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31814 | 38 | 0.22238 | 8.4504
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31814 | 38 | 0.22238 | 8.4504
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.592 | 0 | 0.22235 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60034 | 0 | 0.22235 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32518 | 0 | 0.22235 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25014 | 0 | 0.22235 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4972 | 0 | 0.22233 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3192 | 0 | 0.22233 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3059 | 0 | 0.22233 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.008317 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8963 | 228 | 0.22232 | 50.6899
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53229 | 0 | 0.22232 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52563 | 0 | 0.22232 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68698 | 0 | 0.22232 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61213 | 0 | 0.22232 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.008316 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13472 | 0 | 0.22232 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.008316 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7713 | 213 | 0.22232 | 47.3548
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2386 | 0 | 0.22232 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54118 | 0 | 0.22232 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.008312 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3715 | 165 | 0.22232 | 36.6826
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.008311 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4046 | 169 | 0.22232 | 37.5718
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.008311 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.099732 | 12 | 0.22232 | 2.6678
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.008311 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22232 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.008297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2904 | 0 | 0.2223 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3511 | 0 | 0.22229 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3006 | 0 | 0.22229 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3039 | 0 | 0.22229 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2998 | 0 | 0.22229 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2271 | 0 | 0.22229 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.64475 | 0 | 0.22227 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66128 | 0 | 0.22227 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3801 | 46 | 0.22227 | 10.2244
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3801 | 46 | 0.22227 | 10.2244
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3801 | 46 | 0.22227 | 10.2244
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45447 | 55 | 0.22227 | 12.2249
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45447 | 55 | 0.22227 | 12.2249
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4462 | 54 | 0.22227 | 12.0026
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.53346 | 0 | 0.22221 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.49242 | 0 | 0.22221 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.53346 | 0 | 0.22221 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.53346 | 0 | 0.22221 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74392 | 0 | 0.22218 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71613 | 0 | 0.22218 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71122 | 0 | 0.22218 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44554 | 0 | 0.22218 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.099735 | 0 | 0.22218 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.008093 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.2221 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.008037 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.40185 | 50 | 0.22204 | 11.1022
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56173 | 0 | 0.22194 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5292 | 0 | 0.22194 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4205 | 0 | 0.22194 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2155 | 0 | 0.22194 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2179 | 0 | 0.22194 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2083 | 0 | 0.22194 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.76166 | 0 | 0.22194 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.9359 | 0 | 0.22194 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31736 | 0 | 0.22194 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25386 | 0 | 0.22194 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23799 | 0 | 0.22194 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79568 | 0 | 0.22194 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73698 | 0 | 0.22194 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.81472 | 0 | 0.22194 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.80917 | 0 | 0.22194 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2477 | 161 | 0.22176 | 35.7029
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2865 | 166 | 0.22176 | 36.8117
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.922 | 248 | 0.22176 | 54.9958
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.00775 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.2315 | 546 | 0.22176 | 121.0794
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.00775 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 4.9832 | 0 | 0.22176 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.00775 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10075 | 13 | 0.22176 | 2.8828
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.007689 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25374 | 0 | 0.2217 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2502 | 0 | 0.22168 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2502 | 0 | 0.22168 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8792 | 0 | 0.22168 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.9912 | 651 | 0.22167 | 144.3098
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.3242 | 564 | 0.22167 | 125.0242
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.6002 | 600 | 0.22167 | 133.0044
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.007625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35151 | 0 | 0.22163 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79909 | 0 | 0.22121 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79909 | 0 | 0.22121 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.85668 | 0 | 0.22121 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.78829 | 0 | 0.22121 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50169 | 0 | 0.22107 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07066 | 0 | 0.22107 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42836 | 0 | 0.22092 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4933 | 0 | 0.22092 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3109 | 0 | 0.22092 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.69781 | 0 | 0.22092 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59417 | 0 | 0.22092 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60799 | 0 | 0.22092 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34545 | 0 | 0.22092 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.12436 | 0 | 0.22092 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.64945 | 0 | 0.22092 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48363 | 0 | 0.22092 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43527 | 0 | 0.22092 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49745 | 0 | 0.22092 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4477 | 0 | 0.22092 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.69781 | 0 | 0.22092 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67017 | 0 | 0.22092 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71163 | 0 | 0.22092 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52508 | 0 | 0.22092 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55272 | 0 | 0.22092 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55272 | 0 | 0.22092 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1814 | 0 | 0.22092 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.006258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41303 | 66 | 0.22027 | 14.5375
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.5386 | 569 | 0.22023 | 125.3086
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6132 | 581 | 0.22023 | 127.9514
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.46786 | 76 | 0.22016 | 16.7324
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.46786 | 76 | 0.22016 | 16.7324
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.64638 | 105 | 0.22016 | 23.1171
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45554 | 74 | 0.22016 | 16.2921
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45554 | 74 | 0.22016 | 16.2921
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62791 | 102 | 0.22016 | 22.4566
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 8.0487 | 0 | 0.22005 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 8.0185 | 0 | 0.22005 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6257 | 584 | 0.2185 | 127.6058
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6751 | 595 | 0.2185 | 130.0093
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.004494 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9459 | 433 | 0.2185 | 94.611
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70278 | 158 | 0.21846 | 34.5159
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71168 | 160 | 0.21846 | 34.9528
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7784 | 175 | 0.21846 | 38.2296
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.62006 | 152.5 | 0.21807 | 33.2561
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60787 | 149.5 | 0.21807 | 32.6019
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.94575 | 232.6 | 0.21807 | 50.7238
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.53341 | 132 | 0.21805 | 28.7823
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.54149 | 134 | 0.21805 | 29.2184
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3052 | 323 | 0.21805 | 70.4295
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15288 | 42 | 0.21765 | 9.1412
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16016 | 44 | 0.21765 | 9.5765
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16016 | 44 | 0.21765 | 9.5765
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.17108 | 47 | 0.21765 | 10.2294
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0785 | 310 | 0.21749 | 67.4207
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.4368 | 413 | 0.21749 | 89.8218
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27397 | 0 | 0.21748 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28091 | 0 | 0.21748 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27397 | 0 | 0.21748 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27744 | 0 | 0.21748 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27189 | 0 | 0.21748 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0867 | 0 | 0.21748 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15953 | 0 | 0.21748 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.097104 | 0 | 0.21748 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1512 | 0 | 0.21748 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.25663 | 0 | 0.21748 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16817 | 49 | 0.21744 | 10.6545
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15787 | 46 | 0.21744 | 10.0022
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15787 | 46 | 0.21744 | 10.0022
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1613 | 47 | 0.21744 | 10.2196
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52853 | 154 | 0.21744 | 33.4856
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50794 | 148 | 0.21744 | 32.181
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16474 | 48 | 0.21744 | 10.4371
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16474 | 48 | 0.21744 | 10.4371
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.003392 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16282 | 0 | 0.2174 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026296 | 0 | 0.21729 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026296 | 0 | 0.21729 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.087164 | 0 | 0.21712 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.021791 | 0 | 0.21712 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12141 | 0 | 0.21712 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.046695 | 0 | 0.21712 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.021791 | 0 | 0.21712 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.046695 | 0 | 0.21712 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12141 | 0 | 0.21712 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12141 | 0 | 0.21712 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.003059 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.024472 | 0 | 0.21707 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.045525 | 0 | 0.21704 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.069805 | 0 | 0.21704 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.00293 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21389 | 0 | 0.21694 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.41083 | 144 | 0.21686 | 31.2279
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53636 | 188 | 0.21686 | 40.7697
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13318 | 47.7 | 0.2168 | 10.3413
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10414 | 37.3 | 0.2168 | 8.0866
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12843 | 46 | 0.2168 | 9.9728
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13402 | 48 | 0.2168 | 10.4064
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.002687 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.032244 | 0 | 0.21669 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.006408 | 0 | 0.21668 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.006408 | 0 | 0.21668 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.002652 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.058344 | 22 | 0.21666 | 4.7665
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029172 | 11 | 0.21666 | 2.3832
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029172 | 11 | 0.21666 | 2.3832
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.56759 | 223.9 | 0.21654 | 48.4838
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57037 | 225 | 0.21654 | 48.722
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.56936 | 224.6 | 0.21654 | 48.6354
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57468 | 226.7 | 0.21654 | 49.0901
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33285 | 142 | 0.21635 | 30.7219
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33988 | 145 | 0.21635 | 31.3709
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.35394 | 151 | 0.21635 | 32.669
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.67976 | 290 | 0.21635 | 62.7418
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3694 | 0 | 0.21635 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.35771 | 0 | 0.21635 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.2338 | 0 | 0.21635 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.33901 | 0 | 0.21635 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.34369 | 0 | 0.21635 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.29693 | 0 | 0.21635 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.002338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.028056 | 0 | 0.21635 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0056088 | 0 | 0.21634 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0056088 | 0 | 0.21634 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0065436 | 0 | 0.21634 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 25 | 0.21628 | 5.407
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 25 | 0.21628 | 5.407
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 25 | 0.21628 | 5.407
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.036384 | 16 | 0.21628 | 3.4605
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 25 | 0.21628 | 5.407
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 25 | 0.21628 | 5.407
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 25 | 0.21628 | 5.407
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.03411 | 15 | 0.21628 | 3.2442
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.002193 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3794 | 629 | 0.2162 | 135.9898
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7345 | 336 | 0.21619 | 72.6409
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39348 | 180 | 0.21619 | 38.9148
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.32404 | 0 | 0.21619 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.32469 | 0 | 0.21619 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.33431 | 0 | 0.21619 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39276 | 180 | 0.21619 | 38.914
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.72044 | 334 | 0.21616 | 72.1988
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73338 | 340 | 0.21616 | 73.4958
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38826 | 180 | 0.21616 | 38.9095
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38826 | 180 | 0.21616 | 38.9095
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31561 | 147 | 0.21615 | 31.7746
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29629 | 138 | 0.21615 | 29.8293
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.30058 | 140 | 0.21615 | 30.2616
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31561 | 147 | 0.21615 | 31.7746
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39075 | 182 | 0.21615 | 39.34
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42511 | 198 | 0.21615 | 42.7985
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.053475 | 0 | 0.21615 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.053475 | 0 | 0.21615 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.002137 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.081206 | 0 | 0.21614 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.002119 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.080522 | 0 | 0.21613 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002052 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.012312 | 0 | 0.21606 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002041 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.059189 | 0 | 0.21605 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002018 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008072 | 0 | 0.21603 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1849 | 94 | 0.21597 | 20.3016
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.080647 | 41 | 0.21597 | 8.8549
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.074746 | 38 | 0.21597 | 8.207
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.037373 | 19 | 0.21597 | 4.1035
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1849 | 94 | 0.21597 | 20.3016
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070812 | 36 | 0.21597 | 7.7751
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.084581 | 43 | 0.21597 | 9.2869
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.043274 | 22 | 0.21597 | 4.7514
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.29112 | 148 | 0.21597 | 31.9642
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09835 | 50 | 0.21597 | 10.7987
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10819 | 55 | 0.21597 | 11.8786
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09835 | 50 | 0.21597 | 10.7987
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.001907 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21591 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.072466 | 38 | 0.21591 | 8.2047
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.036805 | 19.3 | 0.21591 | 4.1671
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.028605 | 15 | 0.21591 | 3.2387
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.001907 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.089629 | 47 | 0.21591 | 10.148
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25258 | 144 | 0.21576 | 31.0696
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25258 | 144 | 0.21576 | 31.0696
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29993 | 171 | 0.21576 | 36.8951
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36308 | 207 | 0.21576 | 44.6625
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38009 | 216.7 | 0.21576 | 46.7554
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42447 | 242 | 0.21576 | 52.2142
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.87196 | 546 | 0.2156 | 117.7198
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1978 | 750 | 0.2156 | 161.7031
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2196 | 146.5 | 0.21551 | 31.5716
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2217 | 147.9 | 0.21551 | 31.8733
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25933 | 173 | 0.21551 | 37.2826
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22925 | 155 | 0.21549 | 33.4003
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25143 | 170 | 0.21549 | 36.6326
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22925 | 155 | 0.21549 | 33.4003
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21541 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21541 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21541 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001311 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21532 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04347 | 0 | 0.21525 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.042228 | 0 | 0.21525 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04347 | 0 | 0.21525 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001176 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21518 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.48633 | 424 | 0.21515 | 91.2253
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.48747 | 425 | 0.21515 | 91.4405
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.44743 | 412 | 0.21509 | 88.6183
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.4344 | 400 | 0.21509 | 86.0372
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.22656 | 209 | 0.21509 | 44.954
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23414 | 216 | 0.21509 | 46.4597
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.049864 | 46 | 0.21509 | 9.8942
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.050948 | 47 | 0.21509 | 10.1093
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.049864 | 46 | 0.21509 | 9.8942
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.049864 | 46 | 0.21509 | 9.8942
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.41501 | 396 | 0.21506 | 85.1618
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000964 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.39235 | 407 | 0.21497 | 87.4932
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.035786 | 58 | 0.21462 | 12.4482
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.054913 | 89 | 0.21462 | 19.1015
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.027148 | 44 | 0.21462 | 9.4435
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.027148 | 44 | 0.21462 | 9.4435
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.026531 | 43 | 0.21462 | 9.2288
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.027765 | 45 | 0.21462 | 9.6581
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.038418 | 114 | 0.21434 | 24.4352
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.074814 | 222 | 0.21434 | 47.5844
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.062008 | 184 | 0.21434 | 39.4393
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.075488 | 224 | 0.21434 | 48.0131
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.038755 | 115 | 0.21434 | 24.6496
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21401 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21401 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00036 | 0 | 0.21398 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00033 | 0 | 0.21398 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00036 | 0 | 0.21398 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001494 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21251 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3174 | 100 | 0.21083 | 21.0833
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3174 | 100 | 0.21083 | 21.0833
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.003177 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.059364 | 0 | 0.21071 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.059364 | 0 | 0.21071 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13434 | 0 | 0.20921 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13914 | 0 | 0.20921 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.0053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2366 | 422 | 0.20871 | 88.0744
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10174 | 0 | 0.20836 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10174 | 0 | 0.20836 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.08478 | 0 | 0.20836 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006121 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1469 | 24 | 0.20789 | 4.9893
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.1469 | 24 | 0.20789 | 4.9893
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.14078 | 23 | 0.20789 | 4.7814
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.00796 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10905 | 0 | 0.20605 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.035876 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.17813 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.039493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23696 | 0 | 0.17451 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8164 | 0 | 0.15897 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.376 | 0 | 0.15897 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.055041 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15897 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.057392 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.0055 | 366 | 0.039886 | 14.5984
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7522 | 20 | 0.020104 | 0.40209
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7522 | 20 | 0.020104 | 0.40209
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7522 | 20 | 0.020104 | 0.40209
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.63937 | 17 | 0.020104 | 0.34177
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5402 | 204 | 0.019456 | 3.9691
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4294 | 201 | 0.019456 | 3.9107
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.9448 | 242 | 0.019456 | 4.7084
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3588 | 60 | 0.0051403 | 0.30842
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4267 | 63 | 0.0051403 | 0.32384
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0043593 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.021865 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0043593 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0043593 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.021754 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.4473 | 112.5 | 0.0042483 | 0.47793
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.019856 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0023503 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.77524 | 0 | 0.0018753 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.77524 | 0 | 0.0018753 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.019332 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0018263 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.01925 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.2725 | 170 | 0.0017443 | 0.29653
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.01925 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.01 | 520 | 0.0017443 | 0.90702
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.019084 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.0611 | 370 | 0.0015783 | 0.58396
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6718 | 0 | 0.0015783 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6908 | 0 | 0.0015783 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.897 | 0 | 0.0015783 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.729 | 0 | 0.0015783 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.7481 | 0 | 0.0015783 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.916 | 0 | 0.0015783 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0421 | 160 | 0.0015073 | 0.24116
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.966 | 156 | 0.0015073 | 0.23514
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7265 | 196 | 0.0015073 | 0.29543
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.966 | 156 | 0.0015073 | 0.23514
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.985 | 157 | 0.0015073 | 0.23664
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7646 | 198 | 0.0015073 | 0.29844
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4227 | 0 | 0.0014633 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5099 | 0 | 0.0014633 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.6769 | 0 | 0.0014633 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.5373 | 558 | 0.0013783 | 0.76908
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.9338 | 579 | 0.0013783 | 0.79802
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 15.2583 | 808 | 0.0013783 | 1.1136
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.4138 | 288 | 0.0012923 | 0.37218
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7633 | 147 | 0.0012923 | 0.18996
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7633 | 147 | 0.0012923 | 0.18996
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4654 | 79 | 0.0010433 | 0.082419
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9662 | 106 | 0.0010433 | 0.11059
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7082 | 146 | 0.0010433 | 0.15232
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.018549 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4097 | 76 | 0.0010433 | 0.079289
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.46168 | 25 | 0.00096128 | 0.024032
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.75715 | 41 | 0.00096128 | 0.039412
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.018466 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.36932 | 20 | 0.00096028 | 0.019206
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.018459 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.73836 | 40 | 0.00095328 | 0.038131
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.018377 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.2589 | 395 | 0.00087128 | 0.34415
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.018377 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.994 | 435 | 0.00087128 | 0.37901
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.018366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.9892 | 435 | 0.00086028 | 0.37422
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.018068 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.0104 | 388 | 0.00056228 | 0.21816
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.018068 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.305 | 515 | 0.00056228 | 0.28957
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 161 | 0.00047628 | 0.076681
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.949 | 164 | 0.00047628 | 0.078109
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.949 | 164 | 0.00047628 | 0.078109
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4445 | 414 | 0.00047628 | 0.19718
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9131 | 162 | 0.00047628 | 0.077157
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 161 | 0.00047628 | 0.076681
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9311 | 163 | 0.00047628 | 0.077633
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3546 | 409 | 0.00047628 | 0.1948
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00043228 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00043228 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0717 | 118 | 5.1277e-05 | 0.0060507
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017557 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0191 | 115 | 5.1277e-05 | 0.0058969
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.7617 | 556 | 5.1277e-05 | 0.02851
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1535 | 785 | -0.00074972 | -0.58853
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.321 | 795 | -0.00074972 | -0.59603
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.0697 | 780 | -0.00074972 | -0.58478
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4553 | 0 | -0.00091572 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.1567 | 0 | -0.00091572 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4055 | 0 | -0.00091572 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.6194 | 0 | -0.00091572 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.016465 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.9845 | 242 | -0.0010407 | -0.25185
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.01645 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0010557 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.016434 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.8217 | 50 | -0.0010717 | -0.053586
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.9861 | 182 | -0.0010987 | -0.19997
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.941 | 484 | -0.0010987 | -0.53178
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5091 | 216.4 | -0.0012897 | -0.2791
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5043 | 216.1 | -0.0012897 | -0.27871
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1064 | 196 | -0.0016567 | -0.32472
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7592 | 111 | -0.0016567 | -0.1839
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.015721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.5215 | 224 | -0.0017847 | -0.39978
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4321 | 224 | -0.0021837 | -0.48915
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4628 | 226 | -0.0021837 | -0.49352
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2483 | 212 | -0.0021837 | -0.46295
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2329 | 211 | -0.0021837 | -0.46077
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2772 | 151.5 | -0.0024747 | -0.37492
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2892 | 152.3 | -0.0024747 | -0.3769
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.668 | 177.5 | -0.0024747 | -0.43926
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2561 | 150.7 | -0.0025347 | -0.38198
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2606 | 151 | -0.0025347 | -0.38274
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6559 | 177.4 | -0.0025347 | -0.44966
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.0374 | 615 | -0.0028107 | -1.7286
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.626 | 587 | -0.0028107 | -1.6499
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2477 | 18 | -0.0037447 | -0.067405
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2477 | 18 | -0.0037447 | -0.067405
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.52292 | 38 | -0.0037447 | -0.1423
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.013748 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0037577 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.013587 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.6304 | 120 | -0.0039187 | -0.47025
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.8941 | 827 | -0.0043327 | -3.5832
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.7887 | 819 | -0.0043327 | -3.5485
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.7927 | 855 | -0.0048827 | -4.1747
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.7927 | 855 | -0.0048827 | -4.1747
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9225 | 152.3 | -0.0048827 | -0.74364
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9313 | 153 | -0.0048827 | -0.74706
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8949 | 168 | -0.0062267 | -1.0461
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0151 | 90 | -0.0062267 | -0.56041
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.011251 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.2092 | 463 | -0.0062547 | -2.8959
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.011239 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19106 | 17 | -0.0062667 | -0.10653
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.01123 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.35936 | 0 | -0.0062757 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5376 | 48 | -0.0063057 | -0.30267
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5152 | 46 | -0.0063057 | -0.29006
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.0112 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.176 | 105 | -0.0063057 | -0.6621
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.010958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0065477 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.010958 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.6239 | 787 | -0.0065477 | -5.1531
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.6709 | 0 | -0.0066697 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.6904 | 0 | -0.0066697 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.6904 | 0 | -0.0066697 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.1177 | 0 | -0.0066697 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.73129 | 70 | -0.0070587 | -0.49411
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72084 | 69 | -0.0070587 | -0.48705
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72084 | 69 | -0.0070587 | -0.48705
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.7104 | 68 | -0.0070587 | -0.47999
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070997 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070997 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2351 | 217.3 | -0.0072197 | -1.5688
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.1086 | 205 | -0.0072197 | -1.48
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8019 | 272.4 | -0.0072197 | -1.9667
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.009989 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5472 | 255 | -0.0075167 | -1.9168
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4884 | 149 | -0.0075167 | -1.12
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5283 | 153 | -0.0075167 | -1.1501
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14352 | 0 | -0.0079377 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14352 | 0 | -0.0079377 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3845 | 150 | -0.0082757 | -1.2414
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7384 | 80 | -0.0082757 | -0.66206
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | 10.6201 | 0 | -0.0083267 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | 10.6293 | 0 | -0.0083267 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.098472 | 0 | -0.0092997 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.098472 | 0 | -0.0092997 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.006188 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.45172 | 73 | -0.011318 | -0.82619
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.73637 | 119 | -0.011318 | -1.3468
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.2685 | 205 | -0.011318 | -2.3201
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.63118 | 102 | -0.011318 | -1.1544
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.59405 | 96 | -0.011318 | -1.0865
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0337 | 100 | -0.017169 | -1.7169
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.017506 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.017506 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.02441 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.4646 | 60 | -0.041916 | -2.5149
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.059084 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.07659 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.14784 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.176 | 150 | -0.16535 | -24.8019
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.16616 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.18367 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.1867 | 209 | -0.19065 | -39.8454
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.9025 | 126.5 | -0.19065 | -24.1169
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -43.1124 | 249 | -0.19065 | -47.4713
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.109 | 197 | -0.19065 | -37.5576
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.18556 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1337 | 60 | -0.20307 | -12.184
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.1865 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.666 | 84 | -0.20401 | -17.1365
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.18684 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2935 | 76.5 | -0.20435 | -15.6327
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.18779 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.0229 | 80 | -0.20529 | -16.4233
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.1889 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.3358 | 150 | -0.20641 | -30.9616
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.7394 | 150 | -0.2091 | -31.3653
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.7394 | 150 | -0.2091 | -31.3653
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.1917 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3358 | 80 | -0.2092 | -16.7362
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19172 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3376 | 80 | -0.20923 | -16.7381
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.3906 | 75 | -0.20938 | -15.7036
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.35 | 80 | -0.20938 | -16.7505
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.675 | 40 | -0.20938 | -8.3752
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.4098 | 80 | -0.21013 | -16.8103
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.4098 | 80 | -0.21013 | -16.8103
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.19563 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.93903 | 0 | -0.21314 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.109 | 112.5 | -0.21403 | -24.0783
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.3803 | 149.5 | -0.21403 | -31.9974
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.5535 | 186 | -0.21403 | -39.8095
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.1544 | 214.5 | -0.21403 | -45.9094
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.19833 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.7498 | 150 | -0.21584 | -32.3757
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.1991 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.7243 | 84 | -0.2166 | -18.1948
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3205 | 6.6 | -0.21758 | -1.436
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8626 | 34.3 | -0.21758 | -7.4631
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.9409 | 99 | -0.21893 | -21.6739
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.2868 | 61 | -0.21893 | -13.3547
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | -5.0356 | 0 | -0.21893 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | -9.205 | 0 | -0.21893 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | -9.205 | 0 | -0.21893 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.4142 | 141 | -0.21902 | -30.8825
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.1823 | 120 | -0.21902 | -26.283
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.4585 | 180 | -0.22005 | -39.6095
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.4585 | 180 | -0.22005 | -39.6095
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | -45.578 | 225 | -0.22007 | -49.5168
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.762 | 63 | -0.22008 | -13.8649
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.095 | 35 | -0.22022 | -7.7077
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.0815 | 30 | -0.22022 | -6.6066
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.3814 | 66 | -0.22025 | -14.5368
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.1787 | 65 | -0.22025 | -14.3166
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5842 | 67 | -0.22025 | -14.7571
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5842 | 67 | -0.22025 | -14.7571
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5842 | 67 | -0.22025 | -14.7571
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.20275 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.22025 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.20275 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.22025 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.20276 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.2109 | 149 | -0.22026 | -32.8193
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.20284 | west | 8 | N | N | Nwest | Nwest | 1 | -5.2332 | 0 | -0.22034 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.20327 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.3926 | 120 | -0.22078 | -26.4933
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.20355 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.4259 | 120 | -0.22105 | -26.5266
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.204 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.5022 | 100.5 | -0.22151 | -22.2615
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.20414 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8401 | 58 | -0.22164 | -12.8554
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.20435 | west | 6 | Y | N | Ywest | Nwest | 1 | -43.7716 | 214.2 | -0.22185 | -47.5213
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -42.6866 | 208.2 | -0.22253 | -46.3313
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -29.1343 | 142.1 | -0.22253 | -31.6219
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -27.1456 | 132.4 | -0.22253 | -29.4633
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -27.8837 | 136 | -0.22253 | -30.2645
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -30.139 | 147 | -0.22253 | -32.7123
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -43.0557 | 210 | -0.22253 | -46.7319
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.3534 | 70 | -0.22255 | -15.5788
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.3534 | 70 | -0.22255 | -15.5788
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.0285 | 92.8 | -0.22255 | -20.6531
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.4039 | 80 | -0.22255 | -17.8044
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.4039 | 80 | -0.22255 | -17.8044
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -23.5806 | 115 | -0.22255 | -25.5938
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5724 | 66 | -0.22315 | -14.7277
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -14.1893 | 69 | -0.22315 | -15.3972
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -14.1893 | 69 | -0.22315 | -15.3972
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.778 | 67 | -0.22315 | -14.9509
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.778 | 67 | -0.22315 | -14.9509
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.3667 | 65 | -0.22315 | -14.5046
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | -14.4657 | 0 | -0.22416 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | -15.1683 | 0 | -0.22416 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | -14.5484 | 0 | -0.22416 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.0598 | 150 | -0.22457 | -33.6856
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -45.5543 | 220 | -0.22457 | -49.4056
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -41.413 | 200 | -0.22457 | -44.9141
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.2412 | 121.9 | -0.22457 | -27.3752
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.1072 | 150 | -0.22489 | -33.733
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.9455 | 101 | -0.22489 | -22.7136
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.21461 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.3764 | 169.5 | -0.23212 | -39.3436
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6724 | 125 | -0.23888 | -29.8606
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6724 | 125 | -0.23888 | -29.8606
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.1782 | 120 | -0.24399 | -29.2789
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | -52.771 | 233 | -0.24399 | -56.8498
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.5477 | 170.2 | -0.24399 | -41.5272
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8034 | 37.5 | -0.25226 | -9.4598
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.2363 | 107.5 | -0.25226 | -27.1181
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.6921 | 135 | -0.25226 | -34.0553
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.936 | 119 | -0.25226 | -30.0191
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.6494 | 105 | -0.25226 | -26.4875
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.8979 | 80.5 | -0.25226 | -20.3071
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.24757 | west | 4 | Y | N | Ywest | Nwest | 1 | -160.8469 | 649.7 | -0.26508 | -172.2203
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.32331 | west | 6 | Y | N | Ywest | Nwest | 1 | -129.322 | 400 | -0.34081 | -136.3243
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.32518 | west | 6 | Y | N | Ywest | Nwest | 1 | -76.7427 | 236 | -0.34269 | -80.8741
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.47336 | west | 6 | Y | N | Ywest | Nwest | 1 | -78.1036 | 165 | -0.49086 | -80.992

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:1430 GRHAMES - 1442 COKFIELD C: 1425 FISHRDSS - 6100 OKLA7A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.47336 | west | 6 | Y | N | Ywest | Nwest | 1 | -78.1036 | 0 | -0.49086 | 0 | 0 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.32518 | west | 6 | Y | N | Ywest | Nwest | 1 | -76.7427 | 0 | -0.34269 | 0 | 0 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.32331 | west | 6 | Y | N | Ywest | Nwest | 1 | -129.322 | 0 | -0.34081 | 0 | 0 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.24757 | west | 4 | Y | N | Ywest | Nwest | 1 | -160.8469 | 0 | -0.26508 | 0 | 0 | 0 | Weighted Shift Factors
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8034 | 0 | -0.25226 | 0 | 0 | 0 | West | -0.21401
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.2363 | 0 | -0.25226 | 0 | 0 | 0 | North | 0.017506
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.6921 | 0 | -0.25226 | 0 | 0 | 0 |  | -0.23151
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.936 | 0 | -0.25226 | 0 | 0 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.6494 | 0 | -0.25226 | 0 | 0 | 0 | Line Rating | 1239.6
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.23476 | west | 6 | Y | N | Ywest | Nwest | 1 | -18.8979 | 0 | -0.25226 | 0 | 0 | 0 | Conc Gen | 2410.5
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.1782 | 0 | -0.24399 | 0 | 0 | 0 | Weighted Imp. | 495.3646
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | -52.771 | 0 | -0.24399 | 0 | 0 | 0 | PTDF | 0.2055
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.22648 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.5477 | 0 | -0.24399 | 0 | 0 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6724 | 0 | -0.23888 | 0 | 0 | 0 | Concentration | -0.88765
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.22138 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6724 | 0 | -0.23888 | 0 | 0 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.21461 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.3764 | 0 | -0.23212 | 0 | 0 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.1072 | 0 | -0.22489 | 0 | 0 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.20738 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.9455 | 0 | -0.22489 | 0 | 0 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -31.0598 | 0 | -0.22457 | 0 | 0 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -45.5543 | 0 | -0.22457 | 0 | 0 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -41.413 | 0 | -0.22457 | 0 | 0 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.20706 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.2412 | 0 | -0.22457 | 0 | 0 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | -14.4657 | 0 | -0.22416 | 0 | 0 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | -15.1683 | 0 | -0.22416 | 0 | 0 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.20665 | west | 8 | N | N | Nwest | Nwest | 1 | -14.5484 | 0 | -0.22416 | 0 | 0 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5724 | 66 | -0.22315 | -14.7277 | 66 | 14.7277
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -14.1893 | 69 | -0.22315 | -15.3972 | 135 | 30.1249
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -14.1893 | 69 | -0.22315 | -15.3972 | 204 | 45.5221
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.778 | 67 | -0.22315 | -14.9509 | 271 | 60.473
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.778 | 67 | -0.22315 | -14.9509 | 338 | 75.4239
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.20564 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.3667 | 65 | -0.22315 | -14.5046 | 403 | 89.9285
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.3534 | 70 | -0.22255 | -15.5788 | 473 | 105.5074
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -14.3534 | 70 | -0.22255 | -15.5788 | 543 | 121.0862
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.0285 | 92.8 | -0.22255 | -20.6531 | 635.8 | 141.7393
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.4039 | 80 | -0.22255 | -17.8044 | 715.8 | 159.5436
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -16.4039 | 80 | -0.22255 | -17.8044 | 795.8 | 177.348
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.20505 | west | 9 | Y | Y | Ywest | Ywest | 1 | -23.5806 | 115 | -0.22255 | -25.5938 | 910.8 | 202.9418
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -42.6866 | 208.2 | -0.22253 | -46.3313 | 1119 | 249.2731
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -29.1343 | 142.1 | -0.22253 | -31.6219 | 1261.1 | 280.895
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -27.1456 | 132.4 | -0.22253 | -29.4633 | 1393.5 | 310.3584
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -27.8837 | 136 | -0.22253 | -30.2645 | 1529.5 | 340.6228
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -30.139 | 147 | -0.22253 | -32.7123 | 1676.5 | 373.3351
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.20503 | west | 9 | Y | Y | Ywest | Ywest | 1 | -43.0557 | 210 | -0.22253 | -46.7319 | 1886.5 | 420.067
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.20435 | west | 6 | Y | N | Ywest | Nwest | 1 | -43.7716 | 0 | -0.22185 | 0 | 1886.5 | 420.067
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.20414 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8401 | 0 | -0.22164 | 0 | 1886.5 | 420.067
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.204 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.5022 | 0 | -0.22151 | 0 | 1886.5 | 420.067
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.20355 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.4259 | 0 | -0.22105 | 0 | 1886.5 | 420.067
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.20327 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.3926 | 0 | -0.22078 | 0 | 1886.5 | 420.067
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.20284 | west | 8 | N | N | Nwest | Nwest | 1 | -5.2332 | 0 | -0.22034 | 0 | 1886.5 | 420.067
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.20276 | west | 6 | Y | N | Ywest | Nwest | 1 | -30.2109 | 0 | -0.22026 | 0 | 1886.5 | 420.067
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.3814 | 66 | -0.22025 | -14.5368 | 1952.5 | 434.6038
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.1787 | 65 | -0.22025 | -14.3166 | 2017.5 | 448.9204
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5842 | 67 | -0.22025 | -14.7571 | 2084.5 | 463.6774
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5842 | 67 | -0.22025 | -14.7571 | 2151.5 | 478.4345
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.20275 | west | 13 | Y | Y | Ywest | Ywest | 1 | -13.5842 | 67 | -0.22025 | -14.7571 | 2218.5 | 493.1916
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.20275 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.22025 | 0 | 2218.5 | 493.1916
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.20275 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.22025 | 0 | 2218.5 | 493.1916
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.095 | 0 | -0.22022 | 0 | 2218.5 | 493.1916
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.20272 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.0815 | 0 | -0.22022 | 0 | 2218.5 | 493.1916
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.762 | 0 | -0.22008 | 0 | 2218.5 | 493.1916
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.20257 | west | 6 | Y | N | Ywest | Nwest | 1 | -45.578 | 0 | -0.22007 | 0 | 2218.5 | 493.1916
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.4585 | 0 | -0.22005 | 0 | 2218.5 | 493.1916
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.20255 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.4585 | 0 | -0.22005 | 0 | 2218.5 | 493.1916
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.4142 | 0 | -0.21902 | 0 | 2218.5 | 493.1916
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.20152 | west | 6 | Y | N | Ywest | Nwest | 1 | -24.1823 | 0 | -0.21902 | 0 | 2218.5 | 493.1916
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.9409 | 0 | -0.21893 | 0 | 2218.5 | 493.1916
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.20142 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.2868 | 0 | -0.21893 | 0 | 2218.5 | 493.1916
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | -5.0356 | 0 | -0.21893 | 0 | 2218.5 | 493.1916
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | -9.205 | 0 | -0.21893 | 0 | 2218.5 | 493.1916
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.20142 | west | 7 | N | N | Nwest | Nwest | 1 | -9.205 | 0 | -0.21893 | 0 | 2218.5 | 493.1916
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3205 | 0 | -0.21758 | 0 | 2218.5 | 493.1916
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.20008 | west | 6 | Y | N | Ywest | Nwest | 1 | -6.8626 | 0 | -0.21758 | 0 | 2218.5 | 493.1916
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.1991 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.7243 | 0 | -0.2166 | 0 | 2218.5 | 493.1916
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.19833 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.7498 | 0 | -0.21584 | 0 | 2218.5 | 493.1916
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.109 | 0 | -0.21403 | 0 | 2218.5 | 493.1916
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.3803 | 0 | -0.21403 | 0 | 2218.5 | 493.1916
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.5535 | 0 | -0.21403 | 0 | 2218.5 | 493.1916
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.19652 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.1544 | 0 | -0.21403 | 0 | 2218.5 | 493.1916
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.19563 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.93903 | 0 | -0.21314 | 0 | 2218.5 | 493.1916
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.4098 | 0 | -0.21013 | 0 | 2218.5 | 493.1916
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19262 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.4098 | 0 | -0.21013 | 0 | 2218.5 | 493.1916
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.3906 | 0 | -0.20938 | 0 | 2218.5 | 493.1916
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.35 | 0 | -0.20938 | 0 | 2218.5 | 493.1916
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.19187 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.675 | 0 | -0.20938 | 0 | 2218.5 | 493.1916
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.19172 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3376 | 0 | -0.20923 | 0 | 2218.5 | 493.1916
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.1917 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.3358 | 0 | -0.2092 | 0 | 2218.5 | 493.1916
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.7394 | 0 | -0.2091 | 0 | 2218.5 | 493.1916
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.1916 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.7394 | 0 | -0.2091 | 0 | 2218.5 | 493.1916
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.1889 | west | 6 | Y | N | Ywest | Nwest | 1 | -28.3358 | 0 | -0.20641 | 0 | 2218.5 | 493.1916
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.18779 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.0229 | 0 | -0.20529 | 0 | 2218.5 | 493.1916
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.18684 | west | 6 | Y | N | Ywest | Nwest | 1 | -14.2935 | 0 | -0.20435 | 0 | 2218.5 | 493.1916
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.1865 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.666 | 0 | -0.20401 | 0 | 2218.5 | 493.1916
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.18556 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.1337 | 0 | -0.20307 | 0 | 2218.5 | 493.1916
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.1867 | 0 | -0.19065 | 0 | 2218.5 | 493.1916
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.9025 | 0 | -0.19065 | 0 | 2218.5 | 493.1916
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -43.1124 | 0 | -0.19065 | 0 | 2218.5 | 493.1916
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.17314 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.109 | 0 | -0.19065 | 0 | 2218.5 | 493.1916
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.16616 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.18367 | 0 | 2218.5 | 493.1916
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.14784 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.176 | 0 | -0.16535 | 0 | 2218.5 | 493.1916
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.059084 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.07659 | 0 | 2218.5 | 493.1916
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.02441 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.4646 | 0 | -0.041916 | 0 | 2218.5 | 493.1916
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.017506 | 0 | 2218.5 | 493.1916
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.017506 | 0 | 2218.5 | 493.1916
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0337 | 0 | -0.017169 | 0 | 2218.5 | 493.1916
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.006188 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.45172 | 73 | -0.011318 | -0.82619 | 2291.5 | 494.0178
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.73637 | 119 | -0.011318 | -1.3468 | 2410.5 | 495.3646
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.006188 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.2685 | 205 | -0.011318 | -2.3201
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.63118 | 102 | -0.011318 | -1.1544
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.006188 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.59405 | 96 | -0.011318 | -1.0865
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.098472 | 0 | -0.0092997 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.008206 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.098472 | 0 | -0.0092997 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | 10.6201 | 0 | -0.0083267 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.009179 | north | 3 | N | N | Nnorth | Nnorth | 1 | 10.6293 | 0 | -0.0083267 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3845 | 150 | -0.0082757 | -1.2414
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.00923 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.7384 | 80 | -0.0082757 | -0.66206
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14352 | 0 | -0.0079377 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.009568 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14352 | 0 | -0.0079377 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.009989 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5472 | 255 | -0.0075167 | -1.9168
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4884 | 149 | -0.0075167 | -1.12
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.009989 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.5283 | 153 | -0.0075167 | -1.1501
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2351 | 217.3 | -0.0072197 | -1.5688
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.1086 | 205 | -0.0072197 | -1.48
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.010286 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8019 | 272.4 | -0.0072197 | -1.9667
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070997 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.010406 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0070997 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.73129 | 70 | -0.0070587 | -0.49411
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72084 | 69 | -0.0070587 | -0.48705
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72084 | 69 | -0.0070587 | -0.48705
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.010447 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.7104 | 68 | -0.0070587 | -0.47999
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.6709 | 0 | -0.0066697 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.6904 | 0 | -0.0066697 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.6904 | 0 | -0.0066697 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.010836 | north | 1 | N | N | Nnorth | Nnorth | 1 | 4.1177 | 0 | -0.0066697 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.010958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0065477 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.010958 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.6239 | 787 | -0.0065477 | -5.1531
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5376 | 48 | -0.0063057 | -0.30267
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.0112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.5152 | 46 | -0.0063057 | -0.29006
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.0112 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.176 | 105 | -0.0063057 | -0.6621
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.01123 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.35936 | 0 | -0.0062757 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.011239 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19106 | 17 | -0.0062667 | -0.10653
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.011239 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0062667 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.011251 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 5.2092 | 0 | -0.0062547 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8949 | 168 | -0.0062267 | -1.0461
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.011279 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0151 | 90 | -0.0062267 | -0.56041
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.7927 | 0 | -0.0048827 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.7927 | 0 | -0.0048827 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9225 | 0 | -0.0048827 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.012623 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.9313 | 0 | -0.0048827 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.8941 | 0 | -0.0043327 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.013173 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.7887 | 0 | -0.0043327 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.013587 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.6304 | 0 | -0.0039187 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.013748 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0037577 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2477 | 18 | -0.0037447 | -0.067405
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2477 | 18 | -0.0037447 | -0.067405
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.013761 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.52292 | 38 | -0.0037447 | -0.1423
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.0374 | 0 | -0.0028107 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.014695 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 8.626 | 0 | -0.0028107 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2561 | 150.7 | -0.0025347 | -0.38198
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2606 | 151 | -0.0025347 | -0.38274
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.014971 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6559 | 177.4 | -0.0025347 | -0.44966
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2772 | 151.5 | -0.0024747 | -0.37492
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2892 | 152.3 | -0.0024747 | -0.3769
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.015031 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.668 | 177.5 | -0.0024747 | -0.43926
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4321 | 224 | -0.0021837 | -0.48915
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4628 | 226 | -0.0021837 | -0.49352
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2483 | 212 | -0.0021837 | -0.46295
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.015322 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2329 | 211 | -0.0021837 | -0.46077
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.015721 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.5215 | 224 | -0.0017847 | -0.39978
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1064 | 196 | -0.0016567 | -0.32472
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.015849 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.7592 | 111 | -0.0016567 | -0.1839
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5091 | 216.4 | -0.0012897 | -0.2791
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.016216 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5043 | 216.1 | -0.0012897 | -0.27871
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.9861 | 182 | -0.0010987 | -0.19997
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.016407 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.941 | 484 | -0.0010987 | -0.53178
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.016434 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.8217 | 0 | -0.0010717 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.01645 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.0010557 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.016465 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 3.9845 | 242 | -0.0010407 | -0.25185
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4553 | 0 | -0.00091572 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.1567 | 0 | -0.00091572 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.4055 | 0 | -0.00091572 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.01659 | north | 1 | N | N | Nnorth | Nnorth | 1 | 6.6194 | 0 | -0.00091572 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.1535 | 0 | -0.00074972 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.321 | 0 | -0.00074972 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.016756 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.0697 | 0 | -0.00074972 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.0717 | 118 | 5.1277e-05 | 0.0060507
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.017557 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.0191 | 115 | 5.1277e-05 | 0.0058969
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.017557 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.7617 | 556 | 5.1277e-05 | 0.02851
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00043228 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.017938 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00043228 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 161 | 0.00047628 | 0.076681
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.949 | 164 | 0.00047628 | 0.078109
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.949 | 164 | 0.00047628 | 0.078109
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4445 | 414 | 0.00047628 | 0.19718
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9131 | 162 | 0.00047628 | 0.077157
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8951 | 161 | 0.00047628 | 0.076681
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9311 | 163 | 0.00047628 | 0.077633
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.017982 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.3546 | 409 | 0.00047628 | 0.1948
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.018068 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.0104 | 388 | 0.00056228 | 0.21816
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.018068 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.305 | 515 | 0.00056228 | 0.28957
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.018366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.9892 | 435 | 0.00086028 | 0.37422
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.018377 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.2589 | 395 | 0.00087128 | 0.34415
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.018377 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.994 | 435 | 0.00087128 | 0.37901
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.018459 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.73836 | 40 | 0.00095328 | 0.038131
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.018466 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.36932 | 20 | 0.00096028 | 0.019206
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.46168 | 25 | 0.00096128 | 0.024032
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.018467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.75715 | 41 | 0.00096128 | 0.039412
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4654 | 79 | 0.0010433 | 0.082419
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9662 | 106 | 0.0010433 | 0.11059
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.018549 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7082 | 146 | 0.0010433 | 0.15232
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.018549 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4097 | 76 | 0.0010433 | 0.079289
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.4138 | 288 | 0.0012923 | 0.37218
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7633 | 147 | 0.0012923 | 0.18996
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.018798 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7633 | 147 | 0.0012923 | 0.18996
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.5373 | 0 | 0.0013783 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 10.9338 | 0 | 0.0013783 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.018884 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 15.2583 | 0 | 0.0013783 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.4227 | 0 | 0.0014633 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.5099 | 0 | 0.0014633 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.018969 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.6769 | 0 | 0.0014633 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0421 | 160 | 0.0015073 | 0.24116
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.966 | 156 | 0.0015073 | 0.23514
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7265 | 196 | 0.0015073 | 0.29543
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.966 | 156 | 0.0015073 | 0.23514
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.985 | 157 | 0.0015073 | 0.23664
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.019013 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.7646 | 198 | 0.0015073 | 0.29844
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.019084 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 7.0611 | 370 | 0.0015783 | 0.58396
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6718 | 0 | 0.0015783 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.6908 | 0 | 0.0015783 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.897 | 0 | 0.0015783 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.729 | 0 | 0.0015783 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.7481 | 0 | 0.0015783 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.019084 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.916 | 0 | 0.0015783 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.01925 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.2725 | 170 | 0.0017443 | 0.29653
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.01925 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.01 | 520 | 0.0017443 | 0.90702
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.019332 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0018263 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.77524 | 0 | 0.0018753 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.019381 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.77524 | 0 | 0.0018753 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.019856 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0023503 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.021754 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.4473 | 0 | 0.0042483 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0043593 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.021865 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0043593 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.021865 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0043593 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.3588 | 60 | 0.0051403 | 0.30842
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.022646 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4267 | 63 | 0.0051403 | 0.32384
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5402 | 204 | 0.019456 | 3.9691
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4294 | 201 | 0.019456 | 3.9107
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.036962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.9448 | 242 | 0.019456 | 4.7084
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7522 | 20 | 0.020104 | 0.40209
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7522 | 20 | 0.020104 | 0.40209
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.7522 | 20 | 0.020104 | 0.40209
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.03761 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.63937 | 17 | 0.020104 | 0.34177
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.057392 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.0055 | 366 | 0.039886 | 14.5984
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8164 | 0 | 0.15897 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.055041 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.376 | 0 | 0.15897 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.055041 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.15897 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.039493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.23696 | 0 | 0.17451 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.035876 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.17813 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.00796 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10905 | 0 | 0.20605 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.007603 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.063865 | 8.4 | 0.2064 | 1.7338
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006121 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1469 | 24 | 0.20789 | 4.9893
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.1469 | 24 | 0.20789 | 4.9893
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.006121 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.14078 | 23 | 0.20789 | 4.7814
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10174 | 0 | 0.20836 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10174 | 0 | 0.20836 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.005652 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.08478 | 0 | 0.20836 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.0053 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2366 | 422 | 0.20871 | 88.0744
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13434 | 0 | 0.20921 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.004798 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13914 | 0 | 0.20921 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.059364 | 0 | 0.21071 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.059364 | 0 | 0.21071 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.003177 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3174 | 100 | 0.21083 | 21.0833
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.003174 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.3174 | 100 | 0.21083 | 21.0833
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.003174 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21083 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001494 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21251 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00036 | 0 | 0.21398 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00033 | 0 | 0.21398 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -3e-05 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00036 | 0 | 0.21398 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21401 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21401 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21401 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.038418 | 0 | 0.21434 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.074814 | 0 | 0.21434 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.062008 | 0 | 0.21434 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.075488 | 0 | 0.21434 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000337 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.038755 | 0 | 0.21434 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.035786 | 58 | 0.21462 | 12.4482
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000617 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.054913 | 89 | 0.21462 | 19.1015
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.027148 | 44 | 0.21462 | 9.4435
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.027148 | 44 | 0.21462 | 9.4435
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.026531 | 43 | 0.21462 | 9.2288
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000617 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.027765 | 45 | 0.21462 | 9.6581
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.000964 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.39235 | 407 | 0.21497 | 87.4932
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001048 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.41501 | 0 | 0.21506 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.22656 | 209 | 0.21509 | 44.954
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001084 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.23414 | 216 | 0.21509 | 46.4597
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.049864 | 46 | 0.21509 | 9.8942
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.050948 | 47 | 0.21509 | 10.1093
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.049864 | 46 | 0.21509 | 9.8942
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001084 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.049864 | 46 | 0.21509 | 9.8942
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.44743 | 412 | 0.21509 | 88.6183
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.001086 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.4344 | 400 | 0.21509 | 86.0372
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.48633 | 0 | 0.21515 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.001147 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.48747 | 0 | 0.21515 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001176 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21518 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04347 | 0 | 0.21525 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.042228 | 0 | 0.21525 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.001242 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.04347 | 0 | 0.21525 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001311 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21532 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21541 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21541 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.001403 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.21541 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22925 | 155 | 0.21549 | 33.4003
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25143 | 170 | 0.21549 | 36.6326
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.001479 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.22925 | 155 | 0.21549 | 33.4003
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2196 | 146.5 | 0.21551 | 31.5716
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.2217 | 147.9 | 0.21551 | 31.8733
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.001499 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25933 | 173 | 0.21551 | 37.2826
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.87196 | 0 | 0.2156 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.001597 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.1978 | 0 | 0.2156 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36308 | 207 | 0.21576 | 44.6625
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38009 | 216.7 | 0.21576 | 46.7554
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42447 | 242 | 0.21576 | 52.2142
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25258 | 144 | 0.21576 | 31.0696
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.25258 | 144 | 0.21576 | 31.0696
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.001754 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29993 | 171 | 0.21576 | 36.8951
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.072466 | 38 | 0.21591 | 8.2047
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.036805 | 19.3 | 0.21591 | 4.1671
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.001907 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.028605 | 15 | 0.21591 | 3.2387
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.001907 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.089629 | 47 | 0.21591 | 10.148
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.001907 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.21591 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1849 | 0 | 0.21597 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.080647 | 0 | 0.21597 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.074746 | 0 | 0.21597 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.037373 | 0 | 0.21597 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1849 | 0 | 0.21597 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070812 | 0 | 0.21597 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.084581 | 0 | 0.21597 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.043274 | 0 | 0.21597 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.29112 | 0 | 0.21597 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09835 | 0 | 0.21597 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10819 | 0 | 0.21597 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.001967 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.09835 | 0 | 0.21597 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002018 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008072 | 0 | 0.21603 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002041 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.059189 | 0 | 0.21605 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002052 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.012312 | 0 | 0.21606 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.002119 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.080522 | 0 | 0.21613 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.002137 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.081206 | 0 | 0.21614 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.053475 | 0 | 0.21615 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.002139 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.053475 | 0 | 0.21615 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31561 | 147 | 0.21615 | 31.7746
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.29629 | 138 | 0.21615 | 29.8293
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.30058 | 140 | 0.21615 | 30.2616
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31561 | 147 | 0.21615 | 31.7746
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39075 | 182 | 0.21615 | 39.34
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.002147 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42511 | 198 | 0.21615 | 42.7985
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.72044 | 334 | 0.21616 | 72.1988
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.002157 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73338 | 340 | 0.21616 | 73.4958
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38826 | 180 | 0.21616 | 38.9095
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.002157 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.38826 | 180 | 0.21616 | 38.9095
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002182 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39276 | 180 | 0.21619 | 38.914
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.32404 | 0 | 0.21619 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.32469 | 0 | 0.21619 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.002185 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.33431 | 0 | 0.21619 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7345 | 336 | 0.21619 | 72.6409
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.002186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.39348 | 180 | 0.21619 | 38.9148
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.002193 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3794 | 0 | 0.2162 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 0 | 0.21628 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 0 | 0.21628 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 0 | 0.21628 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.036384 | 0 | 0.21628 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 0 | 0.21628 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 0 | 0.21628 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05685 | 0 | 0.21628 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.002274 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.03411 | 0 | 0.21628 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0056088 | 0 | 0.21634 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0056088 | 0 | 0.21634 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.002337 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0065436 | 0 | 0.21634 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3694 | 0 | 0.21635 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.35771 | 0 | 0.21635 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.2338 | 0 | 0.21635 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.33901 | 0 | 0.21635 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.34369 | 0 | 0.21635 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.002338 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.29693 | 0 | 0.21635 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.002338 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.028056 | 0 | 0.21635 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33285 | 142 | 0.21635 | 30.7219
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33988 | 145 | 0.21635 | 31.3709
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.35394 | 151 | 0.21635 | 32.669
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.002344 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.67976 | 290 | 0.21635 | 62.7418
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.56759 | 223.9 | 0.21654 | 48.4838
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57037 | 225 | 0.21654 | 48.722
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.56936 | 224.6 | 0.21654 | 48.6354
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.002535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57468 | 226.7 | 0.21654 | 49.0901
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.002652 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.058344 | 22 | 0.21666 | 4.7665
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029172 | 11 | 0.21666 | 2.3832
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.002652 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.029172 | 11 | 0.21666 | 2.3832
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.006408 | 0 | 0.21668 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.00267 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.006408 | 0 | 0.21668 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.002687 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.032244 | 0 | 0.21669 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13318 | 47.7 | 0.2168 | 10.3413
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.10414 | 37.3 | 0.2168 | 8.0866
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12843 | 46 | 0.2168 | 9.9728
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.002792 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.13402 | 48 | 0.2168 | 10.4064
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.41083 | 144 | 0.21686 | 31.2279
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.002853 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53636 | 188 | 0.21686 | 40.7697
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.00293 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.21389 | 0 | 0.21694 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.045525 | 0 | 0.21704 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.003035 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.069805 | 0 | 0.21704 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.003059 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.024472 | 0 | 0.21707 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.087164 | 0 | 0.21712 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.021791 | 0 | 0.21712 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12141 | 0 | 0.21712 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.046695 | 0 | 0.21712 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.021791 | 0 | 0.21712 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.046695 | 0 | 0.21712 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12141 | 0 | 0.21712 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.003113 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12141 | 0 | 0.21712 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026296 | 0 | 0.21729 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.003287 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.026296 | 0 | 0.21729 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.003392 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16282 | 0 | 0.2174 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16817 | 49 | 0.21744 | 10.6545
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15787 | 46 | 0.21744 | 10.0022
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15787 | 46 | 0.21744 | 10.0022
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1613 | 47 | 0.21744 | 10.2196
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52853 | 154 | 0.21744 | 33.4856
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.003432 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.50794 | 148 | 0.21744 | 32.181
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16474 | 48 | 0.21744 | 10.4371
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.003432 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16474 | 48 | 0.21744 | 10.4371
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27397 | 0 | 0.21748 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.28091 | 0 | 0.21748 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27397 | 0 | 0.21748 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27744 | 0 | 0.21748 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.27189 | 0 | 0.21748 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0867 | 0 | 0.21748 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15953 | 0 | 0.21748 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.097104 | 0 | 0.21748 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.1512 | 0 | 0.21748 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.003468 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.25663 | 0 | 0.21748 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0785 | 310 | 0.21749 | 67.4207
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.003479 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.4368 | 413 | 0.21749 | 89.8218
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15288 | 42 | 0.21765 | 9.1412
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16016 | 44 | 0.21765 | 9.5765
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.16016 | 44 | 0.21765 | 9.5765
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.00364 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.17108 | 47 | 0.21765 | 10.2294
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.53341 | 132 | 0.21805 | 28.7823
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.54149 | 134 | 0.21805 | 29.2184
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.004041 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3052 | 323 | 0.21805 | 70.4295
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.62006 | 152.5 | 0.21807 | 33.2561
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60787 | 149.5 | 0.21807 | 32.6019
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.004066 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.94575 | 232.6 | 0.21807 | 50.7238
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.004322 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2161 | 50 | 0.21833 | 10.9165
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70278 | 158 | 0.21846 | 34.5159
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.71168 | 160 | 0.21846 | 34.9528
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.004448 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7784 | 175 | 0.21846 | 38.2296
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.004494 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9459 | 0 | 0.2185 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6257 | 0 | 0.2185 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.004496 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.6751 | 0 | 0.2185 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 8.0487 | 0 | 0.22005 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.006038 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 8.0185 | 0 | 0.22005 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.46786 | 76 | 0.22016 | 16.7324
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.46786 | 76 | 0.22016 | 16.7324
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.64638 | 105 | 0.22016 | 23.1171
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45554 | 74 | 0.22016 | 16.2921
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45554 | 74 | 0.22016 | 16.2921
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.006156 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62791 | 102 | 0.22016 | 22.4566
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.5386 | 0 | 0.22023 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.006219 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6132 | 0 | 0.22023 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.006258 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.41303 | 66 | 0.22027 | 14.5375
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42836 | 0 | 0.22092 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4933 | 0 | 0.22092 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3109 | 0 | 0.22092 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.69781 | 0 | 0.22092 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59417 | 0 | 0.22092 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60799 | 0 | 0.22092 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34545 | 0 | 0.22092 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.12436 | 0 | 0.22092 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.64945 | 0 | 0.22092 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.48363 | 0 | 0.22092 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43527 | 0 | 0.22092 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49745 | 0 | 0.22092 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4477 | 0 | 0.22092 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.69781 | 0 | 0.22092 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67017 | 0 | 0.22092 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71163 | 0 | 0.22092 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52508 | 0 | 0.22092 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55272 | 0 | 0.22092 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55272 | 0 | 0.22092 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.006909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.1814 | 0 | 0.22092 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50169 | 0 | 0.22107 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.007066 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.07066 | 0 | 0.22107 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79909 | 0 | 0.22121 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79909 | 0 | 0.22121 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.85668 | 0 | 0.22121 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.007199 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.78829 | 0 | 0.22121 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.007625 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35151 | 0 | 0.22163 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.9912 | 0 | 0.22167 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.3242 | 0 | 0.22167 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.007667 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 4.6002 | 0 | 0.22167 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2502 | 0 | 0.22168 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2502 | 0 | 0.22168 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.00767 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8792 | 0 | 0.22168 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.007689 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25374 | 0 | 0.2217 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2477 | 161 | 0.22176 | 35.7029
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.2865 | 166 | 0.22176 | 36.8117
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.00775 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.922 | 248 | 0.22176 | 54.9958
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.00775 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 4.2315 | 546 | 0.22176 | 121.0794
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.00775 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 4.9832 | 0 | 0.22176 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.00775 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10075 | 13 | 0.22176 | 2.8828
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.79568 | 0 | 0.22194 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.73698 | 0 | 0.22194 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.81472 | 0 | 0.22194 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.007933 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.80917 | 0 | 0.22194 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25386 | 0 | 0.22194 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.007933 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23799 | 0 | 0.22194 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56173 | 0 | 0.22194 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5292 | 0 | 0.22194 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4205 | 0 | 0.22194 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2155 | 0 | 0.22194 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2179 | 0 | 0.22194 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2083 | 0 | 0.22194 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.76166 | 0 | 0.22194 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.007934 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.9359 | 0 | 0.22194 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.007934 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31736 | 0 | 0.22194 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.008037 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.40185 | 50 | 0.22204 | 11.1022
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.008093 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.2221 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.74392 | 0 | 0.22218 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71613 | 0 | 0.22218 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71122 | 0 | 0.22218 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44554 | 0 | 0.22218 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.008175 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.099735 | 0 | 0.22218 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.53346 | 0 | 0.22221 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.49242 | 0 | 0.22221 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.53346 | 0 | 0.22221 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.008207 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.53346 | 0 | 0.22221 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3801 | 46 | 0.22227 | 10.2244
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3801 | 46 | 0.22227 | 10.2244
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.3801 | 46 | 0.22227 | 10.2244
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45447 | 55 | 0.22227 | 12.2249
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.45447 | 55 | 0.22227 | 12.2249
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.008263 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.4462 | 54 | 0.22227 | 12.0026
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.64475 | 0 | 0.22227 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.008266 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66128 | 0 | 0.22227 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3511 | 0 | 0.22229 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3006 | 0 | 0.22229 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3039 | 0 | 0.22229 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.2998 | 0 | 0.22229 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.008279 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.2271 | 0 | 0.22229 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.008297 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2904 | 0 | 0.2223 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.008311 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.099732 | 12 | 0.22232 | 2.6678
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.008311 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.22232 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.008311 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.4046 | 169 | 0.22232 | 37.5718
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.008312 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3715 | 165 | 0.22232 | 36.6826
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2386 | 0 | 0.22232 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.008313 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.54118 | 0 | 0.22232 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.008316 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7713 | 213 | 0.22232 | 47.3548
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.008316 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13472 | 0 | 0.22232 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53229 | 0 | 0.22232 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52563 | 0 | 0.22232 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68698 | 0 | 0.22232 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.008317 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61213 | 0 | 0.22232 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.008317 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8963 | 228 | 0.22232 | 50.6899
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.4972 | 0 | 0.22233 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3192 | 0 | 0.22233 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.008318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3059 | 0 | 0.22233 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.592 | 0 | 0.22235 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.60034 | 0 | 0.22235 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32518 | 0 | 0.22235 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.008338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25014 | 0 | 0.22235 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35162 | 42 | 0.22238 | 9.3399
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.35162 | 42 | 0.22238 | 9.3399
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31814 | 38 | 0.22238 | 8.4504
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.008372 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.31814 | 38 | 0.22238 | 8.4504
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.008373 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1387 | 0 | 0.22238 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.008383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4503 | 0 | 0.22239 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.008383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1317 | 0 | 0.22239 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.87766 | 104 | 0.22245 | 23.1344
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.87766 | 104 | 0.22245 | 23.1344
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.44727 | 53 | 0.22245 | 11.7896
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.48102 | 57 | 0.22245 | 12.6794
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.45571 | 54 | 0.22245 | 12.0121
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.48946 | 58 | 0.22245 | 12.9019
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.008439 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.48946 | 58 | 0.22245 | 12.9019
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.008449 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.21 | 735 | 0.22246 | 163.5052
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28771 | 0 | 0.22247 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29363 | 0 | 0.22247 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27671 | 0 | 0.22247 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.38841 | 0 | 0.22247 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.14978 | 0 | 0.22247 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17262 | 0 | 0.22247 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16839 | 0 | 0.22247 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29617 | 0 | 0.22247 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15232 | 0 | 0.22247 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72265 | 0 | 0.22247 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.008462 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2524 | 0 | 0.22247 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.008487 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.10184 | 12 | 0.22249 | 2.6699
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.0425 | 0 | 0.22251 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.0085 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1785 | 0 | 0.22251 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.008501 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.10201 | 0 | 0.22251 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.55263 | 0 | 0.22251 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.56113 | 0 | 0.22251 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59514 | 0 | 0.22251 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53563 | 0 | 0.22251 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52712 | 0 | 0.22251 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.88421 | 0 | 0.22251 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.008502 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.50162 | 0 | 0.22251 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.008502 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 6.317 | 743 | 0.22251 | 165.3242
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.008514 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3367 | 0 | 0.22252 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4649 | 172 | 0.22252 | 38.2741
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4649 | 172 | 0.22252 | 38.2741
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.008517 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.4649 | 172 | 0.22252 | 38.2741
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3928 | 0 | 0.22256 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3808 | 0 | 0.22256 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.3594 | 0 | 0.22256 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.008555 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 2.303 | 0 | 0.22256 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.008572 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 3.4117 | 398 | 0.22258 | 88.5865
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50716 | 59 | 0.2226 | 13.1336
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.50716 | 59 | 0.2226 | 13.1336
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.008596 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.48138 | 56 | 0.2226 | 12.4658
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5248 | 0 | 0.22282 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.375 | 0 | 0.22282 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3574 | 0 | 0.22282 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.008814 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.3574 | 0 | 0.22282 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.008814 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.4279 | 0 | 0.22282 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1334
| 65 | 1307
| 70 | 1280
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1239.6