## test results
CRE test for: |  | GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3 | [5 empty] | PASS
Line Rating: |  | 1235.45
Direction |  | West | → | North |  | W-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.022185
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0030991
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.26682
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0109
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.023444
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.0026658
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.26746
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.011032
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.01952
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.28965
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.011154
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.27056
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.0078007
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.27785
PTDF tests
West | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | -0.29026 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.29026 | 0.01952
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.27841
[6 empty] | Concentration |  | -0.95917 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.27804
[6 empty] | Concentration |  | -0.95791 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 114.4706
| Percent of line rating => | [6 empty] | 9.266% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -2.8
[7 empty] | B1(N-S) | 0.014528 | -0.040127 | -0.054655 | 0.014528
[7 empty] | B2 (N-W) | -0.0037533 | -0.81477 | -0.81101 | -0.0037533
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.012255 | -0.018975 | -0.03123 | 0.012255
[7 empty] | B4 (S-W) | -0.018196 | -0.77577 | -0.75757 | -0.018196
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0018178 | 0.020024 | 0.021842 | -0.0018178
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.014959 | 0.79294 | 0.77798 | 0.014959
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | 1.788%
Deployment Error Percent | [6 empty] | B2 | -0.4618%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 1.508%
[7 empty] | B4 | -2.239%
[7 empty] | B5 | -0.2237%
[7 empty] | B6 | 1.841%
[7 empty] | Max Abs Error | 2.239% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3 C: LONCREK2 - COKFIELD 345kV 1439 - 1442 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3 C: LONCREK2 - COKFIELD 345kV 1439 - 1442
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.013588 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 3.4649
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.013588 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 2.0246
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.012979 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.19468
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.012979 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.19468
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.013588 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 2.079
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.01257 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 1.8855
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.01257 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 1.0056
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007627 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 0.55677
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007627 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 0.90761
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007627 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 1.5635
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007627 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 0.77795
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.007627 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 0.73219
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.008461 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.10153
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.008461 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.10153
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.015354 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 2.5795
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.015354 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 1.3819
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.30541
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.30541
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.64475
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 6.0621
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.0942
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 3.0942
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.02397 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 2.6966
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.024664 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.98656
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 1.9571
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 2.626
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 3.617
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.024774 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 1.8828
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.02945 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 1.767
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.02945 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 1.8554
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.024669 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.49338
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.02467 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.61675
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.02467 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 1.0115
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.015226 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 7.0496
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -18.1155
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -17.841
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -18.39
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -18.39
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -18.39
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27448 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -31.2904
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.27448 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -141.3557
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -18.2994
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -19.1312
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -19.1312
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -18.5767
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -18.5767
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -18.0222
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -19.6249
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -20.5781
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -19.7371
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -42.1509
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -61.8213
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26773 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -26.5057
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26773 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -16.3318
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.26799 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -37.786
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -6.6933
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -12.2354
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -12.2354
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.26799 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -32.1583
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.27292 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -7.0414
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.27556 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -27.6936
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.27372 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -32.8463
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.27572 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -15.9916
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.27593 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -59.1051
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.27427 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -41.1408
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.26908 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -1.7759
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.26908 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -9.2295
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.27427 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -27.7015
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.27307 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -32.7685
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.086836 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 31.782
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.021367 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 5.1708
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.46932 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -187.7284
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.46891 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -110.6637
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.086836 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 14.3279
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 9.5021
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 9.3624
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 11.2721
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.3158
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.3158
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.3158
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.26843
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.016979 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 2.0375
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.032056 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -1.9234
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 1.8935
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 2.0097
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 2.2318
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 4.0501
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.9488
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 4.9613
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 3.9488
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 3.9741
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 5.012
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.025507 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 4.3362
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.025507 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 13.2636
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.025395 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 9.3962
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 14.0482
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 14.5769
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 20.3422
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.029217 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 3.2723
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.029217 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 2.9217
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.029217 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 11.044
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 3.1083
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 2.9323
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 3.8964
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.018958 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 14.5977
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 1.0014
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.98711
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 0.98711
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 0.97281
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.012844 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 14.8605
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.012844 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 14.8734
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 4.6623
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 4.704
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.021954 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 4.7508
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.021954 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 4.7443
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 4.4126
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 4.3918
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.024881 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 9.828
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.024829 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 10.8006
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.024881 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 10.8232
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.026342 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 3.6352
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.023603 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 2.7852
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.023603 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 2.7143
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.023603 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 13.1233
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.024186 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 9.3842
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.024186 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 12.4558
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 17.657
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 17.8819
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 17.5445
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.022042 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 4.0116
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.022042 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 10.6683
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.021155 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 4.7387
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.02208 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 1.104
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.0221 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.9282
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.019837 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 12.1998
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.019837 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 11.6443
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.014889 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 7.9954
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.014889 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 11.7176
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.01414 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 1.0605
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.01414 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 3.1391
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.008517 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 4.8462
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001612 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.33691
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001612 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.34819
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.001451 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 0.59056
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.074152
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.075764
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.074152
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.074152
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.001696 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 0.7191
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.001696 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 0.7208
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000983 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.057014
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000983 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.087487
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.043252
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.043252
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.042269
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.044235
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.001614 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 0.66497
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.001614 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 0.6456
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002301 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 1.2563
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.002301 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 1.7257
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.12444
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.1938
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.30804
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.33216
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.36431
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.33216
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003709 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.081598
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003709 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.040799
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003709 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.040799
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.18589
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.14536
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.17926
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.18706
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.001248
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.001144
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.008087 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.19409
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.008087 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.19409
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.008087 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.186
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.001559 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 0.61736
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.008249 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 10.9959
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.008249 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 10.9547
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.10294
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.052284
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.040635
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.002709 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.12732
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -19.4546
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.23811 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -35.7168
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.2859 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -48.4597
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.19825 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -29.737
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.27034 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -17.0313
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.11681 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -75.8921
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.025608 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.0243
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.025608 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 1.0243
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.006901 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -2.9122
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.73814
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.74933
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 1.8062
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.96949
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.98176
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 1.0738
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.006197 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 3.619
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.006197 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 3.6872
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.006194 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 2.682
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.7982
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.80212
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.8007
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.80819
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.004585 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.03668
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.004585 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.03668
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.13234
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.13234
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.11028
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.010456 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.14325
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.004223 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.076014
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.004223 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.076014
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.06475
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.0629
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.06475
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.006228 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.17438
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.006228 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.18061
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.27432 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -9.6011
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.27432 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -8.2295
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.29825
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.29825
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.29825
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.29825
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.002921 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.017526
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0079152
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0079152
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.0092344
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.002869 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.011476
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003743 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0089832
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003743 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0089832
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.44703
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.41966
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.42574
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.44703
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.55346
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.60212
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.85766
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.84079
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 1.3081
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.46959
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.47952
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.49936
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 0.95903
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.073908 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.439
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.073908 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.8477
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.001248
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.004084 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.29813
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.3796
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.38921
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.12118
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.030296
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.3796
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.3844
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.37671
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.12012
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.22103
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.003095 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 1.9468
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.00398 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.57312
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.00398 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.74824
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.003764 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.045168
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.052988 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.31793
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.003084 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 1.0362
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003044 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 1.0167
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003044 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 1.035
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.002994 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.11377
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.00302 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.0755
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.00302 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.0755
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.003017 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.11465
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.002888 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.083752
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.45706
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.45799
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.47155
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.5195
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.50306
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.3288
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.47676
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.48334
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.41758
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.31644
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.31946
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.37368
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.51812
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.5424
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.60573
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.36058
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.36058
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.42818
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004842 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 1.501
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004842 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 1.9997
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.21244
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.22255
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.22255
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.23773
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.23412
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.21979
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.21979
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.22457
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.73581
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.70714
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.22934
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.22934
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -19.457
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -19.457
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -25.7944
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -22.2366
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -22.2366
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -31.9651
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -57.8636
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -39.4929
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -36.797
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -37.7975
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -40.8547
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -58.3638
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -48.8805
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -29.5856
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -58.2356
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -46.074
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -56.2012
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -34.2546
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.27412 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -40.8445
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.27106 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -48.7906
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.27106 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -48.7906
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.2712 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -61.0204
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.30374 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -37.9675
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.30374 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -37.9675
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 3.5553
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 3.5807
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 7.8471
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 3.6315
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 3.6569
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 7.8724
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.021374 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 4.1893
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.021374 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 2.3725
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.025763 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.874
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.9462
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 3.9462
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 9.9617
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 3.898
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 3.874
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 3.9221
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 9.8414
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.024036 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.024036 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 3.2974
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 2.8964
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 3.2306
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 8.8897
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 3.0437
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 3.0497
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 3.5829
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 3.0711
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 3.0873
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 3.5981
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.008517 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 4.9484
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 14.5863
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 14.5863
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.015199 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.48637
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.015159 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.72763
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.015159 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.69731
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.18252
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.77571
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01521 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.25857
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.33462
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.38025
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.015159 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 1.5917
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.26223 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -22.0277
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.25915 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -20.7318
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.25901 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -38.8512
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.25901 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -38.8512
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.76372
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.71949
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.57171
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 1.6526
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 1.6558
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 1.6429
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 1.0356
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 2.632
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.43148
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 1.0817
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 1.0019
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 1.1076
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 1.1001
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.010786 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.34515
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.010786 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.32358
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.0881
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 1.0881
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 1.1666
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 1.0734
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 2.5982
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 2.6102
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.011375 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 1.547
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.01046 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.34518
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.47767
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.47767
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.43217
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.43217
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.009626 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.68345
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.009626 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.09626
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.7007
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 1.7007
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 2.5563
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.72494
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.66918
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.72494
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.72494
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 1.683
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.7353
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 1.011
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.97324
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.96657
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.6055
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.13554
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.011548 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 8.5802
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.011476 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 8.4349
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.9897
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.9897
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 1.9897
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 2.0698
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.011388 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 1.9701
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.011388 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 1.5374
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 1.8916
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 1.8753
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 1.8463
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 3.1278
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.72314
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.7141
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.9333
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.83161
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 1.836
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 1.7674
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 1.7719
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 1.7663
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 3.0263
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.011545 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.057725
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.011545 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.24244
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 2.2621
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 2.2885
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 2.2885
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 5.5746
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.011641 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 4.6331
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.51649
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.51649
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.51649
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.61754
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.61754
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.60631
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.017795 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 14.7165
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.017795 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 14.5741
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.010374 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.47824
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.63893
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.63893
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.88274
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.62212
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.62212
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.85751
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 2.0344
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 1.7925
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 1.7744
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.011273 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.39455
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.011 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 5.049
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.75055
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.7621
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.80829
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.72746
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.71591
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 1.2009
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.68127
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 1.8664
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.8425
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 1.8425
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.011964 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 1.9382
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.011564 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 1.8155
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.80429
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.81562
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.44179
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.33984
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.011232 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.8761
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.011232 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.89856
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.18304
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.011294 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 1.8635
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.011292 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 1.9083
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.011298 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 2.4065
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.0113 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 2.5764
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.011291 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.13549
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.011291 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.20324
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.010925 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.54625
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.1923
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 1.1923
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.61906
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.60759
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.61906
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.65345
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.61906
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.61906
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.66491
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.66491
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.011527 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.13832
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65369
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.68871
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65369
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65369
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.68871
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.65369
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.008544 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.5639
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 1.6971
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 1.7498
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 2.6142
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010541 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 5.7554
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010541 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 6.7779
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 6.7899
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 5.8825
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 6.258
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.010541 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.13703
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.011546 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.13855
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.3908
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.39884
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.37585
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.52757
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.20344
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.23448
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.22873
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.40229
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.20689
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.98159
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 1.7011
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.58379
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.6723
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.42372
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.95102
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.80978
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.82861
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.4708
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.16949
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.8851
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.65912
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.59321
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.67795
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.61016
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.95102
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.91335
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.96985
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.71562
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.75328
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.75328
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 1.6101
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.084672
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.2524 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -19.3083
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -20.7515
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -10.3758
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.26043 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -20.8342
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.25918 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -20.7343
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.25373 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -20.2988
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.25195 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -21.1642
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.26043 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -20.8342
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.070338
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -36.1639
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -70.2183
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -51.2925
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.13697
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.11353
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.13821
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.070955
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.0617
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.20577 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -12.3463
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.079012 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.22382 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.2646 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -1.2701
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -11.8166
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -33.8743
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -42.5399
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -37.4981
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -33.0866
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -25.3664
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.26806 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -40.2087
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -29.8547
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -39.6736
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -49.3597
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -56.9229
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.002709 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.048122 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.004127 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.13454
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.2095
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.35557
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.26226
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.11439
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.10602
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.05301
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.26226
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.10044
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.11997
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.06138
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.16879
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.06492
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.030296
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.06492
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.16879
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.16879
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.41292
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.1395
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.15345
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.1395
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003288 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.039456
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.004224 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.06336
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.004224 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.097152
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.004703 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.22574
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.004255 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.03404
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.003078 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.55404
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.003084 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.55512
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003044 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.54792
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003044 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.54792
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004123 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.4123
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004123 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.4123
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08005
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08005
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08005
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.051232
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08005
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08005
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.08005
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.04803
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004123 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004123 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -2.0615
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004123 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -2.0615
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.004123 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.001909 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.073908 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.001864 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.001726 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3 C: LONCREK2 - COKFIELD 345kV 1439 - 1442 | [7 empty] | 114.4706
Number of Bus | Name of Bus | ID | Max MW | L:GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3 C: LONCREK2 - COKFIELD 345kV 1439 - 1442 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.013588 | north | Y | -0.0085975 | 0.010489 | 0.28041 | 0.0026881 | 0.0026881 | houston | Y | 0.0085975 | 1.5069
239 | BOSQUESW | 1 | 149 | 0.013588 | north | Y | -0.0085975 | 0.010489 | 0.28041 | 0.0026881 | 0.0026881 | houston | Y | 0.0085975 | 0.88049
244 | WHITNYDM | 1 | 15 | 0.012979 | north | N | -0.0092065 | 0.0098799 | 0.2798 | 0.0020791 | 0.0020791 | houston | Y | 0.0092065 | 0
245 | WHITNYDM | 2 | 15 | 0.012979 | north | N | -0.0092065 | 0.0098799 | 0.2798 | 0.0020791 | 0.0020791 | houston | Y | 0.0092065 | 0
247 | BOSQUESW | 2 | 153 | 0.013588 | north | Y | -0.0085975 | 0.010489 | 0.28041 | 0.0026881 | 0.0026881 | houston | Y | 0.0085975 | 0.90413
251 | BOSQUESW | 2 | 150 | 0.01257 | north | Y | -0.0096155 | 0.0094709 | 0.27939 | 0.0016701 | 0.0016701 | houston | Y | 0.0096155 | 1.1918
253 | BOSQUESW | 2 | 80 | 0.01257 | north | Y | -0.0096155 | 0.0094709 | 0.27939 | 0.0016701 | 0.0016701 | houston | Y | 0.0096155 | 0.63563
332 | RWMILLER | 1 | 73 | 0.007627 | north | Y | -0.014558 | 0.0045279 | 0.27445 | -0.0032729 | 0.0032729 | houston | Y | 0.014558 | 0.82385
333 | RWMILLER | 2 | 119 | 0.007627 | north | Y | -0.014558 | 0.0045279 | 0.27445 | -0.0032729 | 0.0032729 | houston | Y | 0.014558 | 1.343
334 | RWMILLER | 3 | 205 | 0.007627 | north | Y | -0.014558 | 0.0045279 | 0.27445 | -0.0032729 | 0.0032729 | houston | Y | 0.014558 | 2.3135
335 | RWMILLER | 4 | 102 | 0.007627 | north | Y | -0.014558 | 0.0045279 | 0.27445 | -0.0032729 | 0.0032729 | houston | Y | 0.014558 | 1.1511
336 | RWMILLER | 5 | 96 | 0.007627 | north | Y | -0.014558 | 0.0045279 | 0.27445 | -0.0032729 | 0.0032729 | houston | Y | 0.014558 | 1.0834
344 | MRSSHPRD | 1 | 12 | 0.008461 | north | N | -0.013724 | 0.0053619 | 0.27528 | -0.0024389 | 0.0024389 | houston | Y | 0.013724 | 0
345 | MRSSHPRD | 2 | 12 | 0.008461 | north | N | -0.013724 | 0.0053619 | 0.27528 | -0.0024389 | 0.0024389 | houston | Y | 0.013724 | 0
366 | JNSNCNTY | 1 | 168 | 0.015354 | north | Y | -0.0068315 | 0.012255 | 0.28217 | 0.0044541 | 0.0044541 | houston | Y | 0.0068315 | 0.39939
367 | JNSNCNTY | 2 | 90 | 0.015354 | north | Y | -0.0068315 | 0.012255 | 0.28217 | 0.0044541 | 0.0044541 | houston | Y | 0.0068315 | 0.21396
503 | NTHTEXAS | 1 | 18 | 0.016967 | north | Y | -0.0052185 | 0.013868 | 0.28379 | 0.0060671 | 0.0052185 | North | N | 0.0052185 | 0
504 | NTHTEXAS | 2 | 18 | 0.016967 | north | Y | -0.0052185 | 0.013868 | 0.28379 | 0.0060671 | 0.0052185 | North | N | 0.0052185 | 0
505 | NTHTEXAS | 3 | 38 | 0.016967 | north | Y | -0.0052185 | 0.013868 | 0.28379 | 0.0060671 | 0.0052185 | North | N | 0.0052185 | 0
580 | JCKCNTY8 | 1 | 288 | 0.021049 | north | Y | -0.0011365 | 0.01795 | 0.28787 | 0.010149 | 0.0011365 | North | N | 0.0011365 | 0
581 | JCKCNTY8 | 2 | 147 | 0.021049 | north | Y | -0.0011365 | 0.01795 | 0.28787 | 0.010149 | 0.0011365 | North | N | 0.0011365 | 0
582 | JCKCNTY8 | 3 | 147 | 0.021049 | north | Y | -0.0011365 | 0.01795 | 0.28787 | 0.010149 | 0.0011365 | North | N | 0.0011365 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.02397 | north | Y | 0.0017845 | 0.020871 | 0.29079 | 0.01307 | 0.0017845 | North | N | 0.0017845 | 0
837 | NEWMAN_G | 1 | 40 | 0.024664 | north | Y | 0.0024785 | 0.021565 | 0.29148 | 0.013764 | 0.0024785 | North | N | 0.0024785 | 0
842 | OLINGER_ | 1 | 79 | 0.024774 | north | Y | 0.0025885 | 0.021675 | 0.29159 | 0.013874 | 0.0025885 | North | N | 0.0025885 | 0
843 | OLINGER_ | 1 | 106 | 0.024774 | north | Y | 0.0025885 | 0.021675 | 0.29159 | 0.013874 | 0.0025885 | North | N | 0.0025885 | 0
844 | OLINGER_ | 1 | 146 | 0.024774 | north | Y | 0.0025885 | 0.021675 | 0.29159 | 0.013874 | 0.0025885 | North | N | 0.0025885 | 0
845 | OLINGER_ | 1 | 76 | 0.024774 | north | Y | 0.0025885 | 0.021675 | 0.29159 | 0.013874 | 0.0025885 | North | N | 0.0025885 | 0
923 | SPENCER_ | 1 | 60 | 0.02945 | north | Y | 0.0072645 | 0.026351 | 0.29627 | 0.01855 | 0.0072645 | North | N | 0.0072645 | 0
924 | SPENCER_ | 1 | 63 | 0.02945 | north | Y | 0.0072645 | 0.026351 | 0.29627 | 0.01855 | 0.0072645 | North | N | 0.0072645 | 0
948 | STEAM1 | 1 | 20 | 0.024669 | north | Y | 0.0024835 | 0.02157 | 0.29149 | 0.013769 | 0.0024835 | North | N | 0.0024835 | 0
949 | STEAM2 | 1 | 25 | 0.02467 | north | Y | 0.0024845 | 0.021571 | 0.29149 | 0.01377 | 0.0024845 | North | N | 0.0024845 | 0
950 | STEAM3 | 1 | 41 | 0.02467 | north | Y | 0.0024845 | 0.021571 | 0.29149 | 0.01377 | 0.0024845 | North | N | 0.0024845 | 0
990 | GIBN_CRE | 1 | 463 | 0.015226 | north | Y | -0.0069595 | 0.012127 | 0.28205 | 0.0043261 | 0.0043261 | houston | Y | 0.0069595 | 1.2192
1002 | PBCTAGE_ | A | 66 | -0.27448 | west | Y | -0.29666 | -0.27758 | -0.0076578 | -0.28538 | 0.0076578 | west | N | 0.0076578 | 0
1003 | PBCTBGE_ | B | 65 | -0.27448 | west | Y | -0.29666 | -0.27758 | -0.0076578 | -0.28538 | 0.0076578 | west | N | 0.0076578 | 0
1004 | PBCTCGE_ | C | 67 | -0.27448 | west | Y | -0.29666 | -0.27758 | -0.0076578 | -0.28538 | 0.0076578 | west | N | 0.0076578 | 0
1005 | PBCTDGE_ | D | 67 | -0.27448 | west | Y | -0.29666 | -0.27758 | -0.0076578 | -0.28538 | 0.0076578 | west | N | 0.0076578 | 0
1006 | PBCTEGE_ | E | 67 | -0.27448 | west | Y | -0.29666 | -0.27758 | -0.0076578 | -0.28538 | 0.0076578 | west | N | 0.0076578 | 0
1007 | PB5GEN_6 | MB | 114 | -0.27448 | west | Y | -0.29666 | -0.27758 | -0.0076578 | -0.28538 | 0.0076578 | west | N | 0.0076578 | 0
1008 | PB6GEN_7 | MB | 515 | -0.27448 | west | Y | -0.29666 | -0.27758 | -0.0076578 | -0.28538 | 0.0076578 | west | N | 0.0076578 | 0
1039 | MRGNAG_1 | A | 66 | -0.27726 | west | Y | -0.29945 | -0.28036 | -0.010445 | -0.28816 | 0.010445 | west | N | 0.010445 | 0
1040 | MRGNBG_2 | B | 69 | -0.27726 | west | Y | -0.29945 | -0.28036 | -0.010445 | -0.28816 | 0.010445 | west | N | 0.010445 | 0
1041 | MRGNCG_3 | C | 69 | -0.27726 | west | Y | -0.29945 | -0.28036 | -0.010445 | -0.28816 | 0.010445 | west | N | 0.010445 | 0
1042 | MRGNDG_4 | D | 67 | -0.27726 | west | Y | -0.29945 | -0.28036 | -0.010445 | -0.28816 | 0.010445 | west | N | 0.010445 | 0
1043 | MRGNEG_5 | E | 67 | -0.27726 | west | Y | -0.29945 | -0.28036 | -0.010445 | -0.28816 | 0.010445 | west | N | 0.010445 | 0
1044 | MRGNFG_6 | F | 65 | -0.27726 | west | Y | -0.29945 | -0.28036 | -0.010445 | -0.28816 | 0.010445 | west | N | 0.010445 | 0
1045 | CALENG1G | 1 | 70 | -0.28036 | west | N | -0.30254 | -0.28346 | -0.013537 | -0.29126 | 0.013537 | west | N | 0.013537 | 0
1046 | CALENG2G | 2 | 73.4 | -0.28036 | west | N | -0.30254 | -0.28346 | -0.013537 | -0.29126 | 0.013537 | west | N | 0.013537 | 0
1047 | CALENG3G | 3 | 70.4 | -0.28036 | west | N | -0.30254 | -0.28346 | -0.013537 | -0.29126 | 0.013537 | west | N | 0.013537 | 0
1058 | LONGSHOR | 1 | 150 | -0.28101 | west | Y | -0.30319 | -0.28411 | -0.014187 | -0.29191 | 0.014187 | west | N | 0.014187 | 0
1058 | LONGSHOR | 2 | 220 | -0.28101 | west | Y | -0.30319 | -0.28411 | -0.014187 | -0.29191 | 0.014187 | west | N | 0.014187 | 0
1061 | CIELOGEN | 1 | 99 | -0.26773 | west | Y | -0.28992 | -0.27083 | -0.0009148 | -0.27863 | 0.0009148 | west | N | 0.0009148 | 0
1062 | CIELOGEN | 1 | 61 | -0.26773 | west | Y | -0.28992 | -0.27083 | -0.0009148 | -0.27863 | 0.0009148 | west | N | 0.0009148 | 0
1068 | SCURRYCW | 1 | 141 | -0.26799 | west | Y | -0.29017 | -0.27109 | -0.0011668 | -0.27889 | 0.0011668 | west | N | 0.0011668 | 0
1069 | KINDERMG | 1 | 25 | -0.26773 | west | N | -0.28992 | -0.27083 | -0.0009148 | -0.27863 | 0.0009148 | west | N | 0.0009148 | 0
1070 | KINDERMG | 1 | 45.7 | -0.26773 | west | N | -0.28992 | -0.27083 | -0.0009148 | -0.27863 | 0.0009148 | west | N | 0.0009148 | 0
1071 | KINDERMG | 1 | 45.7 | -0.26773 | west | N | -0.28992 | -0.27083 | -0.0009148 | -0.27863 | 0.0009148 | west | N | 0.0009148 | 0
1073 | SCURRYCW | 2 | 120 | -0.26799 | west | Y | -0.29017 | -0.27109 | -0.0011668 | -0.27889 | 0.0011668 | west | N | 0.0011668 | 0
1320 | BSP 1 | 1 | 25.8 | -0.27292 | west | N | -0.29511 | -0.27602 | -0.0061048 | -0.28382 | 0.0061048 | west | N | 0.0061048 | 0
1326 | STANTONW | 1 | 100.5 | -0.27556 | west | Y | -0.29774 | -0.27866 | -0.0087388 | -0.28646 | 0.0087388 | west | N | 0.0087388 | 0
1327 | WILDHRSE | 1 | 120 | -0.27372 | west | Y | -0.2959 | -0.27682 | -0.0068998 | -0.28462 | 0.0068998 | west | N | 0.0068998 | 0
1328 | OCOTILLO | 1 | 58 | -0.27572 | west | Y | -0.2979 | -0.27882 | -0.0088988 | -0.28662 | 0.0088988 | west | N | 0.0088988 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.27593 | west | Y | -0.29812 | -0.27903 | -0.0091148 | -0.28683 | 0.0091148 | west | N | 0.0091148 | 0
1343 | TRENTIPP | 1 | 150 | -0.27427 | west | Y | -0.29646 | -0.27737 | -0.0074528 | -0.28517 | 0.0074528 | west | N | 0.0074528 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.26908 | west | Y | -0.29127 | -0.27218 | -0.0022638 | -0.27998 | 0.0022638 | west | N | 0.0022638 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.26908 | west | Y | -0.29127 | -0.27218 | -0.0022638 | -0.27998 | 0.0022638 | west | N | 0.0022638 | 0
1354 | AEPWIND_ | 1 | 101 | -0.27427 | west | Y | -0.29646 | -0.27737 | -0.0074528 | -0.28517 | 0.0074528 | west | N | 0.0074528 | 0
1360 | GUNSIGHT | 1 | 120 | -0.27307 | west | Y | -0.29526 | -0.27617 | -0.0062518 | -0.28397 | 0.0062518 | west | N | 0.0062518 | 0
1432 | GRHAMSES | 2 | 366 | 0.086836 | north | Y | 0.064651 | 0.083737 | 0.35366 | 0.075936 | 0.064651 | North | N | 0.064651 | 0
1433 | GRHAMSES | 1 | 242 | 0.021367 | north | Y | -0.00081847 | 0.018268 | 0.28819 | 0.010467 | 0.00081847 | North | N | 0.00081847 | 0
1437 | MESQUITW | 1 | 400 | -0.46932 | west | Y | -0.49151 | -0.47242 | -0.2025 | -0.48022 | 0.2025 | west | N | 0.2025 | 0
1438 | MESQUITW | 1 | 236 | -0.46891 | west | Y | -0.4911 | -0.47201 | -0.20209 | -0.47981 | 0.20209 | west | N | 0.20209 | 0
1442 | COKFIELD | 1 | 165 | 0.086836 | west | Y | 0.064651 | 0.083737 | 0.35366 | 0.075936 | 0.064651 | North | Y | 0.35366 | 47.6858
1453 | WCPWRCO_ | 1 | 204 | 0.046579 | north | Y | 0.024394 | 0.04348 | 0.3134 | 0.035679 | 0.024394 | North | N | 0.024394 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.046579 | north | Y | 0.024394 | 0.04348 | 0.3134 | 0.035679 | 0.024394 | North | N | 0.024394 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.046579 | north | Y | 0.024394 | 0.04348 | 0.3134 | 0.035679 | 0.024394 | North | N | 0.024394 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.01579 | west | Y | -0.0063955 | 0.012691 | 0.28261 | 0.0048901 | 0.0048901 | houston | Y | 0.28261 | 5.5544
1479 | WFCOGEN_ | 2 | 20 | 0.01579 | west | Y | -0.0063955 | 0.012691 | 0.28261 | 0.0048901 | 0.0048901 | houston | Y | 0.28261 | 5.5544
1482 | WFCOGEN_ | 1 | 20 | 0.01579 | west | Y | -0.0063955 | 0.012691 | 0.28261 | 0.0048901 | 0.0048901 | houston | Y | 0.28261 | 5.5544
1482 | WFCOGEN_ | 2 | 17 | 0.01579 | west | Y | -0.0063955 | 0.012691 | 0.28261 | 0.0048901 | 0.0048901 | houston | Y | 0.28261 | 4.7212
1600 | BARTNWND | 1 | 120 | 0.016979 | north | Y | -0.0052065 | 0.01388 | 0.2838 | 0.0060791 | 0.0052065 | North | N | 0.0052065 | 0
1643 | SLSTR1PP | 1 | 60 | -0.032056 | north | Y | -0.054241 | -0.035155 | 0.23476 | -0.042956 | 0.035155 | south | Y | 0.054241 | 1.1452
1675 | PEC_1G | 1 | 75 | 0.025247 | north | N | 0.0030615 | 0.022148 | 0.29207 | 0.014347 | 0.0030615 | North | N | 0.0030615 | 0
1676 | PEC_2G | 2 | 79.6 | 0.025247 | north | N | 0.0030615 | 0.022148 | 0.29207 | 0.014347 | 0.0030615 | North | N | 0.0030615 | 0
1677 | PEC_3G | 3 | 88.4 | 0.025247 | north | N | 0.0030615 | 0.022148 | 0.29207 | 0.014347 | 0.0030615 | North | N | 0.0030615 | 0
1678 | LAMARPWR | 1 | 160 | 0.025313 | north | Y | 0.0031275 | 0.022214 | 0.29213 | 0.014413 | 0.0031275 | North | N | 0.0031275 | 0
1679 | LAMARPWR | 2 | 156 | 0.025313 | north | Y | 0.0031275 | 0.022214 | 0.29213 | 0.014413 | 0.0031275 | North | N | 0.0031275 | 0
1680 | LAMARPWR | 3 | 196 | 0.025313 | north | Y | 0.0031275 | 0.022214 | 0.29213 | 0.014413 | 0.0031275 | North | N | 0.0031275 | 0
1681 | LAMARPWR | 4 | 156 | 0.025313 | north | Y | 0.0031275 | 0.022214 | 0.29213 | 0.014413 | 0.0031275 | North | N | 0.0031275 | 0
1682 | LAMARPWR | 5 | 157 | 0.025313 | north | Y | 0.0031275 | 0.022214 | 0.29213 | 0.014413 | 0.0031275 | North | N | 0.0031275 | 0
1683 | LAMARPWR | 6 | 198 | 0.025313 | north | Y | 0.0031275 | 0.022214 | 0.29213 | 0.014413 | 0.0031275 | North | N | 0.0031275 | 0
1687 | VALLEY_1 | 1 | 170 | 0.025507 | north | Y | 0.0033215 | 0.022408 | 0.29233 | 0.014607 | 0.0033215 | North | N | 0.0033215 | 0
1688 | VALLEY_2 | 2 | 520 | 0.025507 | north | Y | 0.0033215 | 0.022408 | 0.29233 | 0.014607 | 0.0033215 | North | N | 0.0033215 | 0
1689 | VALLEY_3 | 3 | 370 | 0.025395 | north | Y | 0.0032095 | 0.022296 | 0.29221 | 0.014495 | 0.0032095 | North | N | 0.0032095 | 0
1701 | MOSES_1G | 1 | 558 | 0.025176 | north | Y | 0.0029905 | 0.022077 | 0.292 | 0.014276 | 0.0029905 | North | N | 0.0029905 | 0
1702 | MOSES_2G | 2 | 579 | 0.025176 | north | Y | 0.0029905 | 0.022077 | 0.292 | 0.014276 | 0.0029905 | North | N | 0.0029905 | 0
1703 | MOSES_3G | 3 | 808 | 0.025176 | north | Y | 0.0029905 | 0.022077 | 0.292 | 0.014276 | 0.0029905 | North | N | 0.0029905 | 0
1861 | EAGLEMNT | MB | 112 | 0.029217 | north | Y | 0.0070315 | 0.026118 | 0.29604 | 0.018317 | 0.0070315 | North | N | 0.0070315 | 0
1862 | EAGLEMNT | MB | 100 | 0.029217 | north | Y | 0.0070315 | 0.026118 | 0.29604 | 0.018317 | 0.0070315 | North | N | 0.0070315 | 0
1863 | EAGLEMNT | MB | 378 | 0.029217 | north | Y | 0.0070315 | 0.026118 | 0.29604 | 0.018317 | 0.0070315 | North | N | 0.0070315 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.014304 | north | Y | -0.0078815 | 0.011205 | 0.28112 | 0.0034041 | 0.0034041 | houston | Y | 0.0078815 | 0.97293
1878 | WLFHOLW_ | 2 | 205 | 0.014304 | north | Y | -0.0078815 | 0.011205 | 0.28112 | 0.0034041 | 0.0034041 | houston | Y | 0.0078815 | 0.91786
1879 | WLFHOLW_ | 3 | 272.4 | 0.014304 | north | Y | -0.0078815 | 0.011205 | 0.28112 | 0.0034041 | 0.0034041 | houston | Y | 0.0078815 | 1.2196
1889 | DECRDOVA | MB | 770 | 0.018958 | north | Y | -0.0032275 | 0.015859 | 0.28578 | 0.0080581 | 0.0032275 | North | N | 0.0032275 | 0
1892 | DECRDOVA | A | 70 | 0.014306 | north | Y | -0.0078795 | 0.011207 | 0.28113 | 0.0034061 | 0.0034061 | houston | Y | 0.0078795 | 0.31313
1893 | DECRDOVA | B | 69 | 0.014306 | north | Y | -0.0078795 | 0.011207 | 0.28113 | 0.0034061 | 0.0034061 | houston | Y | 0.0078795 | 0.30866
1894 | DECRDOVA | C | 69 | 0.014306 | north | Y | -0.0078795 | 0.011207 | 0.28113 | 0.0034061 | 0.0034061 | houston | Y | 0.0078795 | 0.30866
1895 | DECRDOVA | D | 68 | 0.014306 | north | Y | -0.0078795 | 0.011207 | 0.28113 | 0.0034061 | 0.0034061 | houston | Y | 0.0078795 | 0.30419
1898 | COMCHEPK | 1 | 1157 | 0.012844 | north | N | -0.0093415 | 0.0097449 | 0.27966 | 0.0019441 | 0.0019441 | houston | Y | 0.0093415 | 0
1899 | COMCHEPK | 2 | 1158 | 0.012844 | north | N | -0.0093415 | 0.0097449 | 0.27966 | 0.0019441 | 0.0019441 | houston | Y | 0.0093415 | 0
1937 | MDLTHELP | 5 | 224 | 0.020814 | north | Y | -0.0013715 | 0.017715 | 0.28763 | 0.0099141 | 0.0013715 | North | N | 0.0013715 | 0
1938 | MDLTHELP | 6 | 226 | 0.020814 | north | Y | -0.0013715 | 0.017715 | 0.28763 | 0.0099141 | 0.0013715 | North | N | 0.0013715 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.021954 | north | Y | -0.00023147 | 0.018855 | 0.28877 | 0.011054 | 0.00023147 | North | N | 0.00023147 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.021954 | north | Y | -0.00023147 | 0.018855 | 0.28877 | 0.011054 | 0.00023147 | North | N | 0.00023147 | 0
1943 | MDLTHELP | 3 | 212 | 0.020814 | north | Y | -0.0013715 | 0.017715 | 0.28763 | 0.0099141 | 0.0013715 | North | N | 0.0013715 | 0
1944 | MDLTHELP | 4 | 211 | 0.020814 | north | Y | -0.0013715 | 0.017715 | 0.28763 | 0.0099141 | 0.0013715 | North | N | 0.0013715 | 0
1947 | HANDLEY_ | 3 | 395 | 0.024881 | north | Y | 0.0026955 | 0.021782 | 0.2917 | 0.013981 | 0.0026955 | North | N | 0.0026955 | 0
1948 | HANDLEY_ | 4 | 435 | 0.024829 | north | Y | 0.0026435 | 0.02173 | 0.29165 | 0.013929 | 0.0026435 | North | N | 0.0026435 | 0
1949 | HANDLEY_ | 5 | 435 | 0.024881 | north | Y | 0.0026955 | 0.021782 | 0.2917 | 0.013981 | 0.0026955 | North | N | 0.0026955 | 0
2371 | COLLIN_1 | MB | 138 | 0.026342 | north | Y | 0.0041565 | 0.023243 | 0.29316 | 0.015442 | 0.0041565 | North | N | 0.0041565 | 0
2413 | MTCK6_G | 6 | 118 | 0.023603 | north | Y | 0.0014175 | 0.020504 | 0.29042 | 0.012703 | 0.0014175 | North | N | 0.0014175 | 0
2414 | MTCK7_G | 7 | 115 | 0.023603 | north | Y | 0.0014175 | 0.020504 | 0.29042 | 0.012703 | 0.0014175 | North | N | 0.0014175 | 0
2417 | MTCK8_G | 8 | 556 | 0.023603 | north | Y | 0.0014175 | 0.020504 | 0.29042 | 0.012703 | 0.0014175 | North | N | 0.0014175 | 0
2451 | LKHB1_G | 1 | 388 | 0.024186 | north | Y | 0.0020005 | 0.021087 | 0.29101 | 0.013286 | 0.0020005 | North | N | 0.0020005 | 0
2452 | LKHB2_G | 2 | 515 | 0.024186 | north | Y | 0.0020005 | 0.021087 | 0.29101 | 0.013286 | 0.0020005 | North | N | 0.0020005 | 0
3097 | MARTLAKE | 1 | 785 | 0.022493 | north | Y | 0.00030753 | 0.019394 | 0.28931 | 0.011593 | 0.00030753 | North | N | 0.00030753 | 0
3098 | MARTLAKE | 2 | 795 | 0.022493 | north | Y | 0.00030753 | 0.019394 | 0.28931 | 0.011593 | 0.00030753 | North | N | 0.00030753 | 0
3099 | MARTLAKE | 3 | 780 | 0.022493 | north | Y | 0.00030753 | 0.019394 | 0.28931 | 0.011593 | 0.00030753 | North | N | 0.00030753 | 0
3107 | STRYKER_ | 1 | 182 | 0.022042 | north | Y | -0.00014347 | 0.018943 | 0.28886 | 0.011142 | 0.00014347 | North | N | 0.00014347 | 0
3108 | STRYKER_ | 2 | 484 | 0.022042 | north | Y | -0.00014347 | 0.018943 | 0.28886 | 0.011142 | 0.00014347 | North | N | 0.00014347 | 0
3126 | TRINIDAD | 1 | 224 | 0.021155 | north | Y | -0.0010305 | 0.018056 | 0.28797 | 0.010255 | 0.0010305 | North | N | 0.0010305 | 0
3309 | ASPN_G | 1 | 50 | 0.02208 | north | Y | -0.00010547 | 0.018981 | 0.2889 | 0.01118 | 0.00010547 | North | N | 0.00010547 | 0
3348 | CHAMPION | MB | 42 | 0.0221 | north | N | -8.5468e-05 | 0.019001 | 0.28892 | 0.0112 | 8.5468e-05 | North | N | 8.5468e-05 | 0
3381 | BBRN_1G | 1 | 615 | 0.019837 | north | Y | -0.0023485 | 0.016738 | 0.28666 | 0.0089371 | 0.0023485 | North | N | 0.0023485 | 0
3382 | BBRN_2G | 2 | 587 | 0.019837 | north | Y | -0.0023485 | 0.016738 | 0.28666 | 0.0089371 | 0.0023485 | North | N | 0.0023485 | 0
3403 | THOUSE_1 | MB | 537 | 0.014889 | north | Y | -0.0072965 | 0.01179 | 0.28171 | 0.0039891 | 0.0039891 | houston | Y | 0.0072965 | 0
3404 | THOUSE_2 | 2 | 787 | 0.014889 | north | Y | -0.0072965 | 0.01179 | 0.28171 | 0.0039891 | 0.0039891 | houston | Y | 0.0072965 | 2.6029
3416 | LAKE_CRK | MB | 75 | 0.01414 | north | Y | -0.0080455 | 0.011041 | 0.28096 | 0.0032401 | 0.0032401 | houston | Y | 0.0080455 | 0
3417 | LAKE_CRK | MB | 222 | 0.01414 | north | Y | -0.0080455 | 0.011041 | 0.28096 | 0.0032401 | 0.0032401 | houston | Y | 0.0080455 | 0
3432 | SANDOW_4 | 4 | 569 | 0.008517 | south | Y | -0.013668 | 0.0054179 | 0.27534 | -0.0023829 | 0.0023829 | houston | Y | 0.0054179 | 1.7269
5026 | BRAUNIG_ | 1 | 209 | 0.001612 | south | Y | -0.020573 | -0.0014871 | 0.26843 | -0.0092879 | 0.0014871 | south | N | 0.0014871 | 0
5027 | BRAUNIG_ | 2 | 216 | 0.001612 | south | Y | -0.020573 | -0.0014871 | 0.26843 | -0.0092879 | 0.0014871 | south | N | 0.0014871 | 0
5028 | BRAUNIG_ | 3 | 407 | 0.001451 | south | Y | -0.020734 | -0.0016481 | 0.26827 | -0.0094489 | 0.0016481 | south | N | 0.0016481 | 0
5031 | BRA_VHBC | 1 | 46 | 0.001612 | south | Y | -0.020573 | -0.0014871 | 0.26843 | -0.0092879 | 0.0014871 | south | N | 0.0014871 | 0
5032 | BRA_VHBC | 2 | 47 | 0.001612 | south | Y | -0.020573 | -0.0014871 | 0.26843 | -0.0092879 | 0.0014871 | south | N | 0.0014871 | 0
5033 | BRA_VHBC | 3 | 46 | 0.001612 | south | Y | -0.020573 | -0.0014871 | 0.26843 | -0.0092879 | 0.0014871 | south | N | 0.0014871 | 0
5034 | BRA_VHBC | 4 | 46 | 0.001612 | south | Y | -0.020573 | -0.0014871 | 0.26843 | -0.0092879 | 0.0014871 | south | N | 0.0014871 | 0
5111 | CALAVER_ | 1 | 424 | 0.001696 | south | Y | -0.020489 | -0.0014031 | 0.26852 | -0.0092039 | 0.0014031 | south | N | 0.0014031 | 0
5112 | CALAVER_ | 2 | 425 | 0.001696 | south | Y | -0.020489 | -0.0014031 | 0.26852 | -0.0092039 | 0.0014031 | south | N | 0.0014031 | 0
5264 | LEON_LCP | 3 | 58 | 0.000983 | south | Y | -0.021202 | -0.0021161 | 0.2678 | -0.0099169 | 0.0021161 | south | N | 0.0021161 | 0
5265 | LEON_LCP | 4 | 89 | 0.000983 | south | Y | -0.021202 | -0.0021161 | 0.2678 | -0.0099169 | 0.0021161 | south | N | 0.0021161 | 0
5266 | LEON_LCP | 1 | 44 | 0.000983 | south | Y | -0.021202 | -0.0021161 | 0.2678 | -0.0099169 | 0.0021161 | south | N | 0.0021161 | 0
5267 | LEON_LCP | 2 | 44 | 0.000983 | south | Y | -0.021202 | -0.0021161 | 0.2678 | -0.0099169 | 0.0021161 | south | N | 0.0021161 | 0
5268 | LEON_LCP | 3 | 43 | 0.000983 | south | Y | -0.021202 | -0.0021161 | 0.2678 | -0.0099169 | 0.0021161 | south | N | 0.0021161 | 0
5269 | LEON_LCP | 4 | 45 | 0.000983 | south | Y | -0.021202 | -0.0021161 | 0.2678 | -0.0099169 | 0.0021161 | south | N | 0.0021161 | 0
5396 | CALAVER_ | 1 | 412 | 0.001614 | south | Y | -0.020571 | -0.0014851 | 0.26843 | -0.0092859 | 0.0014851 | south | N | 0.0014851 | 0
5397 | CALAVER_ | 2 | 400 | 0.001614 | south | Y | -0.020571 | -0.0014851 | 0.26843 | -0.0092859 | 0.0014851 | south | N | 0.0014851 | 0
5401 | CALAVER_ | 1 | 546 | 0.002301 | south | Y | -0.019884 | -0.00079815 | 0.26912 | -0.0085989 | 0.00079815 | south | N | 0.00079815 | 0
5402 | CALAVER_ | 2 | 750 | 0.002301 | south | Y | -0.019884 | -0.00079815 | 0.26912 | -0.0085989 | 0.00079815 | south | N | 0.00079815 | 0
5436 | TUTTL_WB | MB | 61 | 0.00204 | south | Y | -0.020145 | -0.0010591 | 0.26886 | -0.0088599 | 0.0010591 | south | N | 0.0010591 | 0
5438 | TUTTL_WB | MB | 95 | 0.00204 | south | Y | -0.020145 | -0.0010591 | 0.26886 | -0.0088599 | 0.0010591 | south | N | 0.0010591 | 0
5439 | TUTTL_WB | MB | 151 | 0.00204 | south | Y | -0.020145 | -0.0010591 | 0.26886 | -0.0088599 | 0.0010591 | south | N | 0.0010591 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.002143 | south | Y | -0.020042 | -0.00095615 | 0.26896 | -0.0087569 | 0.00095615 | south | N | 0.00095615 | 0
5477 | BRA_AVR1 | 1 | 170 | 0.002143 | south | Y | -0.020042 | -0.00095615 | 0.26896 | -0.0087569 | 0.00095615 | south | N | 0.00095615 | 0
5478 | BRA_AVR1 | 1 | 155 | 0.002143 | south | Y | -0.020042 | -0.00095615 | 0.26896 | -0.0087569 | 0.00095615 | south | N | 0.00095615 | 0
5503 | RAYBURNG | 1 | 22 | 0.003709 | south | Y | -0.018476 | 0.00060985 | 0.27053 | -0.0071909 | 0.00060985 | south | N | 0.00060985 | 0
5505 | RAYBURNG | 1 | 11 | 0.003709 | south | Y | -0.018476 | 0.00060985 | 0.27053 | -0.0071909 | 0.00060985 | south | N | 0.00060985 | 0
5506 | RAYBURNG | 1 | 11 | 0.003709 | south | Y | -0.018476 | 0.00060985 | 0.27053 | -0.0071909 | 0.00060985 | south | N | 0.00060985 | 0
5508 | RAYBURNC | 1 | 47.7 | 0.003897 | south | Y | -0.018288 | 0.00079785 | 0.27072 | -0.0070029 | 0.00079785 | south | N | 0.00079785 | 0
5509 | RAYBURNC | 1 | 37.3 | 0.003897 | south | Y | -0.018288 | 0.00079785 | 0.27072 | -0.0070029 | 0.00079785 | south | N | 0.00079785 | 0
5511 | RAYBURNC | 1 | 46 | 0.003897 | south | Y | -0.018288 | 0.00079785 | 0.27072 | -0.0070029 | 0.00079785 | south | N | 0.00079785 | 0
5512 | RAYBURNC | 1 | 48 | 0.003897 | south | Y | -0.018288 | 0.00079785 | 0.27072 | -0.0070029 | 0.00079785 | south | N | 0.00079785 | 0
5728 | FALCONHY | 2 | 12 | 0.000104 | south | N | -0.022081 | -0.0029951 | 0.26692 | -0.010796 | 0.0029951 | south | N | 0.0029951 | 0
5729 | FALCONHY | 3 | 11 | 0.000104 | south | N | -0.022081 | -0.0029951 | 0.26692 | -0.010796 | 0.0029951 | south | N | 0.0029951 | 0
5890 | PEARSALL | 1 | 24 | -0.008087 | south | Y | -0.030272 | -0.011186 | 0.25873 | -0.018987 | 0.011186 | south | N | 0.011186 | 0
5891 | PEARSALL | 1 | 24 | -0.008087 | south | Y | -0.030272 | -0.011186 | 0.25873 | -0.018987 | 0.011186 | south | N | 0.011186 | 0
5892 | PEARSALL | 1 | 23 | -0.008087 | south | Y | -0.030272 | -0.011186 | 0.25873 | -0.018987 | 0.011186 | south | N | 0.011186 | 0
5903 | SANMIGUE | 1 | 396 | 0.001559 | south | Y | -0.020626 | -0.0015401 | 0.26838 | -0.0093409 | 0.0015401 | south | N | 0.0015401 | 0
5911 | STP_GN1_ | 1 | 1333 | 0.008249 | houston | N | -0.013936 | 0.0051499 | 0.27507 | -0.0026509 | 0.0026509 | houston | N | 0.0026509 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.008249 | houston | N | -0.013936 | 0.0051499 | 0.27507 | -0.0026509 | 0.0026509 | houston | N | 0.0026509 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | Y | 0.022185 | 0
5932 | SI_RAY9 | 9 | 38 | 0.002709 | south | Y | -0.019476 | -0.00039015 | 0.26953 | -0.0081909 | 0.00039015 | south | N | 0.00039015 | 0
5933 | SI_RAY6 | 6 | 19.3 | 0.002709 | south | Y | -0.019476 | -0.00039015 | 0.26953 | -0.0081909 | 0.00039015 | south | N | 0.00039015 | 0
5934 | SI_RAY5 | 5 | 15 | 0.002709 | south | Y | -0.019476 | -0.00039015 | 0.26953 | -0.0081909 | 0.00039015 | south | N | 0.00039015 | 0
5935 | SI_RAY10 | 10 | 47 | 0.002709 | south | Y | -0.019476 | -0.00039015 | 0.26953 | -0.0081909 | 0.00039015 | south | N | 0.00039015 | 0
6016 | SWMESA | 1 | 75 | -0.25939 | west | Y | -0.28158 | -0.26249 | 0.0074252 | -0.27029 | 0.0074252 | west | N | 0.0074252 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | Y | 0.26682 | 0
6144 | MCADOO1A | 1 | 150 | -0.23811 | west | Y | -0.2603 | -0.24121 | 0.028707 | -0.24901 | 0.028707 | west | N | 0.028707 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.2859 | west | Y | -0.30808 | -0.289 | -0.019079 | -0.2968 | 0.019079 | west | N | 0.019079 | 0
6476 | LANGFORD | 1 | 150 | -0.19825 | west | Y | -0.22043 | -0.20135 | 0.068572 | -0.20915 | 0.068572 | west | N | 0.068572 | 0
6637 | SNYDERW1 | 1 | 63 | -0.27034 | west | Y | -0.29252 | -0.27344 | -0.0035188 | -0.28124 | 0.0035188 | west | N | 0.0035188 | 0
6752 | OKLA0A | 1 | 649.7 | -0.11681 | west | Y | -0.139 | -0.11991 | 0.15001 | -0.12771 | 0.11991 | south | Y | 0.15001 | 19.5547
6948 | DENISNDM | 1 | 40 | 0.025608 | north | N | 0.0034225 | 0.022509 | 0.29243 | 0.014708 | 0.0034225 | North | N | 0.0034225 | 0
6948 | DENISNDM | 2 | 40 | 0.025608 | north | N | 0.0034225 | 0.022509 | 0.29243 | 0.014708 | 0.0034225 | North | N | 0.0034225 | 0
7000 | L_FERGUS | 1 | 422 | -0.006901 | south | Y | -0.029086 | -0.01 | 0.25992 | -0.017801 | 0.01 | south | N | 0.01 | 0
7004 | L_SIMGID | 1 | 132 | 0.005592 | south | Y | -0.016593 | 0.0024929 | 0.27241 | -0.0053079 | 0.0024929 | south | N | 0.0024929 | 0
7005 | L_SIMGID | 2 | 134 | 0.005592 | south | Y | -0.016593 | 0.0024929 | 0.27241 | -0.0053079 | 0.0024929 | south | N | 0.0024929 | 0
7006 | L_SIMGID | 3 | 323 | 0.005592 | south | Y | -0.016593 | 0.0024929 | 0.27241 | -0.0053079 | 0.0024929 | south | N | 0.0024929 | 0
7007 | L_LOSTPI | 1 | 158 | 0.006136 | south | Y | -0.016049 | 0.0030369 | 0.27296 | -0.0047639 | 0.0030369 | south | N | 0.0030369 | 0
7008 | L_LOSTPI | 2 | 160 | 0.006136 | south | Y | -0.016049 | 0.0030369 | 0.27296 | -0.0047639 | 0.0030369 | south | N | 0.0030369 | 0
7009 | L_LOSTPI | 3 | 175 | 0.006136 | south | Y | -0.016049 | 0.0030369 | 0.27296 | -0.0047639 | 0.0030369 | south | N | 0.0030369 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.006197 | south | Y | -0.015988 | 0.0030979 | 0.27302 | -0.0047029 | 0.0030979 | south | N | 0.0030979 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.006197 | south | Y | -0.015988 | 0.0030979 | 0.27302 | -0.0047029 | 0.0030979 | south | N | 0.0030979 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.006194 | south | Y | -0.015991 | 0.0030949 | 0.27301 | -0.0047059 | 0.0030949 | south | N | 0.0030949 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.003565 | south | Y | -0.01862 | 0.00046585 | 0.27038 | -0.0073349 | 0.00046585 | south | N | 0.00046585 | 0
7015 | L_HAYSEN | 2 | 225 | 0.003565 | south | Y | -0.01862 | 0.00046585 | 0.27038 | -0.0073349 | 0.00046585 | south | N | 0.00046585 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.003565 | south | Y | -0.01862 | 0.00046585 | 0.27038 | -0.0073349 | 0.00046585 | south | N | 0.00046585 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.003565 | south | Y | -0.01862 | 0.00046585 | 0.27038 | -0.0073349 | 0.00046585 | south | N | 0.00046585 | 0
7020 | L_AUSTPL | 1 | 8 | 0.004585 | south | N | -0.0176 | 0.0014859 | 0.2714 | -0.0063149 | 0.0014859 | south | N | 0.0014859 | 0
7020 | L_AUSTPL | 2 | 8 | 0.004585 | south | N | -0.0176 | 0.0014859 | 0.2714 | -0.0063149 | 0.0014859 | south | N | 0.0014859 | 0
7022 | L_BUCHAN | 1 | 18 | -0.007352 | south | N | -0.029537 | -0.010451 | 0.25947 | -0.018252 | 0.010451 | south | N | 0.010451 | 0
7023 | L_BUCHAN | 2 | 18 | -0.007352 | south | N | -0.029537 | -0.010451 | 0.25947 | -0.018252 | 0.010451 | south | N | 0.010451 | 0
7024 | L_BUCHAN | 3 | 15 | -0.007352 | south | N | -0.029537 | -0.010451 | 0.25947 | -0.018252 | 0.010451 | south | N | 0.010451 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.010456 | south | N | -0.032641 | -0.013555 | 0.25636 | -0.021356 | 0.013555 | south | N | 0.013555 | 0
7028 | L_MARBFA | 1 | 18 | -0.004223 | south | N | -0.026408 | -0.0073221 | 0.2626 | -0.015123 | 0.0073221 | south | N | 0.0073221 | 0
7029 | L_MARBFA | 2 | 18 | -0.004223 | south | N | -0.026408 | -0.0073221 | 0.2626 | -0.015123 | 0.0073221 | south | N | 0.0073221 | 0
7031 | L_MARSFO | 1 | 35 | 0.00185 | south | N | -0.020335 | -0.0012491 | 0.26867 | -0.0090499 | 0.0012491 | south | N | 0.0012491 | 0
7032 | L_MARSFO | 2 | 34 | 0.00185 | south | N | -0.020335 | -0.0012491 | 0.26867 | -0.0090499 | 0.0012491 | south | N | 0.0012491 | 0
7033 | L_MARSFO | 3 | 35 | 0.00185 | south | N | -0.020335 | -0.0012491 | 0.26867 | -0.0090499 | 0.0012491 | south | N | 0.0012491 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.006228 | south | N | -0.028413 | -0.0093271 | 0.26059 | -0.017128 | 0.0093271 | south | N | 0.0093271 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.006228 | south | N | -0.028413 | -0.0093271 | 0.26059 | -0.017128 | 0.0093271 | south | N | 0.0093271 | 0
7038 | L_DELAWA | 1 | 35 | -0.27432 | west | Y | -0.2965 | -0.27742 | -0.0074968 | -0.28522 | 0.0074968 | west | N | 0.0074968 | 0
7038 | L_DELAWA | 2 | 30 | -0.27432 | west | Y | -0.2965 | -0.27742 | -0.0074968 | -0.28522 | 0.0074968 | west | N | 0.0074968 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.005965 | south | Y | -0.01622 | 0.0028659 | 0.27278 | -0.0049349 | 0.0028659 | south | N | 0.0028659 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.005965 | south | Y | -0.01622 | 0.0028659 | 0.27278 | -0.0049349 | 0.0028659 | south | N | 0.0028659 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.005965 | south | Y | -0.01622 | 0.0028659 | 0.27278 | -0.0049349 | 0.0028659 | south | N | 0.0028659 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.005965 | south | Y | -0.01622 | 0.0028659 | 0.27278 | -0.0049349 | 0.0028659 | south | N | 0.0028659 | 0
7487 | L_CANYHY | 1 | 6 | 0.002921 | south | N | -0.019264 | -0.00017815 | 0.26974 | -0.0079789 | 0.00017815 | south | N | 0.00017815 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.003298 | south | N | -0.018887 | 0.00019885 | 0.27012 | -0.0076019 | 0.00019885 | south | N | 0.00019885 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.003298 | south | N | -0.018887 | 0.00019885 | 0.27012 | -0.0076019 | 0.00019885 | south | N | 0.00019885 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.003298 | south | N | -0.018887 | 0.00019885 | 0.27012 | -0.0076019 | 0.00019885 | south | N | 0.00019885 | 0
7609 | L_SCHUMA | 1 | 4 | 0.002869 | south | N | -0.019316 | -0.00023015 | 0.26969 | -0.0080309 | 0.00023015 | south | N | 0.00023015 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.003743 | south | N | -0.018442 | 0.00064385 | 0.27056 | -0.0071569 | 0.00064385 | south | N | 0.00064385 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.003743 | south | N | -0.018442 | 0.00064385 | 0.27056 | -0.0071569 | 0.00064385 | south | N | 0.00064385 | 0
7800 | L_GUADGE | 1 | 147 | 0.003041 | south | Y | -0.019144 | -5.8147e-05 | 0.26986 | -0.0078589 | 5.8147e-05 | south | N | 5.8147e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.003041 | south | Y | -0.019144 | -5.8147e-05 | 0.26986 | -0.0078589 | 5.8147e-05 | south | N | 5.8147e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.003041 | south | Y | -0.019144 | -5.8147e-05 | 0.26986 | -0.0078589 | 5.8147e-05 | south | N | 5.8147e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.003041 | south | Y | -0.019144 | -5.8147e-05 | 0.26986 | -0.0078589 | 5.8147e-05 | south | N | 5.8147e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.003041 | south | Y | -0.019144 | -5.8147e-05 | 0.26986 | -0.0078589 | 5.8147e-05 | south | N | 5.8147e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.003041 | south | Y | -0.019144 | -5.8147e-05 | 0.26986 | -0.0078589 | 5.8147e-05 | south | N | 5.8147e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.005624 | south | Y | -0.016561 | 0.0025249 | 0.27244 | -0.0052759 | 0.0025249 | south | N | 0.0025249 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.005624 | south | Y | -0.016561 | 0.0025249 | 0.27244 | -0.0052759 | 0.0025249 | south | N | 0.0025249 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.005624 | south | Y | -0.016561 | 0.0025249 | 0.27244 | -0.0052759 | 0.0025249 | south | N | 0.0025249 | 0
7810 | L_RIONOG | 1 | 142 | 0.003307 | south | Y | -0.018878 | 0.00020785 | 0.27013 | -0.0075929 | 0.00020785 | south | N | 0.00020785 | 0
7811 | L_RIONOG | 2 | 145 | 0.003307 | south | Y | -0.018878 | 0.00020785 | 0.27013 | -0.0075929 | 0.00020785 | south | N | 0.00020785 | 0
7812 | L_RIONOG | 3 | 151 | 0.003307 | south | Y | -0.018878 | 0.00020785 | 0.27013 | -0.0075929 | 0.00020785 | south | N | 0.00020785 | 0
7813 | L_RIONOG | 4 | 290 | 0.003307 | south | Y | -0.018878 | 0.00020785 | 0.27013 | -0.0075929 | 0.00020785 | south | N | 0.00020785 | 0
8032 | AMISTADH | 1 | 33 | -0.073908 | south | N | -0.096093 | -0.077007 | 0.19291 | -0.084808 | 0.077007 | south | N | 0.077007 | 0
8033 | AMISTADH | 2 | 25 | -0.073908 | south | N | -0.096093 | -0.077007 | 0.19291 | -0.084808 | 0.077007 | south | N | 0.077007 | 0
8048 | FALCONHY | 1 | 12 | 0.000104 | south | N | -0.022081 | -0.0029951 | 0.26692 | -0.010796 | 0.0029951 | south | N | 0.0029951 | 0
8066 | DUP1V#1 | 1 | 73 | 0.004084 | south | N | -0.018101 | 0.00098485 | 0.2709 | -0.0068159 | 0.00098485 | south | N | 0.00098485 | 0
8134 | FOR69CG0 | 1 | 79 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
8138 | FOR69CG0 | 2 | 81 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8147 | UCAR #2 | 10 | 28 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
8148 | UCAR #1 | 2 | 7 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
8153 | FOR69CG0 | 3 | 79 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
8154 | FOR69CG0 | 4 | 80 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
8156 | FOR69CG0 | 6 | 25 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
8157 | FOR69CG0 | 7 | 46 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
8161 | COLETOU1 | 1 | 629 | 0.003095 | south | Y | -0.01909 | -4.147e-06 | 0.26991 | -0.0078049 | 4.147e-06 | south | N | 4.147e-06 | 0
8173 | VICEC51A | 5 | 144 | 0.00398 | south | Y | -0.018205 | 0.00088085 | 0.2708 | -0.0069199 | 0.00088085 | south | N | 0.00088085 | 0
8174 | VICEC61A | 6 | 188 | 0.00398 | south | Y | -0.018205 | 0.00088085 | 0.2708 | -0.0069199 | 0.00088085 | south | N | 0.00088085 | 0
8189 | CUERO 2 | 1 | 12 | 0.003764 | south | N | -0.018421 | 0.00066485 | 0.27058 | -0.0071359 | 0.00066485 | south | N | 0.00066485 | 0
8262 | ELPS | 1 | 6 | -0.052988 | south | N | -0.075173 | -0.056087 | 0.21383 | -0.063888 | 0.056087 | south | N | 0.056087 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8442 | NBEC71A | 1 | 336 | 0.003084 | south | Y | -0.019101 | -1.5147e-05 | 0.2699 | -0.0078159 | 1.5147e-05 | south | N | 1.5147e-05 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.022185 | -0.0030991 | 0.26682 | -0.0109 | 0.0030991 | south | N | 0.0030991 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.003044 | south | Y | -0.019141 | -5.5147e-05 | 0.26986 | -0.0078559 | 5.5147e-05 | south | N | 5.5147e-05 | 0
8460 | B_DAVIS2 | 2 | 340 | 0.003044 | south | Y | -0.019141 | -5.5147e-05 | 0.26986 | -0.0078559 | 5.5147e-05 | south | N | 5.5147e-05 | 0
8461 | KOCH_UP0 | 1 | 38 | 0.002994 | south | N | -0.019191 | -0.00010515 | 0.26981 | -0.0079059 | 0.00010515 | south | N | 0.00010515 | 0
8506 | VAL #1 | 1 | 25 | 0.00302 | south | N | -0.019165 | -7.9147e-05 | 0.26984 | -0.0078799 | 7.9147e-05 | south | N | 7.9147e-05 | 0
8507 | VAL #2 | 2 | 25 | 0.00302 | south | N | -0.019165 | -7.9147e-05 | 0.26984 | -0.0078799 | 7.9147e-05 | south | N | 7.9147e-05 | 0
8511 | OXY_CC0A | 1 | 38 | 0.003017 | south | N | -0.019168 | -8.2147e-05 | 0.26984 | -0.0078829 | 8.2147e-05 | south | N | 8.2147e-05 | 0
8517 | CELANEBI | 1 | 29 | 0.002888 | south | N | -0.019297 | -0.00021115 | 0.26971 | -0.0080119 | 0.00021115 | south | N | 0.00021115 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.003082 | south | N | -0.019103 | -1.7147e-05 | 0.2699 | -0.0078179 | 1.7147e-05 | south | N | 1.7147e-05 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.003082 | south | N | -0.019103 | -1.7147e-05 | 0.2699 | -0.0078179 | 1.7147e-05 | south | N | 1.7147e-05 | 0
8562 | CNOPST1 | 3 | 153 | 0.003082 | south | N | -0.019103 | -1.7147e-05 | 0.2699 | -0.0078179 | 1.7147e-05 | south | N | 1.7147e-05 | 0
8926 | LGE_GT10 | 1 | 158 | 0.003288 | south | N | -0.018897 | 0.00018885 | 0.27011 | -0.0076119 | 0.00018885 | south | N | 0.00018885 | 0
8927 | LGE_GT20 | 2 | 153 | 0.003288 | south | N | -0.018897 | 0.00018885 | 0.27011 | -0.0076119 | 0.00018885 | south | N | 0.00018885 | 0
8928 | LGE_STG0 | 3 | 100 | 0.003288 | south | N | -0.018897 | 0.00018885 | 0.27011 | -0.0076119 | 0.00018885 | south | N | 0.00018885 | 0
8930 | ICPGN10A | 1 | 145 | 0.003288 | south | N | -0.018897 | 0.00018885 | 0.27011 | -0.0076119 | 0.00018885 | south | N | 0.00018885 | 0
8931 | ICPGN20A | 2 | 147 | 0.003288 | south | N | -0.018897 | 0.00018885 | 0.27011 | -0.0076119 | 0.00018885 | south | N | 0.00018885 | 0
8932 | ICPGN30A | 3 | 127 | 0.003288 | south | N | -0.018897 | 0.00018885 | 0.27011 | -0.0076119 | 0.00018885 | south | N | 0.00018885 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.00216 | south | Y | -0.020025 | -0.00093915 | 0.26898 | -0.0087399 | 0.00093915 | south | N | 0.00093915 | 0
8934 | FGNTS101 | 2 | 147.9 | 0.00216 | south | Y | -0.020025 | -0.00093915 | 0.26898 | -0.0087399 | 0.00093915 | south | N | 0.00093915 | 0
8935 | FGNTS201 | 3 | 173 | 0.00216 | south | Y | -0.020025 | -0.00093915 | 0.26898 | -0.0087399 | 0.00093915 | south | N | 0.00093915 | 0
8936 | MVGN#1 | 1 | 207 | 0.002503 | south | Y | -0.019682 | -0.00059615 | 0.26932 | -0.0083969 | 0.00059615 | south | N | 0.00059615 | 0
8937 | MVGN#2 | 2 | 216.7 | 0.002503 | south | Y | -0.019682 | -0.00059615 | 0.26932 | -0.0083969 | 0.00059615 | south | N | 0.00059615 | 0
8938 | MVGN#3 | 3 | 242 | 0.002503 | south | Y | -0.019682 | -0.00059615 | 0.26932 | -0.0083969 | 0.00059615 | south | N | 0.00059615 | 0
8981 | HECN1 | 1 | 144 | 0.002504 | south | Y | -0.019681 | -0.00059515 | 0.26932 | -0.0083959 | 0.00059515 | south | N | 0.00059515 | 0
8982 | HECN2 | 2 | 144 | 0.002504 | south | Y | -0.019681 | -0.00059515 | 0.26932 | -0.0083959 | 0.00059515 | south | N | 0.00059515 | 0
8983 | HECN3 | 3 | 171 | 0.002504 | south | Y | -0.019681 | -0.00059515 | 0.26932 | -0.0083959 | 0.00059515 | south | N | 0.00059515 | 0
9000 | DECKR_G1 | 1 | 310 | 0.004842 | south | Y | -0.017343 | 0.0017429 | 0.27166 | -0.0060579 | 0.0017429 | south | N | 0.0017429 | 0
9001 | DECKR_G2 | 2 | 413 | 0.004842 | south | Y | -0.017343 | 0.0017429 | 0.27166 | -0.0060579 | 0.0017429 | south | N | 0.0017429 | 0
9002 | DECKR_G3 | 3 | 42 | 0.005058 | south | Y | -0.017127 | 0.0019589 | 0.27188 | -0.0058419 | 0.0019589 | south | N | 0.0019589 | 0
9003 | DECKR_G4 | 4 | 44 | 0.005058 | south | Y | -0.017127 | 0.0019589 | 0.27188 | -0.0058419 | 0.0019589 | south | N | 0.0019589 | 0
9004 | DECKR_G5 | 5 | 44 | 0.005058 | south | Y | -0.017127 | 0.0019589 | 0.27188 | -0.0058419 | 0.0019589 | south | N | 0.0019589 | 0
9005 | DECKR_G6 | 6 | 47 | 0.005058 | south | Y | -0.017127 | 0.0019589 | 0.27188 | -0.0058419 | 0.0019589 | south | N | 0.0019589 | 0
9016 | SANDH_G1 | 1 | 49 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
9017 | SANDH_G2 | 2 | 46 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
9018 | SANDH_G3 | 3 | 46 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
9019 | SANDH_G4 | 4 | 47 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
9020 | SANDHG5A | 5A | 154 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
9021 | SANDHG5C | 5C | 148 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
9022 | SANDH_G6 | 6 | 48 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
9023 | SANDH_G7 | 7 | 48 | 0.004778 | south | Y | -0.017407 | 0.0016789 | 0.2716 | -0.0061219 | 0.0016789 | south | N | 0.0016789 | 0
11001 | NAV1CT | 1 | 70 | -0.27796 | west | Y | -0.30014 | -0.28106 | -0.011138 | -0.28886 | 0.011138 | west | N | 0.011138 | 0
11009 | NAV2CT | 1 | 70 | -0.27796 | west | Y | -0.30014 | -0.28106 | -0.011138 | -0.28886 | 0.011138 | west | N | 0.011138 | 0
11011 | NAV3ST | 1 | 92.8 | -0.27796 | west | Y | -0.30014 | -0.28106 | -0.011138 | -0.28886 | 0.011138 | west | N | 0.011138 | 0
11012 | NAV4CT | 1 | 80 | -0.27796 | west | Y | -0.30014 | -0.28106 | -0.011138 | -0.28886 | 0.011138 | west | N | 0.011138 | 0
11013 | NAV5CT | 1 | 80 | -0.27796 | west | Y | -0.30014 | -0.28106 | -0.011138 | -0.28886 | 0.011138 | west | N | 0.011138 | 0
11014 | NAV6ST | 1 | 115 | -0.27796 | west | Y | -0.30014 | -0.28106 | -0.011138 | -0.28886 | 0.011138 | west | N | 0.011138 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.27792 | west | Y | -0.30011 | -0.28102 | -0.011104 | -0.28882 | 0.011104 | west | N | 0.011104 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.27792 | west | Y | -0.30011 | -0.28102 | -0.011104 | -0.28882 | 0.011104 | west | N | 0.011104 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.27792 | west | Y | -0.30011 | -0.28102 | -0.011104 | -0.28882 | 0.011104 | west | N | 0.011104 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.27792 | west | Y | -0.30011 | -0.28102 | -0.011104 | -0.28882 | 0.011104 | west | N | 0.011104 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.27792 | west | Y | -0.30011 | -0.28102 | -0.011104 | -0.28882 | 0.011104 | west | N | 0.011104 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.27792 | west | Y | -0.30011 | -0.28102 | -0.011104 | -0.28882 | 0.011104 | west | N | 0.011104 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.23388 | west | Y | -0.25606 | -0.23698 | 0.032941 | -0.24478 | 0.032941 | west | N | 0.032941 | 0
11057 | CHAMPION | 1 | 126.5 | -0.23388 | west | Y | -0.25606 | -0.23698 | 0.032941 | -0.24478 | 0.032941 | west | N | 0.032941 | 0
11058 | PYRON_1G | 1 | 249 | -0.23388 | west | Y | -0.25606 | -0.23698 | 0.032941 | -0.24478 | 0.032941 | west | N | 0.032941 | 0
11059 | INADALE_ | 1 | 197 | -0.23388 | west | Y | -0.25606 | -0.23698 | 0.032941 | -0.24478 | 0.032941 | west | N | 0.032941 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.28101 | west | Y | -0.30319 | -0.28411 | -0.014187 | -0.29191 | 0.014187 | west | N | 0.014187 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.28101 | west | Y | -0.30319 | -0.28411 | -0.014187 | -0.29191 | 0.014187 | west | N | 0.014187 | 0
11147 | NOTREES_ | 1 | 149 | -0.27412 | west | Y | -0.29631 | -0.27722 | -0.0073048 | -0.28502 | 0.0073048 | west | N | 0.0073048 | 0
11309 | BULLCREK | 1 | 180 | -0.27106 | west | Y | -0.29324 | -0.27416 | -0.0042398 | -0.28196 | 0.0042398 | west | N | 0.0042398 | 0
11310 | BULLCREK | 1 | 180 | -0.27106 | west | Y | -0.29324 | -0.27416 | -0.0042398 | -0.28196 | 0.0042398 | west | N | 0.0042398 | 0
11320 | COYOTE_1 | 1 | 225 | -0.2712 | west | Y | -0.29339 | -0.2743 | -0.0043828 | -0.2821 | 0.0043828 | west | N | 0.0043828 | 0
11415 | LORAINE_ | 1 | 125 | -0.30374 | west | Y | -0.32593 | -0.30684 | -0.036921 | -0.31464 | 0.036921 | west | N | 0.036921 | 0
11416 | LORAINE_ | 1 | 125 | -0.30374 | west | Y | -0.32593 | -0.30684 | -0.036921 | -0.31464 | 0.036921 | west | N | 0.036921 | 0
11691 | KMICHICT | 1 | 140 | 0.025395 | north | N | 0.0032095 | 0.022296 | 0.29221 | 0.014495 | 0.0032095 | North | N | 0.0032095 | 0
11692 | KMICHICT | 2 | 141 | 0.025395 | north | N | 0.0032095 | 0.022296 | 0.29221 | 0.014495 | 0.0032095 | North | N | 0.0032095 | 0
11693 | KMICHIST | 3 | 309 | 0.025395 | north | N | 0.0032095 | 0.022296 | 0.29221 | 0.014495 | 0.0032095 | North | N | 0.0032095 | 0
11694 | KMICHICT | 4 | 143 | 0.025395 | north | N | 0.0032095 | 0.022296 | 0.29221 | 0.014495 | 0.0032095 | North | N | 0.0032095 | 0
11695 | KMICHICT | 5 | 144 | 0.025395 | north | N | 0.0032095 | 0.022296 | 0.29221 | 0.014495 | 0.0032095 | North | N | 0.0032095 | 0
11696 | KMICHIST | 6 | 310 | 0.025395 | north | N | 0.0032095 | 0.022296 | 0.29221 | 0.014495 | 0.0032095 | North | N | 0.0032095 | 0
12322 | ENNSTRAC | 1 | 196 | 0.021374 | north | Y | -0.00081147 | 0.018275 | 0.28819 | 0.010474 | 0.00081147 | North | N | 0.00081147 | 0
12323 | ENNSTRAC | 2 | 111 | 0.021374 | north | Y | -0.00081147 | 0.018275 | 0.28819 | 0.010474 | 0.00081147 | North | N | 0.00081147 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.025763 | north | N | 0.0035775 | 0.022664 | 0.29258 | 0.014863 | 0.0035775 | North | N | 0.0035775 | 0
12411 | FPLEFR1A | 1 | 161 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12412 | FPLEFR1B | 2 | 164 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12413 | FPLEFR1C | 3 | 164 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12414 | FPLEFR1S | 4 | 414 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12421 | FPLEFR2A | 1 | 162 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12422 | FPLEFR2B | 2 | 161 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12423 | FPLEFR2C | 3 | 163 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12424 | FPLEFR2S | 4 | 409 | 0.024062 | north | Y | 0.0018765 | 0.020963 | 0.29088 | 0.013162 | 0.0018765 | North | N | 0.0018765 | 0
12440 | PARKD_1S | 1 | 0 | 0.024036 | north | N | 0.0018505 | 0.020937 | 0.29086 | 0.013136 | 0.0018505 | North | N | 0.0018505 | 0
12449 | PARKD_2S | 1 | 0 | 0.024036 | north | N | 0.0018505 | 0.020937 | 0.29086 | 0.013136 | 0.0018505 | North | N | 0.0018505 | 0
13116 | TGATEWAY | 1 | 148 | 0.02228 | north | N | 9.4532e-05 | 0.019181 | 0.2891 | 0.01138 | 9.4532e-05 | North | N | 9.4532e-05 | 0
13117 | TGATEWAY | 2 | 130 | 0.02228 | north | N | 9.4532e-05 | 0.019181 | 0.2891 | 0.01138 | 9.4532e-05 | North | N | 9.4532e-05 | 0
13118 | TGATEWAY | 3 | 145 | 0.02228 | north | N | 9.4532e-05 | 0.019181 | 0.2891 | 0.01138 | 9.4532e-05 | North | N | 9.4532e-05 | 0
13119 | TGATEWAY | 4 | 399 | 0.02228 | north | N | 9.4532e-05 | 0.019181 | 0.2891 | 0.01138 | 9.4532e-05 | North | N | 9.4532e-05 | 0
13131 | CALFREST | 1 | 150.7 | 0.020197 | north | Y | -0.0019885 | 0.017098 | 0.28702 | 0.0092971 | 0.0019885 | North | N | 0.0019885 | 0
13132 | CALFREST | 2 | 151 | 0.020197 | north | Y | -0.0019885 | 0.017098 | 0.28702 | 0.0092971 | 0.0019885 | North | N | 0.0019885 | 0
13133 | CALFREST | 3 | 177.4 | 0.020197 | north | Y | -0.0019885 | 0.017098 | 0.28702 | 0.0092971 | 0.0019885 | North | N | 0.0019885 | 0
13134 | CALFREST | 4 | 151.5 | 0.020271 | north | Y | -0.0019145 | 0.017172 | 0.28709 | 0.0093711 | 0.0019145 | North | N | 0.0019145 | 0
13135 | CALFREST | 5 | 152.3 | 0.020271 | north | Y | -0.0019145 | 0.017172 | 0.28709 | 0.0093711 | 0.0019145 | North | N | 0.0019145 | 0
13136 | CALFREST | 6 | 177.5 | 0.020271 | north | Y | -0.0019145 | 0.017172 | 0.28709 | 0.0093711 | 0.0019145 | North | N | 0.0019145 | 0
13432 | SANDOW_5 | 5 | 581 | 0.008517 | south | Y | -0.013668 | 0.0054179 | 0.27534 | -0.0023829 | 0.0023829 | houston | Y | 0.0054179 | 1.7633
13691 | OAKGROVE | 1 | 855 | 0.01706 | north | Y | -0.0051255 | 0.013961 | 0.28388 | 0.0061601 | 0.0051255 | North | N | 0.0051255 | 0
13692 | OAKGROVE | 2 | 855 | 0.01706 | north | Y | -0.0051255 | 0.013961 | 0.28388 | 0.0061601 | 0.0051255 | North | N | 0.0051255 | 0
32798 | BRYN_TAM | 1 | 32 | 0.015199 | north | N | -0.0069865 | 0.0121 | 0.28202 | 0.0042991 | 0.0042991 | houston | Y | 0.0069865 | 0
32883 | BRYN_DNS | 1 | 48 | 0.015159 | north | Y | -0.0070265 | 0.01206 | 0.28198 | 0.0042591 | 0.0042591 | houston | Y | 0.0070265 | 0.13283
32884 | BRYN_DNS | 1 | 46 | 0.015159 | north | Y | -0.0070265 | 0.01206 | 0.28198 | 0.0042591 | 0.0042591 | houston | Y | 0.0070265 | 0.1273
32886 | BRYN_ATK | MB | 12 | 0.01521 | north | Y | -0.0069755 | 0.012111 | 0.28203 | 0.0043101 | 0.0043101 | houston | Y | 0.0069755 | 0
32887 | BRYN_ATK | MB | 51 | 0.01521 | north | Y | -0.0069755 | 0.012111 | 0.28203 | 0.0043101 | 0.0043101 | houston | Y | 0.0069755 | 0
32888 | BRYN_ATK | 1 | 17 | 0.01521 | north | Y | -0.0069755 | 0.012111 | 0.28203 | 0.0043101 | 0.0043101 | houston | Y | 0.0069755 | 0.045311
32890 | BRYN_ATK | MB | 22 | 0.01521 | north | Y | -0.0069755 | 0.012111 | 0.28203 | 0.0043101 | 0.0043101 | houston | Y | 0.0069755 | 0
32891 | BRYN_ATK | MB | 25 | 0.01521 | north | Y | -0.0069755 | 0.012111 | 0.28203 | 0.0043101 | 0.0043101 | houston | Y | 0.0069755 | 0
32892 | BRYN_DNS | 1 | 105 | 0.015159 | north | Y | -0.0070265 | 0.01206 | 0.28198 | 0.0042591 | 0.0042591 | houston | Y | 0.0070265 | 0.29057
36998 | RDCNYNG1 | 1 | 84 | -0.26223 | west | Y | -0.28442 | -0.26533 | 0.0045852 | -0.27313 | 0.0045852 | west | N | 0.0045852 | 0
38332 | WDWRDU2 | 1 | 80 | -0.25915 | west | Y | -0.28133 | -0.26225 | 0.0076712 | -0.27005 | 0.0076712 | west | N | 0.0076712 | 0
38437 | TNSRBNMS | 1 | 150 | -0.25901 | west | Y | -0.28119 | -0.26211 | 0.0078112 | -0.26991 | 0.0078112 | west | N | 0.0078112 | 0
38438 | TNSRBNMS | 1 | 150 | -0.25901 | west | Y | -0.28119 | -0.26211 | 0.0078112 | -0.26991 | 0.0078112 | west | N | 0.0078112 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38600 | TNBP_CGN | 5 | 53 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38614 | TNBPAMCG | 4 | 96 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38615 | TNBPAMCG | 1 | 244 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38690 | TNBP_CGN | 3 | 40 | 0.010787 | houston | N | -0.011398 | 0.0076879 | 0.27761 | -0.00011288 | 0.00011288 | houston | N | 0.00011288 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.010785 | houston | N | -0.0114 | 0.0076859 | 0.2776 | -0.00011488 | 0.00011488 | houston | N | 0.00011488 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.010785 | houston | N | -0.0114 | 0.0076859 | 0.2776 | -0.00011488 | 0.00011488 | houston | N | 0.00011488 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.010785 | houston | N | -0.0114 | 0.0076859 | 0.2776 | -0.00011488 | 0.00011488 | houston | N | 0.00011488 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.010785 | houston | N | -0.0114 | 0.0076859 | 0.2776 | -0.00011488 | 0.00011488 | houston | N | 0.00011488 | 0
39470 | TNDOWCGN | 1 | 32 | 0.010786 | houston | N | -0.011399 | 0.0076869 | 0.27761 | -0.00011388 | 0.00011388 | houston | N | 0.00011388 | 0
39480 | TNDOWCGN | 1 | 30 | 0.010786 | houston | N | -0.011399 | 0.0076869 | 0.27761 | -0.00011388 | 0.00011388 | houston | N | 0.00011388 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.009803 | houston | N | -0.012382 | 0.0067039 | 0.27662 | -0.0010969 | 0.0010969 | houston | N | 0.0010969 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.009803 | houston | N | -0.012382 | 0.0067039 | 0.27662 | -0.0010969 | 0.0010969 | houston | N | 0.0010969 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.009803 | houston | N | -0.012382 | 0.0067039 | 0.27662 | -0.0010969 | 0.0010969 | houston | N | 0.0010969 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.009803 | houston | N | -0.012382 | 0.0067039 | 0.27662 | -0.0010969 | 0.0010969 | houston | N | 0.0010969 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.01706 | north | Y | -0.0051255 | 0.013961 | 0.28388 | 0.0061601 | 0.0051255 | North | N | 0.0051255 | 0
39970 | TNTNPONE | 1 | 153 | 0.01706 | north | Y | -0.0051255 | 0.013961 | 0.28388 | 0.0061601 | 0.0051255 | North | N | 0.0051255 | 0
48500 | APD_GT1_ | 1 | 136 | 0.011375 | houston | N | -0.01081 | 0.0082759 | 0.27819 | 0.00047512 | 0.00047512 | houston | N | 0.00047512 | 0
48510 | AK_GT1__ | 1 | 33 | 0.01046 | houston | N | -0.011725 | 0.0073609 | 0.27728 | -0.00043988 | 0.00043988 | houston | N | 0.00043988 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.011373 | houston | Y | -0.010812 | 0.0082739 | 0.27819 | 0.00047312 | 0.00047312 | houston | N | 0.00047312 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.011373 | houston | Y | -0.010812 | 0.0082739 | 0.27819 | 0.00047312 | 0.00047312 | houston | N | 0.00047312 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.011373 | houston | Y | -0.010812 | 0.0082739 | 0.27819 | 0.00047312 | 0.00047312 | houston | N | 0.00047312 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.011373 | houston | Y | -0.010812 | 0.0082739 | 0.27819 | 0.00047312 | 0.00047312 | houston | N | 0.00047312 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.009626 | houston | N | -0.012559 | 0.0065269 | 0.27645 | -0.0012739 | 0.0012739 | houston | N | 0.0012739 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.009626 | houston | N | -0.012559 | 0.0065269 | 0.27645 | -0.0012739 | 0.0012739 | houston | N | 0.0012739 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.010434 | houston | N | -0.011751 | 0.0073349 | 0.27725 | -0.00046588 | 0.00046588 | houston | N | 0.00046588 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.010434 | houston | N | -0.011751 | 0.0073349 | 0.27725 | -0.00046588 | 0.00046588 | houston | N | 0.00046588 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.010434 | houston | N | -0.011751 | 0.0073349 | 0.27725 | -0.00046588 | 0.00046588 | houston | N | 0.00046588 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.011153 | houston | N | -0.011032 | 0.0080539 | 0.27797 | 0.00025312 | 0.00025312 | houston | N | 0.00025312 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.011153 | houston | N | -0.011032 | 0.0080539 | 0.27797 | 0.00025312 | 0.00025312 | houston | N | 0.00025312 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.011153 | houston | N | -0.011032 | 0.0080539 | 0.27797 | 0.00025312 | 0.00025312 | houston | N | 0.00025312 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.011153 | houston | N | -0.011032 | 0.0080539 | 0.27797 | 0.00025312 | 0.00025312 | houston | N | 0.00025312 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.011295 | houston | N | -0.01089 | 0.0081959 | 0.27811 | 0.00039512 | 0.00039512 | houston | N | 0.00039512 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.011295 | houston | N | -0.01089 | 0.0081959 | 0.27811 | 0.00039512 | 0.00039512 | houston | N | 0.00039512 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.01111 | houston | N | -0.011075 | 0.0080109 | 0.27793 | 0.00021012 | 0.00021012 | houston | N | 0.00021012 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.01111 | houston | N | -0.011075 | 0.0080109 | 0.27793 | 0.00021012 | 0.00021012 | houston | N | 0.00021012 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.01111 | houston | N | -0.011075 | 0.0080109 | 0.27793 | 0.00021012 | 0.00021012 | houston | N | 0.00021012 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.01111 | houston | N | -0.011075 | 0.0080109 | 0.27793 | 0.00021012 | 0.00021012 | houston | N | 0.00021012 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.01111 | houston | N | -0.011075 | 0.0080109 | 0.27793 | 0.00021012 | 0.00021012 | houston | N | 0.00021012 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.011548 | houston | Y | -0.010637 | 0.0084489 | 0.27837 | 0.00064812 | 0.00064812 | houston | N | 0.00064812 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.011476 | houston | Y | -0.010709 | 0.0083769 | 0.2783 | 0.00057612 | 0.00057612 | houston | N | 0.00057612 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.011568 | houston | Y | -0.010617 | 0.0084689 | 0.27839 | 0.00066812 | 0.00066812 | houston | N | 0.00066812 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.011568 | houston | Y | -0.010617 | 0.0084689 | 0.27839 | 0.00066812 | 0.00066812 | houston | N | 0.00066812 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.011568 | houston | Y | -0.010617 | 0.0084689 | 0.27839 | 0.00066812 | 0.00066812 | houston | N | 0.00066812 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.011964 | houston | N | -0.010221 | 0.0088649 | 0.27878 | 0.0010641 | 0.0010641 | houston | N | 0.0010641 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.011388 | houston | N | -0.010797 | 0.0082889 | 0.27821 | 0.00048812 | 0.00048812 | houston | N | 0.00048812 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.011388 | houston | N | -0.010797 | 0.0082889 | 0.27821 | 0.00048812 | 0.00048812 | houston | N | 0.00048812 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.011619 | houston | N | -0.010566 | 0.0085199 | 0.27844 | 0.00071912 | 0.00071912 | houston | N | 0.00071912 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.011619 | houston | N | -0.010566 | 0.0085199 | 0.27844 | 0.00071912 | 0.00071912 | houston | N | 0.00071912 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.011619 | houston | N | -0.010566 | 0.0085199 | 0.27844 | 0.00071912 | 0.00071912 | houston | N | 0.00071912 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.011619 | houston | N | -0.010566 | 0.0085199 | 0.27844 | 0.00071912 | 0.00071912 | houston | N | 0.00071912 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.011299 | houston | N | -0.010886 | 0.0081999 | 0.27812 | 0.00039912 | 0.00039912 | houston | N | 0.00039912 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.011299 | houston | N | -0.010886 | 0.0081999 | 0.27812 | 0.00039912 | 0.00039912 | houston | N | 0.00039912 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.011299 | houston | N | -0.010886 | 0.0081999 | 0.27812 | 0.00039912 | 0.00039912 | houston | N | 0.00039912 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.011299 | houston | N | -0.010886 | 0.0081999 | 0.27812 | 0.00039912 | 0.00039912 | houston | N | 0.00039912 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.01125 | houston | N | -0.010935 | 0.0081509 | 0.27807 | 0.00035012 | 0.00035012 | houston | N | 0.00035012 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.01125 | houston | N | -0.010935 | 0.0081509 | 0.27807 | 0.00035012 | 0.00035012 | houston | N | 0.00035012 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.01125 | houston | N | -0.010935 | 0.0081509 | 0.27807 | 0.00035012 | 0.00035012 | houston | N | 0.00035012 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.01125 | houston | N | -0.010935 | 0.0081509 | 0.27807 | 0.00035012 | 0.00035012 | houston | N | 0.00035012 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.01125 | houston | N | -0.010935 | 0.0081509 | 0.27807 | 0.00035012 | 0.00035012 | houston | N | 0.00035012 | 0
48651 | EP_1_2 | 1 | 5 | 0.011545 | houston | N | -0.01064 | 0.0084459 | 0.27836 | 0.00064512 | 0.00064512 | houston | N | 0.00064512 | 0
48651 | EP_1_2 | 2 | 21 | 0.011545 | houston | N | -0.01064 | 0.0084459 | 0.27836 | 0.00064512 | 0.00064512 | houston | N | 0.00064512 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.01467 | north | N | -0.0075155 | 0.011571 | 0.28149 | 0.0037701 | 0.0037701 | houston | Y | 0.0075155 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.01467 | north | N | -0.0075155 | 0.011571 | 0.28149 | 0.0037701 | 0.0037701 | houston | Y | 0.0075155 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.01467 | north | N | -0.0075155 | 0.011571 | 0.28149 | 0.0037701 | 0.0037701 | houston | Y | 0.0075155 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.01467 | north | N | -0.0075155 | 0.011571 | 0.28149 | 0.0037701 | 0.0037701 | houston | Y | 0.0075155 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.011641 | houston | Y | -0.010544 | 0.0085419 | 0.27846 | 0.00074112 | 0.00074112 | houston | N | 0.00074112 | 0
48691 | GBY_7374 | A | 46 | 0.011228 | houston | Y | -0.010957 | 0.0081289 | 0.27805 | 0.00032812 | 0.00032812 | houston | N | 0.00032812 | 0
48691 | GBY_7374 | B | 46 | 0.011228 | houston | Y | -0.010957 | 0.0081289 | 0.27805 | 0.00032812 | 0.00032812 | houston | N | 0.00032812 | 0
48692 | GBY_8182 | C | 46 | 0.011228 | houston | Y | -0.010957 | 0.0081289 | 0.27805 | 0.00032812 | 0.00032812 | houston | N | 0.00032812 | 0
48692 | GBY_8182 | D | 55 | 0.011228 | houston | Y | -0.010957 | 0.0081289 | 0.27805 | 0.00032812 | 0.00032812 | houston | N | 0.00032812 | 0
48693 | GBY_8384 | E | 55 | 0.011228 | houston | Y | -0.010957 | 0.0081289 | 0.27805 | 0.00032812 | 0.00032812 | houston | N | 0.00032812 | 0
48693 | GBY_8384 | F | 54 | 0.011228 | houston | Y | -0.010957 | 0.0081289 | 0.27805 | 0.00032812 | 0.00032812 | houston | N | 0.00032812 | 0
48721 | LEG_1___ | 1 | 827 | 0.017795 | north | Y | -0.0043905 | 0.014696 | 0.28461 | 0.0068951 | 0.0043905 | North | N | 0.0043905 | 0
48722 | LEG_2___ | 2 | 819 | 0.017795 | north | Y | -0.0043905 | 0.014696 | 0.28461 | 0.0068951 | 0.0043905 | North | N | 0.0043905 | 0
48730 | MNS_GT | 1 | 46.1 | 0.010374 | houston | N | -0.011811 | 0.0072749 | 0.27719 | -0.00052588 | 0.00052588 | houston | N | 0.00052588 | 0
48731 | CBE_GT1 | 1 | 76 | 0.008407 | houston | Y | -0.013778 | 0.0053079 | 0.27523 | -0.0024929 | 0.0024929 | houston | N | 0.0024929 | 0
48732 | CBE_GT2 | 1 | 76 | 0.008407 | houston | Y | -0.013778 | 0.0053079 | 0.27523 | -0.0024929 | 0.0024929 | houston | N | 0.0024929 | 0
48733 | CBE_ST12 | 1 | 105 | 0.008407 | houston | Y | -0.013778 | 0.0053079 | 0.27523 | -0.0024929 | 0.0024929 | houston | N | 0.0024929 | 0
48734 | CBE_GT3 | 1 | 74 | 0.008407 | houston | Y | -0.013778 | 0.0053079 | 0.27523 | -0.0024929 | 0.0024929 | houston | N | 0.0024929 | 0
48735 | CBE_GT4 | 1 | 74 | 0.008407 | houston | Y | -0.013778 | 0.0053079 | 0.27523 | -0.0024929 | 0.0024929 | houston | N | 0.0024929 | 0
48736 | CBE_ST34 | 1 | 102 | 0.008407 | houston | Y | -0.013778 | 0.0053079 | 0.27523 | -0.0024929 | 0.0024929 | houston | N | 0.0024929 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.011302 | houston | N | -0.010883 | 0.0082029 | 0.27812 | 0.00040212 | 0.00040212 | houston | N | 0.00040212 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.011302 | houston | N | -0.010883 | 0.0082029 | 0.27812 | 0.00040212 | 0.00040212 | houston | N | 0.00040212 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.011302 | houston | N | -0.010883 | 0.0082029 | 0.27812 | 0.00040212 | 0.00040212 | houston | N | 0.00040212 | 0
48761 | PR_GT1__ | 1 | 35 | 0.011273 | houston | N | -0.010912 | 0.0081739 | 0.27809 | 0.00037312 | 0.00037312 | houston | N | 0.00037312 | 0
48772 | PHR_GN2_ | MB | 459 | 0.011 | houston | Y | -0.011185 | 0.0079009 | 0.27782 | 0.00010012 | 0.00010012 | houston | N | 0.00010012 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.011547 | houston | N | -0.010638 | 0.0084479 | 0.27837 | 0.00064712 | 0.00064712 | houston | N | 0.00064712 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.011547 | houston | N | -0.010638 | 0.0084479 | 0.27837 | 0.00064712 | 0.00064712 | houston | N | 0.00064712 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.011547 | houston | N | -0.010638 | 0.0084479 | 0.27837 | 0.00064712 | 0.00064712 | houston | N | 0.00064712 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.011547 | houston | N | -0.010638 | 0.0084479 | 0.27837 | 0.00064712 | 0.00064712 | houston | N | 0.00064712 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.011547 | houston | N | -0.010638 | 0.0084479 | 0.27837 | 0.00064712 | 0.00064712 | houston | N | 0.00064712 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.011547 | houston | N | -0.010638 | 0.0084479 | 0.27837 | 0.00064712 | 0.00064712 | houston | N | 0.00064712 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.011547 | houston | N | -0.010638 | 0.0084479 | 0.27837 | 0.00064712 | 0.00064712 | houston | N | 0.00064712 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.011964 | houston | N | -0.010221 | 0.0088649 | 0.27878 | 0.0010641 | 0.0010641 | houston | N | 0.0010641 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.011964 | houston | N | -0.010221 | 0.0088649 | 0.27878 | 0.0010641 | 0.0010641 | houston | N | 0.0010641 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.011964 | houston | N | -0.010221 | 0.0088649 | 0.27878 | 0.0010641 | 0.0010641 | houston | N | 0.0010641 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.011964 | houston | N | -0.010221 | 0.0088649 | 0.27878 | 0.0010641 | 0.0010641 | houston | N | 0.0010641 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.011564 | houston | N | -0.010621 | 0.0084649 | 0.27838 | 0.00066412 | 0.00066412 | houston | N | 0.00066412 | 0
48820 | SHELLG1_ | 1 | 71 | 0.011328 | houston | N | -0.010857 | 0.0082289 | 0.27815 | 0.00042812 | 0.00042812 | houston | N | 0.00042812 | 0
48821 | SHELLG2 | 2 | 72 | 0.011328 | houston | N | -0.010857 | 0.0082289 | 0.27815 | 0.00042812 | 0.00042812 | houston | N | 0.00042812 | 0
48822 | SHELLG3_ | 1 | 39 | 0.011328 | houston | N | -0.010857 | 0.0082289 | 0.27815 | 0.00042812 | 0.00042812 | houston | N | 0.00042812 | 0
48822 | SHELLG3_ | 2 | 30 | 0.011328 | houston | N | -0.010857 | 0.0082289 | 0.27815 | 0.00042812 | 0.00042812 | houston | N | 0.00042812 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.011232 | houston | N | -0.010953 | 0.0081329 | 0.27805 | 0.00033212 | 0.00033212 | houston | N | 0.00033212 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.011232 | houston | N | -0.010953 | 0.0081329 | 0.27805 | 0.00033212 | 0.00033212 | houston | N | 0.00033212 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.011299 | houston | N | -0.010886 | 0.0081999 | 0.27812 | 0.00039912 | 0.00039912 | houston | N | 0.00039912 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.011294 | houston | Y | -0.010891 | 0.0081949 | 0.27811 | 0.00039412 | 0.00039412 | houston | N | 0.00039412 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.011292 | houston | Y | -0.010893 | 0.0081929 | 0.27811 | 0.00039212 | 0.00039212 | houston | N | 0.00039212 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.011298 | houston | Y | -0.010887 | 0.0081989 | 0.27812 | 0.00039812 | 0.00039812 | houston | N | 0.00039812 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.0113 | houston | Y | -0.010885 | 0.0082009 | 0.27812 | 0.00040012 | 0.00040012 | houston | N | 0.00040012 | 0
48855 | SRB_GT21 | B2 | 12 | 0.011291 | houston | Y | -0.010894 | 0.0081919 | 0.27811 | 0.00039112 | 0.00039112 | houston | N | 0.00039112 | 0
48855 | SRB_GT21 | MB | 18 | 0.011291 | houston | Y | -0.010894 | 0.0081919 | 0.27811 | 0.00039112 | 0.00039112 | houston | N | 0.00039112 | 0
48865 | TECO_GT1 | 1 | 50 | 0.010925 | houston | Y | -0.01126 | 0.0078259 | 0.27774 | 2.5124e-05 | 2.5124e-05 | houston | N | 2.5124e-05 | 0
48873 | THW_ST3_ | 3 | 104 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48874 | THW_ST4_ | 4 | 104 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48875 | THW_3132 | A | 54 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48875 | THW_3132 | B | 53 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48877 | THW_3334 | C | 54 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48877 | THW_3334 | D | 57 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48879 | THW_4142 | E | 54 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48879 | THW_4142 | F | 54 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48881 | THW_4344 | G | 58 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48881 | THW_4344 | H | 58 | 0.011464 | houston | Y | -0.010721 | 0.0083649 | 0.27828 | 0.00056412 | 0.00056412 | houston | N | 0.00056412 | 0
48883 | THW_GT1_ | B2 | 12 | 0.011527 | houston | Y | -0.010658 | 0.0084279 | 0.27835 | 0.00062712 | 0.00062712 | houston | N | 0.00062712 | 0
48885 | THW_5152 | A | 56 | 0.011673 | houston | Y | -0.010512 | 0.0085739 | 0.27849 | 0.00077312 | 0.00077312 | houston | N | 0.00077312 | 0
48885 | THW_5152 | B | 59 | 0.011673 | houston | Y | -0.010512 | 0.0085739 | 0.27849 | 0.00077312 | 0.00077312 | houston | N | 0.00077312 | 0
48886 | THW_5354 | C | 56 | 0.011673 | houston | Y | -0.010512 | 0.0085739 | 0.27849 | 0.00077312 | 0.00077312 | houston | N | 0.00077312 | 0
48886 | THW_5354 | D | 56 | 0.011673 | houston | Y | -0.010512 | 0.0085739 | 0.27849 | 0.00077312 | 0.00077312 | houston | N | 0.00077312 | 0
48887 | THW_5556 | E | 59 | 0.011673 | houston | Y | -0.010512 | 0.0085739 | 0.27849 | 0.00077312 | 0.00077312 | houston | N | 0.00077312 | 0
48887 | THW_5556 | F | 56 | 0.011673 | houston | Y | -0.010512 | 0.0085739 | 0.27849 | 0.00077312 | 0.00077312 | houston | N | 0.00077312 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.008544 | houston | Y | -0.013641 | 0.0054449 | 0.27536 | -0.0023559 | 0.0023559 | houston | N | 0.0023559 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.010541 | houston | Y | -0.011644 | 0.0074419 | 0.27736 | -0.00035888 | 0.00035888 | houston | N | 0.00035888 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.010541 | houston | Y | -0.011644 | 0.0074419 | 0.27736 | -0.00035888 | 0.00035888 | houston | N | 0.00035888 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.010541 | houston | Y | -0.011644 | 0.0074419 | 0.27736 | -0.00035888 | 0.00035888 | houston | N | 0.00035888 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.010541 | houston | Y | -0.011644 | 0.0074419 | 0.27736 | -0.00035888 | 0.00035888 | houston | N | 0.00035888 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.010541 | houston | N | -0.011644 | 0.0074419 | 0.27736 | -0.00035888 | 0.00035888 | houston | N | 0.00035888 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.01043 | houston | Y | -0.011755 | 0.0073309 | 0.27725 | -0.00046988 | 0.00046988 | houston | N | 0.00046988 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.01043 | houston | Y | -0.011755 | 0.0073309 | 0.27725 | -0.00046988 | 0.00046988 | houston | N | 0.00046988 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.01043 | houston | Y | -0.011755 | 0.0073309 | 0.27725 | -0.00046988 | 0.00046988 | houston | N | 0.00046988 | 0
48929 | WAPGT21_ | B1 | 13 | 0.010541 | houston | Y | -0.011644 | 0.0074419 | 0.27736 | -0.00035888 | 0.00035888 | houston | N | 0.00035888 | 0
48940 | WARVUE_G | G1 | 12 | 0.011546 | houston | Y | -0.010639 | 0.0084469 | 0.27837 | 0.00064612 | 0.00064612 | houston | N | 0.00064612 | 0
49803 | EXN_15GT | 1 | 34 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49826 | EXN938GT | 5 | 45.9 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49828 | EXN941GT | 10 | 17.7 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49829 | EXN942GT | 11 | 20.4 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49830 | EXN943GT | 12 | 19.9 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49831 | EXN944GT | 13 | 35 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49832 | EXN945GT | 9 | 18 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49837 | EXN_GT | 4 | 85.4 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49838 | EXN_14GT | 14 | 148 | 0.011494 | houston | N | -0.010691 | 0.0083949 | 0.27831 | 0.00059412 | 0.00059412 | houston | N | 0.00059412 | 0
49851 | DOW17000 | 37 | 62 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49858 | DOW38100 | 31 | 71.4 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49859 | DOW38200 | 33 | 45 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49860 | DOW38300 | 32 | 101 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49862 | DOW39100 | 36 | 86 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49863 | DOW39200 | 35 | 88 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49865 | DOW41000 | 41 | 50 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49866 | DOW42000 | 42 | 18 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49869 | DOW49000 | 45 | 94 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49870 | DOW61000 | 61 | 70 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49871 | DOW62000 | 62 | 63 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49872 | DOW63000 | 63 | 72 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49873 | DOW64000 | 64 | 64.8 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49876 | DOW65000 | 65 | 101 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49877 | DOW66000 | 66 | 97 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49878 | DOW67000 | 67 | 103 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49882 | DOW81000 | 81 | 76 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49884 | DOW82000 | 82 | 80 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49885 | DOW83000 | 83 | 80 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
49886 | DOW84000 | 84 | 171 | 0.009416 | houston | N | -0.012769 | 0.0063169 | 0.27624 | -0.0014839 | 0.0014839 | houston | N | 0.0014839 | 0
58909 | PEARSALL | 1 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58909 | PEARSALL | 2 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58909 | PEARSALL | 3 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58909 | PEARSALL | 4 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58909 | PEARSALL | 5 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58909 | PEARSALL | 6 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58919 | PEARSALL | 1 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58919 | PEARSALL | 2 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58919 | PEARSALL | 3 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58919 | PEARSALL | 4 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58919 | PEARSALL | 5 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58919 | PEARSALL | 6 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58929 | PEARSALL | 1 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58929 | PEARSALL | 2 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58929 | PEARSALL | 3 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58929 | PEARSALL | 4 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58929 | PEARSALL | 5 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58929 | PEARSALL | 6 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58949 | PEARSALL | 1 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58949 | PEARSALL | 2 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58949 | PEARSALL | 3 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58949 | PEARSALL | 4 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58949 | PEARSALL | 5 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
58949 | PEARSALL | 6 | 8.4 | -0.01008 | south | Y | -0.032265 | -0.013179 | 0.25674 | -0.02098 | 0.013179 | south | N | 0.013179 | 0
60000 | DSKY2 | 1 | 76.5 | -0.2524 | west | Y | -0.27458 | -0.2555 | 0.014423 | -0.2633 | 0.014423 | west | N | 0.014423 | 0
60003 | KING_NE1 | 1 | 80 | -0.25939 | west | Y | -0.28158 | -0.26249 | 0.0074252 | -0.27029 | 0.0074252 | west | N | 0.0074252 | 0
60005 | KING_SE1 | 1 | 40 | -0.25939 | west | Y | -0.28158 | -0.26249 | 0.0074252 | -0.27029 | 0.0074252 | west | N | 0.0074252 | 0
60007 | KING_SW1 | 1 | 80 | -0.26043 | west | Y | -0.28261 | -0.26353 | 0.0063912 | -0.27133 | 0.0063912 | west | N | 0.0063912 | 0
60016 | WOODWRD1 | 1 | 80 | -0.25918 | west | Y | -0.28136 | -0.26228 | 0.0076402 | -0.27008 | 0.0076402 | west | N | 0.0076402 | 0
60017 | ORNNWP1 | 1 | 80 | -0.25373 | west | Y | -0.27592 | -0.25683 | 0.013084 | -0.26463 | 0.013084 | west | N | 0.013084 | 0
60018 | DSKY1 | 1 | 84 | -0.25195 | west | Y | -0.27414 | -0.25505 | 0.014864 | -0.26285 | 0.014864 | west | N | 0.014864 | 0
60019 | KING_NW1 | 1 | 80 | -0.26043 | west | Y | -0.28261 | -0.26353 | 0.0063912 | -0.27133 | 0.0063912 | west | N | 0.0063912 | 0
60057 | CALLAHAN | 1 | 114 | 0.000617 | south | Y | -0.021568 | -0.0024821 | 0.26744 | -0.010283 | 0.0024821 | south | N | 0.0024821 | 0
60058 | BUFF_GAP | 1 | 120 | -0.30137 | west | Y | -0.32355 | -0.30447 | -0.034547 | -0.31227 | 0.034547 | west | N | 0.034547 | 0
60060 | CIRELLO | 1 | 233 | -0.30137 | west | Y | -0.32355 | -0.30447 | -0.034547 | -0.31227 | 0.034547 | west | N | 0.034547 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.30137 | west | Y | -0.32355 | -0.30447 | -0.034547 | -0.31227 | 0.034547 | west | N | 0.034547 | 0
60066 | H_HOLLOW | 1 | 222 | 0.000617 | south | Y | -0.021568 | -0.0024821 | 0.26744 | -0.010283 | 0.0024821 | south | N | 0.0024821 | 0
60068 | HHOLLOW2 | 1 | 184 | 0.000617 | south | Y | -0.021568 | -0.0024821 | 0.26744 | -0.010283 | 0.0024821 | south | N | 0.0024821 | 0
60070 | HHOLLOW3 | 1 | 224 | 0.000617 | south | Y | -0.021568 | -0.0024821 | 0.26744 | -0.010283 | 0.0024821 | south | N | 0.0024821 | 0
60072 | HHOLLOW4 | 1 | 115 | 0.000617 | south | Y | -0.021568 | -0.0024821 | 0.26744 | -0.010283 | 0.0024821 | south | N | 0.0024821 | 0
60074 | HORSH5 | 1 | 100 | 0.000617 | south | Y | -0.021568 | -0.0024821 | 0.26744 | -0.010283 | 0.0024821 | south | N | 0.0024821 | 0
60081 | WHRLWIND | 1 | 60 | -0.20577 | west | Y | -0.22796 | -0.20887 | 0.061047 | -0.21667 | 0.061047 | west | N | 0.061047 | 0
60201 | RIO DRCS | F | 0 | -0.079012 | south | N | -0.1012 | -0.082111 | 0.18781 | -0.089912 | 0.082111 | south | N | 0.082111 | 0
60202 | FRIEND_R | F | 0 | -0.22382 | west | N | -0.24601 | -0.22692 | 0.042995 | -0.23472 | 0.042995 | west | N | 0.042995 | 0
60203 | PRES0A | BT | 4.8 | -0.2646 | west | N | -0.28679 | -0.2677 | 0.0022142 | -0.2755 | 0.0022142 | west | N | 0.0022142 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.31511 | west | Y | -0.3373 | -0.31821 | -0.048291 | -0.32601 | 0.048291 | west | N | 0.048291 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.31511 | west | Y | -0.3373 | -0.31821 | -0.048291 | -0.32601 | 0.048291 | west | N | 0.048291 | 0
71057 | L_SWEETW | W1 | 135 | -0.31511 | west | Y | -0.3373 | -0.31821 | -0.048291 | -0.32601 | 0.048291 | west | N | 0.048291 | 0
71059 | L_SWEETW | W1 | 119 | -0.31511 | west | Y | -0.3373 | -0.31821 | -0.048291 | -0.32601 | 0.048291 | west | N | 0.048291 | 0
71060 | L_SWEETW | W1 | 105 | -0.31511 | west | Y | -0.3373 | -0.31821 | -0.048291 | -0.32601 | 0.048291 | west | N | 0.048291 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.31511 | west | Y | -0.3373 | -0.31821 | -0.048291 | -0.32601 | 0.048291 | west | N | 0.048291 | 0
76031 | L_GASCCR | W1 | 150 | -0.26806 | west | Y | -0.29024 | -0.27116 | -0.0012388 | -0.27896 | 0.0012388 | west | N | 0.0012388 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.26538 | west | Y | -0.28756 | -0.26847 | 0.0014442 | -0.27627 | 0.0014442 | west | N | 0.0014442 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.26538 | west | Y | -0.28756 | -0.26847 | 0.0014442 | -0.27627 | 0.0014442 | west | N | 0.0014442 | 0
76096 | L_CAPRSI | W1 | 186 | -0.26538 | west | Y | -0.28756 | -0.26847 | 0.0014442 | -0.27627 | 0.0014442 | west | N | 0.0014442 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.26538 | west | Y | -0.28756 | -0.26847 | 0.0014442 | -0.27627 | 0.0014442 | west | N | 0.0014442 | 0
80003 | MILHWYS | F | 0 | 0.002709 | south | N | -0.019476 | -0.00039015 | 0.26953 | -0.0081909 | 0.00039015 | south | N | 0.00039015 | 0
80010 | EPLVT1 | F | 0 | -0.048122 | south | N | -0.070307 | -0.051221 | 0.2187 | -0.059022 | 0.051221 | south | N | 0.051221 | 0
80012 | LAR | F | 0 | -0.004127 | south | N | -0.026312 | -0.0072261 | 0.26269 | -0.015027 | 0.0072261 | south | N | 0.0072261 | 0
80051 | FORPVCM0 | 8 | 28 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
80053 | FOR69CG0 | 10 | 74 | 0.004805 | south | N | -0.01738 | 0.0017059 | 0.27162 | -0.0060949 | 0.0017059 | south | N | 0.0017059 | 0
80080 | GWINDT11 | 1 | 94 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80080 | GWINDT11 | 2 | 41 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80080 | GWINDT11 | 3 | 38 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80080 | GWINDT11 | 4 | 19 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80081 | GWINDT21 | 1 | 94 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80081 | GWINDT21 | 2 | 36 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80081 | GWINDT21 | 3 | 43 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80081 | GWINDT21 | 4 | 22 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80137 | CSDR89 | 8 | 39 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
80137 | CSDR89 | 9 | 15 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
80138 | CSDR7 | 7 | 7 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
80139 | CSDR56 | 5 | 15 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
80139 | CSDR56 | 6 | 39 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
80140 | CSDR11 | 11 | 39 | 0.004328 | south | N | -0.017857 | 0.0012289 | 0.27115 | -0.0065719 | 0.0012289 | south | N | 0.0012289 | 0
80180 | PNSCALT1 | 1 | 148 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80180 | PNSCALT1 | 2 | 50 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80181 | PNSCALT2 | 1 | 55 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80181 | PNSCALT2 | 2 | 50 | 0.00279 | south | Y | -0.019395 | -0.00030915 | 0.26961 | -0.0081099 | 0.00030915 | south | N | 0.00030915 | 0
80223 | REYSHR G | 1 | 12 | 0.003288 | south | N | -0.018897 | 0.00018885 | 0.27011 | -0.0076119 | 0.00018885 | south | N | 0.00018885 | 0
80224 | VISTRONG | 1 | 15 | 0.004224 | south | N | -0.017961 | 0.0011249 | 0.27104 | -0.0066759 | 0.0011249 | south | N | 0.0011249 | 0
80225 | VISTRONG | 2 | 23 | 0.004224 | south | N | -0.017961 | 0.0011249 | 0.27104 | -0.0066759 | 0.0011249 | south | N | 0.0011249 | 0
80226 | ALCOA G | 1 | 48 | 0.004703 | south | N | -0.017482 | 0.0016039 | 0.27152 | -0.0061969 | 0.0016039 | south | N | 0.0016039 | 0
80227 | AIRCO G | 1 | 8 | 0.004255 | south | N | -0.01793 | 0.0011559 | 0.27107 | -0.0066449 | 0.0011559 | south | N | 0.0011559 | 0
80261 | NBEC81A | 1 | 180 | 0.003078 | south | Y | -0.019107 | -2.1147e-05 | 0.2699 | -0.0078219 | 2.1147e-05 | south | N | 2.1147e-05 | 0
80262 | NBEC91A | 1 | 180 | 0.003084 | south | Y | -0.019101 | -1.5147e-05 | 0.2699 | -0.0078159 | 1.5147e-05 | south | N | 1.5147e-05 | 0
80263 | B_DAVIS3 | 3 | 180 | 0.003044 | south | Y | -0.019141 | -5.5147e-05 | 0.26986 | -0.0078559 | 5.5147e-05 | south | N | 5.5147e-05 | 0
80264 | B_DAVIS4 | 4 | 180 | 0.003044 | south | Y | -0.019141 | -5.5147e-05 | 0.26986 | -0.0078559 | 5.5147e-05 | south | N | 5.5147e-05 | 0
80265 | LARECU40 | 4 | 100 | -0.004123 | south | Y | -0.026308 | -0.0072221 | 0.2627 | -0.015023 | 0.0072221 | south | N | 0.0072221 | 0
80266 | LARECU50 | 5 | 100 | -0.004123 | south | Y | -0.026308 | -0.0072221 | 0.2627 | -0.015023 | 0.0072221 | south | N | 0.0072221 | 0
80291 | PAPALOTE | 1 | 25 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
80291 | PAPALOTE | 2 | 25 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
80291 | PAPALOTE | 3 | 25 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
80291 | PAPALOTE | 4 | 16 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
80294 | PAPALOTE | 5 | 25 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
80294 | PAPALOTE | 6 | 25 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
80294 | PAPALOTE | 7 | 25 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
80294 | PAPALOTE | 8 | 15 | 0.003202 | south | Y | -0.018983 | 0.00010285 | 0.27002 | -0.0076979 | 0.00010285 | south | N | 0.00010285 | 0
86104 | CID-138 | EQ | 0 | -0.004123 | south | N | -0.026308 | -0.0072221 | 0.2627 | -0.015023 | 0.0072221 | south | N | 0.0072221 | 0
86105 | CID-230 | EQ | 500 | -0.004123 | south | N | -0.026308 | -0.0072221 | 0.2627 | -0.015023 | 0.0072221 | south | N | 0.0072221 | 0
86106 | CUF-230 | EQ | 500 | -0.004123 | south | N | -0.026308 | -0.0072221 | 0.2627 | -0.015023 | 0.0072221 | south | N | 0.0072221 | 0
86107 | CUF-138 | EQ | 0 | -0.004123 | south | N | -0.026308 | -0.0072221 | 0.2627 | -0.015023 | 0.0072221 | south | N | 0.0072221 | 0
88198 | BEEVILLE | F | 0 | 0.001909 | south | N | -0.020276 | -0.0011901 | 0.26873 | -0.0089909 | 0.0011901 | south | N | 0.0011901 | 0
88253 | HAMILTON | F | 0 | -0.073908 | south | N | -0.096093 | -0.077007 | 0.19291 | -0.084808 | 0.077007 | south | N | 0.077007 | 0
88299 | ZAPATA | F | 0 | -0.001864 | south | N | -0.024049 | -0.0049631 | 0.26496 | -0.012764 | 0.0049631 | south | N | 0.0049631 | 0
88508 | FALFURRI | F | 0 | 0.001726 | south | N | -0.020459 | -0.0013731 | 0.26855 | -0.0091739 | 0.0013731 | south | N | 0.0013731 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3 C: LONCREK2 - COKFIELD 345kV 1439 - 1442 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0698 | 0 | 0.27878 | 0 | 0 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8664 | 0 | 0.27878 | 0 | 0 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8425 | 0 | 0.27878 | 0 | 0 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8425 | 0 | 0.27878 | 0 | 0 | 0 | Weighted Shift Factors
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.011964 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9382 | 0 | 0.27878 | 0 | 0 | 0 | West | -0.26682
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956 | 56 | 15.5956 | North | 0.023444
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68871 | 59 | 0.27849 | 16.431 | 115 | 32.0266 |  | -0.29026
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956 | 171 | 47.6222
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956 | 227 | 63.2177 | Line Rating | 1235.45
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68871 | 59 | 0.27849 | 16.431 | 286 | 79.6488 | Conc Gen | 2023
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956 | 342 | 95.2443 | Weighted Imp. | 563.2266
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.011641 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.6331 | 398 | 0.27846 | 110.8272 | 740 | 206.0715 | PTDF | 0.27841
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8916 | 0 | 0.27844 | 0 | 740 | 206.0715
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8753 | 0 | 0.27844 | 0 | 740 | 206.0715 | Concentration | -0.95917
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8463 | 0 | 0.27844 | 0 | 740 | 206.0715
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1278 | 0 | 0.27844 | 0 | 740 | 206.0715
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9897 | 172 | 0.27839 | 47.8826 | 912 | 253.9541
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9897 | 172 | 0.27839 | 47.8826 | 1084 | 301.8367
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9897 | 172 | 0.27839 | 47.8826 | 1256 | 349.7193
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.011564 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8155 | 0 | 0.27838 | 0 | 1256 | 349.7193
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.011548 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.5802 | 743 | 0.27837 | 206.8268 | 1999 | 556.5461
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75055 | 0 | 0.27837 | 0 | 1999 | 556.5461
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7621 | 0 | 0.27837 | 0 | 1999 | 556.5461
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80829 | 0 | 0.27837 | 0 | 1999 | 556.5461
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72746 | 0 | 0.27837 | 0 | 1999 | 556.5461
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71591 | 0 | 0.27837 | 0 | 1999 | 556.5461
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2009 | 0 | 0.27837 | 0 | 1999 | 556.5461
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68127 | 0 | 0.27837 | 0 | 1999 | 556.5461
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.011546 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.13855 | 12 | 0.27837 | 3.3404 | 2011 | 559.8865
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.011545 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.057725 | 0 | 0.27836 | 0 | 2011 | 559.8865
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.011545 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24244 | 0 | 0.27836 | 0 | 2011 | 559.8865
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011527 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13832 | 12 | 0.27835 | 3.3402 | 2023 | 563.2266
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3908 | 0 | 0.27831 | 0 | 2023 | 563.2266
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39884 | 0 | 0.27831 | 0 | 2023 | 563.2266
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37585 | 0 | 0.27831 | 0 | 2023 | 563.2266
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52757 | 0 | 0.27831 | 0 | 2023 | 563.2266
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20344 | 0 | 0.27831 | 0 | 2023 | 563.2266
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23448 | 0 | 0.27831 | 0 | 2023 | 563.2266
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22873 | 0 | 0.27831 | 0 | 2023 | 563.2266
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40229 | 0 | 0.27831 | 0 | 2023 | 563.2266
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20689 | 0 | 0.27831 | 0 | 2023 | 563.2266
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98159 | 0 | 0.27831 | 0 | 2023 | 563.2266
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7011 | 0 | 0.27831 | 0 | 2023 | 563.2266
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.011476 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.4349 | 735 | 0.2783 | 204.547
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1923 | 104 | 0.27828 | 28.9415
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1923 | 104 | 0.27828 | 28.9415
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.60759 | 53 | 0.27828 | 14.749
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.65345 | 57 | 0.27828 | 15.8621
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66491 | 58 | 0.27828 | 16.1404
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66491 | 58 | 0.27828 | 16.1404
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.011388 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9701 | 0 | 0.27821 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.011388 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5374 | 0 | 0.27821 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.011375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.547 | 0 | 0.27819 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47767 | 42 | 0.27819 | 11.6841
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47767 | 42 | 0.27819 | 11.6841
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43217 | 38 | 0.27819 | 10.5713
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43217 | 38 | 0.27819 | 10.5713
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80429 | 0 | 0.27815 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81562 | 0 | 0.27815 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44179 | 0 | 0.27815 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33984 | 0 | 0.27815 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0344 | 0 | 0.27812 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7925 | 0 | 0.27812 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7744 | 0 | 0.27812 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.0113 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.5764 | 228 | 0.27812 | 63.4112
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72314 | 0 | 0.27812 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7141 | 0 | 0.27812 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9333 | 0 | 0.27812 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83161 | 0 | 0.27812 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18304 | 0 | 0.27812 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.011298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.4065 | 213 | 0.27812 | 59.239
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.683 | 0 | 0.27811 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7353 | 0 | 0.27811 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.011294 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8635 | 165 | 0.27811 | 45.8887
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.011292 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.9083 | 169 | 0.27811 | 47.0008
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13549 | 12 | 0.27811 | 3.3373
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.011291 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.27811 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.011273 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39455 | 0 | 0.27809 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.836 | 0 | 0.27807 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7674 | 0 | 0.27807 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7719 | 0 | 0.27807 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7663 | 0 | 0.27807 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0263 | 0 | 0.27807 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.011232 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.8761 | 0 | 0.27805 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.011232 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89856 | 0 | 0.27805 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51649 | 46 | 0.27805 | 12.7902
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51649 | 46 | 0.27805 | 12.7902
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51649 | 46 | 0.27805 | 12.7902
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61754 | 55 | 0.27805 | 15.2926
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61754 | 55 | 0.27805 | 15.2926
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.60631 | 54 | 0.27805 | 15.0145
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72494 | 0 | 0.27797 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66918 | 0 | 0.27797 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72494 | 0 | 0.27797 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72494 | 0 | 0.27797 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.011 | 0 | 0.27793 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97324 | 0 | 0.27793 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96657 | 0 | 0.27793 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6055 | 0 | 0.27793 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13554 | 0 | 0.27793 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.011 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.27782 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.010925 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54625 | 50 | 0.27774 | 13.8872
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76372 | 0 | 0.27761 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71949 | 0 | 0.27761 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57171 | 0 | 0.27761 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6526 | 0 | 0.27761 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6558 | 0 | 0.27761 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6429 | 0 | 0.27761 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0356 | 0 | 0.27761 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.632 | 0 | 0.27761 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43148 | 0 | 0.27761 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.010786 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34515 | 0 | 0.27761 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.010786 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32358 | 0 | 0.27761 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0817 | 0 | 0.2776 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0019 | 0 | 0.2776 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1076 | 0 | 0.2776 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1001 | 0 | 0.2776 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.6971 | 161 | 0.27736 | 44.655
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7498 | 166 | 0.27736 | 46.0418
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.6142 | 248 | 0.27736 | 68.7853
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.010541 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 5.7554 | 546 | 0.27736 | 151.4387
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.010541 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 6.7779 | 0 | 0.27736 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.010541 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13703 | 13 | 0.27736 | 3.6057
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.01046 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34518 | 0 | 0.27728 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7007 | 0 | 0.27725 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7007 | 0 | 0.27725 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5563 | 0 | 0.27725 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.7899 | 651 | 0.27725 | 180.4892
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.8825 | 564 | 0.27725 | 156.3685
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.258 | 600 | 0.27725 | 166.3495
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.010374 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47824 | 0 | 0.27719 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0881 | 0 | 0.27662 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0881 | 0 | 0.27662 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1666 | 0 | 0.27662 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0734 | 0 | 0.27662 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.009626 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68345 | 0 | 0.27645 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.009626 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09626 | 0 | 0.27645 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58379 | 0 | 0.27624 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6723 | 0 | 0.27624 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42372 | 0 | 0.27624 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95102 | 0 | 0.27624 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80978 | 0 | 0.27624 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82861 | 0 | 0.27624 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4708 | 0 | 0.27624 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16949 | 0 | 0.27624 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8851 | 0 | 0.27624 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65912 | 0 | 0.27624 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59321 | 0 | 0.27624 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67795 | 0 | 0.27624 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61016 | 0 | 0.27624 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95102 | 0 | 0.27624 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.91335 | 0 | 0.27624 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96985 | 0 | 0.27624 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71562 | 0 | 0.27624 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75328 | 0 | 0.27624 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75328 | 0 | 0.27624 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6101 | 0 | 0.27624 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.008544 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.5639 | 66 | 0.27536 | 18.174
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.008517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.8462 | 569 | 0.27534 | 156.6663
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.008517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.9484 | 581 | 0.27534 | 159.9703
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.63893 | 76 | 0.27523 | 20.9172
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.63893 | 76 | 0.27523 | 20.9172
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.88274 | 105 | 0.27523 | 28.8988
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62212 | 74 | 0.27523 | 20.3667
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62212 | 74 | 0.27523 | 20.3667
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.85751 | 102 | 0.27523 | 28.0731
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.008249 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 10.9959 | 0 | 0.27507 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.008249 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 10.9547 | 0 | 0.27507 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.006197 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.619 | 584 | 0.27302 | 159.4415
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.006197 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6872 | 595 | 0.27302 | 162.4446
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.006194 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.682 | 433 | 0.27301 | 118.2147
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96949 | 158 | 0.27296 | 43.1269
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.98176 | 160 | 0.27296 | 43.6728
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0738 | 175 | 0.27296 | 47.7672
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.85766 | 152.5 | 0.27244 | 41.5476
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84079 | 149.5 | 0.27244 | 40.7303
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.3081 | 232.6 | 0.27244 | 63.3703
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73814 | 132 | 0.27241 | 35.9583
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.74933 | 134 | 0.27241 | 36.5031
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8062 | 323 | 0.27241 | 87.9888
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21244 | 42 | 0.27188 | 11.4188
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22255 | 44 | 0.27188 | 11.9626
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22255 | 44 | 0.27188 | 11.9626
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23773 | 47 | 0.27188 | 12.7782
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004842 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.501 | 310 | 0.27166 | 84.215
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004842 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9997 | 413 | 0.27166 | 112.1961
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3796 | 0 | 0.27162 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38921 | 0 | 0.27162 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3796 | 0 | 0.27162 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3844 | 0 | 0.27162 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37671 | 0 | 0.27162 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12012 | 0 | 0.27162 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22103 | 0 | 0.27162 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13454 | 0 | 0.27162 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2095 | 0 | 0.27162 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.35557 | 0 | 0.27162 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23412 | 49 | 0.2716 | 13.3083
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21979 | 46 | 0.2716 | 12.4935
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21979 | 46 | 0.2716 | 12.4935
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22457 | 47 | 0.2716 | 12.7651
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004778 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.73581 | 154 | 0.2716 | 41.826
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004778 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70714 | 148 | 0.2716 | 40.1964
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22934 | 48 | 0.2716 | 13.0367
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22934 | 48 | 0.2716 | 13.0367
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.004703 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22574 | 0 | 0.27152 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.004585 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03668 | 0 | 0.2714 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.004585 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03668 | 0 | 0.2714 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12118 | 0 | 0.27115 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030296 | 0 | 0.27115 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16879 | 0 | 0.27115 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06492 | 0 | 0.27115 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030296 | 0 | 0.27115 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06492 | 0 | 0.27115 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16879 | 0 | 0.27115 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16879 | 0 | 0.27115 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.004255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.03404 | 0 | 0.27107 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.004224 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06336 | 0 | 0.27104 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.004224 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.097152 | 0 | 0.27104 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.004084 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29813 | 0 | 0.2709 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.00398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57312 | 144 | 0.2708 | 38.9951
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.00398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.74824 | 188 | 0.2708 | 50.9102
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18589 | 47.7 | 0.27072 | 12.9132
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14536 | 37.3 | 0.27072 | 10.0977
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17926 | 46 | 0.27072 | 12.4529
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18706 | 48 | 0.27072 | 12.9944
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003764 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045168 | 0 | 0.27058 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003743 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0089832 | 0 | 0.27056 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003743 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0089832 | 0 | 0.27056 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.081598 | 22 | 0.27053 | 5.9516
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003709 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040799 | 11 | 0.27053 | 2.9758
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003709 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040799 | 11 | 0.27053 | 2.9758
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7982 | 223.9 | 0.27038 | 60.539
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80212 | 225 | 0.27038 | 60.8364
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.8007 | 224.6 | 0.27038 | 60.7283
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80819 | 226.7 | 0.27038 | 61.2961
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.46959 | 142 | 0.27013 | 38.3579
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.47952 | 145 | 0.27013 | 39.1683
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.49936 | 151 | 0.27013 | 40.7891
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.95903 | 290 | 0.27013 | 78.3366
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079152 | 0 | 0.27012 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079152 | 0 | 0.27012 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0092344 | 0 | 0.27012 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.5195 | 0 | 0.27011 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.50306 | 0 | 0.27011 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3288 | 0 | 0.27011 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47676 | 0 | 0.27011 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.48334 | 0 | 0.27011 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41758 | 0 | 0.27011 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.003288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.039456 | 0 | 0.27011 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 25 | 0.27002 | 6.7505
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 25 | 0.27002 | 6.7505
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 25 | 0.27002 | 6.7505
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.051232 | 16 | 0.27002 | 4.3203
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 25 | 0.27002 | 6.7505
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 25 | 0.27002 | 6.7505
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 25 | 0.27002 | 6.7505
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04803 | 15 | 0.27002 | 4.0503
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.003095 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9468 | 629 | 0.26991 | 169.776
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.003084 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0362 | 336 | 0.2699 | 90.6875
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003084 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55512 | 180 | 0.2699 | 48.5826
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45706 | 0 | 0.2699 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45799 | 0 | 0.2699 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47155 | 0 | 0.2699 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003078 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55404 | 180 | 0.2699 | 48.5815
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0167 | 334 | 0.26986 | 90.1343
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.035 | 340 | 0.26986 | 91.7535
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003044 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54792 | 180 | 0.26986 | 48.5754
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003044 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54792 | 180 | 0.26986 | 48.5754
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44703 | 147 | 0.26986 | 39.6694
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.41966 | 138 | 0.26986 | 37.2407
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42574 | 140 | 0.26986 | 37.7804
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44703 | 147 | 0.26986 | 39.6694
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55346 | 182 | 0.26986 | 49.1146
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60212 | 198 | 0.26986 | 53.4323
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.00302 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0755 | 0 | 0.26984 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.00302 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0755 | 0 | 0.26984 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003017 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11465 | 0 | 0.26984 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.002994 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11377 | 0 | 0.26981 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002921 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.017526 | 0 | 0.26974 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.083752 | 0 | 0.26971 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002869 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011476 | 0 | 0.26969 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26226 | 94 | 0.26961 | 25.3433
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11439 | 41 | 0.26961 | 11.054
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10602 | 38 | 0.26961 | 10.2451
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05301 | 19 | 0.26961 | 5.1226
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26226 | 94 | 0.26961 | 25.3433
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10044 | 36 | 0.26961 | 9.7059
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11997 | 43 | 0.26961 | 11.5932
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.06138 | 22 | 0.26961 | 5.9314
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.41292 | 148 | 0.26961 | 39.9022
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1395 | 50 | 0.26961 | 13.4805
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15345 | 55 | 0.26961 | 14.8285
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1395 | 50 | 0.26961 | 13.4805
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.002709 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26953 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10294 | 38 | 0.26953 | 10.2421
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.052284 | 19.3 | 0.26953 | 5.2019
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.040635 | 15 | 0.26953 | 4.0429
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.002709 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12732 | 47 | 0.26953 | 12.6678
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36058 | 144 | 0.26932 | 38.7825
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36058 | 144 | 0.26932 | 38.7825
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42818 | 171 | 0.26932 | 46.0543
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.51812 | 207 | 0.26932 | 55.7497
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.5424 | 216.7 | 0.26932 | 58.3621
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60573 | 242 | 0.26932 | 65.176
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2563 | 546 | 0.26912 | 146.9396
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.7257 | 750 | 0.26912 | 201.8401
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31644 | 146.5 | 0.26898 | 39.4055
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31946 | 147.9 | 0.26898 | 39.782
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37368 | 173 | 0.26898 | 46.5334
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33216 | 155 | 0.26896 | 41.6891
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36431 | 170 | 0.26896 | 45.7236
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33216 | 155 | 0.26896 | 41.6891
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26886 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26886 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26886 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001909 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26873 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.06475 | 0 | 0.26867 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0629 | 0 | 0.26867 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.06475 | 0 | 0.26867 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001726 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26855 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.001696 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.7191 | 424 | 0.26852 | 113.8504
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.001696 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.7208 | 425 | 0.26852 | 114.119
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.001614 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66497 | 412 | 0.26843 | 110.5945
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.001614 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.6456 | 400 | 0.26843 | 107.3733
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001612 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.33691 | 209 | 0.26843 | 56.1021
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001612 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34819 | 216 | 0.26843 | 57.9811
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074152 | 46 | 0.26843 | 12.3478
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.075764 | 47 | 0.26843 | 12.6163
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074152 | 46 | 0.26843 | 12.3478
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074152 | 46 | 0.26843 | 12.3478
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001559 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.61736 | 396 | 0.26838 | 106.2778
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.001451 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.59056 | 407 | 0.26827 | 109.186
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000983 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.057014 | 58 | 0.2678 | 15.5325
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000983 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.087487 | 89 | 0.2678 | 23.8344
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043252 | 44 | 0.2678 | 11.7833
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043252 | 44 | 0.2678 | 11.7833
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.042269 | 43 | 0.2678 | 11.5155
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.044235 | 45 | 0.2678 | 12.0511
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070338 | 114 | 0.26744 | 30.4877
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13697 | 222 | 0.26744 | 59.3708
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11353 | 184 | 0.26744 | 49.2083
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13821 | 224 | 0.26744 | 59.9057
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070955 | 115 | 0.26744 | 30.7552
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001248 | 0 | 0.26692 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001144 | 0 | 0.26692 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001248 | 0 | 0.26692 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26682 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26682 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001864 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26496 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.004123 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4123 | 100 | 0.2627 | 26.2696
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.004123 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4123 | 100 | 0.2627 | 26.2696
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.004127 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26269 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004223 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076014 | 0 | 0.2626 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004223 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076014 | 0 | 0.2626 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.006228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17438 | 0 | 0.26059 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.006228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18061 | 0 | 0.26059 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.006901 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9122 | 422 | 0.25992 | 109.6855
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13234 | 0 | 0.25947 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13234 | 0 | 0.25947 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11028 | 0 | 0.25947 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008087 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.19409 | 24 | 0.25873 | 6.2096
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.19409 | 24 | 0.25873 | 6.2096
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.008087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.186 | 23 | 0.25873 | 5.9508
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.010456 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14325 | 0 | 0.25636 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.048122 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2187 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.052988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31793 | 0 | 0.21383 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.073908 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.439 | 0 | 0.19291 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.073908 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8477 | 0 | 0.19291 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.073908 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.19291 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.086836 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3279 | 165 | 0.063392 | 10.4597
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.086836 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.782 | 366 | 0.063392 | 23.2015
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.5021 | 204 | 0.023135 | 4.7195
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3624 | 201 | 0.023135 | 4.6501
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.2721 | 242 | 0.023135 | 5.5987
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.02945 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.767 | 60 | 0.006006 | 0.36036
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.02945 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8554 | 63 | 0.006006 | 0.37838
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.029217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.005773 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.029217 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.005773 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.029217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.005773 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.026342 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.002898 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.025763 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.002319 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.025608 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0243 | 0 | 0.002164 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.025608 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0243 | 0 | 0.002164 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.025507 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3362 | 170 | 0.002063 | 0.35071
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.025507 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.2636 | 520 | 0.002063 | 1.0728
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.025395 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.3962 | 370 | 0.001951 | 0.72187
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.5553 | 0 | 0.001951 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.5807 | 0 | 0.001951 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.8471 | 0 | 0.001951 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6315 | 0 | 0.001951 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6569 | 0 | 0.001951 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.8724 | 0 | 0.001951 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0501 | 160 | 0.001869 | 0.29904
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9488 | 156 | 0.001869 | 0.29156
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9613 | 196 | 0.001869 | 0.36632
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9488 | 156 | 0.001869 | 0.29156
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9741 | 157 | 0.001869 | 0.29343
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.012 | 198 | 0.001869 | 0.37006
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.8935 | 0 | 0.001803 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.0097 | 0 | 0.001803 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.2318 | 0 | 0.001803 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0482 | 558 | 0.001732 | 0.96646
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5769 | 579 | 0.001732 | 1.0028
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 20.3422 | 808 | 0.001732 | 1.3995
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.024881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.828 | 395 | 0.001437 | 0.56762
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.024881 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8232 | 435 | 0.001437 | 0.6251
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.024829 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8006 | 435 | 0.001385 | 0.60248
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9571 | 79 | 0.00133 | 0.10507
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.626 | 106 | 0.00133 | 0.14098
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.617 | 146 | 0.00133 | 0.19418
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.024774 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8828 | 76 | 0.00133 | 0.10108
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.02467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.61675 | 25 | 0.001226 | 0.03065
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.02467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0115 | 41 | 0.001226 | 0.050266
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.024669 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49338 | 20 | 0.001225 | 0.0245
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.024664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.98656 | 40 | 0.00122 | 0.0488
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.024186 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.3842 | 388 | 0.000742 | 0.2879
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.024186 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.4558 | 515 | 0.000742 | 0.38213
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.874 | 161 | 0.000618 | 0.099498
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9462 | 164 | 0.000618 | 0.10135
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9462 | 164 | 0.000618 | 0.10135
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9617 | 414 | 0.000618 | 0.25585
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.898 | 162 | 0.000618 | 0.10012
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.874 | 161 | 0.000618 | 0.099498
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9221 | 163 | 0.000618 | 0.10073
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8414 | 409 | 0.000618 | 0.25276
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024036 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.000592 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024036 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.000592 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.02397 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.6966 | 112.5 | 0.000526 | 0.059175
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.023603 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7852 | 118 | 0.000159 | 0.018762
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.023603 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7143 | 115 | 0.000159 | 0.018285
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.023603 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.1233 | 556 | 0.000159 | 0.088405
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.657 | 785 | -0.000951 | -0.74653
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.8819 | 795 | -0.000951 | -0.75604
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.5445 | 780 | -0.000951 | -0.74178
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2974 | 0 | -0.001164 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8964 | 0 | -0.001164 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2306 | 0 | -0.001164 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.8897 | 0 | -0.001164 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.0221 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.001344 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.02208 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.104 | 50 | -0.001364 | -0.0682
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.022042 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.0116 | 182 | -0.001402 | -0.25516
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.022042 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.6683 | 484 | -0.001402 | -0.67857
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.021954 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7508 | 216.4 | -0.00149 | -0.32244
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.021954 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7443 | 216.1 | -0.00149 | -0.32199
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.021374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1893 | 196 | -0.00207 | -0.40572
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.021374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3725 | 111 | -0.00207 | -0.22977
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.021367 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.1708 | 242 | -0.002077 | -0.50263
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.021155 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.7387 | 224 | -0.002289 | -0.51274
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0621 | 288 | -0.002395 | -0.68976
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0942 | 147 | -0.002395 | -0.35206
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0942 | 147 | -0.002395 | -0.35206
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6623 | 224 | -0.00263 | -0.58912
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.704 | 226 | -0.00263 | -0.59438
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4126 | 212 | -0.00263 | -0.55756
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3918 | 211 | -0.00263 | -0.55493
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0711 | 151.5 | -0.003173 | -0.48071
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0873 | 152.3 | -0.003173 | -0.48325
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5981 | 177.5 | -0.003173 | -0.56321
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0437 | 150.7 | -0.003247 | -0.48932
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0497 | 151 | -0.003247 | -0.4903
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5829 | 177.4 | -0.003247 | -0.57602
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.019837 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.1998 | 615 | -0.003607 | -2.2183
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.019837 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.6443 | 587 | -0.003607 | -2.1173
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.018958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.004486 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.017795 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.7165 | 827 | -0.005649 | -4.6717
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.017795 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5741 | 819 | -0.005649 | -4.6265
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5863 | 855 | -0.006384 | -5.4583
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5863 | 855 | -0.006384 | -5.4583
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.5982 | 152.3 | -0.006384 | -0.97228
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6102 | 153 | -0.006384 | -0.97675
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.016979 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0375 | 120 | -0.006465 | -0.7758
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30541 | 18 | -0.006477 | -0.11659
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30541 | 18 | -0.006477 | -0.11659
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.64475 | 38 | -0.006477 | -0.24613
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3158 | 20 | -0.007654 | -0.15308
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3158 | 20 | -0.007654 | -0.15308
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3158 | 20 | -0.007654 | -0.15308
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.26843 | 17 | -0.007654 | -0.13012
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.015354 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5795 | 168 | -0.00809 | -1.3591
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.015354 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3819 | 90 | -0.00809 | -0.7281
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.015226 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0496 | 463 | -0.008218 | -3.8049
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.01521 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.25857 | 17 | -0.008234 | -0.13998
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.015199 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.48637 | 0 | -0.008245 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.015159 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72763 | 48 | -0.008285 | -0.39768
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.015159 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.69731 | 46 | -0.008285 | -0.38111
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.015159 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5917 | 105 | -0.008285 | -0.86992
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.014889 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008555 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.014889 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 11.7176 | 787 | -0.008555 | -6.7328
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2621 | 0 | -0.008774 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2885 | 0 | -0.008774 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2885 | 0 | -0.008774 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5746 | 0 | -0.008774 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0014 | 70 | -0.009138 | -0.63966
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98711 | 69 | -0.009138 | -0.63052
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98711 | 69 | -0.009138 | -0.63052
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.97281 | 68 | -0.009138 | -0.62138
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1083 | 217.3 | -0.00914 | -1.9861
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9323 | 205 | -0.00914 | -1.8737
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8964 | 272.4 | -0.00914 | -2.4897
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.01414 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.009304 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.01414 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.009304 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.013588 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4649 | 255 | -0.009856 | -2.5133
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.013588 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0246 | 149 | -0.009856 | -1.4685
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.013588 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.079 | 153 | -0.009856 | -1.508
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.012979 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19468 | 0 | -0.010465 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.012979 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19468 | 0 | -0.010465 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.012844 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.8605 | 0 | -0.0106 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.012844 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.8734 | 0 | -0.0106 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.01257 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8855 | 150 | -0.010874 | -1.6311
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.01257 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0056 | 80 | -0.010874 | -0.86992
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.008461 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10153 | 0 | -0.014983 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.008461 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10153 | 0 | -0.014983 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.007627 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.55677 | 73 | -0.015817 | -1.1546
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.007627 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.90761 | 119 | -0.015817 | -1.8822
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.007627 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.5635 | 205 | -0.015817 | -3.2425
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.007627 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.77795 | 102 | -0.015817 | -1.6133
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.007627 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.73219 | 96 | -0.015817 | -1.5184
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0617 | 100 | -0.022827 | -2.2827
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.023444 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.023444 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.032056 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.9234 | 60 | -0.0555 | -3.33
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.079012 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.10246 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.11681 | west | 4 | Y | N | Ywest | Nwest | 1 | -75.8921 | 649.7 | -0.14025 | -91.1237
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.19825 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.737 | 150 | -0.22169 | -33.2536
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.20577 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.3463 | 60 | -0.22922 | -13.753
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.22382 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.24727 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.8805 | 209 | -0.25732 | -53.7803
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.5856 | 126.5 | -0.25732 | -32.5512
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -58.2356 | 249 | -0.25732 | -64.0732
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.074 | 197 | -0.25732 | -50.6924
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.23811 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.7168 | 150 | -0.26156 | -39.2334
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.25195 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.1642 | 84 | -0.2754 | -23.1335
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.2524 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.3083 | 76.5 | -0.27584 | -21.1018
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25373 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.2988 | 80 | -0.27718 | -22.1743
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.25901 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.8512 | 150 | -0.28245 | -42.3678
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.25901 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.8512 | 150 | -0.28245 | -42.3678
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.25915 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7318 | 80 | -0.28259 | -22.6074
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25918 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7343 | 80 | -0.28262 | -22.6098
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4546 | 75 | -0.28284 | -21.2128
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7515 | 80 | -0.28284 | -22.627
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.3758 | 40 | -0.28284 | -11.3135
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26043 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8342 | 80 | -0.28387 | -22.7098
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26043 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8342 | 80 | -0.28387 | -22.7098
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.26223 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.0277 | 84 | -0.28568 | -23.997
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.2646 | west | #N/A | N | N | Nwest | Nwest | 1 | -1.2701 | 0 | -0.28805 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.8547 | 112.5 | -0.28882 | -32.4921
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -39.6736 | 149.5 | -0.28882 | -43.1784
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.3597 | 186 | -0.28882 | -53.7203
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -56.9229 | 214.5 | -0.28882 | -61.9517
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.26773 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.5057 | 99 | -0.29118 | -28.8266
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.26773 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.3318 | 61 | -0.29118 | -17.7619
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 1 | -6.6933 | 0 | -0.29118 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2354 | 0 | -0.29118 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2354 | 0 | -0.29118 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.26799 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.786 | 141 | -0.29143 | -41.0916
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.26799 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.1583 | 120 | -0.29143 | -34.9716
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.26806 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.2087 | 150 | -0.2915 | -43.7253
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.26908 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7759 | 6.6 | -0.29253 | -1.9307
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.26908 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.2295 | 34.3 | -0.29253 | -10.0337
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.27034 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.0313 | 63 | -0.29378 | -18.5083
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27106 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.7906 | 180 | -0.2945 | -53.0105
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27106 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.7906 | 180 | -0.2945 | -53.0105
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.2712 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.0204 | 225 | -0.29465 | -66.2953
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.27292 | west | 8 | N | N | Nwest | Nwest | 1 | -7.0414 | 0 | -0.29637 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.27307 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.7685 | 120 | -0.29651 | -35.5818
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.27372 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.8463 | 120 | -0.29716 | -35.6596
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.27412 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.8445 | 149 | -0.29757 | -44.3376
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.27427 | west | 6 | Y | N | Ywest | Nwest | 1 | -41.1408 | 150 | -0.29772 | -44.6574
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.27427 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.7015 | 101 | -0.29772 | -30.0693
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.27432 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6011 | 35 | -0.29776 | -10.4216
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.27432 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2295 | 30 | -0.29776 | -8.9328
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.1155 | 66 | -0.29792 | -19.6628
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -17.841 | 65 | -0.29792 | -19.3649
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.39 | 67 | -0.29792 | -19.9607
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.39 | 67 | -0.29792 | -19.9607
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.39 | 67 | -0.29792 | -19.9607
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.27448 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.29792 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.27448 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.29792 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.27556 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6936 | 100.5 | -0.299 | -30.0497
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.27572 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.9916 | 58 | -0.29916 | -17.3514
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.27593 | west | 6 | Y | N | Ywest | Nwest | 1 | -59.1051 | 214.2 | -0.29938 | -64.1268
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.2994 | 66 | -0.30071 | -19.8467
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1312 | 69 | -0.30071 | -20.7489
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1312 | 69 | -0.30071 | -20.7489
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.5767 | 67 | -0.30071 | -20.1474
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.5767 | 67 | -0.30071 | -20.1474
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.0222 | 65 | -0.30071 | -19.546
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -57.8636 | 208.2 | -0.30137 | -62.7446
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -39.4929 | 142.1 | -0.30137 | -42.8243
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -36.797 | 132.4 | -0.30137 | -39.901
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -37.7975 | 136 | -0.30137 | -40.9859
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -40.8547 | 147 | -0.30137 | -44.3009
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -58.3638 | 210 | -0.30137 | -63.2871
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.457 | 70 | -0.3014 | -21.0981
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.457 | 70 | -0.3014 | -21.0981
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -25.7944 | 92.8 | -0.3014 | -27.97
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2366 | 80 | -0.3014 | -24.1121
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2366 | 80 | -0.3014 | -24.1121
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -31.9651 | 115 | -0.3014 | -34.6611
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 1 | -19.6249 | 0 | -0.3038 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 1 | -20.5781 | 0 | -0.3038 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 1 | -19.7371 | 0 | -0.3038 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.1509 | 150 | -0.30445 | -45.6675
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.8213 | 220 | -0.30445 | -66.979
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -56.2012 | 200 | -0.30445 | -60.89
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.2546 | 121.9 | -0.30445 | -37.1125
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.2859 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.4597 | 169.5 | -0.30934 | -52.4335
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.1639 | 120 | -0.32481 | -38.9772
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 1 | -70.2183 | 233 | -0.32481 | -75.6807
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 1 | -51.2925 | 170.2 | -0.32481 | -55.2827
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.30374 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.9675 | 125 | -0.32718 | -40.898
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.30374 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.9675 | 125 | -0.32718 | -40.898
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8166 | 37.5 | -0.33855 | -12.6958
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.8743 | 107.5 | -0.33855 | -36.3946
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.5399 | 135 | -0.33855 | -45.7048
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.4981 | 119 | -0.33855 | -40.2879
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.0866 | 105 | -0.33855 | -35.5482
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.3664 | 80.5 | -0.33855 | -27.2536
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.46891 | west | 6 | Y | N | Ywest | Nwest | 1 | -110.6637 | 236 | -0.49236 | -116.1965
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.46932 | west | 6 | Y | N | Ywest | Nwest | 1 | -187.7284 | 400 | -0.49276 | -197.106

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:GRHAMSES - LONGCREK 345kV 1430 - 1435_ctg3 C: LONCREK2 - COKFIELD 345kV 1439 - 1442 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.46932 | west | 6 | Y | N | Ywest | Nwest | 1 | -187.7284 | 0 | -0.49276 | 0 | 0 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.46891 | west | 6 | Y | N | Ywest | Nwest | 1 | -110.6637 | 0 | -0.49236 | 0 | 0 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -11.8166 | 0 | -0.33855 | 0 | 0 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.8743 | 0 | -0.33855 | 0 | 0 | 0 | Weighted Shift Factors
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.5399 | 0 | -0.33855 | 0 | 0 | 0 | West | -0.26682
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.4981 | 0 | -0.33855 | 0 | 0 | 0 | North | 0.023444
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -33.0866 | 0 | -0.33855 | 0 | 0 | 0 |  | -0.29026
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.31511 | west | 6 | Y | N | Ywest | Nwest | 1 | -25.3664 | 0 | -0.33855 | 0 | 0 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.30374 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.9675 | 0 | -0.32718 | 0 | 0 | 0 | Line Rating | 1235.45
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.30374 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.9675 | 0 | -0.32718 | 0 | 0 | 0 | Conc Gen | 2410.5
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 1 | -36.1639 | 0 | -0.32481 | 0 | 0 | 0 | Weighted Imp. | 670.2272
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 1 | -70.2183 | 0 | -0.32481 | 0 | 0 | 0 | PTDF | 0.27804
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.30137 | west | 6 | Y | N | Ywest | Nwest | 1 | -51.2925 | 0 | -0.32481 | 0 | 0 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.2859 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.4597 | 0 | -0.30934 | 0 | 0 | 0 | Concentration | -0.95791
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -42.1509 | 0 | -0.30445 | 0 | 0 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.8213 | 0 | -0.30445 | 0 | 0 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -56.2012 | 0 | -0.30445 | 0 | 0 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.28101 | west | 6 | Y | N | Ywest | Nwest | 1 | -34.2546 | 0 | -0.30445 | 0 | 0 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 1 | -19.6249 | 0 | -0.3038 | 0 | 0 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 1 | -20.5781 | 0 | -0.3038 | 0 | 0 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.28036 | west | 8 | N | N | Nwest | Nwest | 1 | -19.7371 | 0 | -0.3038 | 0 | 0 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.457 | 70 | -0.3014 | -21.0981 | 70 | 21.0981
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -19.457 | 70 | -0.3014 | -21.0981 | 140 | 42.1961
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -25.7944 | 92.8 | -0.3014 | -27.97 | 232.8 | 70.1662
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2366 | 80 | -0.3014 | -24.1121 | 312.8 | 94.2782
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -22.2366 | 80 | -0.3014 | -24.1121 | 392.8 | 118.3903
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.27796 | west | 9 | Y | Y | Ywest | Ywest | 1 | -31.9651 | 115 | -0.3014 | -34.6611 | 507.8 | 153.0514
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -57.8636 | 208.2 | -0.30137 | -62.7446 | 716 | 215.796
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -39.4929 | 142.1 | -0.30137 | -42.8243 | 858.1 | 258.6203
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -36.797 | 132.4 | -0.30137 | -39.901 | 990.5 | 298.5213
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -37.7975 | 136 | -0.30137 | -40.9859 | 1126.5 | 339.5072
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -40.8547 | 147 | -0.30137 | -44.3009 | 1273.5 | 383.8081
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.27792 | west | 9 | Y | Y | Ywest | Ywest | 1 | -58.3638 | 210 | -0.30137 | -63.2871 | 1483.5 | 447.0952
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.2994 | 66 | -0.30071 | -19.8467 | 1549.5 | 466.9419
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1312 | 69 | -0.30071 | -20.7489 | 1618.5 | 487.6908
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -19.1312 | 69 | -0.30071 | -20.7489 | 1687.5 | 508.4396
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.5767 | 67 | -0.30071 | -20.1474 | 1754.5 | 528.5871
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.5767 | 67 | -0.30071 | -20.1474 | 1821.5 | 548.7345
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.27726 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.0222 | 65 | -0.30071 | -19.546 | 1886.5 | 568.2805
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.27593 | west | 6 | Y | N | Ywest | Nwest | 1 | -59.1051 | 0 | -0.29938 | 0 | 1886.5 | 568.2805
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.27572 | west | 6 | Y | N | Ywest | Nwest | 1 | -15.9916 | 0 | -0.29916 | 0 | 1886.5 | 568.2805
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.27556 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.6936 | 0 | -0.299 | 0 | 1886.5 | 568.2805
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.1155 | 66 | -0.29792 | -19.6628 | 1952.5 | 587.9433
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -17.841 | 65 | -0.29792 | -19.3649 | 2017.5 | 607.3082
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.39 | 67 | -0.29792 | -19.9607 | 2084.5 | 627.2689
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.39 | 67 | -0.29792 | -19.9607 | 2151.5 | 647.2296
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.27448 | west | 13 | Y | Y | Ywest | Ywest | 1 | -18.39 | 67 | -0.29792 | -19.9607 | 2218.5 | 667.1903
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.27448 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.29792 | 0 | 2218.5 | 667.1903
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.27448 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.29792 | 0 | 2218.5 | 667.1903
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.27432 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.6011 | 0 | -0.29776 | 0 | 2218.5 | 667.1903
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.27432 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2295 | 0 | -0.29776 | 0 | 2218.5 | 667.1903
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.27427 | west | 6 | Y | N | Ywest | Nwest | 1 | -41.1408 | 0 | -0.29772 | 0 | 2218.5 | 667.1903
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.27427 | west | 6 | Y | N | Ywest | Nwest | 1 | -27.7015 | 0 | -0.29772 | 0 | 2218.5 | 667.1903
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.27412 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.8445 | 0 | -0.29757 | 0 | 2218.5 | 667.1903
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.27372 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.8463 | 0 | -0.29716 | 0 | 2218.5 | 667.1903
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.27307 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.7685 | 0 | -0.29651 | 0 | 2218.5 | 667.1903
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.27292 | west | 8 | N | N | Nwest | Nwest | 1 | -7.0414 | 0 | -0.29637 | 0 | 2218.5 | 667.1903
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.2712 | west | 6 | Y | N | Ywest | Nwest | 1 | -61.0204 | 0 | -0.29465 | 0 | 2218.5 | 667.1903
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27106 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.7906 | 0 | -0.2945 | 0 | 2218.5 | 667.1903
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.27106 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.7906 | 0 | -0.2945 | 0 | 2218.5 | 667.1903
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.27034 | west | 6 | Y | N | Ywest | Nwest | 1 | -17.0313 | 0 | -0.29378 | 0 | 2218.5 | 667.1903
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.26908 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.7759 | 0 | -0.29253 | 0 | 2218.5 | 667.1903
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.26908 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.2295 | 0 | -0.29253 | 0 | 2218.5 | 667.1903
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.26806 | west | 6 | Y | N | Ywest | Nwest | 1 | -40.2087 | 0 | -0.2915 | 0 | 2218.5 | 667.1903
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.26799 | west | 6 | Y | N | Ywest | Nwest | 1 | -37.786 | 0 | -0.29143 | 0 | 2218.5 | 667.1903
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.26799 | west | 6 | Y | N | Ywest | Nwest | 1 | -32.1583 | 0 | -0.29143 | 0 | 2218.5 | 667.1903
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.26773 | west | 6 | Y | N | Ywest | Nwest | 1 | -26.5057 | 0 | -0.29118 | 0 | 2218.5 | 667.1903
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.26773 | west | 6 | Y | N | Ywest | Nwest | 1 | -16.3318 | 0 | -0.29118 | 0 | 2218.5 | 667.1903
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 1 | -6.6933 | 0 | -0.29118 | 0 | 2218.5 | 667.1903
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2354 | 0 | -0.29118 | 0 | 2218.5 | 667.1903
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.26773 | west | 7 | N | N | Nwest | Nwest | 1 | -12.2354 | 0 | -0.29118 | 0 | 2218.5 | 667.1903
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.8547 | 0 | -0.28882 | 0 | 2218.5 | 667.1903
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -39.6736 | 0 | -0.28882 | 0 | 2218.5 | 667.1903
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -49.3597 | 0 | -0.28882 | 0 | 2218.5 | 667.1903
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.26538 | west | 6 | Y | N | Ywest | Nwest | 1 | -56.9229 | 0 | -0.28882 | 0 | 2218.5 | 667.1903
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.2646 | west | #N/A | N | N | Nwest | Nwest | 1 | -1.2701 | 0 | -0.28805 | 0 | 2218.5 | 667.1903
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.26223 | west | 6 | Y | N | Ywest | Nwest | 1 | -22.0277 | 0 | -0.28568 | 0 | 2218.5 | 667.1903
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26043 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8342 | 0 | -0.28387 | 0 | 2218.5 | 667.1903
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.26043 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.8342 | 0 | -0.28387 | 0 | 2218.5 | 667.1903
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.4546 | 0 | -0.28284 | 0 | 2218.5 | 667.1903
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7515 | 0 | -0.28284 | 0 | 2218.5 | 667.1903
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.25939 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.3758 | 0 | -0.28284 | 0 | 2218.5 | 667.1903
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25918 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7343 | 0 | -0.28262 | 0 | 2218.5 | 667.1903
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.25915 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.7318 | 0 | -0.28259 | 0 | 2218.5 | 667.1903
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.25901 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.8512 | 0 | -0.28245 | 0 | 2218.5 | 667.1903
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.25901 | west | 6 | Y | N | Ywest | Nwest | 1 | -38.8512 | 0 | -0.28245 | 0 | 2218.5 | 667.1903
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.25373 | west | 6 | Y | N | Ywest | Nwest | 1 | -20.2988 | 0 | -0.27718 | 0 | 2218.5 | 667.1903
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.2524 | west | 6 | Y | N | Ywest | Nwest | 1 | -19.3083 | 0 | -0.27584 | 0 | 2218.5 | 667.1903
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.25195 | west | 6 | Y | N | Ywest | Nwest | 1 | -21.1642 | 0 | -0.2754 | 0 | 2218.5 | 667.1903
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.23811 | west | 6 | Y | N | Ywest | Nwest | 1 | -35.7168 | 0 | -0.26156 | 0 | 2218.5 | 667.1903
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -48.8805 | 0 | -0.25732 | 0 | 2218.5 | 667.1903
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.5856 | 0 | -0.25732 | 0 | 2218.5 | 667.1903
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -58.2356 | 0 | -0.25732 | 0 | 2218.5 | 667.1903
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.23388 | west | 6 | Y | N | Ywest | Nwest | 1 | -46.074 | 0 | -0.25732 | 0 | 2218.5 | 667.1903
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.22382 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.24727 | 0 | 2218.5 | 667.1903
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.20577 | west | 6 | Y | N | Ywest | Nwest | 1 | -12.3463 | 0 | -0.22922 | 0 | 2218.5 | 667.1903
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.19825 | west | 6 | Y | N | Ywest | Nwest | 1 | -29.737 | 0 | -0.22169 | 0 | 2218.5 | 667.1903
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.11681 | west | 4 | Y | N | Ywest | Nwest | 1 | -75.8921 | 0 | -0.14025 | 0 | 2218.5 | 667.1903
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.079012 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.10246 | 0 | 2218.5 | 667.1903
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.032056 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -1.9234 | 0 | -0.0555 | 0 | 2218.5 | 667.1903
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.023444 | 0 | 2218.5 | 667.1903
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.023444 | 0 | 2218.5 | 667.1903
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.0617 | 0 | -0.022827 | 0 | 2218.5 | 667.1903
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.007627 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.55677 | 73 | -0.015817 | -1.1546 | 2291.5 | 668.3449
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.007627 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.90761 | 119 | -0.015817 | -1.8822 | 2410.5 | 670.2272
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.007627 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 1.5635 | 205 | -0.015817 | -3.2425
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.007627 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.77795 | 102 | -0.015817 | -1.6133
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.007627 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.73219 | 96 | -0.015817 | -1.5184
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.008461 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10153 | 0 | -0.014983 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.008461 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.10153 | 0 | -0.014983 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.01257 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.8855 | 150 | -0.010874 | -1.6311
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.01257 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0056 | 80 | -0.010874 | -0.86992
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.012844 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.8605 | 0 | -0.0106 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.012844 | north | 3 | N | N | Nnorth | Nnorth | 1 | 14.8734 | 0 | -0.0106 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.012979 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19468 | 0 | -0.010465 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.012979 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.19468 | 0 | -0.010465 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.013588 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.4649 | 255 | -0.009856 | -2.5133
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.013588 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.0246 | 149 | -0.009856 | -1.4685
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.013588 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.079 | 153 | -0.009856 | -1.508
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.01414 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.009304 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.01414 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.009304 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.1083 | 217.3 | -0.00914 | -1.9861
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.9323 | 205 | -0.00914 | -1.8737
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.014304 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.8964 | 272.4 | -0.00914 | -2.4897
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.0014 | 70 | -0.009138 | -0.63966
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98711 | 69 | -0.009138 | -0.63052
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.98711 | 69 | -0.009138 | -0.63052
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.014306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.97281 | 68 | -0.009138 | -0.62138
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2621 | 0 | -0.008774 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2885 | 0 | -0.008774 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.2885 | 0 | -0.008774 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.01467 | north | 1 | N | N | Nnorth | Nnorth | 1 | 5.5746 | 0 | -0.008774 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.014889 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008555 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.014889 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 11.7176 | 787 | -0.008555 | -6.7328
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.015159 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.72763 | 48 | -0.008285 | -0.39768
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.015159 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.69731 | 46 | -0.008285 | -0.38111
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.015159 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.5917 | 105 | -0.008285 | -0.86992
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.015199 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.48637 | 0 | -0.008245 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.01521 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.25857 | 17 | -0.008234 | -0.13998
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.01521 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.008234 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.015226 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 7.0496 | 0 | -0.008218 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.015354 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.5795 | 168 | -0.00809 | -1.3591
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.015354 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.3819 | 90 | -0.00809 | -0.7281
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3158 | 20 | -0.007654 | -0.15308
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3158 | 20 | -0.007654 | -0.15308
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3158 | 20 | -0.007654 | -0.15308
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.01579 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.26843 | 17 | -0.007654 | -0.13012
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30541 | 18 | -0.006477 | -0.11659
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.30541 | 18 | -0.006477 | -0.11659
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.016967 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.64475 | 38 | -0.006477 | -0.24613
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.016979 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.0375 | 0 | -0.006465 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5863 | 0 | -0.006384 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5863 | 0 | -0.006384 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.5982 | 0 | -0.006384 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.01706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.6102 | 0 | -0.006384 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.017795 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.7165 | 0 | -0.005649 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.017795 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5741 | 0 | -0.005649 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.018958 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.004486 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.019837 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 12.1998 | 0 | -0.003607 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.019837 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 11.6443 | 0 | -0.003607 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0437 | 150.7 | -0.003247 | -0.48932
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0497 | 151 | -0.003247 | -0.4903
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.020197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5829 | 177.4 | -0.003247 | -0.57602
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0711 | 151.5 | -0.003173 | -0.48071
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0873 | 152.3 | -0.003173 | -0.48325
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.020271 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.5981 | 177.5 | -0.003173 | -0.56321
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.6623 | 224 | -0.00263 | -0.58912
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.704 | 226 | -0.00263 | -0.59438
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.4126 | 212 | -0.00263 | -0.55756
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.020814 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.3918 | 211 | -0.00263 | -0.55493
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.0621 | 288 | -0.002395 | -0.68976
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0942 | 147 | -0.002395 | -0.35206
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.021049 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.0942 | 147 | -0.002395 | -0.35206
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.021155 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.7387 | 224 | -0.002289 | -0.51274
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.021367 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 5.1708 | 242 | -0.002077 | -0.50263
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.021374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.1893 | 196 | -0.00207 | -0.40572
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.021374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.3725 | 111 | -0.00207 | -0.22977
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.021954 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7508 | 216.4 | -0.00149 | -0.32244
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.021954 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.7443 | 216.1 | -0.00149 | -0.32199
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.022042 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.0116 | 182 | -0.001402 | -0.25516
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.022042 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 10.6683 | 484 | -0.001402 | -0.67857
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.02208 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 1.104 | 0 | -0.001364 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.0221 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.001344 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2974 | 0 | -0.001164 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 2.8964 | 0 | -0.001164 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.2306 | 0 | -0.001164 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.02228 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.8897 | 0 | -0.001164 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.657 | 0 | -0.000951 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.8819 | 0 | -0.000951 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.022493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 17.5445 | 0 | -0.000951 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.023603 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 2.7852 | 118 | 0.000159 | 0.018762
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.023603 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.7143 | 115 | 0.000159 | 0.018285
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.023603 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.1233 | 556 | 0.000159 | 0.088405
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.02397 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.6966 | 0 | 0.000526 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024036 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.000592 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.024036 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.000592 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.874 | 161 | 0.000618 | 0.099498
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9462 | 164 | 0.000618 | 0.10135
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9462 | 164 | 0.000618 | 0.10135
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.9617 | 414 | 0.000618 | 0.25585
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.898 | 162 | 0.000618 | 0.10012
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.874 | 161 | 0.000618 | 0.099498
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9221 | 163 | 0.000618 | 0.10073
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.024062 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.8414 | 409 | 0.000618 | 0.25276
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.024186 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.3842 | 388 | 0.000742 | 0.2879
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.024186 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.4558 | 515 | 0.000742 | 0.38213
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.024664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.98656 | 40 | 0.00122 | 0.0488
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.024669 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.49338 | 20 | 0.001225 | 0.0245
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.02467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.61675 | 25 | 0.001226 | 0.03065
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.02467 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0115 | 41 | 0.001226 | 0.050266
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.9571 | 79 | 0.00133 | 0.10507
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.626 | 106 | 0.00133 | 0.14098
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.024774 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.617 | 146 | 0.00133 | 0.19418
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.024774 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.8828 | 76 | 0.00133 | 0.10108
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.024829 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8006 | 435 | 0.001385 | 0.60248
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.024881 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.828 | 395 | 0.001437 | 0.56762
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.024881 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 10.8232 | 435 | 0.001437 | 0.6251
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.0482 | 0 | 0.001732 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 14.5769 | 0 | 0.001732 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.025176 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 20.3422 | 0 | 0.001732 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | 1 | 1.8935 | 0 | 0.001803 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.0097 | 0 | 0.001803 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.025247 | north | 8 | N | N | Nnorth | Nnorth | 1 | 2.2318 | 0 | 0.001803 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.0501 | 160 | 0.001869 | 0.29904
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9488 | 156 | 0.001869 | 0.29156
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 4.9613 | 196 | 0.001869 | 0.36632
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9488 | 156 | 0.001869 | 0.29156
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.9741 | 157 | 0.001869 | 0.29343
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.025313 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.012 | 198 | 0.001869 | 0.37006
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.025395 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 9.3962 | 370 | 0.001951 | 0.72187
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.5553 | 0 | 0.001951 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.5807 | 0 | 0.001951 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.8471 | 0 | 0.001951 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6315 | 0 | 0.001951 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6569 | 0 | 0.001951 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.025395 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.8724 | 0 | 0.001951 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.025507 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3362 | 170 | 0.002063 | 0.35071
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.025507 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.2636 | 520 | 0.002063 | 1.0728
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.025608 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0243 | 0 | 0.002164 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.025608 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.0243 | 0 | 0.002164 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.025763 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.002319 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.026342 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.002898 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.029217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.005773 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.029217 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.005773 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.029217 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.005773 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.02945 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.767 | 60 | 0.006006 | 0.36036
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.02945 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.8554 | 63 | 0.006006 | 0.37838
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.5021 | 204 | 0.023135 | 4.7195
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3624 | 201 | 0.023135 | 4.6501
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.046579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.2721 | 242 | 0.023135 | 5.5987
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.086836 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 31.782 | 366 | 0.063392 | 23.2015
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.086836 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3279 | 0 | 0.063392 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.073908 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.439 | 0 | 0.19291 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.073908 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8477 | 0 | 0.19291 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.073908 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.19291 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.052988 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.31793 | 0 | 0.21383 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.048122 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2187 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.010456 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.14325 | 0 | 0.25636 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.01008 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.084672 | 8.4 | 0.25674 | 2.1566
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008087 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.19409 | 24 | 0.25873 | 6.2096
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.008087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.19409 | 24 | 0.25873 | 6.2096
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.008087 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.186 | 23 | 0.25873 | 5.9508
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13234 | 0 | 0.25947 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13234 | 0 | 0.25947 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.007352 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11028 | 0 | 0.25947 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.006901 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.9122 | 422 | 0.25992 | 109.6855
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.006228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.17438 | 0 | 0.26059 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.006228 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18061 | 0 | 0.26059 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004223 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076014 | 0 | 0.2626 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004223 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.076014 | 0 | 0.2626 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.004127 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26269 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.004123 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4123 | 100 | 0.2627 | 26.2696
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.004123 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.4123 | 100 | 0.2627 | 26.2696
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.004123 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.2627 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.001864 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26496 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26682 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26682 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26682 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001248 | 0 | 0.26692 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001144 | 0 | 0.26692 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.000104 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.001248 | 0 | 0.26692 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070338 | 0 | 0.26744 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13697 | 0 | 0.26744 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11353 | 0 | 0.26744 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13821 | 0 | 0.26744 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.000617 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.070955 | 0 | 0.26744 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.000983 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.057014 | 58 | 0.2678 | 15.5325
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.000983 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.087487 | 89 | 0.2678 | 23.8344
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043252 | 44 | 0.2678 | 11.7833
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.043252 | 44 | 0.2678 | 11.7833
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.042269 | 43 | 0.2678 | 11.5155
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.000983 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.044235 | 45 | 0.2678 | 12.0511
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.001451 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.59056 | 407 | 0.26827 | 109.186
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.001559 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.61736 | 0 | 0.26838 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.001612 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.33691 | 209 | 0.26843 | 56.1021
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.001612 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.34819 | 216 | 0.26843 | 57.9811
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074152 | 46 | 0.26843 | 12.3478
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.075764 | 47 | 0.26843 | 12.6163
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074152 | 46 | 0.26843 | 12.3478
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.001612 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.074152 | 46 | 0.26843 | 12.3478
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.001614 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.66497 | 412 | 0.26843 | 110.5945
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.001614 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.6456 | 400 | 0.26843 | 107.3733
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.001696 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.7191 | 0 | 0.26852 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.001696 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 0.7208 | 0 | 0.26852 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.001726 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26855 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.06475 | 0 | 0.26867 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0629 | 0 | 0.26867 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.00185 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.06475 | 0 | 0.26867 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.001909 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26873 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26886 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26886 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.00204 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.26886 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33216 | 155 | 0.26896 | 41.6891
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36431 | 170 | 0.26896 | 45.7236
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.002143 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.33216 | 155 | 0.26896 | 41.6891
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31644 | 146.5 | 0.26898 | 39.4055
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.31946 | 147.9 | 0.26898 | 39.782
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.00216 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.37368 | 173 | 0.26898 | 46.5334
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.002301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.2563 | 0 | 0.26912 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.002301 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.7257 | 0 | 0.26912 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.51812 | 207 | 0.26932 | 55.7497
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.5424 | 216.7 | 0.26932 | 58.3621
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.002503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60573 | 242 | 0.26932 | 65.176
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36058 | 144 | 0.26932 | 38.7825
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.36058 | 144 | 0.26932 | 38.7825
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.002504 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42818 | 171 | 0.26932 | 46.0543
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.10294 | 38 | 0.26953 | 10.2421
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.052284 | 19.3 | 0.26953 | 5.2019
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.002709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.040635 | 15 | 0.26953 | 4.0429
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.002709 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.12732 | 47 | 0.26953 | 12.6678
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.002709 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.26953 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26226 | 0 | 0.26961 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11439 | 0 | 0.26961 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10602 | 0 | 0.26961 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.05301 | 0 | 0.26961 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.26226 | 0 | 0.26961 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.10044 | 0 | 0.26961 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11997 | 0 | 0.26961 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.06138 | 0 | 0.26961 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.41292 | 0 | 0.26961 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1395 | 0 | 0.26961 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15345 | 0 | 0.26961 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.00279 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.1395 | 0 | 0.26961 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.002869 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011476 | 0 | 0.26969 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.002888 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.083752 | 0 | 0.26971 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.002921 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.017526 | 0 | 0.26974 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.002994 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11377 | 0 | 0.26981 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003017 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.11465 | 0 | 0.26984 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.00302 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0755 | 0 | 0.26984 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.00302 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.0755 | 0 | 0.26984 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44703 | 147 | 0.26986 | 39.6694
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.41966 | 138 | 0.26986 | 37.2407
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.42574 | 140 | 0.26986 | 37.7804
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44703 | 147 | 0.26986 | 39.6694
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55346 | 182 | 0.26986 | 49.1146
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003041 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.60212 | 198 | 0.26986 | 53.4323
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0167 | 334 | 0.26986 | 90.1343
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003044 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.035 | 340 | 0.26986 | 91.7535
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003044 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54792 | 180 | 0.26986 | 48.5754
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003044 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54792 | 180 | 0.26986 | 48.5754
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003078 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55404 | 180 | 0.2699 | 48.5815
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45706 | 0 | 0.2699 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.45799 | 0 | 0.2699 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.003082 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47155 | 0 | 0.2699 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.003084 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0362 | 336 | 0.2699 | 90.6875
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003084 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.55512 | 180 | 0.2699 | 48.5826
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.003095 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.9468 | 0 | 0.26991 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 0 | 0.27002 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 0 | 0.27002 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 0 | 0.27002 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.051232 | 0 | 0.27002 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 0 | 0.27002 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 0 | 0.27002 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.08005 | 0 | 0.27002 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.003202 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.04803 | 0 | 0.27002 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.5195 | 0 | 0.27011 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.50306 | 0 | 0.27011 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3288 | 0 | 0.27011 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47676 | 0 | 0.27011 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.48334 | 0 | 0.27011 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.003288 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.41758 | 0 | 0.27011 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.003288 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.039456 | 0 | 0.27011 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079152 | 0 | 0.27012 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0079152 | 0 | 0.27012 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.003298 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0092344 | 0 | 0.27012 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.46959 | 142 | 0.27013 | 38.3579
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.47952 | 145 | 0.27013 | 39.1683
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.49936 | 151 | 0.27013 | 40.7891
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.003307 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.95903 | 290 | 0.27013 | 78.3366
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7982 | 223.9 | 0.27038 | 60.539
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80212 | 225 | 0.27038 | 60.8364
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.8007 | 224.6 | 0.27038 | 60.7283
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003565 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.80819 | 226.7 | 0.27038 | 61.2961
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003709 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.081598 | 22 | 0.27053 | 5.9516
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003709 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040799 | 11 | 0.27053 | 2.9758
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003709 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.040799 | 11 | 0.27053 | 2.9758
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003743 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0089832 | 0 | 0.27056 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003743 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0089832 | 0 | 0.27056 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003764 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.045168 | 0 | 0.27058 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18589 | 47.7 | 0.27072 | 12.9132
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.14536 | 37.3 | 0.27072 | 10.0977
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.17926 | 46 | 0.27072 | 12.4529
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003897 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.18706 | 48 | 0.27072 | 12.9944
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.00398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57312 | 144 | 0.2708 | 38.9951
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.00398 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.74824 | 188 | 0.2708 | 50.9102
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.004084 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.29813 | 0 | 0.2709 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.004224 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06336 | 0 | 0.27104 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.004224 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.097152 | 0 | 0.27104 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.004255 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.03404 | 0 | 0.27107 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12118 | 0 | 0.27115 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030296 | 0 | 0.27115 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16879 | 0 | 0.27115 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06492 | 0 | 0.27115 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.030296 | 0 | 0.27115 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.06492 | 0 | 0.27115 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16879 | 0 | 0.27115 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.004328 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.16879 | 0 | 0.27115 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.004585 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03668 | 0 | 0.2714 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.004585 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03668 | 0 | 0.2714 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.004703 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22574 | 0 | 0.27152 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23412 | 49 | 0.2716 | 13.3083
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21979 | 46 | 0.2716 | 12.4935
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21979 | 46 | 0.2716 | 12.4935
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22457 | 47 | 0.2716 | 12.7651
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004778 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.73581 | 154 | 0.2716 | 41.826
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004778 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.70714 | 148 | 0.2716 | 40.1964
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22934 | 48 | 0.2716 | 13.0367
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004778 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22934 | 48 | 0.2716 | 13.0367
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3796 | 0 | 0.27162 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.38921 | 0 | 0.27162 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3796 | 0 | 0.27162 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.3844 | 0 | 0.27162 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.37671 | 0 | 0.27162 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12012 | 0 | 0.27162 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.22103 | 0 | 0.27162 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.13454 | 0 | 0.27162 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2095 | 0 | 0.27162 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.004805 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.35557 | 0 | 0.27162 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004842 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.501 | 310 | 0.27166 | 84.215
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004842 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.9997 | 413 | 0.27166 | 112.1961
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.21244 | 42 | 0.27188 | 11.4188
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22255 | 44 | 0.27188 | 11.9626
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.22255 | 44 | 0.27188 | 11.9626
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.005058 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.23773 | 47 | 0.27188 | 12.7782
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.73814 | 132 | 0.27241 | 35.9583
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.74933 | 134 | 0.27241 | 36.5031
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.005592 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.8062 | 323 | 0.27241 | 87.9888
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.85766 | 152.5 | 0.27244 | 41.5476
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84079 | 149.5 | 0.27244 | 40.7303
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.005624 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.3081 | 232.6 | 0.27244 | 63.3703
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.005965 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.29825 | 50 | 0.27278 | 13.6392
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.96949 | 158 | 0.27296 | 43.1269
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.98176 | 160 | 0.27296 | 43.6728
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.006136 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0738 | 175 | 0.27296 | 47.7672
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.006194 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.682 | 0 | 0.27301 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.006197 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.619 | 0 | 0.27302 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.006197 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 3.6872 | 0 | 0.27302 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.008249 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 10.9959 | 0 | 0.27507 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.008249 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 10.9547 | 0 | 0.27507 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.63893 | 76 | 0.27523 | 20.9172
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.63893 | 76 | 0.27523 | 20.9172
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.88274 | 105 | 0.27523 | 28.8988
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62212 | 74 | 0.27523 | 20.3667
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.62212 | 74 | 0.27523 | 20.3667
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.008407 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.85751 | 102 | 0.27523 | 28.0731
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.008517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.8462 | 0 | 0.27534 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.008517 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 4.9484 | 0 | 0.27534 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.008544 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.5639 | 66 | 0.27536 | 18.174
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58379 | 0 | 0.27624 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6723 | 0 | 0.27624 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.42372 | 0 | 0.27624 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95102 | 0 | 0.27624 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80978 | 0 | 0.27624 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.82861 | 0 | 0.27624 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.4708 | 0 | 0.27624 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.16949 | 0 | 0.27624 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8851 | 0 | 0.27624 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.65912 | 0 | 0.27624 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.59321 | 0 | 0.27624 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.67795 | 0 | 0.27624 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.61016 | 0 | 0.27624 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.95102 | 0 | 0.27624 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.91335 | 0 | 0.27624 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96985 | 0 | 0.27624 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71562 | 0 | 0.27624 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75328 | 0 | 0.27624 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75328 | 0 | 0.27624 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.009416 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.6101 | 0 | 0.27624 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.009626 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68345 | 0 | 0.27645 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.009626 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.09626 | 0 | 0.27645 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0881 | 0 | 0.27662 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0881 | 0 | 0.27662 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1666 | 0 | 0.27662 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.009803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0734 | 0 | 0.27662 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.010374 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.47824 | 0 | 0.27719 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.7899 | 0 | 0.27725 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 5.8825 | 0 | 0.27725 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.01043 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 6.258 | 0 | 0.27725 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7007 | 0 | 0.27725 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7007 | 0 | 0.27725 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.010434 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.5563 | 0 | 0.27725 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.01046 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34518 | 0 | 0.27728 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.6971 | 161 | 0.27736 | 44.655
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.7498 | 166 | 0.27736 | 46.0418
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.010541 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.6142 | 248 | 0.27736 | 68.7853
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.010541 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 5.7554 | 546 | 0.27736 | 151.4387
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.010541 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 6.7779 | 0 | 0.27736 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.010541 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13703 | 13 | 0.27736 | 3.6057
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0817 | 0 | 0.2776 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0019 | 0 | 0.2776 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1076 | 0 | 0.2776 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.010785 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.1001 | 0 | 0.2776 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.010786 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34515 | 0 | 0.27761 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.010786 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32358 | 0 | 0.27761 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.76372 | 0 | 0.27761 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71949 | 0 | 0.27761 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57171 | 0 | 0.27761 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6526 | 0 | 0.27761 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6558 | 0 | 0.27761 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.6429 | 0 | 0.27761 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.0356 | 0 | 0.27761 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.010787 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.632 | 0 | 0.27761 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.010787 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.43148 | 0 | 0.27761 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.010925 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.54625 | 50 | 0.27774 | 13.8872
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.011 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.27782 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.011 | 0 | 0.27793 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.97324 | 0 | 0.27793 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.96657 | 0 | 0.27793 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.6055 | 0 | 0.27793 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.01111 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13554 | 0 | 0.27793 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72494 | 0 | 0.27797 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.66918 | 0 | 0.27797 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72494 | 0 | 0.27797 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.011153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.72494 | 0 | 0.27797 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51649 | 46 | 0.27805 | 12.7902
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51649 | 46 | 0.27805 | 12.7902
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.51649 | 46 | 0.27805 | 12.7902
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61754 | 55 | 0.27805 | 15.2926
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.61754 | 55 | 0.27805 | 15.2926
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.011228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.60631 | 54 | 0.27805 | 15.0145
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.011232 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.8761 | 0 | 0.27805 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.011232 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.89856 | 0 | 0.27805 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.836 | 0 | 0.27807 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7674 | 0 | 0.27807 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7719 | 0 | 0.27807 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7663 | 0 | 0.27807 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.01125 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 3.0263 | 0 | 0.27807 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.011273 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39455 | 0 | 0.27809 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011291 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13549 | 12 | 0.27811 | 3.3373
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.011291 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.27811 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.011292 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.9083 | 169 | 0.27811 | 47.0008
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.011294 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.8635 | 165 | 0.27811 | 45.8887
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.683 | 0 | 0.27811 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.011295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7353 | 0 | 0.27811 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.011298 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.4065 | 213 | 0.27812 | 59.239
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18304 | 0 | 0.27812 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72314 | 0 | 0.27812 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7141 | 0 | 0.27812 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.9333 | 0 | 0.27812 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.011299 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.83161 | 0 | 0.27812 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.0113 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 2.5764 | 228 | 0.27812 | 63.4112
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0344 | 0 | 0.27812 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7925 | 0 | 0.27812 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.011302 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.7744 | 0 | 0.27812 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80429 | 0 | 0.27815 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.81562 | 0 | 0.27815 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.44179 | 0 | 0.27815 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.011328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.33984 | 0 | 0.27815 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47767 | 42 | 0.27819 | 11.6841
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.47767 | 42 | 0.27819 | 11.6841
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43217 | 38 | 0.27819 | 10.5713
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.011373 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.43217 | 38 | 0.27819 | 10.5713
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.011375 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.547 | 0 | 0.27819 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.011388 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9701 | 0 | 0.27821 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.011388 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.5374 | 0 | 0.27821 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1923 | 104 | 0.27828 | 28.9415
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.1923 | 104 | 0.27828 | 28.9415
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.60759 | 53 | 0.27828 | 14.749
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.65345 | 57 | 0.27828 | 15.8621
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.61906 | 54 | 0.27828 | 15.0273
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66491 | 58 | 0.27828 | 16.1404
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.011464 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.66491 | 58 | 0.27828 | 16.1404
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.011476 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.4349 | 735 | 0.2783 | 204.547
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3908 | 0 | 0.27831 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.39884 | 0 | 0.27831 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.37585 | 0 | 0.27831 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52757 | 0 | 0.27831 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20344 | 0 | 0.27831 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23448 | 0 | 0.27831 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22873 | 0 | 0.27831 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.40229 | 0 | 0.27831 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20689 | 0 | 0.27831 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.98159 | 0 | 0.27831 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.011494 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.7011 | 0 | 0.27831 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.011527 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.13832 | 12 | 0.27835 | 3.3402
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.011545 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.057725 | 0 | 0.27836 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.011545 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24244 | 0 | 0.27836 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.011546 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.13855 | 0 | 0.27837 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.75055 | 0 | 0.27837 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.7621 | 0 | 0.27837 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.80829 | 0 | 0.27837 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.72746 | 0 | 0.27837 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.71591 | 0 | 0.27837 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.2009 | 0 | 0.27837 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.011547 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.68127 | 0 | 0.27837 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.011548 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 8.5802 | 743 | 0.27837 | 206.8268
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.011564 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8155 | 0 | 0.27838 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9897 | 172 | 0.27839 | 47.8826
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9897 | 172 | 0.27839 | 47.8826
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.011568 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 1.9897 | 172 | 0.27839 | 47.8826
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8916 | 0 | 0.27844 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8753 | 0 | 0.27844 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.8463 | 0 | 0.27844 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.011619 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 3.1278 | 0 | 0.27844 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.011641 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 4.6331 | 398 | 0.27846 | 110.8272
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68871 | 59 | 0.27849 | 16.431
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.68871 | 59 | 0.27849 | 16.431
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.011673 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.65369 | 56 | 0.27849 | 15.5956
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 2.0698 | 0 | 0.27878 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8664 | 0 | 0.27878 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8425 | 0 | 0.27878 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.011964 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 1.8425 | 0 | 0.27878 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.011964 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 1.9382 | 0 | 0.27878 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 1340
| 25 | 1340
| 30 | 1340
| 35 | 1340
| 40 | 1340
| 45 | 1340
| 50 | 1340
| 55 | 1340
| 60 | 1307
| 65 | 1280
| 70 | 1251
| 75 | 1251
| 80 | 1223
| 85 | 1194
| 90 | 1163
| 95 | 1132
| 100 | 1098
| 105 | 1065
| 110 | 1031
| 115 | 994
| Max | 1340
| Min | 994
| Avg | 1235.45