## test results
CRE test for: |  | LINGLVLL - FLATCRK_ 138 kV 1640 - 1642 | [5 empty] | FAIL
Line Rating: |  | 381.35
Direction |  | West | → | North |  | W-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | LINGLVLL - FLATCRK_ 138 kV 1640 - 1642
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.00035793
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | 0.0035718
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | -0.037775
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | 0.0033579
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | LINGLVLL - FLATCRK_ 138 kV 1640 - 1642
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.0020842
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | 0.0035134
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | -0.03739
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | 0.0033522
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | LINGLVLL - FLATCRK_ 138 kV 1640 - 1642
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | -0.0031554
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.037748
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | -0.0029943
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | 0.040962
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.00021388
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | -0.041127
PTDF tests
West | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | -0.039859 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.039859 | -0.0031554
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.042638
[6 empty] | Concentration |  | -1.0697 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.049077
[6 empty] | Concentration |  | -1.2313 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 47.1843
| Percent of line rating => | [6 empty] | 12.37% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -20.3902
[7 empty] | B1(N-S) | -0.10447 | -0.040127 | 0.06434 | -0.10447
[7 empty] | B2 (N-W) | -0.045078 | -0.81477 | -0.76969 | -0.045078
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.080029 | -0.018975 | 0.061054 | -0.080029
[7 empty] | B4 (S-W) | 0.059452 | -0.77577 | -0.83522 | 0.059452
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.024385 | 0.020024 | -0.0043611 | 0.024385
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.04565 | 0.79294 | 0.83859 | -0.04565
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | -12.85%
Deployment Error Percent | [6 empty] | B2 | -5.546%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -9.847%
[7 empty] | B4 | 7.315%
[7 empty] | B5 | 3%
[7 empty] | B6 | -5.617%
[7 empty] | Max Abs Error | 12.85% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:LINGLVLL - FLATCRK_ 138 kV 1640 - 1642 C: COMCHESS - SARC7A 345kV 1440 - 6444 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:LINGLVLL - FLATCRK_ 138 kV 1640 - 1642 C: COMCHESS - SARC7A 345kV 1440 - 6444
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011117 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 2.8348
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011117 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 1.6564
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.016587 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.2488
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.016587 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 0.2488
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.011117 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 1.7009
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.015307 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 2.2961
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.015307 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 1.2246
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041732 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 3.0464
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041732 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 4.9661
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041732 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 8.5551
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041732 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 4.2567
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.041732 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 4.0063
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.014105 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.16926
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | -0.014105 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | -0.16926
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.011578 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 1.9451
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.011578 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 1.042
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.2362
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 0.2362
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 0.49864
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 0.81216
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.41454
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 0.41454
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | -0.003489 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | -0.39251
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.000516 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.02064
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 0.035155
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 0.04717
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 0.06497
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.000445 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 0.03382
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.002454 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | -0.14724
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | -0.002454 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | -0.1546
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.00996
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.01245
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.020418
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.003161 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 1.4635
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | -2.4606
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | -2.4233
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -2.4979
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -2.4979
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | -2.4979
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.037282 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | -4.2501
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | -0.037282 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | -19.2002
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | -2.5942
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -2.7121
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | -2.7121
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -2.6335
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | -2.6335
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | -2.5549
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | -2.6107
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | -2.7375
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | -2.6256
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | -5.5888
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | -8.197
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.041309 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | -4.0896
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.041309 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | -2.5198
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.041248 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | -5.816
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | -1.0327
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.8878
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | -1.8878
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | -0.041248 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | -4.9498
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | -0.039409 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | -1.0168
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | -0.038236 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | -3.8427
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | -0.039473 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | -4.7368
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | -0.038407 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | -2.2276
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | -0.038533 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | -8.2538
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.0545 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | -8.175
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.039271 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | -0.25919
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | -0.039271 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | -1.347
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | -0.0545 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | -5.5045
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | -0.03966 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | -4.7592
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | -0.024081 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | -8.8136
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | -0.062441 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | -15.1107
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | -0.033173 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | -13.2692
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | -0.033151 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | -7.8236
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | -0.030974 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | -5.1107
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | -2.6445
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | -2.6056
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | -3.137
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.5982
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.5982
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | -0.5982
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | -0.50847
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | -0.02175 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | -2.61
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.68669 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -41.2015
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 0.009975
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 0.010587
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 0.011757
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 0.01664
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.016224
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 0.020384
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.016224
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 0.016328
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 0.020592
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -6.6e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -0.01122
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -6.6e-05 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -0.03432
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 5.6e-05 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 0.02072
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 0.10769
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 0.11175
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 0.15594
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.001362 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | -0.15254
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.001362 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | -0.1362
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | -0.001362 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | -0.51484
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 0.81922
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 0.77285
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 1.0269
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.004436 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 3.4157
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 1.4982
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.4768
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 1.4768
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 1.4554
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.004139 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 4.7888
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.004139 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 4.793
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 0.64758
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 0.65337
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.002064 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 0.44665
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.002064 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 0.44603
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 0.61289
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 0.61
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.000798 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 0.31521
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.000871 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 0.37889
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.000798 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 0.34713
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -0.000465 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -0.06417
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.001218 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 0.14372
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.001218 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 0.14007
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.001218 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 0.67721
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.00077 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 0.29876
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.00077 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 0.39655
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 1.1689
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 1.1838
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 1.1614
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.001684 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 0.30649
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.001684 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 0.81506
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.003046 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 0.6823
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.001663 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 0.08315
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.001655 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 0.06951
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.002502 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 1.5387
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.002502 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 1.4687
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.005883 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 3.1592
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.005883 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 4.6299
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006314 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 0.47355
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.006314 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 1.4017
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.004863 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 2.767
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003281 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | 0.68573
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003281 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | 0.7087
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | 0.003258 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | 1.326
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.15093
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | 0.15421
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.15093
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | 0.15093
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.003297 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | 1.3979
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | 0.003297 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | 1.4012
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.00318 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | 0.18444
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.00318 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | 0.28302
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.13992
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | 0.13992
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | 0.13674
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | 0.1431
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.003283 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | 1.3526
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | 0.003283 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | 1.3132
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.003366 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | 1.8378
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | 0.003366 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | 2.5245
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | 0.20435
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | 0.31825
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | 0.50585
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.52018
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | 0.57052
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | 0.52018
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003242 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | 0.071324
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003242 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.035662
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | 0.003242 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | 0.035662
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | 0.1566
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | 0.12246
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | 0.15102
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | 0.15758
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.033372
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | 0.030591
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.001627 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.039048
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.001627 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.039048
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 0.001627 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.037421
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | 0.003154 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | 1.249
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.003433 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | 4.5762
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | 0.003433 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | 4.559
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | 0.11962
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | 0.060756
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | 0.04722
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | 0.003148 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | 0.14796
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | -2.6908
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | -0.047213 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | -7.0819
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | -0.042114 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | -7.1383
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | -0.02985 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | -4.4775
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | -0.041115 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | -2.5902
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | -0.031852 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | -20.6942
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.000161 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.00644
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -0.000161 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.00644
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.003759 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 1.5863
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | 0.56126
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | 0.56977
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | 1.3734
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | 0.66802
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | 0.67648
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | 0.7399
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.00406 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | 2.371
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | 0.00406 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | 2.4157
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | 0.004058 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | 1.7571
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | 0.83
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | 0.83408
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | 0.83259
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | 0.84038
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.00433 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.03464
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | 0.00433 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | 0.03464
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.084402
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.084402
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.070335
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.003701 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.050704
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.003911 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.070398
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.003911 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.070398
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.14896
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | 0.1447
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | 0.14896
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003908 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.10942
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003908 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.11333
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.037389 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | -1.3086
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | -0.037389 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | -1.1217
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.20475
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.20475
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.20475
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | 0.20475
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | 0.022518
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0087312
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | 0.0087312
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | 0.010186
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | 0.003551 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | 0.014204
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003671 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0088104
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | 0.003671 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | 0.0088104
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.517
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | 0.48535
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | 0.49238
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | 0.517
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | 0.64009
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | 0.69637
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | 0.64111
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | 0.6285
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | 0.97785
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | 0.5129
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | 0.52374
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | 0.54541
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | 1.0475
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.008922 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -0.29443
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.008922 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -0.22305
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | 0.033372
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | 0.003313 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | 0.24185
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.26307
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | 0.26973
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | 0.092596
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.023149
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | 0.26307
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | 0.2664
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | 0.26107
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | 0.08325
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | 0.15318
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | 0.003251 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | 2.0449
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.003313 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | 0.47707
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | 0.003313 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | 0.62284
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | 0.003562 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | 0.042744
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.005575 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.03345
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | 1.0712
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003186 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | 1.0641
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003186 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | 1.0832
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | 0.00318 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | 0.12084
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.003183 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.079575
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | 0.003183 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | 0.079575
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | 0.003184 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | 0.12099
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | 0.003171 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | 0.091959
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | 0.47278
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | 0.47374
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | 0.48776
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | 0.50623
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | 0.49021
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | 0.3204
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | 0.46458
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | 0.47099
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | 0.40691
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | 0.4499
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | 0.4542
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | 0.53128
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | 0.64584
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | 0.6761
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | 0.75504
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.44928
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | 0.44928
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | 0.53352
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004338 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | 1.3448
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | 0.004338 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | 1.7916
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | 0.18358
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.19232
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | 0.19232
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | 0.20544
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | 0.2105
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.19762
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | 0.19762
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | 0.20191
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | 0.66158
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | 0.63581
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.20621
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | 0.20621
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -2.6097
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | -2.6097
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | -3.4598
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -2.9826
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | -2.9826
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | -4.2874
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | -7.7621
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | -5.2978
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | -4.9361
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | -5.0704
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | -5.4805
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | -7.8292
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | -7.4277
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | -4.4957
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | -8.8492
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | -7.0012
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | -7.4518
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | -4.5419
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | -0.03764 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | -5.6084
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.04024 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -7.2432
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | -0.04024 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | -7.2432
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | -0.040141 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | -9.0317
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.036772 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -4.5965
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | -0.036772 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | -4.5965
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 0.00784
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 0.007896
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 0.017304
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 0.008008
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 0.008064
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 0.01736
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.0033 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 0.6468
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.0033 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 0.3663
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -8.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.12735
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.12972
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.12972
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 0.32747
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 0.12814
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.12735
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 0.12893
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 0.32352
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.000872 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.000872 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 0.23414
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 0.20566
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 0.22939
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 0.63122
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 0.35776
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 0.35847
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 0.42115
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 0.35709
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 0.35897
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 0.41837
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.004863 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 2.8254
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.565
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 2.565
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.003269 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.10461
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.00331 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.15888
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.00331 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.15226
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.03924
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.16677
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00327 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.05559
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.07194
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.08175
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.00331 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 0.34755
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | -0.042405 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | -3.562
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | -0.035849 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | -2.8679
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.035836 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -5.3754
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | -0.035836 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | -5.3754
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | 0.23789
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | 0.22411
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | 0.17808
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | 0.51475
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | 0.51576
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | 0.51173
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | 0.32256
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | 0.81984
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | 0.1344
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | 0.33701
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | 0.31214
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | 0.34507
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | 0.34272
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | 0.10752
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | 0.1008
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.37662
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | 0.37662
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | 0.40377
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | 0.37153
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 0.4569
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 0.459
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | 0.003339 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | 0.4541
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | 0.003371 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | 0.11124
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.1402
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | 0.1402
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.12684
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | 0.12684
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.003396 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | 0.24112
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | 0.003396 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | 0.03396
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 0.55061
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | 0.55061
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | 0.82761
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.21749
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | 0.20076
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.21749
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | 0.21749
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | 0.49781
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | 0.2175
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | 0.30467
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | 0.29328
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | 0.29128
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | 0.18247
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | 0.040846
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | 0.003331 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | 2.4749
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | 0.003334 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | 2.4505
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.57276
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.57276
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | 0.57276
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | 0.57332
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.003338 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | 0.57747
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | 0.003338 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | 0.45063
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | 0.5418
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | 0.53714
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | 0.52882
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | 0.8959
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | 0.21382
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | 0.21115
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | 0.27597
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | 0.2459
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | 0.54541
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | 0.52503
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | 0.52636
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | 0.52469
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | 0.899
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | 0.016655
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | 0.069951
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 0.49174
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.49748
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 0.49748
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 1.2118
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | 0.003328 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | 1.3245
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.15392
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.15392
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | 0.15392
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.18403
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | 0.18403
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | 0.18068
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.002936 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 2.4281
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.002936 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 2.4046
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | 0.003374 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | 0.15554
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.26205
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | 0.26205
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | 0.36204
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.25515
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | 0.25515
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | 0.3517
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | 0.60138
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | 0.52988
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | 0.52454
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | 0.003342 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | 0.11697
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | 0.003352 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | 1.5386
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | 0.21652
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | 0.21985
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | 0.23317
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | 0.20985
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | 0.20652
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | 0.34642
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | 0.19653
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | 0.51698
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.51036
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | 0.51036
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | 0.003314 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | 0.53687
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | 0.003331 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | 0.52297
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | 0.23714
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | 0.24048
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | 0.13026
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | 0.1002
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.003343 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | 0.26075
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | 0.003343 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | 0.26744
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | 0.054124
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | 0.55127
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | 0.56463
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | 0.71163
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | 0.76175
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.003341 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | 0.040092
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | 0.003341 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | 0.060138
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | 0.003358 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | 0.1679
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.34694
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | 0.34694
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18014
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | 0.17681
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18014
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | 0.19015
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18014
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | 0.18014
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.19349
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | 0.19349
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | 0.003333 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | 0.039996
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.18631
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.19629
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.18631
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.18631
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | 0.19629
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | 0.18631
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | 0.003422 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | 0.22585
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | 0.54386
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | 0.56075
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | 0.83774
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.003378 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | 1.8444
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.003378 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | 2.1721
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | 2.1991
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | 1.9052
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | 2.0268
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | 0.003378 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | 0.043914
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | 0.003331 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | 0.039972
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | 0.11332
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | 0.11566
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | 0.10899
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | 0.15298
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | 0.058994
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | 0.067993
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | 0.066327
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | 0.11665
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | 0.059994
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | 0.28464
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | 0.49328
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | 0.21092
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | 0.2429
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | 0.15309
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.3436
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | 0.29257
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | 0.29938
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | 0.1701
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | 0.061236
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | 0.31979
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | 0.23814
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | 0.21433
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | 0.24494
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | 0.22045
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | 0.3436
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | 0.32999
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | 0.35041
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | 0.25855
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.27216
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | 0.27216
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | 0.58174
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.011021
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | -0.035241 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | -2.6959
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | -2.8702
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | -1.4351
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.035986 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -2.8789
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | -0.035852 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | -2.8682
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | -0.0353 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | -2.824
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | -0.035119 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | -2.95
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | -0.035986 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | -2.8789
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | 0.37529
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | -5.225
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | -10.1453
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | -7.4108
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | 0.73082
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | 0.60573
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | 0.73741
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | 0.37858
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | 0.3292
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | -0.048808 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | -2.9285
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.009459 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | -0.032223 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | -0.036359 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | -0.17452
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | -1.4288
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | -4.0959
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | -5.1436
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | -4.534
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | -4.0006
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | -3.0671
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | -0.037795 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | -5.6692
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | -4.2639
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | -5.6662
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | -7.0496
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | -8.1298
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | 0.003148 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.004796 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | 0.002203 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | 0.09324
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | 0.14519
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | 0.24642
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.29695
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | 0.12952
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | 0.12004
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | 0.060021
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | 0.29695
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | 0.11372
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | 0.13584
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | 0.069498
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.12897
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.049605
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | 0.023149
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | 0.049605
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.12897
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | 0.12897
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | 0.46753
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.15795
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | 0.17375
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | 0.15795
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | 0.003204 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | 0.038448
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | 0.049605
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | 0.076061
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | 0.003326 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | 0.15965
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | 0.003302 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | 0.026416
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | 0.57384
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | 0.57384
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003186 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.57348
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | 0.003186 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | 0.57348
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002204 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.2204
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002204 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | 0.2204
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.079925
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.079925
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.079925
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | 0.051152
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.079925
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.079925
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | 0.079925
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | 0.047955
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002204 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002204 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 1.102
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002204 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | 1.102
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | 0.002204 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | 0.003094 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.008922 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | 0.002504 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | 0.003024 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:LINGLVLL - FLATCRK_ 138 kV 1640 - 1642 C: COMCHESS - SARC7A 345kV 1440 - 6444 | [7 empty] | 47.1843
Number of Bus | Name of Bus | ID | Max MW | L:LINGLVLL - FLATCRK_ 138 kV 1640 - 1642 C: COMCHESS - SARC7A 345kV 1440 - 6444 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.011117 | north | Y | 0.010759 | 0.0075452 | 0.048892 | 0.0077591 | 0.0075452 | south | Y | 0.010759 | 0.81953
239 | BOSQUESW | 1 | 149 | 0.011117 | north | Y | 0.010759 | 0.0075452 | 0.048892 | 0.0077591 | 0.0075452 | south | Y | 0.010759 | 0.47886
244 | WHITNYDM | 1 | 15 | 0.016587 | north | N | 0.016229 | 0.013015 | 0.054362 | 0.013229 | 0.013015 | south | Y | 0.016229 | 0
245 | WHITNYDM | 2 | 15 | 0.016587 | north | N | 0.016229 | 0.013015 | 0.054362 | 0.013229 | 0.013015 | south | Y | 0.016229 | 0
247 | BOSQUESW | 2 | 153 | 0.011117 | north | Y | 0.010759 | 0.0075452 | 0.048892 | 0.0077591 | 0.0075452 | south | Y | 0.010759 | 0.49172
251 | BOSQUESW | 2 | 150 | 0.015307 | north | Y | 0.014949 | 0.011735 | 0.053082 | 0.011949 | 0.011735 | south | Y | 0.014949 | 0.48207
253 | BOSQUESW | 2 | 80 | 0.015307 | north | Y | 0.014949 | 0.011735 | 0.053082 | 0.011949 | 0.011735 | south | Y | 0.014949 | 0.25711
332 | RWMILLER | 1 | 73 | 0.041732 | north | Y | 0.041374 | 0.03816 | 0.079507 | 0.038374 | 0.03816 | south | Y | 0.041374 | 0.23461
333 | RWMILLER | 2 | 119 | 0.041732 | north | Y | 0.041374 | 0.03816 | 0.079507 | 0.038374 | 0.03816 | south | Y | 0.041374 | 0.38245
334 | RWMILLER | 3 | 205 | 0.041732 | north | Y | 0.041374 | 0.03816 | 0.079507 | 0.038374 | 0.03816 | south | Y | 0.041374 | 0.65884
335 | RWMILLER | 4 | 102 | 0.041732 | north | Y | 0.041374 | 0.03816 | 0.079507 | 0.038374 | 0.03816 | south | Y | 0.041374 | 0.32781
336 | RWMILLER | 5 | 96 | 0.041732 | north | Y | 0.041374 | 0.03816 | 0.079507 | 0.038374 | 0.03816 | south | Y | 0.041374 | 0.30853
344 | MRSSHPRD | 1 | 12 | -0.014105 | north | N | -0.014463 | -0.017677 | 0.02367 | -0.017463 | 0.014463 | North | N | 0.014463 | 0
345 | MRSSHPRD | 2 | 12 | -0.014105 | north | N | -0.014463 | -0.017677 | 0.02367 | -0.017463 | 0.014463 | North | N | 0.014463 | 0
366 | JNSNCNTY | 1 | 168 | 0.011578 | north | Y | 0.01122 | 0.0080062 | 0.049353 | 0.0082201 | 0.0080062 | south | Y | 0.01122 | 0.53992
367 | JNSNCNTY | 2 | 90 | 0.011578 | north | Y | 0.01122 | 0.0080062 | 0.049353 | 0.0082201 | 0.0080062 | south | Y | 0.01122 | 0.28924
503 | NTHTEXAS | 1 | 18 | 0.013122 | north | Y | 0.012764 | 0.0095502 | 0.050897 | 0.0097641 | 0.0095502 | south | Y | 0.012764 | 0.057849
504 | NTHTEXAS | 2 | 18 | 0.013122 | north | Y | 0.012764 | 0.0095502 | 0.050897 | 0.0097641 | 0.0095502 | south | Y | 0.012764 | 0.057849
505 | NTHTEXAS | 3 | 38 | 0.013122 | north | Y | 0.012764 | 0.0095502 | 0.050897 | 0.0097641 | 0.0095502 | south | Y | 0.012764 | 0.12213
580 | JCKCNTY8 | 1 | 288 | 0.00282 | north | Y | 0.0024621 | -0.00075176 | 0.040595 | -0.00053788 | 0.00053788 | houston | Y | 0.0024621 | 0.55417
581 | JCKCNTY8 | 2 | 147 | 0.00282 | north | Y | 0.0024621 | -0.00075176 | 0.040595 | -0.00053788 | 0.00053788 | houston | Y | 0.0024621 | 0.28286
582 | JCKCNTY8 | 3 | 147 | 0.00282 | north | Y | 0.0024621 | -0.00075176 | 0.040595 | -0.00053788 | 0.00053788 | houston | Y | 0.0024621 | 0.28286
728 | WOLFRIDG | 1 | 112.5 | -0.003489 | north | Y | -0.0038469 | -0.0070608 | 0.034286 | -0.0068469 | 0.0038469 | North | N | 0.0038469 | 0
837 | NEWMAN_G | 1 | 40 | 0.000516 | north | Y | 0.00015807 | -0.0030558 | 0.038291 | -0.0028419 | 0.00015807 | North | N | 0.00015807 | 0
842 | OLINGER_ | 1 | 79 | 0.000445 | north | Y | 8.707e-05 | -0.0031268 | 0.03822 | -0.0029129 | 8.707e-05 | North | N | 8.707e-05 | 0
843 | OLINGER_ | 1 | 106 | 0.000445 | north | Y | 8.707e-05 | -0.0031268 | 0.03822 | -0.0029129 | 8.707e-05 | North | N | 8.707e-05 | 0
844 | OLINGER_ | 1 | 146 | 0.000445 | north | Y | 8.707e-05 | -0.0031268 | 0.03822 | -0.0029129 | 8.707e-05 | North | N | 8.707e-05 | 0
845 | OLINGER_ | 1 | 76 | 0.000445 | north | Y | 8.707e-05 | -0.0031268 | 0.03822 | -0.0029129 | 8.707e-05 | North | N | 8.707e-05 | 0
923 | SPENCER_ | 1 | 60 | -0.002454 | north | Y | -0.0028119 | -0.0060258 | 0.035321 | -0.0058119 | 0.0028119 | North | N | 0.0028119 | 0
924 | SPENCER_ | 1 | 63 | -0.002454 | north | Y | -0.0028119 | -0.0060258 | 0.035321 | -0.0058119 | 0.0028119 | North | N | 0.0028119 | 0
948 | STEAM1 | 1 | 20 | 0.000498 | north | Y | 0.00014007 | -0.0030738 | 0.038273 | -0.0028599 | 0.00014007 | North | N | 0.00014007 | 0
949 | STEAM2 | 1 | 25 | 0.000498 | north | Y | 0.00014007 | -0.0030738 | 0.038273 | -0.0028599 | 0.00014007 | North | N | 0.00014007 | 0
950 | STEAM3 | 1 | 41 | 0.000498 | north | Y | 0.00014007 | -0.0030738 | 0.038273 | -0.0028599 | 0.00014007 | North | N | 0.00014007 | 0
990 | GIBN_CRE | 1 | 463 | 0.003161 | north | Y | 0.0028031 | -0.00041076 | 0.040936 | -0.00019688 | 0.00019688 | houston | Y | 0.0028031 | 1.2067
1002 | PBCTAGE_ | A | 66 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
1003 | PBCTBGE_ | B | 65 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
1004 | PBCTCGE_ | C | 67 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
1005 | PBCTDGE_ | D | 67 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
1006 | PBCTEGE_ | E | 67 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
1007 | PB5GEN_6 | MB | 114 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
1008 | PB6GEN_7 | MB | 515 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
1039 | MRGNAG_1 | A | 66 | -0.039306 | west | Y | -0.039664 | -0.042878 | -0.0015313 | -0.042664 | 0.0015313 | west | N | 0.0015313 | 0
1040 | MRGNBG_2 | B | 69 | -0.039306 | west | Y | -0.039664 | -0.042878 | -0.0015313 | -0.042664 | 0.0015313 | west | N | 0.0015313 | 0
1041 | MRGNCG_3 | C | 69 | -0.039306 | west | Y | -0.039664 | -0.042878 | -0.0015313 | -0.042664 | 0.0015313 | west | N | 0.0015313 | 0
1042 | MRGNDG_4 | D | 67 | -0.039306 | west | Y | -0.039664 | -0.042878 | -0.0015313 | -0.042664 | 0.0015313 | west | N | 0.0015313 | 0
1043 | MRGNEG_5 | E | 67 | -0.039306 | west | Y | -0.039664 | -0.042878 | -0.0015313 | -0.042664 | 0.0015313 | west | N | 0.0015313 | 0
1044 | MRGNFG_6 | F | 65 | -0.039306 | west | Y | -0.039664 | -0.042878 | -0.0015313 | -0.042664 | 0.0015313 | west | N | 0.0015313 | 0
1045 | CALENG1G | 1 | 70 | -0.037295 | west | N | -0.037653 | -0.040867 | 0.00047971 | -0.040653 | 0.00047971 | west | N | 0.00047971 | 0
1046 | CALENG2G | 2 | 73.4 | -0.037295 | west | N | -0.037653 | -0.040867 | 0.00047971 | -0.040653 | 0.00047971 | west | N | 0.00047971 | 0
1047 | CALENG3G | 3 | 70.4 | -0.037295 | west | N | -0.037653 | -0.040867 | 0.00047971 | -0.040653 | 0.00047971 | west | N | 0.00047971 | 0
1058 | LONGSHOR | 1 | 150 | -0.037259 | west | Y | -0.037617 | -0.040831 | 0.00051571 | -0.040617 | 0.00051571 | west | N | 0.00051571 | 0
1058 | LONGSHOR | 2 | 220 | -0.037259 | west | Y | -0.037617 | -0.040831 | 0.00051571 | -0.040617 | 0.00051571 | west | N | 0.00051571 | 0
1061 | CIELOGEN | 1 | 99 | -0.041309 | west | Y | -0.041667 | -0.044881 | -0.0035343 | -0.044667 | 0.0035343 | west | N | 0.0035343 | 0
1062 | CIELOGEN | 1 | 61 | -0.041309 | west | Y | -0.041667 | -0.044881 | -0.0035343 | -0.044667 | 0.0035343 | west | N | 0.0035343 | 0
1068 | SCURRYCW | 1 | 141 | -0.041248 | west | Y | -0.041606 | -0.04482 | -0.0034733 | -0.044606 | 0.0034733 | west | N | 0.0034733 | 0
1069 | KINDERMG | 1 | 25 | -0.041309 | west | N | -0.041667 | -0.044881 | -0.0035343 | -0.044667 | 0.0035343 | west | N | 0.0035343 | 0
1070 | KINDERMG | 1 | 45.7 | -0.041309 | west | N | -0.041667 | -0.044881 | -0.0035343 | -0.044667 | 0.0035343 | west | N | 0.0035343 | 0
1071 | KINDERMG | 1 | 45.7 | -0.041309 | west | N | -0.041667 | -0.044881 | -0.0035343 | -0.044667 | 0.0035343 | west | N | 0.0035343 | 0
1073 | SCURRYCW | 2 | 120 | -0.041248 | west | Y | -0.041606 | -0.04482 | -0.0034733 | -0.044606 | 0.0034733 | west | N | 0.0034733 | 0
1320 | BSP 1 | 1 | 25.8 | -0.039409 | west | N | -0.039767 | -0.042981 | -0.0016343 | -0.042767 | 0.0016343 | west | N | 0.0016343 | 0
1326 | STANTONW | 1 | 100.5 | -0.038236 | west | Y | -0.038594 | -0.041808 | -0.00046129 | -0.041594 | 0.00046129 | west | N | 0.00046129 | 0
1327 | WILDHRSE | 1 | 120 | -0.039473 | west | Y | -0.039831 | -0.043045 | -0.0016983 | -0.042831 | 0.0016983 | west | N | 0.0016983 | 0
1328 | OCOTILLO | 1 | 58 | -0.038407 | west | Y | -0.038765 | -0.041979 | -0.00063229 | -0.041765 | 0.00063229 | west | N | 0.00063229 | 0
1333 | MCDDONAL | 1 | 214.2 | -0.038533 | west | Y | -0.038891 | -0.042105 | -0.00075829 | -0.041891 | 0.00075829 | west | N | 0.00075829 | 0
1343 | TRENTIPP | 1 | 150 | -0.0545 | west | Y | -0.054858 | -0.058072 | -0.016725 | -0.057858 | 0.016725 | west | N | 0.016725 | 0
1349 | WESTXWIN | 1 | 6.6 | -0.039271 | west | Y | -0.039629 | -0.042843 | -0.0014963 | -0.042629 | 0.0014963 | west | N | 0.0014963 | 0
1350 | NWPWRG1_ | 1 | 34.3 | -0.039271 | west | Y | -0.039629 | -0.042843 | -0.0014963 | -0.042629 | 0.0014963 | west | N | 0.0014963 | 0
1354 | AEPWIND_ | 1 | 101 | -0.0545 | west | Y | -0.054858 | -0.058072 | -0.016725 | -0.057858 | 0.016725 | west | N | 0.016725 | 0
1360 | GUNSIGHT | 1 | 120 | -0.03966 | west | Y | -0.040018 | -0.043232 | -0.0018853 | -0.043018 | 0.0018853 | west | N | 0.0018853 | 0
1432 | GRHAMSES | 2 | 366 | -0.024081 | north | Y | -0.024439 | -0.027653 | 0.013694 | -0.027439 | 0.013694 | west | Y | 0.024439 | 3.9327
1433 | GRHAMSES | 1 | 242 | -0.062441 | north | Y | -0.062799 | -0.066013 | -0.024666 | -0.065799 | 0.024666 | west | Y | 0.062799 | 9.2281
1437 | MESQUITW | 1 | 400 | -0.033173 | west | Y | -0.033531 | -0.036745 | 0.0046017 | -0.036531 | 0.0046017 | west | N | 0.0046017 | 0
1438 | MESQUITW | 1 | 236 | -0.033151 | west | Y | -0.033509 | -0.036723 | 0.0046237 | -0.036509 | 0.0046237 | west | N | 0.0046237 | 0
1442 | COKFIELD | 1 | 165 | -0.030974 | west | Y | -0.031332 | -0.034546 | 0.0068007 | -0.034332 | 0.0068007 | west | N | 0.0068007 | 0
1453 | WCPWRCO_ | 1 | 204 | -0.012963 | north | Y | -0.013321 | -0.016535 | 0.024812 | -0.016321 | 0.013321 | North | N | 0.013321 | 0
1454 | WCPWRCO_ | 2 | 201 | -0.012963 | north | Y | -0.013321 | -0.016535 | 0.024812 | -0.016321 | 0.013321 | North | N | 0.013321 | 0
1455 | WCPWRCO_ | 3 | 242 | -0.012963 | north | Y | -0.013321 | -0.016535 | 0.024812 | -0.016321 | 0.013321 | North | N | 0.013321 | 0
1479 | WFCOGEN_ | 1 | 20 | -0.02991 | west | Y | -0.030268 | -0.033482 | 0.0078647 | -0.033268 | 0.0078647 | west | N | 0.0078647 | 0
1479 | WFCOGEN_ | 2 | 20 | -0.02991 | west | Y | -0.030268 | -0.033482 | 0.0078647 | -0.033268 | 0.0078647 | west | N | 0.0078647 | 0
1482 | WFCOGEN_ | 1 | 20 | -0.02991 | west | Y | -0.030268 | -0.033482 | 0.0078647 | -0.033268 | 0.0078647 | west | N | 0.0078647 | 0
1482 | WFCOGEN_ | 2 | 17 | -0.02991 | west | Y | -0.030268 | -0.033482 | 0.0078647 | -0.033268 | 0.0078647 | west | N | 0.0078647 | 0
1600 | BARTNWND | 1 | 120 | -0.02175 | north | Y | -0.022108 | -0.025322 | 0.016025 | -0.025108 | 0.016025 | west | Y | 0.022108 | 0.72999
1643 | SLSTR1PP | 1 | 60 | -0.68669 | north | Y | -0.68705 | -0.69026 | -0.64892 | -0.69005 | 0.64892 | west | Y | 0.68705 | 2.288
1675 | PEC_1G | 1 | 75 | 0.000133 | north | N | -0.00022493 | -0.0034388 | 0.037908 | -0.0032249 | 0.00022493 | North | N | 0.00022493 | 0
1676 | PEC_2G | 2 | 79.6 | 0.000133 | north | N | -0.00022493 | -0.0034388 | 0.037908 | -0.0032249 | 0.00022493 | North | N | 0.00022493 | 0
1677 | PEC_3G | 3 | 88.4 | 0.000133 | north | N | -0.00022493 | -0.0034388 | 0.037908 | -0.0032249 | 0.00022493 | North | N | 0.00022493 | 0
1678 | LAMARPWR | 1 | 160 | 0.000104 | north | Y | -0.00025393 | -0.0034678 | 0.037879 | -0.0032539 | 0.00025393 | North | N | 0.00025393 | 0
1679 | LAMARPWR | 2 | 156 | 0.000104 | north | Y | -0.00025393 | -0.0034678 | 0.037879 | -0.0032539 | 0.00025393 | North | N | 0.00025393 | 0
1680 | LAMARPWR | 3 | 196 | 0.000104 | north | Y | -0.00025393 | -0.0034678 | 0.037879 | -0.0032539 | 0.00025393 | North | N | 0.00025393 | 0
1681 | LAMARPWR | 4 | 156 | 0.000104 | north | Y | -0.00025393 | -0.0034678 | 0.037879 | -0.0032539 | 0.00025393 | North | N | 0.00025393 | 0
1682 | LAMARPWR | 5 | 157 | 0.000104 | north | Y | -0.00025393 | -0.0034678 | 0.037879 | -0.0032539 | 0.00025393 | North | N | 0.00025393 | 0
1683 | LAMARPWR | 6 | 198 | 0.000104 | north | Y | -0.00025393 | -0.0034678 | 0.037879 | -0.0032539 | 0.00025393 | North | N | 0.00025393 | 0
1687 | VALLEY_1 | 1 | 170 | -6.6e-05 | north | Y | -0.00042393 | -0.0036378 | 0.037709 | -0.0034239 | 0.00042393 | North | N | 0.00042393 | 0
1688 | VALLEY_2 | 2 | 520 | -6.6e-05 | north | Y | -0.00042393 | -0.0036378 | 0.037709 | -0.0034239 | 0.00042393 | North | N | 0.00042393 | 0
1689 | VALLEY_3 | 3 | 370 | 5.6e-05 | north | Y | -0.00030193 | -0.0035158 | 0.037831 | -0.0033019 | 0.00030193 | North | N | 0.00030193 | 0
1701 | MOSES_1G | 1 | 558 | 0.000193 | north | Y | -0.00016493 | -0.0033788 | 0.037968 | -0.0031649 | 0.00016493 | North | N | 0.00016493 | 0
1702 | MOSES_2G | 2 | 579 | 0.000193 | north | Y | -0.00016493 | -0.0033788 | 0.037968 | -0.0031649 | 0.00016493 | North | N | 0.00016493 | 0
1703 | MOSES_3G | 3 | 808 | 0.000193 | north | Y | -0.00016493 | -0.0033788 | 0.037968 | -0.0031649 | 0.00016493 | North | N | 0.00016493 | 0
1861 | EAGLEMNT | MB | 112 | -0.001362 | north | Y | -0.0017199 | -0.0049338 | 0.036413 | -0.0047199 | 0.0017199 | North | N | 0.0017199 | 0
1862 | EAGLEMNT | MB | 100 | -0.001362 | north | Y | -0.0017199 | -0.0049338 | 0.036413 | -0.0047199 | 0.0017199 | North | N | 0.0017199 | 0
1863 | EAGLEMNT | MB | 378 | -0.001362 | north | Y | -0.0017199 | -0.0049338 | 0.036413 | -0.0047199 | 0.0017199 | North | N | 0.0017199 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.00377 | north | Y | 0.0034121 | 0.00019824 | 0.041545 | 0.00041212 | 0.00019824 | south | Y | 0.0034121 | 0.69837
1878 | WLFHOLW_ | 2 | 205 | 0.00377 | north | Y | 0.0034121 | 0.00019824 | 0.041545 | 0.00041212 | 0.00019824 | south | Y | 0.0034121 | 0.65884
1879 | WLFHOLW_ | 3 | 272.4 | 0.00377 | north | Y | 0.0034121 | 0.00019824 | 0.041545 | 0.00041212 | 0.00019824 | south | Y | 0.0034121 | 0.87545
1889 | DECRDOVA | MB | 770 | 0.004436 | north | Y | 0.0040781 | 0.00086424 | 0.042211 | 0.0010781 | 0.00086424 | south | Y | 0.0040781 | 0
1892 | DECRDOVA | A | 70 | 0.021403 | north | Y | 0.021045 | 0.017831 | 0.059178 | 0.018045 | 0.017831 | south | Y | 0.021045 | 0.22497
1893 | DECRDOVA | B | 69 | 0.021403 | north | Y | 0.021045 | 0.017831 | 0.059178 | 0.018045 | 0.017831 | south | Y | 0.021045 | 0.22175
1894 | DECRDOVA | C | 69 | 0.021403 | north | Y | 0.021045 | 0.017831 | 0.059178 | 0.018045 | 0.017831 | south | Y | 0.021045 | 0.22175
1895 | DECRDOVA | D | 68 | 0.021403 | north | Y | 0.021045 | 0.017831 | 0.059178 | 0.018045 | 0.017831 | south | Y | 0.021045 | 0.21854
1898 | COMCHEPK | 1 | 1157 | 0.004139 | north | N | 0.0037811 | 0.00056724 | 0.041914 | 0.00078112 | 0.00056724 | south | Y | 0.0037811 | 0
1899 | COMCHEPK | 2 | 1158 | 0.004139 | north | N | 0.0037811 | 0.00056724 | 0.041914 | 0.00078112 | 0.00056724 | south | Y | 0.0037811 | 0
1937 | MDLTHELP | 5 | 224 | 0.002891 | north | Y | 0.0025331 | -0.00068076 | 0.040666 | -0.00046688 | 0.00046688 | houston | Y | 0.0025331 | 0.46283
1938 | MDLTHELP | 6 | 226 | 0.002891 | north | Y | 0.0025331 | -0.00068076 | 0.040666 | -0.00046688 | 0.00046688 | houston | Y | 0.0025331 | 0.46696
1941 | MDLTHELP | 1 | 216.4 | 0.002064 | north | Y | 0.0017061 | -0.0015078 | 0.039839 | -0.0012939 | 0.0012939 | houston | Y | 0.0017061 | 0.089198
1942 | MDLTHELP | 2 | 216.1 | 0.002064 | north | Y | 0.0017061 | -0.0015078 | 0.039839 | -0.0012939 | 0.0012939 | houston | Y | 0.0017061 | 0.089074
1943 | MDLTHELP | 3 | 212 | 0.002891 | north | Y | 0.0025331 | -0.00068076 | 0.040666 | -0.00046688 | 0.00046688 | houston | Y | 0.0025331 | 0.43803
1944 | MDLTHELP | 4 | 211 | 0.002891 | north | Y | 0.0025331 | -0.00068076 | 0.040666 | -0.00046688 | 0.00046688 | houston | Y | 0.0025331 | 0.43597
1947 | HANDLEY_ | 3 | 395 | 0.000798 | north | Y | 0.00044007 | -0.0027738 | 0.038573 | -0.0025599 | 0.00044007 | North | N | 0.00044007 | 0
1948 | HANDLEY_ | 4 | 435 | 0.000871 | north | Y | 0.00051307 | -0.0027008 | 0.038646 | -0.0024869 | 0.00051307 | North | N | 0.00051307 | 0
1949 | HANDLEY_ | 5 | 435 | 0.000798 | north | Y | 0.00044007 | -0.0027738 | 0.038573 | -0.0025599 | 0.00044007 | North | N | 0.00044007 | 0
2371 | COLLIN_1 | MB | 138 | -0.000465 | north | Y | -0.00082293 | -0.0040368 | 0.03731 | -0.0038229 | 0.00082293 | North | N | 0.00082293 | 0
2413 | MTCK6_G | 6 | 118 | 0.001218 | north | Y | 0.00086007 | -0.0023538 | 0.038993 | -0.0021399 | 0.00086007 | North | N | 0.00086007 | 0
2414 | MTCK7_G | 7 | 115 | 0.001218 | north | Y | 0.00086007 | -0.0023538 | 0.038993 | -0.0021399 | 0.00086007 | North | N | 0.00086007 | 0
2417 | MTCK8_G | 8 | 556 | 0.001218 | north | Y | 0.00086007 | -0.0023538 | 0.038993 | -0.0021399 | 0.00086007 | North | N | 0.00086007 | 0
2451 | LKHB1_G | 1 | 388 | 0.00077 | north | Y | 0.00041207 | -0.0028018 | 0.038545 | -0.0025879 | 0.00041207 | North | N | 0.00041207 | 0
2452 | LKHB2_G | 2 | 515 | 0.00077 | north | Y | 0.00041207 | -0.0028018 | 0.038545 | -0.0025879 | 0.00041207 | North | N | 0.00041207 | 0
3097 | MARTLAKE | 1 | 785 | 0.001489 | north | Y | 0.0011311 | -0.0020828 | 0.039264 | -0.0018689 | 0.0011311 | North | N | 0.0011311 | 0
3098 | MARTLAKE | 2 | 795 | 0.001489 | north | Y | 0.0011311 | -0.0020828 | 0.039264 | -0.0018689 | 0.0011311 | North | N | 0.0011311 | 0
3099 | MARTLAKE | 3 | 780 | 0.001489 | north | Y | 0.0011311 | -0.0020828 | 0.039264 | -0.0018689 | 0.0011311 | North | N | 0.0011311 | 0
3107 | STRYKER_ | 1 | 182 | 0.001684 | north | Y | 0.0013261 | -0.0018878 | 0.039459 | -0.0016739 | 0.0013261 | North | N | 0.0013261 | 0
3108 | STRYKER_ | 2 | 484 | 0.001684 | north | Y | 0.0013261 | -0.0018878 | 0.039459 | -0.0016739 | 0.0013261 | North | N | 0.0013261 | 0
3126 | TRINIDAD | 1 | 224 | 0.003046 | north | Y | 0.0026881 | -0.00052576 | 0.040821 | -0.00031188 | 0.00031188 | houston | Y | 0.0026881 | 0.53227
3309 | ASPN_G | 1 | 50 | 0.001663 | north | Y | 0.0013051 | -0.0019088 | 0.039438 | -0.0016949 | 0.0013051 | North | N | 0.0013051 | 0
3348 | CHAMPION | MB | 42 | 0.001655 | north | N | 0.0012971 | -0.0019168 | 0.03943 | -0.0017029 | 0.0012971 | North | N | 0.0012971 | 0
3381 | BBRN_1G | 1 | 615 | 0.002502 | north | Y | 0.0021441 | -0.0010698 | 0.040277 | -0.00085588 | 0.00085588 | houston | Y | 0.0021441 | 0.79224
3382 | BBRN_2G | 2 | 587 | 0.002502 | north | Y | 0.0021441 | -0.0010698 | 0.040277 | -0.00085588 | 0.00085588 | houston | Y | 0.0021441 | 0.75617
3403 | THOUSE_1 | MB | 537 | 0.005883 | north | Y | 0.0055251 | 0.0023112 | 0.043658 | 0.0025251 | 0.0023112 | south | Y | 0.0055251 | 0
3404 | THOUSE_2 | 2 | 787 | 0.005883 | north | Y | 0.0055251 | 0.0023112 | 0.043658 | 0.0025251 | 0.0023112 | south | Y | 0.0055251 | 2.5293
3416 | LAKE_CRK | MB | 75 | 0.006314 | north | Y | 0.0059561 | 0.0027422 | 0.044089 | 0.0029561 | 0.0027422 | south | Y | 0.0059561 | 0
3417 | LAKE_CRK | MB | 222 | 0.006314 | north | Y | 0.0059561 | 0.0027422 | 0.044089 | 0.0029561 | 0.0027422 | south | Y | 0.0059561 | 0
3432 | SANDOW_4 | 4 | 569 | 0.004863 | south | Y | 0.0045051 | 0.0012912 | 0.042638 | 0.0015051 | 0.0012912 | south | N | 0.0012912 | 0
5026 | BRAUNIG_ | 1 | 209 | 0.003281 | south | Y | 0.0029231 | -0.00029076 | 0.041056 | -7.688e-05 | 7.688e-05 | houston | Y | 0.00029076 | 0.044701
5027 | BRAUNIG_ | 2 | 216 | 0.003281 | south | Y | 0.0029231 | -0.00029076 | 0.041056 | -7.688e-05 | 7.688e-05 | houston | Y | 0.00029076 | 0.046198
5028 | BRAUNIG_ | 3 | 407 | 0.003258 | south | Y | 0.0029001 | -0.00031376 | 0.041033 | -9.988e-05 | 9.988e-05 | houston | Y | 0.00031376 | 0.08705
5031 | BRA_VHBC | 1 | 46 | 0.003281 | south | Y | 0.0029231 | -0.00029076 | 0.041056 | -7.688e-05 | 7.688e-05 | houston | Y | 0.00029076 | 0.0098386
5032 | BRA_VHBC | 2 | 47 | 0.003281 | south | Y | 0.0029231 | -0.00029076 | 0.041056 | -7.688e-05 | 7.688e-05 | houston | Y | 0.00029076 | 0.010052
5033 | BRA_VHBC | 3 | 46 | 0.003281 | south | Y | 0.0029231 | -0.00029076 | 0.041056 | -7.688e-05 | 7.688e-05 | houston | Y | 0.00029076 | 0.0098386
5034 | BRA_VHBC | 4 | 46 | 0.003281 | south | Y | 0.0029231 | -0.00029076 | 0.041056 | -7.688e-05 | 7.688e-05 | houston | Y | 0.00029076 | 0.0098386
5111 | CALAVER_ | 1 | 424 | 0.003297 | south | Y | 0.0029391 | -0.00027476 | 0.041072 | -6.088e-05 | 6.088e-05 | houston | Y | 0.00027476 | 0.090686
5112 | CALAVER_ | 2 | 425 | 0.003297 | south | Y | 0.0029391 | -0.00027476 | 0.041072 | -6.088e-05 | 6.088e-05 | houston | Y | 0.00027476 | 0.0909
5264 | LEON_LCP | 3 | 58 | 0.00318 | south | Y | 0.0028221 | -0.00039176 | 0.040955 | -0.00017788 | 0.00017788 | houston | Y | 0.00039176 | 0.012405
5265 | LEON_LCP | 4 | 89 | 0.00318 | south | Y | 0.0028221 | -0.00039176 | 0.040955 | -0.00017788 | 0.00017788 | houston | Y | 0.00039176 | 0.019035
5266 | LEON_LCP | 1 | 44 | 0.00318 | south | Y | 0.0028221 | -0.00039176 | 0.040955 | -0.00017788 | 0.00017788 | houston | Y | 0.00039176 | 0.0094108
5267 | LEON_LCP | 2 | 44 | 0.00318 | south | Y | 0.0028221 | -0.00039176 | 0.040955 | -0.00017788 | 0.00017788 | houston | Y | 0.00039176 | 0.0094108
5268 | LEON_LCP | 3 | 43 | 0.00318 | south | Y | 0.0028221 | -0.00039176 | 0.040955 | -0.00017788 | 0.00017788 | houston | Y | 0.00039176 | 0.0091969
5269 | LEON_LCP | 4 | 45 | 0.00318 | south | Y | 0.0028221 | -0.00039176 | 0.040955 | -0.00017788 | 0.00017788 | houston | Y | 0.00039176 | 0.0096247
5396 | CALAVER_ | 1 | 412 | 0.003283 | south | Y | 0.0029251 | -0.00028876 | 0.041058 | -7.488e-05 | 7.488e-05 | houston | Y | 0.00028876 | 0.088119
5397 | CALAVER_ | 2 | 400 | 0.003283 | south | Y | 0.0029251 | -0.00028876 | 0.041058 | -7.488e-05 | 7.488e-05 | houston | Y | 0.00028876 | 0.085553
5401 | CALAVER_ | 1 | 546 | 0.003366 | south | Y | 0.0030081 | -0.00020576 | 0.041141 | 8.1196e-06 | 8.1196e-06 | houston | Y | 0.00020576 | 0.10791
5402 | CALAVER_ | 2 | 750 | 0.003366 | south | Y | 0.0030081 | -0.00020576 | 0.041141 | 8.1196e-06 | 8.1196e-06 | houston | Y | 0.00020576 | 0.14823
5436 | TUTTL_WB | MB | 61 | 0.00335 | south | Y | 0.0029921 | -0.00022176 | 0.041125 | -7.8804e-06 | 7.8804e-06 | houston | Y | 0.00022176 | 0
5438 | TUTTL_WB | MB | 95 | 0.00335 | south | Y | 0.0029921 | -0.00022176 | 0.041125 | -7.8804e-06 | 7.8804e-06 | houston | Y | 0.00022176 | 0
5439 | TUTTL_WB | MB | 151 | 0.00335 | south | Y | 0.0029921 | -0.00022176 | 0.041125 | -7.8804e-06 | 7.8804e-06 | houston | Y | 0.00022176 | 0
5476 | BRA_AVR1 | 1 | 155 | 0.003356 | south | Y | 0.0029981 | -0.00021576 | 0.041131 | -1.8804e-06 | 1.8804e-06 | houston | Y | 0.00021576 | 0.033152
5477 | BRA_AVR1 | 1 | 170 | 0.003356 | south | Y | 0.0029981 | -0.00021576 | 0.041131 | -1.8804e-06 | 1.8804e-06 | houston | Y | 0.00021576 | 0.03636
5478 | BRA_AVR1 | 1 | 155 | 0.003356 | south | Y | 0.0029981 | -0.00021576 | 0.041131 | -1.8804e-06 | 1.8804e-06 | houston | Y | 0.00021576 | 0.033152
5503 | RAYBURNG | 1 | 22 | 0.003242 | south | Y | 0.0028841 | -0.00032976 | 0.041017 | -0.00011588 | 0.00011588 | houston | Y | 0.00032976 | 0.0047054
5505 | RAYBURNG | 1 | 11 | 0.003242 | south | Y | 0.0028841 | -0.00032976 | 0.041017 | -0.00011588 | 0.00011588 | houston | Y | 0.00032976 | 0.0023527
5506 | RAYBURNG | 1 | 11 | 0.003242 | south | Y | 0.0028841 | -0.00032976 | 0.041017 | -0.00011588 | 0.00011588 | houston | Y | 0.00032976 | 0.0023527
5508 | RAYBURNC | 1 | 47.7 | 0.003283 | south | Y | 0.0029251 | -0.00028876 | 0.041058 | -7.488e-05 | 7.488e-05 | houston | Y | 0.00028876 | 0.010202
5509 | RAYBURNC | 1 | 37.3 | 0.003283 | south | Y | 0.0029251 | -0.00028876 | 0.041058 | -7.488e-05 | 7.488e-05 | houston | Y | 0.00028876 | 0.0079778
5511 | RAYBURNC | 1 | 46 | 0.003283 | south | Y | 0.0029251 | -0.00028876 | 0.041058 | -7.488e-05 | 7.488e-05 | houston | Y | 0.00028876 | 0.0098386
5512 | RAYBURNC | 1 | 48 | 0.003283 | south | Y | 0.0029251 | -0.00028876 | 0.041058 | -7.488e-05 | 7.488e-05 | houston | Y | 0.00028876 | 0.010266
5728 | FALCONHY | 2 | 12 | 0.002781 | south | N | 0.0024231 | -0.00079076 | 0.040556 | -0.00057688 | 0.00057688 | houston | Y | 0.00079076 | 0
5729 | FALCONHY | 3 | 11 | 0.002781 | south | N | 0.0024231 | -0.00079076 | 0.040556 | -0.00057688 | 0.00057688 | houston | Y | 0.00079076 | 0
5890 | PEARSALL | 1 | 24 | 0.001627 | south | Y | 0.0012691 | -0.0019448 | 0.039402 | -0.0017309 | 0.0012691 | North | Y | 0.0019448 | 0.016217
5891 | PEARSALL | 1 | 24 | 0.001627 | south | Y | 0.0012691 | -0.0019448 | 0.039402 | -0.0017309 | 0.0012691 | North | Y | 0.0019448 | 0.016217
5892 | PEARSALL | 1 | 23 | 0.001627 | south | Y | 0.0012691 | -0.0019448 | 0.039402 | -0.0017309 | 0.0012691 | North | Y | 0.0019448 | 0.015541
5903 | SANMIGUE | 1 | 396 | 0.003154 | south | Y | 0.0027961 | -0.00041776 | 0.040929 | -0.00020388 | 0.00020388 | houston | Y | 0.00041776 | 0.084697
5911 | STP_GN1_ | 1 | 1333 | 0.003433 | houston | N | 0.0030751 | -0.00013876 | 0.041208 | 7.512e-05 | 7.512e-05 | houston | N | 7.512e-05 | 0
5912 | STP_GN2_ | 2 | 1328 | 0.003433 | houston | N | 0.0030751 | -0.00013876 | 0.041208 | 7.512e-05 | 7.512e-05 | houston | N | 7.512e-05 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | N | 0.00035793 | 0
5932 | SI_RAY9 | 9 | 38 | 0.003148 | south | Y | 0.0027901 | -0.00042376 | 0.040923 | -0.00020988 | 0.00020988 | houston | Y | 0.00042376 | 0.0081275
5933 | SI_RAY6 | 6 | 19.3 | 0.003148 | south | Y | 0.0027901 | -0.00042376 | 0.040923 | -0.00020988 | 0.00020988 | houston | Y | 0.00042376 | 0.0041279
5934 | SI_RAY5 | 5 | 15 | 0.003148 | south | Y | 0.0027901 | -0.00042376 | 0.040923 | -0.00020988 | 0.00020988 | houston | Y | 0.00042376 | 0.0032082
5935 | SI_RAY10 | 10 | 47 | 0.003148 | south | Y | 0.0027901 | -0.00042376 | 0.040923 | -0.00020988 | 0.00020988 | houston | Y | 0.00042376 | 0.010052
6016 | SWMESA | 1 | 75 | -0.035877 | west | Y | -0.036235 | -0.039449 | 0.0018977 | -0.039235 | 0.0018977 | west | N | 0.0018977 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.037775 | 0
6144 | MCADOO1A | 1 | 150 | -0.047213 | west | Y | -0.047571 | -0.050785 | -0.0094383 | -0.050571 | 0.0094383 | west | N | 0.0094383 | 0
6407 | TURKTRAK | 1 | 169.5 | -0.042114 | west | Y | -0.042472 | -0.045686 | -0.0043393 | -0.045472 | 0.0043393 | west | N | 0.0043393 | 0
6476 | LANGFORD | 1 | 150 | -0.02985 | west | Y | -0.030208 | -0.033422 | 0.0079247 | -0.033208 | 0.0079247 | west | N | 0.0079247 | 0
6637 | SNYDERW1 | 1 | 63 | -0.041115 | west | Y | -0.041473 | -0.044687 | -0.0033403 | -0.044473 | 0.0033403 | west | N | 0.0033403 | 0
6752 | OKLA0A | 1 | 649.7 | -0.031852 | west | Y | -0.03221 | -0.035424 | 0.0059227 | -0.03521 | 0.0059227 | west | N | 0.0059227 | 0
6948 | DENISNDM | 1 | 40 | -0.000161 | north | N | -0.00051893 | -0.0037328 | 0.037614 | -0.0035189 | 0.00051893 | North | N | 0.00051893 | 0
6948 | DENISNDM | 2 | 40 | -0.000161 | north | N | -0.00051893 | -0.0037328 | 0.037614 | -0.0035189 | 0.00051893 | North | N | 0.00051893 | 0
7000 | L_FERGUS | 1 | 422 | 0.003759 | south | Y | 0.0034011 | 0.00018724 | 0.041534 | 0.00040112 | 0.00018724 | south | N | 0.00018724 | 0
7004 | L_SIMGID | 1 | 132 | 0.004252 | south | Y | 0.0038941 | 0.00068024 | 0.042027 | 0.00089412 | 0.00068024 | south | N | 0.00068024 | 0
7005 | L_SIMGID | 2 | 134 | 0.004252 | south | Y | 0.0038941 | 0.00068024 | 0.042027 | 0.00089412 | 0.00068024 | south | N | 0.00068024 | 0
7006 | L_SIMGID | 3 | 323 | 0.004252 | south | Y | 0.0038941 | 0.00068024 | 0.042027 | 0.00089412 | 0.00068024 | south | N | 0.00068024 | 0
7007 | L_LOSTPI | 1 | 158 | 0.004228 | south | Y | 0.0038701 | 0.00065624 | 0.042003 | 0.00087012 | 0.00065624 | south | N | 0.00065624 | 0
7008 | L_LOSTPI | 2 | 160 | 0.004228 | south | Y | 0.0038701 | 0.00065624 | 0.042003 | 0.00087012 | 0.00065624 | south | N | 0.00065624 | 0
7009 | L_LOSTPI | 3 | 175 | 0.004228 | south | Y | 0.0038701 | 0.00065624 | 0.042003 | 0.00087012 | 0.00065624 | south | N | 0.00065624 | 0
7010 | L_FPPYD1 | 1 | 584 | 0.00406 | south | Y | 0.0037021 | 0.00048824 | 0.041835 | 0.00070212 | 0.00048824 | south | N | 0.00048824 | 0
7011 | L_FPPYD1 | 2 | 595 | 0.00406 | south | Y | 0.0037021 | 0.00048824 | 0.041835 | 0.00070212 | 0.00048824 | south | N | 0.00048824 | 0
7012 | L_FPPYD2 | 3 | 433 | 0.004058 | south | Y | 0.0037001 | 0.00048624 | 0.041833 | 0.00070012 | 0.00048624 | south | N | 0.00048624 | 0
7014 | L_HAYSEN | 1 | 223.9 | 0.003707 | south | Y | 0.0033491 | 0.00013524 | 0.041482 | 0.00034912 | 0.00013524 | south | N | 0.00013524 | 0
7015 | L_HAYSEN | 2 | 225 | 0.003707 | south | Y | 0.0033491 | 0.00013524 | 0.041482 | 0.00034912 | 0.00013524 | south | N | 0.00013524 | 0
7016 | L_HAYSEN | 3 | 224.6 | 0.003707 | south | Y | 0.0033491 | 0.00013524 | 0.041482 | 0.00034912 | 0.00013524 | south | N | 0.00013524 | 0
7017 | L_HAYSEN | 4 | 226.7 | 0.003707 | south | Y | 0.0033491 | 0.00013524 | 0.041482 | 0.00034912 | 0.00013524 | south | N | 0.00013524 | 0
7020 | L_AUSTPL | 1 | 8 | 0.00433 | south | N | 0.0039721 | 0.00075824 | 0.042105 | 0.00097212 | 0.00075824 | south | N | 0.00075824 | 0
7020 | L_AUSTPL | 2 | 8 | 0.00433 | south | N | 0.0039721 | 0.00075824 | 0.042105 | 0.00097212 | 0.00075824 | south | N | 0.00075824 | 0
7022 | L_BUCHAN | 1 | 18 | 0.004689 | south | N | 0.0043311 | 0.0011172 | 0.042464 | 0.0013311 | 0.0011172 | south | N | 0.0011172 | 0
7023 | L_BUCHAN | 2 | 18 | 0.004689 | south | N | 0.0043311 | 0.0011172 | 0.042464 | 0.0013311 | 0.0011172 | south | N | 0.0011172 | 0
7024 | L_BUCHAN | 3 | 15 | 0.004689 | south | N | 0.0043311 | 0.0011172 | 0.042464 | 0.0013311 | 0.0011172 | south | N | 0.0011172 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.003701 | south | N | 0.0033431 | 0.00012924 | 0.041476 | 0.00034312 | 0.00012924 | south | N | 0.00012924 | 0
7028 | L_MARBFA | 1 | 18 | 0.003911 | south | N | 0.0035531 | 0.00033924 | 0.041686 | 0.00055312 | 0.00033924 | south | N | 0.00033924 | 0
7029 | L_MARBFA | 2 | 18 | 0.003911 | south | N | 0.0035531 | 0.00033924 | 0.041686 | 0.00055312 | 0.00033924 | south | N | 0.00033924 | 0
7031 | L_MARSFO | 1 | 35 | 0.004256 | south | N | 0.0038981 | 0.00068424 | 0.042031 | 0.00089812 | 0.00068424 | south | N | 0.00068424 | 0
7032 | L_MARSFO | 2 | 34 | 0.004256 | south | N | 0.0038981 | 0.00068424 | 0.042031 | 0.00089812 | 0.00068424 | south | N | 0.00068424 | 0
7033 | L_MARSFO | 3 | 35 | 0.004256 | south | N | 0.0038981 | 0.00068424 | 0.042031 | 0.00089812 | 0.00068424 | south | N | 0.00068424 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.003908 | south | N | 0.0035501 | 0.00033624 | 0.041683 | 0.00055012 | 0.00033624 | south | N | 0.00033624 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.003908 | south | N | 0.0035501 | 0.00033624 | 0.041683 | 0.00055012 | 0.00033624 | south | N | 0.00033624 | 0
7038 | L_DELAWA | 1 | 35 | -0.037389 | west | Y | -0.037747 | -0.040961 | 0.00038571 | -0.040747 | 0.00038571 | west | N | 0.00038571 | 0
7038 | L_DELAWA | 2 | 30 | -0.037389 | west | Y | -0.037747 | -0.040961 | 0.00038571 | -0.040747 | 0.00038571 | west | N | 0.00038571 | 0
7303 | L_WPPGS1 | 1 | 50 | 0.004095 | south | Y | 0.0037371 | 0.00052324 | 0.04187 | 0.00073712 | 0.00052324 | south | N | 0.00052324 | 0
7303 | L_WPPGS1 | 2 | 50 | 0.004095 | south | Y | 0.0037371 | 0.00052324 | 0.04187 | 0.00073712 | 0.00052324 | south | N | 0.00052324 | 0
7305 | L_WPPGS3 | 3 | 50 | 0.004095 | south | Y | 0.0037371 | 0.00052324 | 0.04187 | 0.00073712 | 0.00052324 | south | N | 0.00052324 | 0
7305 | L_WPPGS3 | 4 | 50 | 0.004095 | south | Y | 0.0037371 | 0.00052324 | 0.04187 | 0.00073712 | 0.00052324 | south | N | 0.00052324 | 0
7487 | L_CANYHY | 1 | 6 | 0.003753 | south | N | 0.0033951 | 0.00018124 | 0.041528 | 0.00039512 | 0.00018124 | south | N | 0.00018124 | 0
7605 | L_MCQUEE | 1 | 2.4 | 0.003638 | south | N | 0.0032801 | 6.6238e-05 | 0.041413 | 0.00028012 | 6.6238e-05 | south | N | 6.6238e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | 0.003638 | south | N | 0.0032801 | 6.6238e-05 | 0.041413 | 0.00028012 | 6.6238e-05 | south | N | 6.6238e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | 0.003638 | south | N | 0.0032801 | 6.6238e-05 | 0.041413 | 0.00028012 | 6.6238e-05 | south | N | 6.6238e-05 | 0
7609 | L_SCHUMA | 1 | 4 | 0.003551 | south | N | 0.0031931 | -2.0762e-05 | 0.041326 | 0.00019312 | 2.0762e-05 | south | N | 2.0762e-05 | 0
7624 | L_LAKEWO | 1 | 2.4 | 0.003671 | south | N | 0.0033131 | 9.9238e-05 | 0.041446 | 0.00031312 | 9.9238e-05 | south | N | 9.9238e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | 0.003671 | south | N | 0.0033131 | 9.9238e-05 | 0.041446 | 0.00031312 | 9.9238e-05 | south | N | 9.9238e-05 | 0
7800 | L_GUADGE | 1 | 147 | 0.003517 | south | Y | 0.0031591 | -5.4762e-05 | 0.041292 | 0.00015912 | 5.4762e-05 | south | N | 5.4762e-05 | 0
7801 | L_GUADGE | 2 | 138 | 0.003517 | south | Y | 0.0031591 | -5.4762e-05 | 0.041292 | 0.00015912 | 5.4762e-05 | south | N | 5.4762e-05 | 0
7802 | L_GUADGE | 3 | 140 | 0.003517 | south | Y | 0.0031591 | -5.4762e-05 | 0.041292 | 0.00015912 | 5.4762e-05 | south | N | 5.4762e-05 | 0
7803 | L_GUADGE | 4 | 147 | 0.003517 | south | Y | 0.0031591 | -5.4762e-05 | 0.041292 | 0.00015912 | 5.4762e-05 | south | N | 5.4762e-05 | 0
7804 | L_GUADGE | 5 | 182 | 0.003517 | south | Y | 0.0031591 | -5.4762e-05 | 0.041292 | 0.00015912 | 5.4762e-05 | south | N | 5.4762e-05 | 0
7805 | L_GUADGE | 6 | 198 | 0.003517 | south | Y | 0.0031591 | -5.4762e-05 | 0.041292 | 0.00015912 | 5.4762e-05 | south | N | 5.4762e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | 0.004204 | south | Y | 0.0038461 | 0.00063224 | 0.041979 | 0.00084612 | 0.00063224 | south | N | 0.00063224 | 0
7808 | L_BASTEN | 1 | 149.5 | 0.004204 | south | Y | 0.0038461 | 0.00063224 | 0.041979 | 0.00084612 | 0.00063224 | south | N | 0.00063224 | 0
7809 | L_BASTEN | 1 | 232.6 | 0.004204 | south | Y | 0.0038461 | 0.00063224 | 0.041979 | 0.00084612 | 0.00063224 | south | N | 0.00063224 | 0
7810 | L_RIONOG | 1 | 142 | 0.003612 | south | Y | 0.0032541 | 4.0238e-05 | 0.041387 | 0.00025412 | 4.0238e-05 | south | N | 4.0238e-05 | 0
7811 | L_RIONOG | 2 | 145 | 0.003612 | south | Y | 0.0032541 | 4.0238e-05 | 0.041387 | 0.00025412 | 4.0238e-05 | south | N | 4.0238e-05 | 0
7812 | L_RIONOG | 3 | 151 | 0.003612 | south | Y | 0.0032541 | 4.0238e-05 | 0.041387 | 0.00025412 | 4.0238e-05 | south | N | 4.0238e-05 | 0
7813 | L_RIONOG | 4 | 290 | 0.003612 | south | Y | 0.0032541 | 4.0238e-05 | 0.041387 | 0.00025412 | 4.0238e-05 | south | N | 4.0238e-05 | 0
8032 | AMISTADH | 1 | 33 | -0.008922 | south | N | -0.0092799 | -0.012494 | 0.028853 | -0.01228 | 0.0092799 | North | Y | 0.012494 | 0
8033 | AMISTADH | 2 | 25 | -0.008922 | south | N | -0.0092799 | -0.012494 | 0.028853 | -0.01228 | 0.0092799 | North | Y | 0.012494 | 0
8048 | FALCONHY | 1 | 12 | 0.002781 | south | N | 0.0024231 | -0.00079076 | 0.040556 | -0.00057688 | 0.00057688 | houston | Y | 0.00079076 | 0
8066 | DUP1V#1 | 1 | 73 | 0.003313 | south | N | 0.0029551 | -0.00025876 | 0.041088 | -4.488e-05 | 4.488e-05 | houston | Y | 0.00025876 | 0
8134 | FOR69CG0 | 1 | 79 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
8138 | FOR69CG0 | 2 | 81 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8147 | UCAR #2 | 10 | 28 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
8148 | UCAR #1 | 2 | 7 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
8153 | FOR69CG0 | 3 | 79 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
8154 | FOR69CG0 | 4 | 80 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
8155 | FOR69CG0 | 5 | 78.4 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
8156 | FOR69CG0 | 6 | 25 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
8157 | FOR69CG0 | 7 | 46 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
8161 | COLETOU1 | 1 | 629 | 0.003251 | south | Y | 0.0028931 | -0.00032076 | 0.041026 | -0.00010688 | 0.00010688 | houston | Y | 0.00032076 | 0.13453
8173 | VICEC51A | 5 | 144 | 0.003313 | south | Y | 0.0029551 | -0.00025876 | 0.041088 | -4.488e-05 | 4.488e-05 | houston | Y | 0.00025876 | 0.030799
8174 | VICEC61A | 6 | 188 | 0.003313 | south | Y | 0.0029551 | -0.00025876 | 0.041088 | -4.488e-05 | 4.488e-05 | houston | Y | 0.00025876 | 0.04021
8189 | CUERO 2 | 1 | 12 | 0.003562 | south | N | 0.0032041 | -9.7621e-06 | 0.041337 | 0.00020412 | 9.7621e-06 | south | N | 9.7621e-06 | 0
8262 | ELPS | 1 | 6 | -0.005575 | south | N | -0.0059329 | -0.0091468 | 0.0322 | -0.0089329 | 0.0059329 | North | Y | 0.0091468 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8442 | NBEC71A | 1 | 336 | 0.003188 | south | Y | 0.0028301 | -0.00038376 | 0.040963 | -0.00016988 | 0.00016988 | houston | Y | 0.00038376 | 0.071864
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.00035793 | -0.0035718 | 0.037775 | -0.0033579 | 0.00035793 | North | Y | 0.0035718 | 0
8459 | B_DAVIS1 | 1 | 334 | 0.003186 | south | Y | 0.0028281 | -0.00038576 | 0.040961 | -0.00017188 | 0.00017188 | houston | Y | 0.00038576 | 0.071436
8460 | B_DAVIS2 | 2 | 340 | 0.003186 | south | Y | 0.0028281 | -0.00038576 | 0.040961 | -0.00017188 | 0.00017188 | houston | Y | 0.00038576 | 0.07272
8461 | KOCH_UP0 | 1 | 38 | 0.00318 | south | N | 0.0028221 | -0.00039176 | 0.040955 | -0.00017788 | 0.00017788 | houston | Y | 0.00039176 | 0
8506 | VAL #1 | 1 | 25 | 0.003183 | south | N | 0.0028251 | -0.00038876 | 0.040958 | -0.00017488 | 0.00017488 | houston | Y | 0.00038876 | 0
8507 | VAL #2 | 2 | 25 | 0.003183 | south | N | 0.0028251 | -0.00038876 | 0.040958 | -0.00017488 | 0.00017488 | houston | Y | 0.00038876 | 0
8511 | OXY_CC0A | 1 | 38 | 0.003184 | south | N | 0.0028261 | -0.00038776 | 0.040959 | -0.00017388 | 0.00017388 | houston | Y | 0.00038776 | 0
8517 | CELANEBI | 1 | 29 | 0.003171 | south | N | 0.0028131 | -0.00040076 | 0.040946 | -0.00018688 | 0.00018688 | houston | Y | 0.00040076 | 0
8560 | CNOPGT1 | 1 | 148.3 | 0.003188 | south | N | 0.0028301 | -0.00038376 | 0.040963 | -0.00016988 | 0.00016988 | houston | Y | 0.00038376 | 0
8561 | CNOPGT2 | 2 | 148.6 | 0.003188 | south | N | 0.0028301 | -0.00038376 | 0.040963 | -0.00016988 | 0.00016988 | houston | Y | 0.00038376 | 0
8562 | CNOPST1 | 3 | 153 | 0.003188 | south | N | 0.0028301 | -0.00038376 | 0.040963 | -0.00016988 | 0.00016988 | houston | Y | 0.00038376 | 0
8926 | LGE_GT10 | 1 | 158 | 0.003204 | south | N | 0.0028461 | -0.00036776 | 0.040979 | -0.00015388 | 0.00015388 | houston | Y | 0.00036776 | 0
8927 | LGE_GT20 | 2 | 153 | 0.003204 | south | N | 0.0028461 | -0.00036776 | 0.040979 | -0.00015388 | 0.00015388 | houston | Y | 0.00036776 | 0
8928 | LGE_STG0 | 3 | 100 | 0.003204 | south | N | 0.0028461 | -0.00036776 | 0.040979 | -0.00015388 | 0.00015388 | houston | Y | 0.00036776 | 0
8930 | ICPGN10A | 1 | 145 | 0.003204 | south | N | 0.0028461 | -0.00036776 | 0.040979 | -0.00015388 | 0.00015388 | houston | Y | 0.00036776 | 0
8931 | ICPGN20A | 2 | 147 | 0.003204 | south | N | 0.0028461 | -0.00036776 | 0.040979 | -0.00015388 | 0.00015388 | houston | Y | 0.00036776 | 0
8932 | ICPGN30A | 3 | 127 | 0.003204 | south | N | 0.0028461 | -0.00036776 | 0.040979 | -0.00015388 | 0.00015388 | houston | Y | 0.00036776 | 0
8933 | FGNTS001 | 1 | 146.5 | 0.003071 | south | Y | 0.0027131 | -0.00050076 | 0.040846 | -0.00028688 | 0.00028688 | houston | Y | 0.00050076 | 0.031334
8934 | FGNTS101 | 2 | 147.9 | 0.003071 | south | Y | 0.0027131 | -0.00050076 | 0.040846 | -0.00028688 | 0.00028688 | houston | Y | 0.00050076 | 0.031633
8935 | FGNTS201 | 3 | 173 | 0.003071 | south | Y | 0.0027131 | -0.00050076 | 0.040846 | -0.00028688 | 0.00028688 | houston | Y | 0.00050076 | 0.037002
8936 | MVGN#1 | 1 | 207 | 0.00312 | south | Y | 0.0027621 | -0.00045176 | 0.040895 | -0.00023788 | 0.00023788 | houston | Y | 0.00045176 | 0.044273
8937 | MVGN#2 | 2 | 216.7 | 0.00312 | south | Y | 0.0027621 | -0.00045176 | 0.040895 | -0.00023788 | 0.00023788 | houston | Y | 0.00045176 | 0.046348
8938 | MVGN#3 | 3 | 242 | 0.00312 | south | Y | 0.0027621 | -0.00045176 | 0.040895 | -0.00023788 | 0.00023788 | houston | Y | 0.00045176 | 0.051759
8981 | HECN1 | 1 | 144 | 0.00312 | south | Y | 0.0027621 | -0.00045176 | 0.040895 | -0.00023788 | 0.00023788 | houston | Y | 0.00045176 | 0.030799
8982 | HECN2 | 2 | 144 | 0.00312 | south | Y | 0.0027621 | -0.00045176 | 0.040895 | -0.00023788 | 0.00023788 | houston | Y | 0.00045176 | 0.030799
8983 | HECN3 | 3 | 171 | 0.00312 | south | Y | 0.0027621 | -0.00045176 | 0.040895 | -0.00023788 | 0.00023788 | houston | Y | 0.00045176 | 0.036574
9000 | DECKR_G1 | 1 | 310 | 0.004338 | south | Y | 0.0039801 | 0.00076624 | 0.042113 | 0.00098012 | 0.00076624 | south | N | 0.00076624 | 0
9001 | DECKR_G2 | 2 | 413 | 0.004338 | south | Y | 0.0039801 | 0.00076624 | 0.042113 | 0.00098012 | 0.00076624 | south | N | 0.00076624 | 0
9002 | DECKR_G3 | 3 | 42 | 0.004371 | south | Y | 0.0040131 | 0.00079924 | 0.042146 | 0.0010131 | 0.00079924 | south | N | 0.00079924 | 0
9003 | DECKR_G4 | 4 | 44 | 0.004371 | south | Y | 0.0040131 | 0.00079924 | 0.042146 | 0.0010131 | 0.00079924 | south | N | 0.00079924 | 0
9004 | DECKR_G5 | 5 | 44 | 0.004371 | south | Y | 0.0040131 | 0.00079924 | 0.042146 | 0.0010131 | 0.00079924 | south | N | 0.00079924 | 0
9005 | DECKR_G6 | 6 | 47 | 0.004371 | south | Y | 0.0040131 | 0.00079924 | 0.042146 | 0.0010131 | 0.00079924 | south | N | 0.00079924 | 0
9016 | SANDH_G1 | 1 | 49 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
9017 | SANDH_G2 | 2 | 46 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
9018 | SANDH_G3 | 3 | 46 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
9019 | SANDH_G4 | 4 | 47 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
9020 | SANDHG5A | 5A | 154 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
9021 | SANDHG5C | 5C | 148 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
9022 | SANDH_G6 | 6 | 48 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
9023 | SANDH_G7 | 7 | 48 | 0.004296 | south | Y | 0.0039381 | 0.00072424 | 0.042071 | 0.00093812 | 0.00072424 | south | N | 0.00072424 | 0
11001 | NAV1CT | 1 | 70 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11009 | NAV2CT | 1 | 70 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11011 | NAV3ST | 1 | 92.8 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11012 | NAV4CT | 1 | 80 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11013 | NAV5CT | 1 | 80 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11014 | NAV6ST | 1 | 115 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11020 | TIEHVSG_ | 1 | 208.2 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11021 | TIEHVCG_ | 1 | 142.1 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11022 | TIEHVCG_ | 1 | 132.4 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11023 | TIEHVCG_ | 1 | 136 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11024 | TIEHVCG_ | 1 | 147 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11025 | TIEHVSG_ | 1 | 210 | -0.037282 | west | Y | -0.03764 | -0.040854 | 0.00049271 | -0.04064 | 0.00049271 | west | N | 0.00049271 | 0
11056 | ROSCOE_1 | 1 | 209 | -0.035539 | west | Y | -0.035897 | -0.039111 | 0.0022357 | -0.038897 | 0.0022357 | west | N | 0.0022357 | 0
11057 | CHAMPION | 1 | 126.5 | -0.035539 | west | Y | -0.035897 | -0.039111 | 0.0022357 | -0.038897 | 0.0022357 | west | N | 0.0022357 | 0
11058 | PYRON_1G | 1 | 249 | -0.035539 | west | Y | -0.035897 | -0.039111 | 0.0022357 | -0.038897 | 0.0022357 | west | N | 0.0022357 | 0
11059 | INADALE_ | 1 | 197 | -0.035539 | west | Y | -0.035897 | -0.039111 | 0.0022357 | -0.038897 | 0.0022357 | west | N | 0.0022357 | 0
11061 | PNTHRCK1 | 1 | 200 | -0.037259 | west | Y | -0.037617 | -0.040831 | 0.00051571 | -0.040617 | 0.00051571 | west | N | 0.00051571 | 0
11065 | ELBOWCK_ | 1 | 121.9 | -0.037259 | west | Y | -0.037617 | -0.040831 | 0.00051571 | -0.040617 | 0.00051571 | west | N | 0.00051571 | 0
11147 | NOTREES_ | 1 | 149 | -0.03764 | west | Y | -0.037998 | -0.041212 | 0.00013471 | -0.040998 | 0.00013471 | west | N | 0.00013471 | 0
11309 | BULLCREK | 1 | 180 | -0.04024 | west | Y | -0.040598 | -0.043812 | -0.0024653 | -0.043598 | 0.0024653 | west | N | 0.0024653 | 0
11310 | BULLCREK | 1 | 180 | -0.04024 | west | Y | -0.040598 | -0.043812 | -0.0024653 | -0.043598 | 0.0024653 | west | N | 0.0024653 | 0
11320 | COYOTE_1 | 1 | 225 | -0.040141 | west | Y | -0.040499 | -0.043713 | -0.0023663 | -0.043499 | 0.0023663 | west | N | 0.0023663 | 0
11415 | LORAINE_ | 1 | 125 | -0.036772 | west | Y | -0.03713 | -0.040344 | 0.0010027 | -0.04013 | 0.0010027 | west | N | 0.0010027 | 0
11416 | LORAINE_ | 1 | 125 | -0.036772 | west | Y | -0.03713 | -0.040344 | 0.0010027 | -0.04013 | 0.0010027 | west | N | 0.0010027 | 0
11691 | KMICHICT | 1 | 140 | 5.6e-05 | north | N | -0.00030193 | -0.0035158 | 0.037831 | -0.0033019 | 0.00030193 | North | N | 0.00030193 | 0
11692 | KMICHICT | 2 | 141 | 5.6e-05 | north | N | -0.00030193 | -0.0035158 | 0.037831 | -0.0033019 | 0.00030193 | North | N | 0.00030193 | 0
11693 | KMICHIST | 3 | 309 | 5.6e-05 | north | N | -0.00030193 | -0.0035158 | 0.037831 | -0.0033019 | 0.00030193 | North | N | 0.00030193 | 0
11694 | KMICHICT | 4 | 143 | 5.6e-05 | north | N | -0.00030193 | -0.0035158 | 0.037831 | -0.0033019 | 0.00030193 | North | N | 0.00030193 | 0
11695 | KMICHICT | 5 | 144 | 5.6e-05 | north | N | -0.00030193 | -0.0035158 | 0.037831 | -0.0033019 | 0.00030193 | North | N | 0.00030193 | 0
11696 | KMICHIST | 6 | 310 | 5.6e-05 | north | N | -0.00030193 | -0.0035158 | 0.037831 | -0.0033019 | 0.00030193 | North | N | 0.00030193 | 0
12322 | ENNSTRAC | 1 | 196 | 0.0033 | north | Y | 0.0029421 | -0.00027176 | 0.041075 | -5.788e-05 | 5.788e-05 | houston | Y | 0.0029421 | 0.5653
12323 | ENNSTRAC | 2 | 111 | 0.0033 | north | Y | 0.0029421 | -0.00027176 | 0.041075 | -5.788e-05 | 5.788e-05 | houston | Y | 0.0029421 | 0.32015
12357 | RNRTPL_1 | 1 | 0 | -8.5e-05 | north | N | -0.00044293 | -0.0036568 | 0.03769 | -0.0034429 | 0.00044293 | North | N | 0.00044293 | 0
12411 | FPLEFR1A | 1 | 161 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12412 | FPLEFR1B | 2 | 164 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12413 | FPLEFR1C | 3 | 164 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12414 | FPLEFR1S | 4 | 414 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12421 | FPLEFR2A | 1 | 162 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12422 | FPLEFR2B | 2 | 161 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12423 | FPLEFR2C | 3 | 163 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12424 | FPLEFR2S | 4 | 409 | 0.000791 | north | Y | 0.00043307 | -0.0027808 | 0.038566 | -0.0025669 | 0.00043307 | North | N | 0.00043307 | 0
12440 | PARKD_1S | 1 | 0 | 0.000872 | north | N | 0.00051407 | -0.0026998 | 0.038647 | -0.0024859 | 0.00051407 | North | N | 0.00051407 | 0
12449 | PARKD_2S | 1 | 0 | 0.000872 | north | N | 0.00051407 | -0.0026998 | 0.038647 | -0.0024859 | 0.00051407 | North | N | 0.00051407 | 0
13116 | TGATEWAY | 1 | 148 | 0.001582 | north | N | 0.0012241 | -0.0019898 | 0.039357 | -0.0017759 | 0.0012241 | North | N | 0.0012241 | 0
13117 | TGATEWAY | 2 | 130 | 0.001582 | north | N | 0.0012241 | -0.0019898 | 0.039357 | -0.0017759 | 0.0012241 | North | N | 0.0012241 | 0
13118 | TGATEWAY | 3 | 145 | 0.001582 | north | N | 0.0012241 | -0.0019898 | 0.039357 | -0.0017759 | 0.0012241 | North | N | 0.0012241 | 0
13119 | TGATEWAY | 4 | 399 | 0.001582 | north | N | 0.0012241 | -0.0019898 | 0.039357 | -0.0017759 | 0.0012241 | North | N | 0.0012241 | 0
13131 | CALFREST | 1 | 150.7 | 0.002374 | north | Y | 0.0020161 | -0.0011978 | 0.040149 | -0.00098388 | 0.00098388 | houston | Y | 0.0020161 | 0.15555
13132 | CALFREST | 2 | 151 | 0.002374 | north | Y | 0.0020161 | -0.0011978 | 0.040149 | -0.00098388 | 0.00098388 | houston | Y | 0.0020161 | 0.15586
13133 | CALFREST | 3 | 177.4 | 0.002374 | north | Y | 0.0020161 | -0.0011978 | 0.040149 | -0.00098388 | 0.00098388 | houston | Y | 0.0020161 | 0.18311
13134 | CALFREST | 4 | 151.5 | 0.002357 | north | Y | 0.0019991 | -0.0012148 | 0.040132 | -0.0010009 | 0.0010009 | houston | Y | 0.0019991 | 0.15123
13135 | CALFREST | 5 | 152.3 | 0.002357 | north | Y | 0.0019991 | -0.0012148 | 0.040132 | -0.0010009 | 0.0010009 | houston | Y | 0.0019991 | 0.15202
13136 | CALFREST | 6 | 177.5 | 0.002357 | north | Y | 0.0019991 | -0.0012148 | 0.040132 | -0.0010009 | 0.0010009 | houston | Y | 0.0019991 | 0.17718
13432 | SANDOW_5 | 5 | 581 | 0.004863 | south | Y | 0.0045051 | 0.0012912 | 0.042638 | 0.0015051 | 0.0012912 | south | N | 0.0012912 | 0
13691 | OAKGROVE | 1 | 855 | 0.003 | north | Y | 0.0026421 | -0.00057176 | 0.040775 | -0.00035788 | 0.00035788 | houston | Y | 0.0026421 | 1.953
13692 | OAKGROVE | 2 | 855 | 0.003 | north | Y | 0.0026421 | -0.00057176 | 0.040775 | -0.00035788 | 0.00035788 | houston | Y | 0.0026421 | 1.953
32798 | BRYN_TAM | 1 | 32 | 0.003269 | north | N | 0.0029111 | -0.00030276 | 0.041044 | -8.888e-05 | 8.888e-05 | houston | Y | 0.0029111 | 0
32883 | BRYN_DNS | 1 | 48 | 0.00331 | north | Y | 0.0029521 | -0.00026176 | 0.041085 | -4.788e-05 | 4.788e-05 | houston | Y | 0.0029521 | 0.1394
32884 | BRYN_DNS | 1 | 46 | 0.00331 | north | Y | 0.0029521 | -0.00026176 | 0.041085 | -4.788e-05 | 4.788e-05 | houston | Y | 0.0029521 | 0.13359
32886 | BRYN_ATK | MB | 12 | 0.00327 | north | Y | 0.0029121 | -0.00030176 | 0.041045 | -8.788e-05 | 8.788e-05 | houston | Y | 0.0029121 | 0
32887 | BRYN_ATK | MB | 51 | 0.00327 | north | Y | 0.0029121 | -0.00030176 | 0.041045 | -8.788e-05 | 8.788e-05 | houston | Y | 0.0029121 | 0
32888 | BRYN_ATK | 1 | 17 | 0.00327 | north | Y | 0.0029121 | -0.00030176 | 0.041045 | -8.788e-05 | 8.788e-05 | houston | Y | 0.0029121 | 0.048011
32890 | BRYN_ATK | MB | 22 | 0.00327 | north | Y | 0.0029121 | -0.00030176 | 0.041045 | -8.788e-05 | 8.788e-05 | houston | Y | 0.0029121 | 0
32891 | BRYN_ATK | MB | 25 | 0.00327 | north | Y | 0.0029121 | -0.00030176 | 0.041045 | -8.788e-05 | 8.788e-05 | houston | Y | 0.0029121 | 0
32892 | BRYN_DNS | 1 | 105 | 0.00331 | north | Y | 0.0029521 | -0.00026176 | 0.041085 | -4.788e-05 | 4.788e-05 | houston | Y | 0.0029521 | 0.30494
36998 | RDCNYNG1 | 1 | 84 | -0.042405 | west | Y | -0.042763 | -0.045977 | -0.0046303 | -0.045763 | 0.0046303 | west | N | 0.0046303 | 0
38332 | WDWRDU2 | 1 | 80 | -0.035849 | west | Y | -0.036207 | -0.039421 | 0.0019257 | -0.039207 | 0.0019257 | west | N | 0.0019257 | 0
38437 | TNSRBNMS | 1 | 150 | -0.035836 | west | Y | -0.036194 | -0.039408 | 0.0019387 | -0.039194 | 0.0019387 | west | N | 0.0019387 | 0
38438 | TNSRBNMS | 1 | 150 | -0.035836 | west | Y | -0.036194 | -0.039408 | 0.0019387 | -0.039194 | 0.0019387 | west | N | 0.0019387 | 0
38580 | TNBP_CGN | 1 | 70.8 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38590 | TNBP_CGN | 2 | 66.7 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38600 | TNBP_CGN | 5 | 53 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38611 | TNBPAMCG | 1 | 153.2 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38612 | TNBPAMCG | 2 | 153.5 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38613 | TNBPAMCG | 3 | 152.3 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38614 | TNBPAMCG | 4 | 96 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38615 | TNBPAMCG | 1 | 244 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38690 | TNBP_CGN | 3 | 40 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38711 | TNTXCTY1 | 1 | 100.3 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38712 | TNTXCTY2 | 1 | 92.9 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38713 | TNTXCTY3 | 1 | 102.7 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
38714 | TNTXCTY4 | 1 | 102 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
39470 | TNDOWCGN | 1 | 32 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
39480 | TNDOWCGN | 1 | 30 | 0.00336 | houston | N | 0.0030021 | -0.00021176 | 0.041135 | 2.1196e-06 | 2.1196e-06 | houston | N | 2.1196e-06 | 0
39760 | TNSCLP1_ | 1 | 111 | 0.003393 | houston | N | 0.0030351 | -0.00017876 | 0.041168 | 3.512e-05 | 3.512e-05 | houston | N | 3.512e-05 | 0
39770 | TNSCLP2_ | 1 | 111 | 0.003393 | houston | N | 0.0030351 | -0.00017876 | 0.041168 | 3.512e-05 | 3.512e-05 | houston | N | 3.512e-05 | 0
39775 | TNSCLP4_ | 1 | 119 | 0.003393 | houston | N | 0.0030351 | -0.00017876 | 0.041168 | 3.512e-05 | 3.512e-05 | houston | N | 3.512e-05 | 0
39790 | TNSCLP3_ | 1 | 109.5 | 0.003393 | houston | N | 0.0030351 | -0.00017876 | 0.041168 | 3.512e-05 | 3.512e-05 | houston | N | 3.512e-05 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.003 | north | Y | 0.0026421 | -0.00057176 | 0.040775 | -0.00035788 | 0.00035788 | houston | Y | 0.0026421 | 0.34788
39970 | TNTNPONE | 1 | 153 | 0.003 | north | Y | 0.0026421 | -0.00057176 | 0.040775 | -0.00035788 | 0.00035788 | houston | Y | 0.0026421 | 0.34948
48500 | APD_GT1_ | 1 | 136 | 0.003339 | houston | N | 0.0029811 | -0.00023276 | 0.041114 | -1.888e-05 | 1.888e-05 | houston | N | 1.888e-05 | 0
48510 | AK_GT1__ | 1 | 33 | 0.003371 | houston | N | 0.0030131 | -0.00020076 | 0.041146 | 1.312e-05 | 1.312e-05 | houston | N | 1.312e-05 | 0
48511 | LPE_GT1_ | 1 | 42 | 0.003338 | houston | Y | 0.0029801 | -0.00023376 | 0.041113 | -1.988e-05 | 1.988e-05 | houston | N | 1.988e-05 | 0
48512 | LPE_GT2_ | 2 | 42 | 0.003338 | houston | Y | 0.0029801 | -0.00023376 | 0.041113 | -1.988e-05 | 1.988e-05 | houston | N | 1.988e-05 | 0
48513 | LPE_GT3_ | 3 | 38 | 0.003338 | houston | Y | 0.0029801 | -0.00023376 | 0.041113 | -1.988e-05 | 1.988e-05 | houston | N | 1.988e-05 | 0
48514 | LPE_GT4_ | 4 | 38 | 0.003338 | houston | Y | 0.0029801 | -0.00023376 | 0.041113 | -1.988e-05 | 1.988e-05 | houston | N | 1.988e-05 | 0
48520 | BSF_GT1_ | 1 | 71 | 0.003396 | houston | N | 0.0030381 | -0.00017576 | 0.041171 | 3.812e-05 | 3.812e-05 | houston | N | 3.812e-05 | 0
48520 | BSF_GT1_ | 2 | 10 | 0.003396 | houston | N | 0.0030381 | -0.00017576 | 0.041171 | 3.812e-05 | 3.812e-05 | houston | N | 3.812e-05 | 0
48521 | BVE_GT1_ | 1 | 163 | 0.003378 | houston | N | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48522 | BVE_GT2_ | 2 | 163 | 0.003378 | houston | N | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48523 | BVE_ST1_ | 3 | 245 | 0.003378 | houston | N | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48531 | BYU_GT1_ | 1 | 65 | 0.003346 | houston | N | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48532 | BYU_GT2_ | 2 | 60 | 0.003346 | houston | N | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48533 | BYU_GT3_ | 3 | 65 | 0.003346 | houston | N | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48534 | BYU_GT4_ | 4 | 65 | 0.003346 | houston | N | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48551 | CAL_GT1_ | 1 | 149 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48552 | CAL_ST1_ | 2 | 65.1 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48561 | CTL_GT2_ | 1 | 91 | 0.003348 | houston | N | 0.0029901 | -0.00022376 | 0.041123 | -9.8804e-06 | 9.8804e-06 | houston | N | 9.8804e-06 | 0
48562 | CTL_GT3_ | 2 | 87.6 | 0.003348 | houston | N | 0.0029901 | -0.00022376 | 0.041123 | -9.8804e-06 | 9.8804e-06 | houston | N | 9.8804e-06 | 0
48563 | CTL_GT4_ | 3 | 87 | 0.003348 | houston | N | 0.0029901 | -0.00022376 | 0.041123 | -9.8804e-06 | 9.8804e-06 | houston | N | 9.8804e-06 | 0
48564 | CTL_GN1_ | 4 | 54.5 | 0.003348 | houston | N | 0.0029901 | -0.00022376 | 0.041123 | -9.8804e-06 | 9.8804e-06 | houston | N | 9.8804e-06 | 0
48565 | CTL_GN2_ | 5 | 12.2 | 0.003348 | houston | N | 0.0029901 | -0.00022376 | 0.041123 | -9.8804e-06 | 9.8804e-06 | houston | N | 9.8804e-06 | 0
48581 | CBY_GN1_ | 1 | 743 | 0.003331 | houston | Y | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48582 | CBY_GN2_ | 2 | 735 | 0.003334 | houston | Y | 0.0029761 | -0.00023776 | 0.041109 | -2.388e-05 | 2.388e-05 | houston | N | 2.388e-05 | 0
48583 | CBY_GT4_ | 1 | 172 | 0.00333 | houston | Y | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | N | 2.788e-05 | 0
48584 | CBY_GT4_ | 2 | 172 | 0.00333 | houston | Y | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | N | 2.788e-05 | 0
48585 | CBY_ST4_ | 3 | 172 | 0.00333 | houston | Y | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | N | 2.788e-05 | 0
48591 | CHE_GT2_ | 2 | 173 | 0.003314 | houston | N | 0.0029561 | -0.00025776 | 0.041089 | -4.388e-05 | 4.388e-05 | houston | N | 4.388e-05 | 0
48593 | CHE_GT1_ | 1 | 173 | 0.003338 | houston | N | 0.0029801 | -0.00023376 | 0.041113 | -1.988e-05 | 1.988e-05 | houston | N | 1.988e-05 | 0
48594 | CHE_GN4_ | 4 | 135 | 0.003338 | houston | N | 0.0029801 | -0.00023376 | 0.041113 | -1.988e-05 | 1.988e-05 | houston | N | 1.988e-05 | 0
48595 | BTE_GT2_ | 1 | 162.8 | 0.003328 | houston | N | 0.0029701 | -0.00024376 | 0.041103 | -2.988e-05 | 2.988e-05 | houston | N | 2.988e-05 | 0
48596 | BTE_GT3_ | 2 | 161.4 | 0.003328 | houston | N | 0.0029701 | -0.00024376 | 0.041103 | -2.988e-05 | 2.988e-05 | houston | N | 2.988e-05 | 0
48597 | BTE_GT4_ | 3 | 158.9 | 0.003328 | houston | N | 0.0029701 | -0.00024376 | 0.041103 | -2.988e-05 | 2.988e-05 | houston | N | 2.988e-05 | 0
48598 | BTE_ST1_ | 4 | 269.2 | 0.003328 | houston | N | 0.0029701 | -0.00024376 | 0.041103 | -2.988e-05 | 2.988e-05 | houston | N | 2.988e-05 | 0
48611 | DIB_GT1_ | 1 | 64 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48612 | DIB_GT2_ | 2 | 63.2 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48613 | DIB_ST1_ | 3 | 82.6 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48614 | DIB_GT3_ | 4 | 73.6 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48641 | DPEC_GT1 | 1 | 163.2 | 0.003342 | houston | N | 0.0029841 | -0.00022976 | 0.041117 | -1.588e-05 | 1.588e-05 | houston | N | 1.588e-05 | 0
48642 | DPEC_GT2 | 2 | 157.1 | 0.003342 | houston | N | 0.0029841 | -0.00022976 | 0.041117 | -1.588e-05 | 1.588e-05 | houston | N | 1.588e-05 | 0
48643 | DPEC_GT3 | 3 | 157.5 | 0.003342 | houston | N | 0.0029841 | -0.00022976 | 0.041117 | -1.588e-05 | 1.588e-05 | houston | N | 1.588e-05 | 0
48644 | DPEC_GT4 | 4 | 157 | 0.003342 | houston | N | 0.0029841 | -0.00022976 | 0.041117 | -1.588e-05 | 1.588e-05 | houston | N | 1.588e-05 | 0
48645 | DPEC_ST5 | 5 | 269 | 0.003342 | houston | N | 0.0029841 | -0.00022976 | 0.041117 | -1.588e-05 | 1.588e-05 | houston | N | 1.588e-05 | 0
48651 | EP_1_2 | 1 | 5 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48651 | EP_1_2 | 2 | 21 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.003189 | north | N | 0.0028311 | -0.00038276 | 0.040964 | -0.00016888 | 0.00016888 | houston | Y | 0.0028311 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.003189 | north | N | 0.0028311 | -0.00038276 | 0.040964 | -0.00016888 | 0.00016888 | houston | Y | 0.0028311 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.003189 | north | N | 0.0028311 | -0.00038276 | 0.040964 | -0.00016888 | 0.00016888 | houston | Y | 0.0028311 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.003189 | north | N | 0.0028311 | -0.00038276 | 0.040964 | -0.00016888 | 0.00016888 | houston | Y | 0.0028311 | 0
48690 | GBY_GN5_ | 5 | 398 | 0.003328 | houston | Y | 0.0029701 | -0.00024376 | 0.041103 | -2.988e-05 | 2.988e-05 | houston | N | 2.988e-05 | 0
48691 | GBY_7374 | A | 46 | 0.003346 | houston | Y | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48691 | GBY_7374 | B | 46 | 0.003346 | houston | Y | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48692 | GBY_8182 | C | 46 | 0.003346 | houston | Y | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48692 | GBY_8182 | D | 55 | 0.003346 | houston | Y | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48693 | GBY_8384 | E | 55 | 0.003346 | houston | Y | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48693 | GBY_8384 | F | 54 | 0.003346 | houston | Y | 0.0029881 | -0.00022576 | 0.041121 | -1.188e-05 | 1.188e-05 | houston | N | 1.188e-05 | 0
48721 | LEG_1___ | 1 | 827 | 0.002936 | north | Y | 0.0025781 | -0.00063576 | 0.040711 | -0.00042188 | 0.00042188 | houston | Y | 0.0025781 | 1.7832
48722 | LEG_2___ | 2 | 819 | 0.002936 | north | Y | 0.0025781 | -0.00063576 | 0.040711 | -0.00042188 | 0.00042188 | houston | Y | 0.0025781 | 1.7659
48730 | MNS_GT | 1 | 46.1 | 0.003374 | houston | N | 0.0030161 | -0.00019776 | 0.041149 | 1.612e-05 | 1.612e-05 | houston | N | 1.612e-05 | 0
48731 | CBE_GT1 | 1 | 76 | 0.003448 | houston | Y | 0.0030901 | -0.00012376 | 0.041223 | 9.012e-05 | 9.012e-05 | houston | N | 9.012e-05 | 0
48732 | CBE_GT2 | 1 | 76 | 0.003448 | houston | Y | 0.0030901 | -0.00012376 | 0.041223 | 9.012e-05 | 9.012e-05 | houston | N | 9.012e-05 | 0
48733 | CBE_ST12 | 1 | 105 | 0.003448 | houston | Y | 0.0030901 | -0.00012376 | 0.041223 | 9.012e-05 | 9.012e-05 | houston | N | 9.012e-05 | 0
48734 | CBE_GT3 | 1 | 74 | 0.003448 | houston | Y | 0.0030901 | -0.00012376 | 0.041223 | 9.012e-05 | 9.012e-05 | houston | N | 9.012e-05 | 0
48735 | CBE_GT4 | 1 | 74 | 0.003448 | houston | Y | 0.0030901 | -0.00012376 | 0.041223 | 9.012e-05 | 9.012e-05 | houston | N | 9.012e-05 | 0
48736 | CBE_ST34 | 1 | 102 | 0.003448 | houston | Y | 0.0030901 | -0.00012376 | 0.041223 | 9.012e-05 | 9.012e-05 | houston | N | 9.012e-05 | 0
48740 | PSG_GN2_ | 1 | 180 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48741 | PSG_GT2_ | 1 | 158.6 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48742 | PSG_GT3_ | 1 | 157 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48761 | PR_GT1__ | 1 | 35 | 0.003342 | houston | N | 0.0029841 | -0.00022976 | 0.041117 | -1.588e-05 | 1.588e-05 | houston | N | 1.588e-05 | 0
48772 | PHR_GN2_ | MB | 459 | 0.003352 | houston | Y | 0.0029941 | -0.00021976 | 0.041127 | -5.8804e-06 | 5.8804e-06 | houston | N | 5.8804e-06 | 0
48791 | PSA_GT1_ | 1 | 65 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48792 | PSA_GT2_ | 2 | 66 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48793 | PSA_GT3_ | 3 | 70 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48794 | PSA_GT4_ | 4 | 63 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48795 | PSA_GT5_ | 5 | 62 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48796 | PSA_GN1_ | 1 | 104 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48797 | PSA_GT6_ | 6 | 59 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48811 | CVC_GT3_ | 3 | 156 | 0.003314 | houston | N | 0.0029561 | -0.00025776 | 0.041089 | -4.388e-05 | 4.388e-05 | houston | N | 4.388e-05 | 0
48812 | CVC_GT2_ | 2 | 154 | 0.003314 | houston | N | 0.0029561 | -0.00025776 | 0.041089 | -4.388e-05 | 4.388e-05 | houston | N | 4.388e-05 | 0
48813 | CVC_GT1_ | 1 | 154 | 0.003314 | houston | N | 0.0029561 | -0.00025776 | 0.041089 | -4.388e-05 | 4.388e-05 | houston | N | 4.388e-05 | 0
48814 | CVC_ST5_ | 1 | 162 | 0.003314 | houston | N | 0.0029561 | -0.00025776 | 0.041089 | -4.388e-05 | 4.388e-05 | houston | N | 4.388e-05 | 0
48815 | CVC_GT4_ | 4 | 157 | 0.003331 | houston | N | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
48820 | SHELLG1_ | 1 | 71 | 0.00334 | houston | N | 0.0029821 | -0.00023176 | 0.041115 | -1.788e-05 | 1.788e-05 | houston | N | 1.788e-05 | 0
48821 | SHELLG2 | 2 | 72 | 0.00334 | houston | N | 0.0029821 | -0.00023176 | 0.041115 | -1.788e-05 | 1.788e-05 | houston | N | 1.788e-05 | 0
48822 | SHELLG3_ | 1 | 39 | 0.00334 | houston | N | 0.0029821 | -0.00023176 | 0.041115 | -1.788e-05 | 1.788e-05 | houston | N | 1.788e-05 | 0
48822 | SHELLG3_ | 2 | 30 | 0.00334 | houston | N | 0.0029821 | -0.00023176 | 0.041115 | -1.788e-05 | 1.788e-05 | houston | N | 1.788e-05 | 0
48841 | SJS_GT1_ | 1 | 78 | 0.003343 | houston | N | 0.0029851 | -0.00022876 | 0.041118 | -1.488e-05 | 1.488e-05 | houston | N | 1.488e-05 | 0
48842 | SJS_GT2_ | 2 | 80 | 0.003343 | houston | N | 0.0029851 | -0.00022876 | 0.041118 | -1.488e-05 | 1.488e-05 | houston | N | 1.488e-05 | 0
48845 | SOL_GT1 | 1 | 16.2 | 0.003341 | houston | N | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48851 | SRB_GN1_ | 1 | 165 | 0.003341 | houston | Y | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48852 | SRB_GN2_ | 2 | 169 | 0.003341 | houston | Y | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48853 | SRB_GN3_ | 3 | 213 | 0.003341 | houston | Y | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48854 | SRB_GN4_ | 4 | 228 | 0.003341 | houston | Y | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48855 | SRB_GT21 | B2 | 12 | 0.003341 | houston | Y | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48855 | SRB_GT21 | MB | 18 | 0.003341 | houston | Y | 0.0029831 | -0.00023076 | 0.041116 | -1.688e-05 | 1.688e-05 | houston | N | 1.688e-05 | 0
48865 | TECO_GT1 | 1 | 50 | 0.003358 | houston | Y | 0.0030001 | -0.00021376 | 0.041133 | 1.1958e-07 | 1.1958e-07 | houston | N | 1.1958e-07 | 0
48873 | THW_ST3_ | 3 | 104 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48874 | THW_ST4_ | 4 | 104 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48875 | THW_3132 | A | 54 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48875 | THW_3132 | B | 53 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48877 | THW_3334 | C | 54 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48877 | THW_3334 | D | 57 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48879 | THW_4142 | E | 54 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48879 | THW_4142 | F | 54 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48881 | THW_4344 | G | 58 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48881 | THW_4344 | H | 58 | 0.003336 | houston | Y | 0.0029781 | -0.00023576 | 0.041111 | -2.188e-05 | 2.188e-05 | houston | N | 2.188e-05 | 0
48883 | THW_GT1_ | B2 | 12 | 0.003333 | houston | Y | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
48885 | THW_5152 | A | 56 | 0.003327 | houston | Y | 0.0029691 | -0.00024476 | 0.041102 | -3.088e-05 | 3.088e-05 | houston | N | 3.088e-05 | 0
48885 | THW_5152 | B | 59 | 0.003327 | houston | Y | 0.0029691 | -0.00024476 | 0.041102 | -3.088e-05 | 3.088e-05 | houston | N | 3.088e-05 | 0
48886 | THW_5354 | C | 56 | 0.003327 | houston | Y | 0.0029691 | -0.00024476 | 0.041102 | -3.088e-05 | 3.088e-05 | houston | N | 3.088e-05 | 0
48886 | THW_5354 | D | 56 | 0.003327 | houston | Y | 0.0029691 | -0.00024476 | 0.041102 | -3.088e-05 | 3.088e-05 | houston | N | 3.088e-05 | 0
48887 | THW_5556 | E | 59 | 0.003327 | houston | Y | 0.0029691 | -0.00024476 | 0.041102 | -3.088e-05 | 3.088e-05 | houston | N | 3.088e-05 | 0
48887 | THW_5556 | F | 56 | 0.003327 | houston | Y | 0.0029691 | -0.00024476 | 0.041102 | -3.088e-05 | 3.088e-05 | houston | N | 3.088e-05 | 0
48911 | TGF_GT1_ | 1 | 66 | 0.003422 | houston | Y | 0.0030641 | -0.00014976 | 0.041197 | 6.412e-05 | 6.412e-05 | houston | N | 6.412e-05 | 0
48921 | WAP_GN1_ | 1 | 161 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48922 | WAP_GN2_ | 2 | 166 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48923 | WAP_GN3_ | 3 | 248 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48924 | WAP_GN4_ | 4 | 546 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48925 | WAP_GN5_ | 5 | 643 | 0.003378 | houston | N | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48926 | WAP_GN6_ | 6 | 651 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48927 | WAP_GN7_ | 7 | 564 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48928 | WAP_GN8_ | 8 | 600 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48929 | WAPGT21_ | B1 | 13 | 0.003378 | houston | Y | 0.0030201 | -0.00019376 | 0.041153 | 2.012e-05 | 2.012e-05 | houston | N | 2.012e-05 | 0
48940 | WARVUE_G | G1 | 12 | 0.003331 | houston | Y | 0.0029731 | -0.00024076 | 0.041106 | -2.688e-05 | 2.688e-05 | houston | N | 2.688e-05 | 0
49803 | EXN_15GT | 1 | 34 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49804 | EXN_16GT | 2 | 34.7 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49805 | EXN_17GT | 3 | 32.7 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49826 | EXN938GT | 5 | 45.9 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49828 | EXN941GT | 10 | 17.7 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49829 | EXN942GT | 11 | 20.4 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49830 | EXN943GT | 12 | 19.9 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49831 | EXN944GT | 13 | 35 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49832 | EXN945GT | 9 | 18 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49837 | EXN_GT | 4 | 85.4 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49838 | EXN_14GT | 14 | 148 | 0.003333 | houston | N | 0.0029751 | -0.00023876 | 0.041108 | -2.488e-05 | 2.488e-05 | houston | N | 2.488e-05 | 0
49851 | DOW17000 | 37 | 62 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49858 | DOW38100 | 31 | 71.4 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49859 | DOW38200 | 33 | 45 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49860 | DOW38300 | 32 | 101 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49862 | DOW39100 | 36 | 86 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49863 | DOW39200 | 35 | 88 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49865 | DOW41000 | 41 | 50 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49866 | DOW42000 | 42 | 18 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49869 | DOW49000 | 45 | 94 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49870 | DOW61000 | 61 | 70 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49871 | DOW62000 | 62 | 63 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49872 | DOW63000 | 63 | 72 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49873 | DOW64000 | 64 | 64.8 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49876 | DOW65000 | 65 | 101 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49877 | DOW66000 | 66 | 97 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49878 | DOW67000 | 67 | 103 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49882 | DOW81000 | 81 | 76 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49884 | DOW82000 | 82 | 80 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49885 | DOW83000 | 83 | 80 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
49886 | DOW84000 | 84 | 171 | 0.003402 | houston | N | 0.0030441 | -0.00016976 | 0.041177 | 4.412e-05 | 4.412e-05 | houston | N | 4.412e-05 | 0
58909 | PEARSALL | 1 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58909 | PEARSALL | 2 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58909 | PEARSALL | 3 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58909 | PEARSALL | 4 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58909 | PEARSALL | 5 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58909 | PEARSALL | 6 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58919 | PEARSALL | 1 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58919 | PEARSALL | 2 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58919 | PEARSALL | 3 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58919 | PEARSALL | 4 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58919 | PEARSALL | 5 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58919 | PEARSALL | 6 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58929 | PEARSALL | 1 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58929 | PEARSALL | 2 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58929 | PEARSALL | 3 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58929 | PEARSALL | 4 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58929 | PEARSALL | 5 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58929 | PEARSALL | 6 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58949 | PEARSALL | 1 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58949 | PEARSALL | 2 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58949 | PEARSALL | 3 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58949 | PEARSALL | 4 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58949 | PEARSALL | 5 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
58949 | PEARSALL | 6 | 8.4 | 0.001312 | south | Y | 0.00095407 | -0.0022598 | 0.039087 | -0.0020459 | 0.00095407 | North | Y | 0.0022598 | 0.010968
60000 | DSKY2 | 1 | 76.5 | -0.035241 | west | Y | -0.035599 | -0.038813 | 0.0025337 | -0.038599 | 0.0025337 | west | N | 0.0025337 | 0
60003 | KING_NE1 | 1 | 80 | -0.035877 | west | Y | -0.036235 | -0.039449 | 0.0018977 | -0.039235 | 0.0018977 | west | N | 0.0018977 | 0
60005 | KING_SE1 | 1 | 40 | -0.035877 | west | Y | -0.036235 | -0.039449 | 0.0018977 | -0.039235 | 0.0018977 | west | N | 0.0018977 | 0
60007 | KING_SW1 | 1 | 80 | -0.035986 | west | Y | -0.036344 | -0.039558 | 0.0017887 | -0.039344 | 0.0017887 | west | N | 0.0017887 | 0
60016 | WOODWRD1 | 1 | 80 | -0.035852 | west | Y | -0.03621 | -0.039424 | 0.0019227 | -0.03921 | 0.0019227 | west | N | 0.0019227 | 0
60017 | ORNNWP1 | 1 | 80 | -0.0353 | west | Y | -0.035658 | -0.038872 | 0.0024747 | -0.038658 | 0.0024747 | west | N | 0.0024747 | 0
60018 | DSKY1 | 1 | 84 | -0.035119 | west | Y | -0.035477 | -0.038691 | 0.0026557 | -0.038477 | 0.0026557 | west | N | 0.0026557 | 0
60019 | KING_NW1 | 1 | 80 | -0.035986 | west | Y | -0.036344 | -0.039558 | 0.0017887 | -0.039344 | 0.0017887 | west | N | 0.0017887 | 0
60057 | CALLAHAN | 1 | 114 | 0.003292 | south | Y | 0.0029341 | -0.00027976 | 0.041067 | -6.588e-05 | 6.588e-05 | houston | Y | 0.00027976 | 0.024383
60058 | BUFF_GAP | 1 | 120 | -0.043542 | west | Y | -0.0439 | -0.047114 | -0.0057673 | -0.0469 | 0.0057673 | west | N | 0.0057673 | 0
60060 | CIRELLO | 1 | 233 | -0.043542 | west | Y | -0.0439 | -0.047114 | -0.0057673 | -0.0469 | 0.0057673 | west | N | 0.0057673 | 0
60063 | BUFF_GAP | 1 | 170.2 | -0.043542 | west | Y | -0.0439 | -0.047114 | -0.0057673 | -0.0469 | 0.0057673 | west | N | 0.0057673 | 0
60066 | H_HOLLOW | 1 | 222 | 0.003292 | south | Y | 0.0029341 | -0.00027976 | 0.041067 | -6.588e-05 | 6.588e-05 | houston | Y | 0.00027976 | 0.047482
60068 | HHOLLOW2 | 1 | 184 | 0.003292 | south | Y | 0.0029341 | -0.00027976 | 0.041067 | -6.588e-05 | 6.588e-05 | houston | Y | 0.00027976 | 0.039354
60070 | HHOLLOW3 | 1 | 224 | 0.003292 | south | Y | 0.0029341 | -0.00027976 | 0.041067 | -6.588e-05 | 6.588e-05 | houston | Y | 0.00027976 | 0.047909
60072 | HHOLLOW4 | 1 | 115 | 0.003292 | south | Y | 0.0029341 | -0.00027976 | 0.041067 | -6.588e-05 | 6.588e-05 | houston | Y | 0.00027976 | 0.024596
60074 | HORSH5 | 1 | 100 | 0.003292 | south | Y | 0.0029341 | -0.00027976 | 0.041067 | -6.588e-05 | 6.588e-05 | houston | Y | 0.00027976 | 0.021388
60081 | WHRLWIND | 1 | 60 | -0.048808 | west | Y | -0.049166 | -0.05238 | -0.011033 | -0.052166 | 0.011033 | west | N | 0.011033 | 0
60201 | RIO DRCS | F | 0 | -0.009459 | south | N | -0.0098169 | -0.013031 | 0.028316 | -0.012817 | 0.0098169 | North | Y | 0.013031 | 0
60202 | FRIEND_R | F | 0 | -0.032223 | west | N | -0.032581 | -0.035795 | 0.0055517 | -0.035581 | 0.0055517 | west | N | 0.0055517 | 0
60203 | PRES0A | BT | 4.8 | -0.036359 | west | N | -0.036717 | -0.039931 | 0.0014157 | -0.039717 | 0.0014157 | west | N | 0.0014157 | 0
71051 | L_BITTCR | W1 | 37.5 | -0.038101 | west | Y | -0.038459 | -0.041673 | -0.00032629 | -0.041459 | 0.00032629 | west | N | 0.00032629 | 0
71054 | L_SWEETW | W1 | 107.5 | -0.038101 | west | Y | -0.038459 | -0.041673 | -0.00032629 | -0.041459 | 0.00032629 | west | N | 0.00032629 | 0
71057 | L_SWEETW | W1 | 135 | -0.038101 | west | Y | -0.038459 | -0.041673 | -0.00032629 | -0.041459 | 0.00032629 | west | N | 0.00032629 | 0
71059 | L_SWEETW | W1 | 119 | -0.038101 | west | Y | -0.038459 | -0.041673 | -0.00032629 | -0.041459 | 0.00032629 | west | N | 0.00032629 | 0
71060 | L_SWEETW | W1 | 105 | -0.038101 | west | Y | -0.038459 | -0.041673 | -0.00032629 | -0.041459 | 0.00032629 | west | N | 0.00032629 | 0
71061 | L_SWEETW | W1 | 80.5 | -0.038101 | west | Y | -0.038459 | -0.041673 | -0.00032629 | -0.041459 | 0.00032629 | west | N | 0.00032629 | 0
76031 | L_GASCCR | W1 | 150 | -0.037795 | west | Y | -0.038153 | -0.041367 | -2.0287e-05 | -0.041153 | 2.0287e-05 | west | N | 2.0287e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | -0.037901 | west | Y | -0.038259 | -0.041473 | -0.00012629 | -0.041259 | 0.00012629 | west | N | 0.00012629 | 0
76095 | L_CAPRSI | W1 | 149.5 | -0.037901 | west | Y | -0.038259 | -0.041473 | -0.00012629 | -0.041259 | 0.00012629 | west | N | 0.00012629 | 0
76096 | L_CAPRSI | W1 | 186 | -0.037901 | west | Y | -0.038259 | -0.041473 | -0.00012629 | -0.041259 | 0.00012629 | west | N | 0.00012629 | 0
76097 | L_CAPRGE | W1 | 214.5 | -0.037901 | west | Y | -0.038259 | -0.041473 | -0.00012629 | -0.041259 | 0.00012629 | west | N | 0.00012629 | 0
80003 | MILHWYS | F | 0 | 0.003148 | south | N | 0.0027901 | -0.00042376 | 0.040923 | -0.00020988 | 0.00020988 | houston | Y | 0.00042376 | 0
80010 | EPLVT1 | F | 0 | -0.004796 | south | N | -0.0051539 | -0.0083678 | 0.032979 | -0.0081539 | 0.0051539 | North | Y | 0.0083678 | 0
80012 | LAR | F | 0 | 0.002203 | south | N | 0.0018451 | -0.0013688 | 0.039978 | -0.0011549 | 0.0011549 | houston | Y | 0.0013688 | 0
80051 | FORPVCM0 | 8 | 28 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
80052 | FOR69CG0 | 9 | 43.6 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
80053 | FOR69CG0 | 10 | 74 | 0.00333 | south | N | 0.0029721 | -0.00024176 | 0.041105 | -2.788e-05 | 2.788e-05 | houston | Y | 0.00024176 | 0
80080 | GWINDT11 | 1 | 94 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.020105
80080 | GWINDT11 | 2 | 41 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.0087691
80080 | GWINDT11 | 3 | 38 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.0081275
80080 | GWINDT11 | 4 | 19 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.0040638
80081 | GWINDT21 | 1 | 94 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.020105
80081 | GWINDT21 | 2 | 36 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.0076997
80081 | GWINDT21 | 3 | 43 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.0091969
80081 | GWINDT21 | 4 | 22 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.0047054
80137 | CSDR89 | 8 | 39 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80137 | CSDR89 | 9 | 15 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80138 | CSDR7 | 7 | 7 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80139 | CSDR56 | 5 | 15 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80139 | CSDR56 | 6 | 39 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80140 | CSDR11 | 11 | 39 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80180 | PNSCALT1 | 1 | 148 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.031654
80180 | PNSCALT1 | 2 | 50 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.010694
80181 | PNSCALT2 | 1 | 55 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.011763
80181 | PNSCALT2 | 2 | 50 | 0.003159 | south | Y | 0.0028011 | -0.00041276 | 0.040934 | -0.00019888 | 0.00019888 | houston | Y | 0.00041276 | 0.010694
80223 | REYSHR G | 1 | 12 | 0.003204 | south | N | 0.0028461 | -0.00036776 | 0.040979 | -0.00015388 | 0.00015388 | houston | Y | 0.00036776 | 0
80224 | VISTRONG | 1 | 15 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80225 | VISTRONG | 2 | 23 | 0.003307 | south | N | 0.0029491 | -0.00026476 | 0.041082 | -5.088e-05 | 5.088e-05 | houston | Y | 0.00026476 | 0
80226 | ALCOA G | 1 | 48 | 0.003326 | south | N | 0.0029681 | -0.00024576 | 0.041101 | -3.188e-05 | 3.188e-05 | houston | Y | 0.00024576 | 0
80227 | AIRCO G | 1 | 8 | 0.003302 | south | N | 0.0029441 | -0.00026976 | 0.041077 | -5.588e-05 | 5.588e-05 | houston | Y | 0.00026976 | 0
80261 | NBEC81A | 1 | 180 | 0.003188 | south | Y | 0.0028301 | -0.00038376 | 0.040963 | -0.00016988 | 0.00016988 | houston | Y | 0.00038376 | 0.038499
80262 | NBEC91A | 1 | 180 | 0.003188 | south | Y | 0.0028301 | -0.00038376 | 0.040963 | -0.00016988 | 0.00016988 | houston | Y | 0.00038376 | 0.038499
80263 | B_DAVIS3 | 3 | 180 | 0.003186 | south | Y | 0.0028281 | -0.00038576 | 0.040961 | -0.00017188 | 0.00017188 | houston | Y | 0.00038576 | 0.038499
80264 | B_DAVIS4 | 4 | 180 | 0.003186 | south | Y | 0.0028281 | -0.00038576 | 0.040961 | -0.00017188 | 0.00017188 | houston | Y | 0.00038576 | 0.038499
80265 | LARECU40 | 4 | 100 | 0.002204 | south | Y | 0.0018461 | -0.0013678 | 0.039979 | -0.0011539 | 0.0011539 | houston | Y | 0.0013678 | 0.021388
80266 | LARECU50 | 5 | 100 | 0.002204 | south | Y | 0.0018461 | -0.0013678 | 0.039979 | -0.0011539 | 0.0011539 | houston | Y | 0.0013678 | 0.021388
80291 | PAPALOTE | 1 | 25 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.005347
80291 | PAPALOTE | 2 | 25 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.005347
80291 | PAPALOTE | 3 | 25 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.005347
80291 | PAPALOTE | 4 | 16 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.0034221
80294 | PAPALOTE | 5 | 25 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.005347
80294 | PAPALOTE | 6 | 25 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.005347
80294 | PAPALOTE | 7 | 25 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.005347
80294 | PAPALOTE | 8 | 15 | 0.003197 | south | Y | 0.0028391 | -0.00037476 | 0.040972 | -0.00016088 | 0.00016088 | houston | Y | 0.00037476 | 0.0032082
86104 | CID-138 | EQ | 0 | 0.002204 | south | N | 0.0018461 | -0.0013678 | 0.039979 | -0.0011539 | 0.0011539 | houston | Y | 0.0013678 | 0
86105 | CID-230 | EQ | 500 | 0.002204 | south | N | 0.0018461 | -0.0013678 | 0.039979 | -0.0011539 | 0.0011539 | houston | Y | 0.0013678 | 0
86106 | CUF-230 | EQ | 500 | 0.002204 | south | N | 0.0018461 | -0.0013678 | 0.039979 | -0.0011539 | 0.0011539 | houston | Y | 0.0013678 | 0
86107 | CUF-138 | EQ | 0 | 0.002204 | south | N | 0.0018461 | -0.0013678 | 0.039979 | -0.0011539 | 0.0011539 | houston | Y | 0.0013678 | 0
88198 | BEEVILLE | F | 0 | 0.003094 | south | N | 0.0027361 | -0.00047776 | 0.040869 | -0.00026388 | 0.00026388 | houston | Y | 0.00047776 | 0
88253 | HAMILTON | F | 0 | -0.008922 | south | N | -0.0092799 | -0.012494 | 0.028853 | -0.01228 | 0.0092799 | North | Y | 0.012494 | 0
88299 | ZAPATA | F | 0 | 0.002504 | south | N | 0.0021461 | -0.0010678 | 0.040279 | -0.00085388 | 0.00085388 | houston | Y | 0.0010678 | 0
88508 | FALFURRI | F | 0 | 0.003024 | south | N | 0.0026661 | -0.00054776 | 0.040799 | -0.00033388 | 0.00033388 | houston | Y | 0.00054776 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:LINGLVLL - FLATCRK_ 138 kV 1640 - 1642 C: COMCHESS - SARC7A 345kV 1440 - 6444 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.004863 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.767 | 569 | 0.042638 | 24.2609 | 569 | 24.2609
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.004863 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.8254 | 581 | 0.042638 | 24.7725
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084402 | 0 | 0.042464 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084402 | 0 | 0.042464 | 0 |  |  | Weighted Shift Factors
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070335 | 0 | 0.042464 | 0 |  |  | West | -0.037775
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18358 | 42 | 0.042146 | 1.7701 |  |  | North | 0.0020842
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19232 | 44 | 0.042146 | 1.8544 |  |  |  | -0.039859
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19232 | 44 | 0.042146 | 1.8544
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20544 | 47 | 0.042146 | 1.9808 |  |  | Line Rating | 381.35
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004338 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3448 | 310 | 0.042113 | 13.0549 |  |  | Conc Gen | 569
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004338 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7916 | 413 | 0.042113 | 17.3926 |  |  | Weighted Imp. | 24.2609
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.00433 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03464 | 0 | 0.042105 | 0 |  |  | PTDF | 0.042638
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.00433 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03464 | 0 | 0.042105 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2105 | 49 | 0.042071 | 2.0615 |  |  | Concentration | -1.0697
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19762 | 46 | 0.042071 | 1.9353
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19762 | 46 | 0.042071 | 1.9353
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20191 | 47 | 0.042071 | 1.9773
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004296 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.66158 | 154 | 0.042071 | 6.4789
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004296 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.63581 | 148 | 0.042071 | 6.2265
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20621 | 48 | 0.042071 | 2.0194
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20621 | 48 | 0.042071 | 2.0194
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14896 | 0 | 0.042031 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1447 | 0 | 0.042031 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14896 | 0 | 0.042031 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56126 | 132 | 0.042027 | 5.5475
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56977 | 134 | 0.042027 | 5.6316
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3734 | 323 | 0.042027 | 13.5746
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.66802 | 158 | 0.042003 | 6.6364
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.67648 | 160 | 0.042003 | 6.7204
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7399 | 175 | 0.042003 | 7.3505
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64111 | 152.5 | 0.041979 | 6.4018
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.6285 | 149.5 | 0.041979 | 6.2758
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.97785 | 232.6 | 0.041979 | 9.7642
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.00406 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.371 | 584 | 0.041835 | 24.4315
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.00406 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.4157 | 595 | 0.041835 | 24.8917
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.004058 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.7571 | 433 | 0.041833 | 18.1136
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.003911 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070398 | 0 | 0.041686 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.003911 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070398 | 0 | 0.041686 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003908 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10942 | 0 | 0.041683 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003908 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11333 | 0 | 0.041683 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.003759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5863 | 422 | 0.041534 | 17.5272
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.022518 | 0 | 0.041528 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.83 | 223.9 | 0.041482 | 9.2878
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.83408 | 225 | 0.041482 | 9.3334
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.83259 | 224.6 | 0.041482 | 9.3168
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84038 | 226.7 | 0.041482 | 9.4039
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.003701 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.050704 | 0 | 0.041476 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003671 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0088104 | 0 | 0.041446 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003671 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0088104 | 0 | 0.041446 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0087312 | 0 | 0.041413 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0087312 | 0 | 0.041413 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010186 | 0 | 0.041413 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.5129 | 142 | 0.041387 | 5.8769
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52374 | 145 | 0.041387 | 6.0011
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54541 | 151 | 0.041387 | 6.2494
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0475 | 290 | 0.041387 | 12.0021
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003562 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.042744 | 0 | 0.041337 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.003551 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014204 | 0 | 0.041326 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.517 | 147 | 0.041292 | 6.0699
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48535 | 138 | 0.041292 | 5.6983
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.49238 | 140 | 0.041292 | 5.7808
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.517 | 147 | 0.041292 | 6.0699
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64009 | 182 | 0.041292 | 7.5151
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.69637 | 198 | 0.041292 | 8.1758
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26205 | 76 | 0.041223 | 3.1329
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26205 | 76 | 0.041223 | 3.1329
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.36204 | 105 | 0.041223 | 4.3284
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25515 | 74 | 0.041223 | 3.0505
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25515 | 74 | 0.041223 | 3.0505
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.3517 | 102 | 0.041223 | 4.2047
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.003433 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 4.5762 | 0 | 0.041208 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.003433 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 4.559 | 0 | 0.041208 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.003422 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22585 | 66 | 0.041197 | 2.719
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21092 | 0 | 0.041177 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2429 | 0 | 0.041177 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15309 | 0 | 0.041177 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3436 | 0 | 0.041177 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29257 | 0 | 0.041177 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29938 | 0 | 0.041177 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1701 | 0 | 0.041177 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.061236 | 0 | 0.041177 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31979 | 0 | 0.041177 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23814 | 0 | 0.041177 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21433 | 0 | 0.041177 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24494 | 0 | 0.041177 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22045 | 0 | 0.041177 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3436 | 0 | 0.041177 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32999 | 0 | 0.041177 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35041 | 0 | 0.041177 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25855 | 0 | 0.041177 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27216 | 0 | 0.041177 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27216 | 0 | 0.041177 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58174 | 0 | 0.041177 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.003396 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24112 | 0 | 0.041171 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.003396 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.03396 | 0 | 0.041171 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37662 | 0 | 0.041168 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37662 | 0 | 0.041168 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.40377 | 0 | 0.041168 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37153 | 0 | 0.041168 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55061 | 0 | 0.041153 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55061 | 0 | 0.041153 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.82761 | 0 | 0.041153 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 2.1991 | 651 | 0.041153 | 26.7904
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.9052 | 564 | 0.041153 | 23.2101
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 2.0268 | 600 | 0.041153 | 24.6916
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.54386 | 161 | 0.041153 | 6.6256
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.56075 | 166 | 0.041153 | 6.8314
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.83774 | 248 | 0.041153 | 10.2059
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.003378 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.8444 | 546 | 0.041153 | 22.4694
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.003378 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 2.1721 | 0 | 0.041153 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.003378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.043914 | 13 | 0.041153 | 0.53499
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.003374 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15554 | 0 | 0.041149 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.003371 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11124 | 0 | 0.041146 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.003366 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.8378 | 546 | 0.041141 | 22.4628
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.003366 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.5245 | 750 | 0.041141 | 30.8555
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23789 | 0 | 0.041135 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22411 | 0 | 0.041135 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17808 | 0 | 0.041135 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51475 | 0 | 0.041135 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51576 | 0 | 0.041135 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51173 | 0 | 0.041135 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.32256 | 0 | 0.041135 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.81984 | 0 | 0.041135 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1344 | 0 | 0.041135 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10752 | 0 | 0.041135 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1008 | 0 | 0.041135 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33701 | 0 | 0.041135 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.31214 | 0 | 0.041135 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.34507 | 0 | 0.041135 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.34272 | 0 | 0.041135 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.003358 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.1679 | 50 | 0.041133 | 2.0566
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52018 | 155 | 0.041131 | 6.3753
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57052 | 170 | 0.041131 | 6.9922
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52018 | 155 | 0.041131 | 6.3753
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.003352 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041127 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041125 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041125 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041125 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30467 | 0 | 0.041123 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29328 | 0 | 0.041123 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29128 | 0 | 0.041123 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18247 | 0 | 0.041123 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.040846 | 0 | 0.041123 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.21749 | 0 | 0.041121 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.20076 | 0 | 0.041121 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.21749 | 0 | 0.041121 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.21749 | 0 | 0.041121 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15392 | 46 | 0.041121 | 1.8916
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15392 | 46 | 0.041121 | 1.8916
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15392 | 46 | 0.041121 | 1.8916
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18403 | 55 | 0.041121 | 2.2616
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18403 | 55 | 0.041121 | 2.2616
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18068 | 54 | 0.041121 | 2.2205
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.003343 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.26075 | 0 | 0.041118 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.003343 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.26744 | 0 | 0.041118 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54541 | 0 | 0.041117 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52503 | 0 | 0.041117 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52636 | 0 | 0.041117 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52469 | 0 | 0.041117 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.899 | 0 | 0.041117 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.003342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11697 | 0 | 0.041117 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49781 | 0 | 0.041116 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2175 | 0 | 0.041116 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.55127 | 165 | 0.041116 | 6.7841
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.56463 | 169 | 0.041116 | 6.9486
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.003341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.040092 | 12 | 0.041116 | 0.49339
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.003341 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041116 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.60138 | 0 | 0.041116 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52988 | 0 | 0.041116 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52454 | 0 | 0.041116 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.76175 | 228 | 0.041116 | 9.3744
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21382 | 0 | 0.041116 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21115 | 0 | 0.041116 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27597 | 0 | 0.041116 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2459 | 0 | 0.041116 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.054124 | 0 | 0.041116 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.71163 | 213 | 0.041116 | 8.7576
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23714 | 0 | 0.041115 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24048 | 0 | 0.041115 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13026 | 0 | 0.041115 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1002 | 0 | 0.041115 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.003339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4541 | 0 | 0.041114 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.1402 | 42 | 0.041113 | 1.7267
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.1402 | 42 | 0.041113 | 1.7267
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.12684 | 38 | 0.041113 | 1.5623
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.12684 | 38 | 0.041113 | 1.5623
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.003338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57747 | 0 | 0.041113 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.003338 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.45063 | 0 | 0.041113 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34694 | 104 | 0.041111 | 4.2755
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34694 | 104 | 0.041111 | 4.2755
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.17681 | 53 | 0.041111 | 2.1789
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19015 | 57 | 0.041111 | 2.3433
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19349 | 58 | 0.041111 | 2.3844
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19349 | 58 | 0.041111 | 2.3844
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.003334 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.4505 | 735 | 0.041109 | 30.2149
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11332 | 0 | 0.041108 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11566 | 0 | 0.041108 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10899 | 0 | 0.041108 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15298 | 0 | 0.041108 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.058994 | 0 | 0.041108 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.067993 | 0 | 0.041108 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066327 | 0 | 0.041108 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11665 | 0 | 0.041108 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.059994 | 0 | 0.041108 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28464 | 0 | 0.041108 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49328 | 0 | 0.041108 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.003333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.039996 | 12 | 0.041108 | 0.49329
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.003331 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.4749 | 743 | 0.041106 | 30.5415
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.003331 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.039972 | 12 | 0.041106 | 0.49327
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21652 | 0 | 0.041106 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21985 | 0 | 0.041106 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23317 | 0 | 0.041106 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20985 | 0 | 0.041106 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20652 | 0 | 0.041106 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34642 | 0 | 0.041106 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19653 | 0 | 0.041106 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.016655 | 0 | 0.041106 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.069951 | 0 | 0.041106 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.003331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52297 | 0 | 0.041106 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26307 | 0 | 0.041105 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26973 | 0 | 0.041105 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26307 | 0 | 0.041105 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2664 | 0 | 0.041105 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26107 | 0 | 0.041105 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.08325 | 0 | 0.041105 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15318 | 0 | 0.041105 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.09324 | 0 | 0.041105 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14519 | 0 | 0.041105 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.24642 | 0 | 0.041105 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.57276 | 172 | 0.041105 | 7.07
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.57276 | 172 | 0.041105 | 7.07
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.57276 | 172 | 0.041105 | 7.07
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5418 | 0 | 0.041103 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53714 | 0 | 0.041103 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52882 | 0 | 0.041103 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8959 | 0 | 0.041103 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.003328 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3245 | 398 | 0.041103 | 16.3589
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19629 | 59 | 0.041102 | 2.425
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19629 | 59 | 0.041102 | 2.425
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.003326 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15965 | 0 | 0.041101 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.57332 | 0 | 0.041089 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51698 | 0 | 0.041089 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51036 | 0 | 0.041089 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51036 | 0 | 0.041089 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.003314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53687 | 0 | 0.041089 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.003313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.47707 | 144 | 0.041088 | 5.9166
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.003313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.62284 | 188 | 0.041088 | 7.7245
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.003313 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.24185 | 0 | 0.041088 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049605 | 0 | 0.041082 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.076061 | 0 | 0.041082 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.092596 | 0 | 0.041082 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.023149 | 0 | 0.041082 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12897 | 0 | 0.041082 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049605 | 0 | 0.041082 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.023149 | 0 | 0.041082 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049605 | 0 | 0.041082 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12897 | 0 | 0.041082 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12897 | 0 | 0.041082 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.003302 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.026416 | 0 | 0.041077 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.003297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3979 | 424 | 0.041072 | 17.4144
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.003297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.4012 | 425 | 0.041072 | 17.4555
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.37529 | 114 | 0.041067 | 4.6816
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.73082 | 222 | 0.041067 | 9.1168
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.60573 | 184 | 0.041067 | 7.5563
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.73741 | 224 | 0.041067 | 9.1989
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.37858 | 115 | 0.041067 | 4.7227
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.003283 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3526 | 412 | 0.041058 | 16.9158
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.003283 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3132 | 400 | 0.041058 | 16.4231
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1566 | 47.7 | 0.041058 | 1.9585
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12246 | 37.3 | 0.041058 | 1.5315
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15102 | 46 | 0.041058 | 1.8887
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15758 | 48 | 0.041058 | 1.9708
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.003281 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.68573 | 209 | 0.041056 | 8.5806
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.003281 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.7087 | 216 | 0.041056 | 8.868
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15093 | 46 | 0.041056 | 1.8886
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15421 | 47 | 0.041056 | 1.9296
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15093 | 46 | 0.041056 | 1.8886
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15093 | 46 | 0.041056 | 1.8886
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.003258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.326 | 407 | 0.041033 | 16.7003
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.003251 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.0449 | 629 | 0.041026 | 25.8052
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003242 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.071324 | 22 | 0.041017 | 0.90237
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003242 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035662 | 11 | 0.041017 | 0.45118
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003242 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035662 | 11 | 0.041017 | 0.45118
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.50623 | 0 | 0.040979 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.49021 | 0 | 0.040979 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3204 | 0 | 0.040979 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.46458 | 0 | 0.040979 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47099 | 0 | 0.040979 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.40691 | 0 | 0.040979 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.003204 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.038448 | 0 | 0.040979 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 25 | 0.040972 | 1.0243
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 25 | 0.040972 | 1.0243
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 25 | 0.040972 | 1.0243
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.051152 | 16 | 0.040972 | 0.65555
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 25 | 0.040972 | 1.0243
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 25 | 0.040972 | 1.0243
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 25 | 0.040972 | 1.0243
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.047955 | 15 | 0.040972 | 0.61458
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57384 | 180 | 0.040963 | 7.3733
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0712 | 336 | 0.040963 | 13.7635
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57384 | 180 | 0.040963 | 7.3733
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47278 | 0 | 0.040963 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47374 | 0 | 0.040963 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.48776 | 0 | 0.040963 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003186 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0641 | 334 | 0.040961 | 13.6809
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003186 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0832 | 340 | 0.040961 | 13.9266
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57348 | 180 | 0.040961 | 7.3729
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57348 | 180 | 0.040961 | 7.3729
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003184 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12099 | 0 | 0.040959 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.003183 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.079575 | 0 | 0.040958 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.003183 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.079575 | 0 | 0.040958 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.00318 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.18444 | 58 | 0.040955 | 2.3754
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.00318 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.28302 | 89 | 0.040955 | 3.645
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.13992 | 44 | 0.040955 | 1.802
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.13992 | 44 | 0.040955 | 1.802
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.13674 | 43 | 0.040955 | 1.7611
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1431 | 45 | 0.040955 | 1.843
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.00318 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12084 | 0 | 0.040955 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.003171 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.091959 | 0 | 0.040946 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.29695 | 94 | 0.040934 | 3.8478
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12952 | 41 | 0.040934 | 1.6783
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12004 | 38 | 0.040934 | 1.5555
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.060021 | 19 | 0.040934 | 0.77774
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.29695 | 94 | 0.040934 | 3.8478
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11372 | 36 | 0.040934 | 1.4736
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13584 | 43 | 0.040934 | 1.7601
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.069498 | 22 | 0.040934 | 0.90054
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.46753 | 148 | 0.040934 | 6.0582
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15795 | 50 | 0.040934 | 2.0467
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.17375 | 55 | 0.040934 | 2.2514
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15795 | 50 | 0.040934 | 2.0467
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.003154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.249 | 396 | 0.040929 | 16.2078
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.003148 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040923 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11962 | 38 | 0.040923 | 1.5551
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.060756 | 19.3 | 0.040923 | 0.78981
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.04722 | 15 | 0.040923 | 0.61384
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.003148 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14796 | 47 | 0.040923 | 1.9234
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44928 | 144 | 0.040895 | 5.8888
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44928 | 144 | 0.040895 | 5.8888
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53352 | 171 | 0.040895 | 6.993
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64584 | 207 | 0.040895 | 8.4652
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.6761 | 216.7 | 0.040895 | 8.8619
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.75504 | 242 | 0.040895 | 9.8965
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.003094 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040869 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4499 | 146.5 | 0.040846 | 5.9839
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4542 | 147.9 | 0.040846 | 6.0411
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53128 | 173 | 0.040846 | 7.0663
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.003024 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040799 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033372 | 0 | 0.040556 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.030591 | 0 | 0.040556 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033372 | 0 | 0.040556 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.002504 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040279 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002204 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2204 | 100 | 0.039979 | 3.9979
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002204 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2204 | 100 | 0.039979 | 3.9979
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002203 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039978 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.041732 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 3.0464 | 73 | 0.039648 | 2.8943
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.041732 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.9661 | 119 | 0.039648 | 4.7181
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.041732 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.5551 | 205 | 0.039648 | 8.1278
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.041732 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2567 | 102 | 0.039648 | 4.0441
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.041732 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.0063 | 96 | 0.039648 | 3.8062
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001627 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.039048 | 24 | 0.039402 | 0.94564
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001627 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.039048 | 24 | 0.039402 | 0.94564
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.001627 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.037421 | 23 | 0.039402 | 0.90624
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.037775 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.037775 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.004796 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.032979 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.005575 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03345 | 0 | 0.0322 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.008922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29443 | 0 | 0.028853 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.008922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22305 | 0 | 0.028853 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.008922 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028853 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4982 | 70 | 0.019319 | 1.3523
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4768 | 69 | 0.019319 | 1.333
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4768 | 69 | 0.019319 | 1.333
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4554 | 68 | 0.019319 | 1.3137
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.016587 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2488 | 0 | 0.014503 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.016587 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2488 | 0 | 0.014503 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.015307 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2961 | 150 | 0.013223 | 1.9834
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.015307 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2246 | 80 | 0.013223 | 1.0578
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2362 | 18 | 0.011038 | 0.19868
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2362 | 18 | 0.011038 | 0.19868
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.49864 | 38 | 0.011038 | 0.41944
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.011578 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9451 | 168 | 0.0094938 | 1.595
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.011578 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.042 | 90 | 0.0094938 | 0.85444
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011117 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8348 | 255 | 0.0090328 | 2.3034
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011117 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6564 | 149 | 0.0090328 | 1.3459
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011117 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7009 | 153 | 0.0090328 | 1.382
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006314 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0042298 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006314 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0042298 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.005883 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0037988 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.005883 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.6299 | 787 | 0.0037988 | 2.9896
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.004436 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0023518 | 0
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.004139 | north | 3 | N | N | Nnorth | Nnorth | 1 | 4.7888 | 0 | 0.0020548 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.004139 | north | 3 | N | N | Nnorth | Nnorth | 1 | 4.793 | 0 | 0.0020548 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.81922 | 217.3 | 0.0016858 | 0.36632
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.77285 | 205 | 0.0016858 | 0.34559
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0269 | 272.4 | 0.0016858 | 0.45921
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.00331 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15888 | 48 | 0.0012258 | 0.058838
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.00331 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15226 | 46 | 0.0012258 | 0.056386
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.00331 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.34755 | 105 | 0.0012258 | 0.12871
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.0033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.6468 | 196 | 0.0012158 | 0.2383
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.0033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.3663 | 111 | 0.0012158 | 0.13495
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.3292 | 100 | 0.0012078 | 0.12078
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.00327 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.05559 | 17 | 0.0011858 | 0.020158
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.003269 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.10461 | 0 | 0.0011848 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.49174 | 0 | 0.0011048 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.49748 | 0 | 0.0011048 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.49748 | 0 | 0.0011048 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.2118 | 0 | 0.0011048 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.003161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.4635 | 463 | 0.0010768 | 0.49855
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.003046 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.6823 | 224 | 0.00096179 | 0.21544
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.565 | 855 | 0.00091579 | 0.783
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.565 | 855 | 0.00091579 | 0.783
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.4569 | 152.3 | 0.00091579 | 0.13948
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.459 | 153 | 0.00091579 | 0.14012
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.002936 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4281 | 827 | 0.00085179 | 0.70443
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.002936 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4046 | 819 | 0.00085179 | 0.69762
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64758 | 224 | 0.00080679 | 0.18072
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.65337 | 226 | 0.00080679 | 0.18234
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61289 | 212 | 0.00080679 | 0.17104
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61 | 211 | 0.00080679 | 0.17023
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.81216 | 288 | 0.00073579 | 0.21191
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.41454 | 147 | 0.00073579 | 0.10816
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.41454 | 147 | 0.00073579 | 0.10816
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.002502 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.5387 | 615 | 0.00041779 | 0.25694
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.002502 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.4687 | 587 | 0.00041779 | 0.24524
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35776 | 150.7 | 0.00028979 | 0.043672
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35847 | 151 | 0.00028979 | 0.043759
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.42115 | 177.4 | 0.00028979 | 0.051409
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35709 | 151.5 | 0.00027279 | 0.041328
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35897 | 152.3 | 0.00027279 | 0.041546
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.41837 | 177.5 | 0.00027279 | 0.048421
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.002064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.44665 | 216.4 | -2.0208e-05 | -0.0043729
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.002064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.44603 | 216.1 | -2.0208e-05 | -0.0043669
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.001684 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.30649 | 182 | -0.00040021 | -0.072838
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.001684 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.81506 | 484 | -0.00040021 | -0.1937
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.001663 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.08315 | 50 | -0.00042121 | -0.02106
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.001655 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.00042921 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.23414 | 0 | -0.00050221 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.20566 | 0 | -0.00050221 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.22939 | 0 | -0.00050221 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.63122 | 0 | -0.00050221 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1689 | 785 | -0.00059521 | -0.46724
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1838 | 795 | -0.00059521 | -0.47319
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1614 | 780 | -0.00059521 | -0.46426
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.001218 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.14372 | 118 | -0.00086621 | -0.10221
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.001218 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.14007 | 115 | -0.00086621 | -0.099614
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.001218 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.67721 | 556 | -0.00086621 | -0.48161
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000872 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012122 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000872 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012122 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.000871 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.37889 | 435 | -0.0012132 | -0.52775
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.000798 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.31521 | 395 | -0.0012862 | -0.50805
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.000798 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.34713 | 435 | -0.0012862 | -0.5595
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12735 | 161 | -0.0012932 | -0.20821
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12972 | 164 | -0.0012932 | -0.21209
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12972 | 164 | -0.0012932 | -0.21209
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.32747 | 414 | -0.0012932 | -0.53539
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12814 | 162 | -0.0012932 | -0.2095
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12735 | 161 | -0.0012932 | -0.20821
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12893 | 163 | -0.0012932 | -0.21079
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.32352 | 409 | -0.0012932 | -0.52892
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.00077 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.29876 | 388 | -0.0013142 | -0.50991
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.00077 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.39655 | 515 | -0.0013142 | -0.67682
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.000516 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.02064 | 40 | -0.0015682 | -0.062728
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.00996 | 20 | -0.0015862 | -0.031724
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.01245 | 25 | -0.0015862 | -0.039655
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.020418 | 41 | -0.0015862 | -0.065035
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.035155 | 79 | -0.0016392 | -0.1295
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04717 | 106 | -0.0016392 | -0.17376
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.06497 | 146 | -0.0016392 | -0.23932
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.000445 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.03382 | 76 | -0.0016392 | -0.12458
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.10769 | 558 | -0.0018912 | -1.0553
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.11175 | 579 | -0.0018912 | -1.095
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.15594 | 808 | -0.0018912 | -1.5281
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.009975 | 0 | -0.0019512 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.010587 | 0 | -0.0019512 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.011757 | 0 | -0.0019512 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.01664 | 160 | -0.0019802 | -0.31683
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.016224 | 156 | -0.0019802 | -0.30891
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.020384 | 196 | -0.0019802 | -0.38812
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.016224 | 156 | -0.0019802 | -0.30891
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.016328 | 157 | -0.0019802 | -0.31089
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.020592 | 198 | -0.0019802 | -0.39208
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 5.6e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.02072 | 370 | -0.0020282 | -0.75044
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.00784 | 0 | -0.0020282 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.007896 | 0 | -0.0020282 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.017304 | 0 | -0.0020282 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.008008 | 0 | -0.0020282 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.008064 | 0 | -0.0020282 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.01736 | 0 | -0.0020282 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0020842 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0020842 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -6.6e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.01122 | 170 | -0.0021502 | -0.36554
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -6.6e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.03432 | 520 | -0.0021502 | -1.1181
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -8.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0021692 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.000161 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00644 | 0 | -0.0022452 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.000161 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00644 | 0 | -0.0022452 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.000465 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0025492 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.001362 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034462 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.001362 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034462 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.001362 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034462 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.002454 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.14724 | 60 | -0.0045382 | -0.27229
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.002454 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.1546 | 63 | -0.0045382 | -0.28591
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.003489 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.39251 | 112.5 | -0.0055732 | -0.62699
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.009459 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.011543 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6445 | 204 | -0.015047 | -3.0696
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6056 | 201 | -0.015047 | -3.0245
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.137 | 242 | -0.015047 | -3.6414
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.014105 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.16926 | 0 | -0.016189 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.014105 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.16926 | 0 | -0.016189 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.02175 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.61 | 120 | -0.023834 | -2.8601
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.024081 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.8136 | 366 | -0.026165 | -9.5765
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.02985 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4775 | 150 | -0.031934 | -4.7901
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5982 | 20 | -0.031994 | -0.63988
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5982 | 20 | -0.031994 | -0.63988
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5982 | 20 | -0.031994 | -0.63988
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.50847 | 17 | -0.031994 | -0.5439
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.030974 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1107 | 165 | -0.033058 | -5.4546
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.031852 | west | 4 | Y | N | Ywest | Nwest | 1 | -20.6942 | 649.7 | -0.033936 | -22.0484
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.032223 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.034307 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.033151 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.8236 | 236 | -0.035235 | -8.3155
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.033173 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.2692 | 400 | -0.035257 | -14.1029
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.035119 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.95 | 84 | -0.037203 | -3.1251
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.035241 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6959 | 76.5 | -0.037325 | -2.8554
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.0353 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.824 | 80 | -0.037384 | -2.9907
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4277 | 209 | -0.037623 | -7.8633
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4957 | 126.5 | -0.037623 | -4.7593
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8492 | 249 | -0.037623 | -9.3682
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0012 | 197 | -0.037623 | -7.4118
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.035836 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3754 | 150 | -0.03792 | -5.688
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.035836 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3754 | 150 | -0.03792 | -5.688
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.035849 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8679 | 80 | -0.037933 | -3.0347
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035852 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8682 | 80 | -0.037936 | -3.0349
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6908 | 75 | -0.037961 | -2.8471
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8702 | 80 | -0.037961 | -3.0369
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4351 | 40 | -0.037961 | -1.5184
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035986 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8789 | 80 | -0.03807 | -3.0456
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035986 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8789 | 80 | -0.03807 | -3.0456
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.036359 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.17452 | 0 | -0.038443 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.036772 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5965 | 125 | -0.038856 | -4.857
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.036772 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5965 | 125 | -0.038856 | -4.857
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5888 | 150 | -0.039343 | -5.9015
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.197 | 220 | -0.039343 | -8.6555
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4518 | 200 | -0.039343 | -7.8686
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5419 | 121.9 | -0.039343 | -4.7959
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6097 | 70 | -0.039366 | -2.7556
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6097 | 70 | -0.039366 | -2.7556
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.4598 | 92.8 | -0.039366 | -3.6532
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9826 | 80 | -0.039366 | -3.1493
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9826 | 80 | -0.039366 | -3.1493
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.2874 | 115 | -0.039366 | -4.5271
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.7621 | 208.2 | -0.039366 | -8.196
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.2978 | 142.1 | -0.039366 | -5.5939
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.9361 | 132.4 | -0.039366 | -5.2121
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.0704 | 136 | -0.039366 | -5.3538
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.4805 | 147 | -0.039366 | -5.7868
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.8292 | 210 | -0.039366 | -8.2669
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4606 | 66 | -0.039366 | -2.5982
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4233 | 65 | -0.039366 | -2.5588
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4979 | 67 | -0.039366 | -2.6375
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4979 | 67 | -0.039366 | -2.6375
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4979 | 67 | -0.039366 | -2.6375
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.037282 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039366 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.037282 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039366 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 1 | -2.6107 | 0 | -0.039379 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 1 | -2.7375 | 0 | -0.039379 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 1 | -2.6256 | 0 | -0.039379 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.037389 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3086 | 35 | -0.039473 | -1.3816
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.037389 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1217 | 30 | -0.039473 | -1.1842
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.03764 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6084 | 149 | -0.039724 | -5.9189
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.037795 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6692 | 150 | -0.039879 | -5.9819
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2639 | 112.5 | -0.039985 | -4.4983
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6662 | 149.5 | -0.039985 | -5.9778
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0496 | 186 | -0.039985 | -7.4372
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1298 | 214.5 | -0.039985 | -8.5768
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4288 | 37.5 | -0.040185 | -1.5069
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0959 | 107.5 | -0.040185 | -4.3199
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1436 | 135 | -0.040185 | -5.425
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.534 | 119 | -0.040185 | -4.782
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0006 | 105 | -0.040185 | -4.2194
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0671 | 80.5 | -0.040185 | -3.2349
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.038236 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8427 | 100.5 | -0.04032 | -4.0522
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.038407 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2276 | 58 | -0.040491 | -2.3485
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.038533 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2538 | 214.2 | -0.040617 | -8.7002
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.039271 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.25919 | 6.6 | -0.041355 | -0.27294
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.039271 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.347 | 34.3 | -0.041355 | -1.4185
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.5942 | 66 | -0.04139 | -2.7318
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.7121 | 69 | -0.04139 | -2.8559
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.7121 | 69 | -0.04139 | -2.8559
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.6335 | 67 | -0.04139 | -2.7731
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.6335 | 67 | -0.04139 | -2.7731
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.5549 | 65 | -0.04139 | -2.6904
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.039409 | west | 8 | N | N | Nwest | Nwest | 1 | -1.0168 | 0 | -0.041493 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.039473 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7368 | 120 | -0.041557 | -4.9869
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.03966 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7592 | 120 | -0.041744 | -5.0093
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.040141 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.0317 | 225 | -0.042225 | -9.5007
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.04024 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2432 | 180 | -0.042324 | -7.6184
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.04024 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2432 | 180 | -0.042324 | -7.6184
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.041115 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5902 | 63 | -0.043199 | -2.7216
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.041248 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.816 | 141 | -0.043332 | -6.1098
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.041248 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9498 | 120 | -0.043332 | -5.1999
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.041309 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0896 | 99 | -0.043393 | -4.2959
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.041309 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5198 | 61 | -0.043393 | -2.647
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 1 | -1.0327 | 0 | -0.043393 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 1 | -1.8878 | 0 | -0.043393 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 1 | -1.8878 | 0 | -0.043393 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.042114 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.1383 | 169.5 | -0.044198 | -7.4916
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.042405 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.562 | 84 | -0.044489 | -3.7371
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.225 | 120 | -0.045626 | -5.4751
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.1453 | 233 | -0.045626 | -10.6309
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4108 | 170.2 | -0.045626 | -7.7656
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.047213 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0819 | 150 | -0.049297 | -7.3946
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.048808 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9285 | 60 | -0.050892 | -3.0535
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.0545 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.175 | 150 | -0.056584 | -8.4876
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.0545 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5045 | 101 | -0.056584 | -5.715
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.062441 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -15.1107 | 242 | -0.064525 | -15.6151
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.68669 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -41.2015 | 60 | -0.68878 | -41.3265

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:LINGLVLL - FLATCRK_ 138 kV 1640 - 1642 C: COMCHESS - SARC7A 345kV 1440 - 6444 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.68669 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -41.2015 | 0 | -0.68878 | 0 | 0 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | -0.062441 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -15.1107 | 242 | -0.064525 | -15.6151 | 242 | 15.6151
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | -0.0545 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.175 | 0 | -0.056584 | 0 | 242 | 15.6151
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | -0.0545 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5045 | 0 | -0.056584 | 0 | 242 | 15.6151 | Weighted Shift Factors
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | -0.048808 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.9285 | 0 | -0.050892 | 0 | 242 | 15.6151 | West | -0.037775
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | -0.047213 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0819 | 0 | -0.049297 | 0 | 242 | 15.6151 | North | 0.0020842
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.225 | 0 | -0.045626 | 0 | 242 | 15.6151 |  | -0.039859
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 1 | -10.1453 | 0 | -0.045626 | 0 | 242 | 15.6151
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | -0.043542 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4108 | 0 | -0.045626 | 0 | 242 | 15.6151 | Line Rating | 381.35
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | -0.042405 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.562 | 0 | -0.044489 | 0 | 242 | 15.6151 | Conc Gen | 711
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | -0.042114 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.1383 | 0 | -0.044198 | 0 | 242 | 15.6151 | Weighted Imp. | 34.8935
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | -0.041309 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0896 | 0 | -0.043393 | 0 | 242 | 15.6151 | PTDF | 0.049077
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | -0.041309 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5198 | 0 | -0.043393 | 0 | 242 | 15.6151
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 1 | -1.0327 | 0 | -0.043393 | 0 | 242 | 15.6151 | Concentration | -1.2313
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 1 | -1.8878 | 0 | -0.043393 | 0 | 242 | 15.6151
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | -0.041309 | west | 7 | N | N | Nwest | Nwest | 1 | -1.8878 | 0 | -0.043393 | 0 | 242 | 15.6151
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | -0.041248 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.816 | 0 | -0.043332 | 0 | 242 | 15.6151
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | -0.041248 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.9498 | 0 | -0.043332 | 0 | 242 | 15.6151
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | -0.041115 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.5902 | 0 | -0.043199 | 0 | 242 | 15.6151
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.04024 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2432 | 0 | -0.042324 | 0 | 242 | 15.6151
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | -0.04024 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.2432 | 0 | -0.042324 | 0 | 242 | 15.6151
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | -0.040141 | west | 6 | Y | N | Ywest | Nwest | 1 | -9.0317 | 0 | -0.042225 | 0 | 242 | 15.6151
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | -0.03966 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7592 | 0 | -0.041744 | 0 | 242 | 15.6151
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | -0.039473 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.7368 | 0 | -0.041557 | 0 | 242 | 15.6151
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | -0.039409 | west | 8 | N | N | Nwest | Nwest | 1 | -1.0168 | 0 | -0.041493 | 0 | 242 | 15.6151
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.5942 | 66 | -0.04139 | -2.7318 | 308 | 18.3469
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.7121 | 69 | -0.04139 | -2.8559 | 377 | 21.2028
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.7121 | 69 | -0.04139 | -2.8559 | 446 | 24.0587
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.6335 | 67 | -0.04139 | -2.7731 | 513 | 26.8318
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.6335 | 67 | -0.04139 | -2.7731 | 580 | 29.605
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | -0.039306 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.5549 | 65 | -0.04139 | -2.6904 | 645 | 32.2954
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | -0.039271 | west | 6 | Y | N | Ywest | Nwest | 1 | -0.25919 | 0 | -0.041355 | 0 | 645 | 32.2954
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | -0.039271 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.347 | 0 | -0.041355 | 0 | 645 | 32.2954
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | -0.038533 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.2538 | 0 | -0.040617 | 0 | 645 | 32.2954
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | -0.038407 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.2276 | 0 | -0.040491 | 0 | 645 | 32.2954
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | -0.038236 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.8427 | 0 | -0.04032 | 0 | 645 | 32.2954
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4288 | 0 | -0.040185 | 0 | 645 | 32.2954
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0959 | 0 | -0.040185 | 0 | 645 | 32.2954
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1436 | 0 | -0.040185 | 0 | 645 | 32.2954
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.534 | 0 | -0.040185 | 0 | 645 | 32.2954
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.0006 | 0 | -0.040185 | 0 | 645 | 32.2954
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | -0.038101 | west | 6 | Y | N | Ywest | Nwest | 1 | -3.0671 | 0 | -0.040185 | 0 | 645 | 32.2954
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.2639 | 0 | -0.039985 | 0 | 645 | 32.2954
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6662 | 0 | -0.039985 | 0 | 645 | 32.2954
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0496 | 0 | -0.039985 | 0 | 645 | 32.2954
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | -0.037901 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.1298 | 0 | -0.039985 | 0 | 645 | 32.2954
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | -0.037795 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6692 | 0 | -0.039879 | 0 | 645 | 32.2954
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | -0.03764 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.6084 | 0 | -0.039724 | 0 | 645 | 32.2954
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | -0.037389 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.3086 | 0 | -0.039473 | 0 | 645 | 32.2954
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | -0.037389 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.1217 | 0 | -0.039473 | 0 | 645 | 32.2954
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 1 | -2.6107 | 0 | -0.039379 | 0 | 645 | 32.2954
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 1 | -2.7375 | 0 | -0.039379 | 0 | 645 | 32.2954
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | -0.037295 | west | 8 | N | N | Nwest | Nwest | 1 | -2.6256 | 0 | -0.039379 | 0 | 645 | 32.2954
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4606 | 66 | -0.039366 | -2.5982 | 711 | 34.8935
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4233 | 65 | -0.039366 | -2.5588
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4979 | 67 | -0.039366 | -2.6375
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4979 | 67 | -0.039366 | -2.6375
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | -0.037282 | west | 13 | Y | Y | Ywest | Ywest | 1 | -2.4979 | 67 | -0.039366 | -2.6375
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | -0.037282 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039366 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | -0.037282 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.039366 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.7621 | 208.2 | -0.039366 | -8.196
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.2978 | 142.1 | -0.039366 | -5.5939
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.9361 | 132.4 | -0.039366 | -5.2121
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.0704 | 136 | -0.039366 | -5.3538
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -5.4805 | 147 | -0.039366 | -5.7868
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -7.8292 | 210 | -0.039366 | -8.2669
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6097 | 70 | -0.039366 | -2.7556
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.6097 | 70 | -0.039366 | -2.7556
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -3.4598 | 92.8 | -0.039366 | -3.6532
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9826 | 80 | -0.039366 | -3.1493
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -2.9826 | 80 | -0.039366 | -3.1493
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | -0.037282 | west | 9 | Y | Y | Ywest | Ywest | 1 | -4.2874 | 115 | -0.039366 | -4.5271
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.5888 | 0 | -0.039343 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.197 | 0 | -0.039343 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4518 | 0 | -0.039343 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | -0.037259 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5419 | 0 | -0.039343 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.036772 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5965 | 0 | -0.038856 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | -0.036772 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.5965 | 0 | -0.038856 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | -0.036359 | west | #N/A | N | N | Nwest | Nwest | 1 | -0.17452 | 0 | -0.038443 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035986 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8789 | 0 | -0.03807 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035986 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8789 | 0 | -0.03807 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6908 | 0 | -0.037961 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8702 | 0 | -0.037961 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | -0.035877 | west | 6 | Y | N | Ywest | Nwest | 1 | -1.4351 | 0 | -0.037961 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | -0.035852 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8682 | 0 | -0.037936 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | -0.035849 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.8679 | 0 | -0.037933 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | -0.035836 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3754 | 0 | -0.03792 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | -0.035836 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.3754 | 0 | -0.03792 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.4277 | 0 | -0.037623 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4957 | 0 | -0.037623 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -8.8492 | 0 | -0.037623 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | -0.035539 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.0012 | 0 | -0.037623 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | -0.0353 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.824 | 0 | -0.037384 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | -0.035241 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.6959 | 0 | -0.037325 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | -0.035119 | west | 6 | Y | N | Ywest | Nwest | 1 | -2.95 | 0 | -0.037203 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | -0.033173 | west | 6 | Y | N | Ywest | Nwest | 1 | -13.2692 | 0 | -0.035257 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | -0.033151 | west | 6 | Y | N | Ywest | Nwest | 1 | -7.8236 | 0 | -0.035235 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | -0.032223 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.034307 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | -0.031852 | west | 4 | Y | N | Ywest | Nwest | 1 | -20.6942 | 0 | -0.033936 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | -0.030974 | west | 6 | Y | N | Ywest | Nwest | 1 | -5.1107 | 0 | -0.033058 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5982 | 20 | -0.031994 | -0.63988
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5982 | 20 | -0.031994 | -0.63988
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.5982 | 20 | -0.031994 | -0.63988
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | -0.02991 | west | 9 | Y | Y | Ywest | Ywest | 1 | -0.50847 | 17 | -0.031994 | -0.5439
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | -0.02985 | west | 6 | Y | N | Ywest | Nwest | 1 | -4.4775 | 0 | -0.031934 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.024081 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -8.8136 | 366 | -0.026165 | -9.5765
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | -0.02175 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -2.61 | 0 | -0.023834 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | -0.014105 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.16926 | 0 | -0.016189 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | -0.014105 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.16926 | 0 | -0.016189 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6445 | 204 | -0.015047 | -3.0696
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.6056 | 201 | -0.015047 | -3.0245
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.012963 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -3.137 | 242 | -0.015047 | -3.6414
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.009459 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.011543 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | -0.003489 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.39251 | 0 | -0.0055732 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.002454 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.14724 | 60 | -0.0045382 | -0.27229
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.002454 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.1546 | 63 | -0.0045382 | -0.28591
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.001362 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034462 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.001362 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034462 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.001362 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0034462 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.000465 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0025492 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.000161 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00644 | 0 | -0.0022452 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.000161 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00644 | 0 | -0.0022452 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -8.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0021692 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -6.6e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.01122 | 170 | -0.0021502 | -0.36554
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -6.6e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.03432 | 520 | -0.0021502 | -1.1181
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0020842 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.0020842 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 5.6e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.02072 | 370 | -0.0020282 | -0.75044
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.00784 | 0 | -0.0020282 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.007896 | 0 | -0.0020282 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.017304 | 0 | -0.0020282 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.008008 | 0 | -0.0020282 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.008064 | 0 | -0.0020282 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 5.6e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.01736 | 0 | -0.0020282 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.01664 | 160 | -0.0019802 | -0.31683
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.016224 | 156 | -0.0019802 | -0.30891
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.020384 | 196 | -0.0019802 | -0.38812
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.016224 | 156 | -0.0019802 | -0.30891
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.016328 | 157 | -0.0019802 | -0.31089
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.000104 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.020592 | 198 | -0.0019802 | -0.39208
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.009975 | 0 | -0.0019512 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.010587 | 0 | -0.0019512 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.000133 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.011757 | 0 | -0.0019512 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.10769 | 0 | -0.0018912 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.11175 | 0 | -0.0018912 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.000193 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.15594 | 0 | -0.0018912 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.035155 | 79 | -0.0016392 | -0.1295
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04717 | 106 | -0.0016392 | -0.17376
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.000445 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.06497 | 146 | -0.0016392 | -0.23932
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.000445 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.03382 | 76 | -0.0016392 | -0.12458
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.00996 | 20 | -0.0015862 | -0.031724
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.01245 | 25 | -0.0015862 | -0.039655
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.000498 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.020418 | 41 | -0.0015862 | -0.065035
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.000516 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.02064 | 40 | -0.0015682 | -0.062728
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.00077 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.29876 | 388 | -0.0013142 | -0.50991
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.00077 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.39655 | 515 | -0.0013142 | -0.67682
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12735 | 161 | -0.0012932 | -0.20821
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12972 | 164 | -0.0012932 | -0.21209
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12972 | 164 | -0.0012932 | -0.21209
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.32747 | 414 | -0.0012932 | -0.53539
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12814 | 162 | -0.0012932 | -0.2095
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12735 | 161 | -0.0012932 | -0.20821
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.12893 | 163 | -0.0012932 | -0.21079
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.000791 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.32352 | 409 | -0.0012932 | -0.52892
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.000798 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.31521 | 395 | -0.0012862 | -0.50805
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.000798 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.34713 | 435 | -0.0012862 | -0.5595
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.000871 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.37889 | 435 | -0.0012132 | -0.52775
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000872 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012122 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000872 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0012122 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.001218 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.14372 | 118 | -0.00086621 | -0.10221
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.001218 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.14007 | 115 | -0.00086621 | -0.099614
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.001218 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.67721 | 556 | -0.00086621 | -0.48161
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1689 | 0 | -0.00059521 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1838 | 0 | -0.00059521 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.001489 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1614 | 0 | -0.00059521 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.23414 | 0 | -0.00050221 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.20566 | 0 | -0.00050221 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.22939 | 0 | -0.00050221 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.001582 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.63122 | 0 | -0.00050221 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.001655 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.00042921 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.001663 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.08315 | 0 | -0.00042121 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.001684 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.30649 | 182 | -0.00040021 | -0.072838
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.001684 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.81506 | 484 | -0.00040021 | -0.1937
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.002064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.44665 | 216.4 | -2.0208e-05 | -0.0043729
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.002064 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.44603 | 216.1 | -2.0208e-05 | -0.0043669
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35709 | 151.5 | 0.00027279 | 0.041328
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35897 | 152.3 | 0.00027279 | 0.041546
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.002357 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.41837 | 177.5 | 0.00027279 | 0.048421
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35776 | 150.7 | 0.00028979 | 0.043672
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.35847 | 151 | 0.00028979 | 0.043759
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.002374 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.42115 | 177.4 | 0.00028979 | 0.051409
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.002502 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.5387 | 0 | 0.00041779 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.002502 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.4687 | 0 | 0.00041779 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.81216 | 288 | 0.00073579 | 0.21191
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.41454 | 147 | 0.00073579 | 0.10816
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.00282 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.41454 | 147 | 0.00073579 | 0.10816
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.64758 | 224 | 0.00080679 | 0.18072
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.65337 | 226 | 0.00080679 | 0.18234
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61289 | 212 | 0.00080679 | 0.17104
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.002891 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.61 | 211 | 0.00080679 | 0.17023
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.002936 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4281 | 0 | 0.00085179 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.002936 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.4046 | 0 | 0.00085179 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.565 | 0 | 0.00091579 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 2.565 | 0 | 0.00091579 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.4569 | 0 | 0.00091579 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.003 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.459 | 0 | 0.00091579 | 0
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.003046 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.6823 | 224 | 0.00096179 | 0.21544
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.003161 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.4635 | 0 | 0.0010768 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.49174 | 0 | 0.0011048 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.49748 | 0 | 0.0011048 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.49748 | 0 | 0.0011048 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.003189 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.2118 | 0 | 0.0011048 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.003269 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.10461 | 0 | 0.0011848 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.00327 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.05559 | 17 | 0.0011858 | 0.020158
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.00327 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0011858 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | 1 | 0.3292 | 0 | 0.0012078 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.0033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.6468 | 196 | 0.0012158 | 0.2383
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.0033 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.3663 | 111 | 0.0012158 | 0.13495
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.00331 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15888 | 48 | 0.0012258 | 0.058838
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.00331 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.15226 | 46 | 0.0012258 | 0.056386
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.00331 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.34755 | 105 | 0.0012258 | 0.12871
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.81922 | 217.3 | 0.0016858 | 0.36632
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.77285 | 205 | 0.0016858 | 0.34559
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.00377 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.0269 | 272.4 | 0.0016858 | 0.45921
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.004139 | north | 3 | N | N | Nnorth | Nnorth | 1 | 4.7888 | 0 | 0.0020548 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.004139 | north | 3 | N | N | Nnorth | Nnorth | 1 | 4.793 | 0 | 0.0020548 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.004436 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0023518 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.005883 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0037988 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.005883 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.6299 | 787 | 0.0037988 | 2.9896
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.006314 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0042298 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.006314 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0042298 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.011117 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.8348 | 255 | 0.0090328 | 2.3034
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.011117 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.6564 | 149 | 0.0090328 | 1.3459
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.011117 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.7009 | 153 | 0.0090328 | 1.382
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.011578 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.9451 | 168 | 0.0094938 | 1.595
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.011578 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.042 | 90 | 0.0094938 | 0.85444
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2362 | 18 | 0.011038 | 0.19868
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.2362 | 18 | 0.011038 | 0.19868
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.013122 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.49864 | 38 | 0.011038 | 0.41944
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.015307 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.2961 | 150 | 0.013223 | 1.9834
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.015307 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 1.2246 | 80 | 0.013223 | 1.0578
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.016587 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2488 | 0 | 0.014503 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.016587 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.2488 | 0 | 0.014503 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4982 | 70 | 0.019319 | 1.3523
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4768 | 69 | 0.019319 | 1.333
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4768 | 69 | 0.019319 | 1.333
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.021403 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 1.4554 | 68 | 0.019319 | 1.3137
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.008922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.29443 | 0 | 0.028853 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.008922 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.22305 | 0 | 0.028853 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.008922 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028853 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.005575 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03345 | 0 | 0.0322 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.004796 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.032979 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.037775 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.037775 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.037775 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.001312 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.011021 | 8.4 | 0.039087 | 0.32833
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001627 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.039048 | 24 | 0.039402 | 0.94564
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.001627 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.039048 | 24 | 0.039402 | 0.94564
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.001627 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.037421 | 23 | 0.039402 | 0.90624
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.041732 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 3.0464 | 73 | 0.039648 | 2.8943
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.041732 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 4.9661 | 119 | 0.039648 | 4.7181
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.041732 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.5551 | 205 | 0.039648 | 8.1278
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.041732 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2567 | 102 | 0.039648 | 4.0441
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.041732 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.0063 | 96 | 0.039648 | 3.8062
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002203 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039978 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002204 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2204 | 100 | 0.039979 | 3.9979
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002204 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2204 | 100 | 0.039979 | 3.9979
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002204 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.039979 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | 0.002504 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040279 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033372 | 0 | 0.040556 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.030591 | 0 | 0.040556 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | 0.002781 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033372 | 0 | 0.040556 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | 0.003024 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040799 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4499 | 146.5 | 0.040846 | 5.9839
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.4542 | 147.9 | 0.040846 | 6.0411
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | 0.003071 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53128 | 173 | 0.040846 | 7.0663
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | 0.003094 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040869 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64584 | 207 | 0.040895 | 8.4652
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.6761 | 216.7 | 0.040895 | 8.8619
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.75504 | 242 | 0.040895 | 9.8965
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44928 | 144 | 0.040895 | 5.8888
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.44928 | 144 | 0.040895 | 5.8888
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | 0.00312 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.53352 | 171 | 0.040895 | 6.993
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.11962 | 38 | 0.040923 | 1.5551
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.060756 | 19.3 | 0.040923 | 0.78981
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | 0.003148 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.04722 | 15 | 0.040923 | 0.61384
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | 0.003148 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.14796 | 47 | 0.040923 | 1.9234
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | 0.003148 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.040923 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | 0.003154 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.249 | 0 | 0.040929 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.29695 | 0 | 0.040934 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12952 | 0 | 0.040934 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.12004 | 0 | 0.040934 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.060021 | 0 | 0.040934 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.29695 | 0 | 0.040934 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.11372 | 0 | 0.040934 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.13584 | 0 | 0.040934 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.069498 | 0 | 0.040934 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.46753 | 0 | 0.040934 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15795 | 0 | 0.040934 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.17375 | 0 | 0.040934 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | 0.003159 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.15795 | 0 | 0.040934 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | 0.003171 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.091959 | 0 | 0.040946 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | 0.00318 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12084 | 0 | 0.040955 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | 0.00318 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.18444 | 58 | 0.040955 | 2.3754
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | 0.00318 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.28302 | 89 | 0.040955 | 3.645
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.13992 | 44 | 0.040955 | 1.802
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.13992 | 44 | 0.040955 | 1.802
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.13674 | 43 | 0.040955 | 1.7611
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | 0.00318 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.1431 | 45 | 0.040955 | 1.843
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | 0.003183 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.079575 | 0 | 0.040958 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | 0.003183 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.079575 | 0 | 0.040958 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | 0.003184 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12099 | 0 | 0.040959 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | 0.003186 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0641 | 334 | 0.040961 | 13.6809
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | 0.003186 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.0832 | 340 | 0.040961 | 13.9266
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | 0.003186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57348 | 180 | 0.040961 | 7.3729
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | 0.003186 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57348 | 180 | 0.040961 | 7.3729
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47278 | 0 | 0.040963 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47374 | 0 | 0.040963 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | 0.003188 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.48776 | 0 | 0.040963 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0712 | 336 | 0.040963 | 13.7635
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57384 | 180 | 0.040963 | 7.3733
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | 0.003188 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57384 | 180 | 0.040963 | 7.3733
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 0 | 0.040972 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 0 | 0.040972 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 0 | 0.040972 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.051152 | 0 | 0.040972 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 0 | 0.040972 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 0 | 0.040972 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.079925 | 0 | 0.040972 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | 0.003197 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.047955 | 0 | 0.040972 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.50623 | 0 | 0.040979 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.49021 | 0 | 0.040979 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.3204 | 0 | 0.040979 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.46458 | 0 | 0.040979 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.47099 | 0 | 0.040979 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | 0.003204 | south | 8 | N | N | Nsouth | Nsouth | -1 | 0.40691 | 0 | 0.040979 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | 0.003204 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.038448 | 0 | 0.040979 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | 0.003242 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.071324 | 22 | 0.041017 | 0.90237
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003242 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035662 | 11 | 0.041017 | 0.45118
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | 0.003242 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.035662 | 11 | 0.041017 | 0.45118
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | 0.003251 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.0449 | 0 | 0.041026 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | 0.003258 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.326 | 407 | 0.041033 | 16.7003
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | 0.003281 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.68573 | 209 | 0.041056 | 8.5806
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | 0.003281 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.7087 | 216 | 0.041056 | 8.868
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15093 | 46 | 0.041056 | 1.8886
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15421 | 47 | 0.041056 | 1.9296
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15093 | 46 | 0.041056 | 1.8886
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | 0.003281 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.15093 | 46 | 0.041056 | 1.8886
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.1566 | 47.7 | 0.041058 | 1.9585
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.12246 | 37.3 | 0.041058 | 1.5315
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15102 | 46 | 0.041058 | 1.8887
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | 0.003283 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.15758 | 48 | 0.041058 | 1.9708
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | 0.003283 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3526 | 412 | 0.041058 | 16.9158
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | 0.003283 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3132 | 400 | 0.041058 | 16.4231
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.37529 | 0 | 0.041067 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.73082 | 0 | 0.041067 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.60573 | 0 | 0.041067 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.73741 | 0 | 0.041067 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | 0.003292 | south | 6 | Y | N | Ysouth | Nsouth | -1 | 0.37858 | 0 | 0.041067 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | 0.003297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.3979 | 0 | 0.041072 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | 0.003297 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.4012 | 0 | 0.041072 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | 0.003302 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.026416 | 0 | 0.041077 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.092596 | 0 | 0.041082 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.023149 | 0 | 0.041082 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12897 | 0 | 0.041082 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049605 | 0 | 0.041082 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.023149 | 0 | 0.041082 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049605 | 0 | 0.041082 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12897 | 0 | 0.041082 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.12897 | 0 | 0.041082 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.049605 | 0 | 0.041082 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | 0.003307 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.076061 | 0 | 0.041082 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | 0.003313 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.24185 | 0 | 0.041088 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | 0.003313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.47707 | 144 | 0.041088 | 5.9166
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | 0.003313 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.62284 | 188 | 0.041088 | 7.7245
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.57332 | 0 | 0.041089 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51698 | 0 | 0.041089 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51036 | 0 | 0.041089 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | 0.003314 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51036 | 0 | 0.041089 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | 0.003314 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53687 | 0 | 0.041089 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | 0.003326 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15965 | 0 | 0.041101 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19629 | 59 | 0.041102 | 2.425
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.19629 | 59 | 0.041102 | 2.425
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | 0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18631 | 56 | 0.041102 | 2.3017
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | 0.003328 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 1.3245 | 398 | 0.041103 | 16.3589
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.5418 | 0 | 0.041103 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.53714 | 0 | 0.041103 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.52882 | 0 | 0.041103 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | 0.003328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.8959 | 0 | 0.041103 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.57276 | 172 | 0.041105 | 7.07
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.57276 | 172 | 0.041105 | 7.07
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | 0.00333 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.57276 | 172 | 0.041105 | 7.07
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26307 | 0 | 0.041105 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26973 | 0 | 0.041105 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26307 | 0 | 0.041105 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.2664 | 0 | 0.041105 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.26107 | 0 | 0.041105 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.08325 | 0 | 0.041105 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.15318 | 0 | 0.041105 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.09324 | 0 | 0.041105 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.14519 | 0 | 0.041105 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | 0.00333 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0.24642 | 0 | 0.041105 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | 0.003331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52297 | 0 | 0.041106 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.016655 | 0 | 0.041106 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.069951 | 0 | 0.041106 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21652 | 0 | 0.041106 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21985 | 0 | 0.041106 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23317 | 0 | 0.041106 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20985 | 0 | 0.041106 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.20652 | 0 | 0.041106 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.34642 | 0 | 0.041106 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | 0.003331 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.19653 | 0 | 0.041106 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | 0.003331 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | 0.039972 | 0 | 0.041106 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | 0.003331 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.4749 | 743 | 0.041106 | 30.5415
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.003333 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.039996 | 12 | 0.041108 | 0.49329
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11332 | 0 | 0.041108 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11566 | 0 | 0.041108 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10899 | 0 | 0.041108 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15298 | 0 | 0.041108 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.058994 | 0 | 0.041108 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.067993 | 0 | 0.041108 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.066327 | 0 | 0.041108 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11665 | 0 | 0.041108 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.059994 | 0 | 0.041108 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.28464 | 0 | 0.041108 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | 0.003333 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49328 | 0 | 0.041108 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | 0.003334 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 2.4505 | 735 | 0.041109 | 30.2149
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34694 | 104 | 0.041111 | 4.2755
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.34694 | 104 | 0.041111 | 4.2755
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.17681 | 53 | 0.041111 | 2.1789
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19015 | 57 | 0.041111 | 2.3433
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.18014 | 54 | 0.041111 | 2.22
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19349 | 58 | 0.041111 | 2.3844
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | 0.003336 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.19349 | 58 | 0.041111 | 2.3844
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | 0.003338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.57747 | 0 | 0.041113 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | 0.003338 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.45063 | 0 | 0.041113 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.1402 | 42 | 0.041113 | 1.7267
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.1402 | 42 | 0.041113 | 1.7267
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.12684 | 38 | 0.041113 | 1.5623
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | 0.003338 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.12684 | 38 | 0.041113 | 1.5623
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | 0.003339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.4541 | 0 | 0.041114 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23714 | 0 | 0.041115 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24048 | 0 | 0.041115 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.13026 | 0 | 0.041115 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | 0.00334 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1002 | 0 | 0.041115 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.71163 | 213 | 0.041116 | 8.7576
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.054124 | 0 | 0.041116 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21382 | 0 | 0.041116 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21115 | 0 | 0.041116 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27597 | 0 | 0.041116 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2459 | 0 | 0.041116 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.76175 | 228 | 0.041116 | 9.3744
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.60138 | 0 | 0.041116 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52988 | 0 | 0.041116 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | 0.003341 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52454 | 0 | 0.041116 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | 0.003341 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.040092 | 12 | 0.041116 | 0.49339
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | 0.003341 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041116 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.56463 | 169 | 0.041116 | 6.9486
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | 0.003341 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.55127 | 165 | 0.041116 | 6.7841
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.49781 | 0 | 0.041116 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | 0.003341 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2175 | 0 | 0.041116 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | 0.003342 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11697 | 0 | 0.041117 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.54541 | 0 | 0.041117 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52503 | 0 | 0.041117 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52636 | 0 | 0.041117 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.52469 | 0 | 0.041117 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | 0.003342 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.899 | 0 | 0.041117 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | 0.003343 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.26075 | 0 | 0.041118 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | 0.003343 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.26744 | 0 | 0.041118 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15392 | 46 | 0.041121 | 1.8916
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15392 | 46 | 0.041121 | 1.8916
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.15392 | 46 | 0.041121 | 1.8916
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18403 | 55 | 0.041121 | 2.2616
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18403 | 55 | 0.041121 | 2.2616
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | 0.003346 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.18068 | 54 | 0.041121 | 2.2205
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.21749 | 0 | 0.041121 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.20076 | 0 | 0.041121 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.21749 | 0 | 0.041121 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | 0.003346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.21749 | 0 | 0.041121 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.30467 | 0 | 0.041123 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29328 | 0 | 0.041123 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29128 | 0 | 0.041123 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.18247 | 0 | 0.041123 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | 0.003348 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.040846 | 0 | 0.041123 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041125 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041125 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | 0.00335 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041125 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | 0.003352 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.041127 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52018 | 155 | 0.041131 | 6.3753
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.57052 | 170 | 0.041131 | 6.9922
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | 0.003356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52018 | 155 | 0.041131 | 6.3753
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | 0.003358 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.1679 | 50 | 0.041133 | 2.0566
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.33701 | 0 | 0.041135 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.31214 | 0 | 0.041135 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.34507 | 0 | 0.041135 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.34272 | 0 | 0.041135 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.10752 | 0 | 0.041135 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1008 | 0 | 0.041135 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23789 | 0 | 0.041135 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22411 | 0 | 0.041135 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.17808 | 0 | 0.041135 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51475 | 0 | 0.041135 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51576 | 0 | 0.041135 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.51173 | 0 | 0.041135 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.32256 | 0 | 0.041135 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | 0.00336 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.81984 | 0 | 0.041135 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | 0.00336 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1344 | 0 | 0.041135 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | 0.003366 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.8378 | 0 | 0.041141 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | 0.003366 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.5245 | 0 | 0.041141 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | 0.003371 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.11124 | 0 | 0.041146 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | 0.003374 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15554 | 0 | 0.041149 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.54386 | 161 | 0.041153 | 6.6256
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.56075 | 166 | 0.041153 | 6.8314
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | 0.003378 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | 0.83774 | 248 | 0.041153 | 10.2059
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | 0.003378 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | 1.8444 | 546 | 0.041153 | 22.4694
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | 0.003378 | houston | 1 | N | N | Nhouston | Nhouston | -1 | 2.1721 | 0 | 0.041153 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | 0.003378 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.043914 | 13 | 0.041153 | 0.53499
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 2.1991 | 0 | 0.041153 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 1.9052 | 0 | 0.041153 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | 0.003378 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | 2.0268 | 0 | 0.041153 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55061 | 0 | 0.041153 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.55061 | 0 | 0.041153 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | 0.003378 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.82761 | 0 | 0.041153 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37662 | 0 | 0.041168 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37662 | 0 | 0.041168 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.40377 | 0 | 0.041168 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | 0.003393 | houston | 8 | N | N | Nhouston | Nhouston | -1 | 0.37153 | 0 | 0.041168 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | 0.003396 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24112 | 0 | 0.041171 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | 0.003396 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.03396 | 0 | 0.041171 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21092 | 0 | 0.041177 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.2429 | 0 | 0.041177 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.15309 | 0 | 0.041177 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3436 | 0 | 0.041177 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29257 | 0 | 0.041177 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.29938 | 0 | 0.041177 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.1701 | 0 | 0.041177 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.061236 | 0 | 0.041177 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.31979 | 0 | 0.041177 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.23814 | 0 | 0.041177 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.21433 | 0 | 0.041177 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.24494 | 0 | 0.041177 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.22045 | 0 | 0.041177 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.3436 | 0 | 0.041177 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.32999 | 0 | 0.041177 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.35041 | 0 | 0.041177 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.25855 | 0 | 0.041177 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27216 | 0 | 0.041177 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.27216 | 0 | 0.041177 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | 0.003402 | houston | 7 | N | N | Nhouston | Nhouston | -1 | 0.58174 | 0 | 0.041177 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | 0.003422 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | 0.22585 | 66 | 0.041197 | 2.719
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | 0.003433 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 4.5762 | 0 | 0.041208 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | 0.003433 | houston | 3 | N | N | Nhouston | Nhouston | -1 | 4.559 | 0 | 0.041208 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26205 | 76 | 0.041223 | 3.1329
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.26205 | 76 | 0.041223 | 3.1329
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.36204 | 105 | 0.041223 | 4.3284
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25515 | 74 | 0.041223 | 3.0505
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.25515 | 74 | 0.041223 | 3.0505
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | 0.003448 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | 0.3517 | 102 | 0.041223 | 4.2047
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.517 | 147 | 0.041292 | 6.0699
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.48535 | 138 | 0.041292 | 5.6983
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.49238 | 140 | 0.041292 | 5.7808
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.517 | 147 | 0.041292 | 6.0699
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64009 | 182 | 0.041292 | 7.5151
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | 0.003517 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.69637 | 198 | 0.041292 | 8.1758
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | 0.003551 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.014204 | 0 | 0.041326 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | 0.003562 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.042744 | 0 | 0.041337 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.5129 | 142 | 0.041387 | 5.8769
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.52374 | 145 | 0.041387 | 6.0011
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.54541 | 151 | 0.041387 | 6.2494
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | 0.003612 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 1.0475 | 290 | 0.041387 | 12.0021
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0087312 | 0 | 0.041413 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0087312 | 0 | 0.041413 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | 0.003638 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.010186 | 0 | 0.041413 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | 0.003671 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0088104 | 0 | 0.041446 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | 0.003671 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0088104 | 0 | 0.041446 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.003701 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.050704 | 0 | 0.041476 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.83 | 223.9 | 0.041482 | 9.2878
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.83408 | 225 | 0.041482 | 9.3334
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.83259 | 224.6 | 0.041482 | 9.3168
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | 0.003707 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.84038 | 226.7 | 0.041482 | 9.4039
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | 0.003753 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.022518 | 0 | 0.041528 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.003759 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.5863 | 422 | 0.041534 | 17.5272
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003908 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.10942 | 0 | 0.041683 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003908 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.11333 | 0 | 0.041683 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.003911 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070398 | 0 | 0.041686 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.003911 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070398 | 0 | 0.041686 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | 0.004058 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 1.7571 | 0 | 0.041833 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | 0.00406 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.371 | 0 | 0.041835 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | 0.00406 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.4157 | 0 | 0.041835 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | 0.004095 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20475 | 50 | 0.04187 | 2.0935
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.64111 | 152.5 | 0.041979 | 6.4018
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.6285 | 149.5 | 0.041979 | 6.2758
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | 0.004204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.97785 | 232.6 | 0.041979 | 9.7642
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.66802 | 158 | 0.042003 | 6.6364
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.67648 | 160 | 0.042003 | 6.7204
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | 0.004228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.7399 | 175 | 0.042003 | 7.3505
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56126 | 132 | 0.042027 | 5.5475
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.56977 | 134 | 0.042027 | 5.6316
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | 0.004252 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3734 | 323 | 0.042027 | 13.5746
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14896 | 0 | 0.042031 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.1447 | 0 | 0.042031 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | 0.004256 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.14896 | 0 | 0.042031 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.2105 | 49 | 0.042071 | 2.0615
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19762 | 46 | 0.042071 | 1.9353
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19762 | 46 | 0.042071 | 1.9353
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20191 | 47 | 0.042071 | 1.9773
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | 0.004296 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.66158 | 154 | 0.042071 | 6.4789
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | 0.004296 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | 0.63581 | 148 | 0.042071 | 6.2265
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20621 | 48 | 0.042071 | 2.0194
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | 0.004296 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20621 | 48 | 0.042071 | 2.0194
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | 0.00433 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03464 | 0 | 0.042105 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | 0.00433 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.03464 | 0 | 0.042105 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | 0.004338 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.3448 | 310 | 0.042113 | 13.0549
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | 0.004338 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.7916 | 413 | 0.042113 | 17.3926
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.18358 | 42 | 0.042146 | 1.7701
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19232 | 44 | 0.042146 | 1.8544
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.19232 | 44 | 0.042146 | 1.8544
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | 0.004371 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | 0.20544 | 47 | 0.042146 | 1.9808
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084402 | 0 | 0.042464 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.084402 | 0 | 0.042464 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.004689 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.070335 | 0 | 0.042464 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.004863 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.767 | 0 | 0.042638 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.004863 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 2.8254 | 0 | 0.042638 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 416
| 25 | 413
| 30 | 409
| 35 | 406
| 40 | 403
| 45 | 399
| 50 | 395
| 55 | 392
| 60 | 388
| 65 | 384
| 70 | 380
| 75 | 376
| 80 | 373
| 85 | 369
| 90 | 365
| 95 | 360
| 100 | 356
| 105 | 352
| 110 | 348
| 115 | 343
| Max | 416
| Min | 343
| Avg | 381.35