## test results
CRE test for: |  | Leon Switch - Flatcreek 138kV 1624-1642 | [5 empty] | FAIL
Line Rating: |  | 96.8
Direction |  | West | → | North |  | W-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Leon Switch - Flatcreek 138kV 1624-1642
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.0013694
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.0041075
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.031097
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.0030021
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Leon Switch - Flatcreek 138kV 1624-1642
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.0008211
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.0040985
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.030679
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.002981
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Leon Switch - Flatcreek 138kV 1624-1642
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.002729
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.032048
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.0016116
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.034786
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.0011054
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.034078
PTDF tests
West | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | 0.031918 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.031918 | 0.002729
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.060787
[6 empty] | Concentration |  | 1.9045 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.044156
[6 empty] | Concentration |  | 1.3834 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 24.0834
| Percent of line rating => | [6 empty] | 24.88% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 25.4631
[7 empty] | B1(N-S) | -0.10962 | -0.040127 | 0.069489 | -0.10962
[7 empty] | B2 (N-W) | 0.0012743 | -0.81477 | -0.81604 | 0.0012743
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.06001 | -0.018975 | 0.041035 | -0.06001
[7 empty] | B4 (S-W) | 0.10999 | -0.77577 | -0.88576 | 0.10999
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.048172 | 0.020024 | -0.028148 | 0.048172
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.074793 | 0.79294 | 0.86773 | -0.074793
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | -13.49%
Deployment Error Percent | [6 empty] | B2 | 0.1568%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -7.384%
[7 empty] | B4 | 13.53%
[7 empty] | B5 | 5.927%
[7 empty] | B6 | -9.203%
[7 empty] | Max Abs Error | 13.53% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:Leon Switch - Flatcreek 138kV 1624-1642 C:Comanchee SS Auto 1440-1441 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:Leon Switch - Flatcreek 138kV 1624-1642 C:Comanchee SS Auto 1440-1441
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.010896 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -2.7785
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.010896 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -1.6235
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.016741 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.25111
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.016741 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.25111
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.010896 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -1.6671
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.015486 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -2.3229
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.015486 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -1.2389
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.044977 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -3.2833
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.044977 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -5.3523
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.044977 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -9.2203
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.044977 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -4.5877
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.044977 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -4.3178
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.01221 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.14652
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.01221 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.14652
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.009406 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -1.5802
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.009406 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -0.84654
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.25184
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.25184
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.53166
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -0.81936
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -0.41822
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -0.41822
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.004079 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 0.45889
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.001096 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 0.04384
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 0.091877
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 0.12328
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 0.1698
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.001163 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 0.088388
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.00375 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 0.225
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.00375 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 0.23625
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 0.0222
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 0.02775
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 0.04551
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.002303 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -1.0663
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 2.0003
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 1.97
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.0306
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.0306
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 2.0306
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.030307 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 3.455
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.030307 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 15.6081
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 2.1453
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.2428
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 2.2428
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.1778
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 2.1778
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 2.1128
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 2.1328
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 2.2364
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 2.1449
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 4.5674
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 6.6988
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034617 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 3.4271
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034617 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 2.1116
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.034552 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 4.8718
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.86542
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.582
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 1.582
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.034552 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 4.1462
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.032305 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.83347
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.031303 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 3.146
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.032566 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 3.9079
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.031499 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 1.8269
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.03164 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 6.7773
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.047455 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 7.1182
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.031641 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.20883
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.031641 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.0853
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.047455 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 4.793
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.032763 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 3.9316
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.022615 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 8.2771
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.059966 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 14.5118
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.028705 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 11.482
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.028688 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 6.7704
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.027231 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 4.4931
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 2.7118
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 2.6719
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 3.2169
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.56598
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.56598
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.56598
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.48108
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.019725 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 2.367
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.32207 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -19.3243
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 0.108
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 0.11462
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 0.1273
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 0.23536
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.22948
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 0.28832
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 0.22948
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 0.23095
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 0.29126
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.001608 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 0.27336
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.001608 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 0.83616
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.001516 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 0.56092
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 0.77674
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 0.80597
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 1.1247
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.002849 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 0.31909
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.002849 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 0.2849
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.002849 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 1.0769
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 0.23142
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 0.21832
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 0.29011
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.00096 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -0.7392
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -1.4183
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.398
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -1.398
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -1.3777
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.001106 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 1.2796
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.001106 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 1.2807
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -0.14784
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -0.14916
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.000191 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -0.041332
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.000191 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -0.041275
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -0.13992
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -0.13926
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.001234 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 0.48743
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.001108 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 0.48198
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.001234 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 0.53679
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.002008 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 0.2771
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.000556 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 0.065608
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.000556 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 0.06394
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.000556 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 0.30914
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.000877 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 0.34028
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.000877 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 0.45165
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 0.066725
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 0.067575
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 0.0663
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.000136 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -0.024752
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.000136 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -0.065824
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.001579 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -0.3537
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.000102 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.0051
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -9.4e-05 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.003948
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.001029 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -0.63284
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.001029 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -0.60402
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.005165 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -2.7736
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.005165 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -4.0649
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.005771 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.43283
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.005771 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -1.2812
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.005028 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -2.8609
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003872 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -0.80925
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003872 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -0.83635
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.00386 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -1.571
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.17811
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.18198
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.17811
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.17811
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.003888 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -1.6485
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.003888 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -1.6524
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003799 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.22034
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003799 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -0.33811
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.16716
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.16716
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.16336
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.17095
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.003876 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -1.5969
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.003876 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -1.5504
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.003918 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -2.1392
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.003918 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -2.9385
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.23924
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -0.37259
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -0.59222
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.60837
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -0.66725
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.60837
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.00358 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.07876
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.00358 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.03938
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.00358 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.03938
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.17253
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.13491
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.16638
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.17362
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.039672
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.036366
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.002531 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.060744
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.002531 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.060744
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.002531 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.058213
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.003683 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -1.4585
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.003373 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -4.4962
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.003373 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -4.4793
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.13505
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.068592
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.05331
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.003554 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.16704
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 2.1353
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.040971 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 6.1456
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.033018 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 5.5966
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.020878 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 3.1317
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.034374 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 2.1656
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.02855 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 18.5489
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.001682 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.06728
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.001682 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 0.06728
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.006615 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -2.7915
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.62608
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.63556
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -1.532
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -0.72554
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -0.73472
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -0.8036
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.00439 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -2.5638
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.00439 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -2.612
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.004388 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -1.9
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -0.94822
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -0.95288
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -0.95118
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -0.96007
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.00504 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.04032
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.00504 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.04032
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.15633
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.15633
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.13028
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.007305 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.10008
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.006284 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.11311
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.006284 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.11311
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.19369
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.18816
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.19369
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.006767 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.18948
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.006767 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.19624
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.030419 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.0647
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.030419 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.91257
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2241
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2241
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2241
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.2241
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.004431 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.026586
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.010039
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.010039
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.011712
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.004111 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.016444
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.004173 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.010015
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.004173 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.010015
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.59344
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -0.55711
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -0.56518
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.59344
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -0.73473
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -0.79933
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.70699
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.69308
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -1.0783
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -0.58717
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -0.59957
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -0.62438
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -1.1991
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.005582 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.18421
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.005582 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.13955
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.039672
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.00364 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.26572
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.28337
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -0.29055
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.10097
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.025242
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.28337
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -0.28696
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -0.28122
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.089675
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.165
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.003659 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -2.3015
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.003651 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -0.52574
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.003651 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -0.68639
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.004014 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.048168
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.003011 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.018066
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -1.2002
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003572 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -1.193
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003572 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -1.2145
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.003569 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.13562
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.08925
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.08925
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.003572 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.13574
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.003568 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.10347
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -0.52973
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -0.5308
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -0.54652
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -0.56438
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -0.54652
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -0.3572
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -0.51794
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -0.52508
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -0.45364
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -0.51319
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -0.51809
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -0.60602
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -0.73174
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -0.76603
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -0.85547
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.50904
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.50904
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -0.60449
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.004999 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -1.5497
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.004999 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -2.0646
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.21025
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.22026
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.22026
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.23528
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.24255
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.2277
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.2277
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.23265
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.7623
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.7326
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.2376
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.2376
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.1273
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 2.1273
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 2.8202
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.4312
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 2.4312
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 3.4949
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 6.327
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 4.3183
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 4.0235
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 4.1329
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 4.4672
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 6.3817
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 6.1538
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 3.7247
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 7.3316
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 5.8005
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 6.0898
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 3.7117
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.030686 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 4.5722
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.033455 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 6.0219
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.033455 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 6.0219
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.033348 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 7.5033
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.030257 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.7821
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.030257 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 3.7821
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 0.21224
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 0.21376
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 0.46844
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 0.21679
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 0.2183
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 0.46996
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.001622 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -0.31791
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.001622 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -0.18004
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.001681 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.13347
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.13596
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 0.13596
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 0.34321
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 0.1343
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 0.13347
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 0.13513
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 0.33906
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.000802 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.000802 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -0.002072
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -0.00182
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -0.00203
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -0.005586
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -0.13216
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -0.13243
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -0.15558
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -0.13074
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -0.13143
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -0.15318
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.005028 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -2.9213
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -1.645
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -1.645
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.002431 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.077792
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.002483 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.11918
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.002483 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.11422
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.029172
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.12398
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.002431 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.041327
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.053482
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.060775
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.002483 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -0.26071
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.035797 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 3.0069
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.028441 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 2.2753
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.028424 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.2636
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.028424 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 4.2636
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.2136
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.20123
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.1599
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -0.4622
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -0.46311
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -0.45949
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.28963
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -0.73615
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.12068
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.30271
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.28037
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.30995
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.30784
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.003018 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.096576
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.003018 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.09054
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.35087
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.35087
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.37616
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.34613
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -0.29303
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -0.29437
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.002929 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.39834
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.10114
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.12298
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.12298
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.11126
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.11126
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.003183 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.22599
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.003183 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.03183
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.50155
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.50155
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -0.75387
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.19253
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.17772
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.19253
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.19253
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00294 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.43806
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00294 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.19139
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.27009
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.26
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.25822
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.16176
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.03621
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.0029 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -2.1547
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.002912 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -2.1403
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.49828
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.49828
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.49828
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.49045
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002926 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -0.5062
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.002926 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.39501
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.47033
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.46628
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.45906
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -0.77772
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.1881
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.18574
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.24276
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.21631
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.48079
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.46282
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.46399
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.46252
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -0.79247
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.014505
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.060921
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.36946
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.37378
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.37378
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -0.91048
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.002887 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -1.149
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.13584
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.13584
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.13584
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.16242
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.16242
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.15946
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.001774 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -1.4671
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.001774 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -1.4529
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.003078 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.1419
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.25642
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.25642
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.35427
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.24968
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.24968
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.34415
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -0.52902
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.46613
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.46142
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.002944 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.10304
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.002985 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -1.3701
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.18857
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.19147
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.20307
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.18276
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.17986
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.3017
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.17116
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.44226
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.43659
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.43659
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.002835 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.45927
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.002899 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.45514
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.20838
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.21132
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.11446
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.08805
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.002949 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.23002
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.002949 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.23592
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.047612
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.00294 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.4851
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.00294 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -0.49686
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.002939 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -0.62601
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.002939 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -0.67009
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.002941 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.035292
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.002941 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.052938
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.003 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.15
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.30326
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.30326
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15746
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.15455
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15746
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.16621
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15746
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.15746
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.16913
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.16913
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.002906 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.034872
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.16139
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.17004
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.16139
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.16139
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.17004
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.16139
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.21958
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -0.49346
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -0.50879
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -0.76012
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.003065 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -1.6735
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.003065 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -1.9708
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -2.0031
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -1.7354
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -1.8462
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.003065 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.039845
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.002901 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.034812
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.098906
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.10094
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.095124
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.13352
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.051489
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.059344
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.057889
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.10182
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.052362
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.24843
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.43053
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.19914
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.22934
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.14454
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.32441
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.27623
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.28266
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.1606
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.057816
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.30193
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.22484
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.20236
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.23126
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.20814
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.32441
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.31156
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.33084
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.24411
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.25696
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.25696
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -0.54925
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.019244
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.027621 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 2.113
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 2.2777
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.1388
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.028597 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.2878
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.028445 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 2.2756
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.02778 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 2.2224
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.027563 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 2.3153
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.028597 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 2.2878
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -0.46398
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 4.2311
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 8.2153
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 6.0011
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -0.90354
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -0.74888
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -0.91168
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -0.46805
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -0.407
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.043174 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 2.5904
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.004475 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.024129 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.029105 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.1397
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 1.1863
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 3.4008
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 4.2707
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 3.7646
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 3.3217
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 2.5466
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.029123 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 4.3685
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 3.247
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 4.3149
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 5.3683
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 6.1909
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.003554 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.002413 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.002928 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.10044
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.15639
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -0.26544
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.33473
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.146
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.13532
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.067659
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.33473
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.1282
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.15312
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.078342
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.14063
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.05409
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.025242
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.05409
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.14063
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.14063
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -0.52703
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.17805
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.19586
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.17805
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.003572 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.042864
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.003617 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.054255
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.003617 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.083191
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.17246
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.028848
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -0.64296
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -0.64296
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.64296
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.64296
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.002929 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.2929
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.002929 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.2929
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.089275
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.089275
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.089275
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.057136
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.089275
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.089275
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.089275
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.053565
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.002929 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.002929 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -1.4645
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.002929 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -1.4645
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.002929 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.003561 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.005582 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.003118 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.003481 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:Leon Switch - Flatcreek 138kV 1624-1642 C:Comanchee SS Auto 1440-1441 | [7 empty] | 24.0834
Number of Bus | Name of Bus | ID | Max MW | L:Leon Switch - Flatcreek 138kV 1624-1642 C:Comanchee SS Auto 1440-1441 | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.010896 | north | Y | -0.0095266 | -0.0067885 | -0.041993 | -0.0078939 | 0.0067885 | south | Y | 0.0095266 | 0.6982
239 | BOSQUESW | 1 | 149 | -0.010896 | north | Y | -0.0095266 | -0.0067885 | -0.041993 | -0.0078939 | 0.0067885 | south | Y | 0.0095266 | 0.40797
244 | WHITNYDM | 1 | 15 | -0.016741 | north | N | -0.015372 | -0.012634 | -0.047838 | -0.013739 | 0.012634 | south | Y | 0.015372 | 0
245 | WHITNYDM | 2 | 15 | -0.016741 | north | N | -0.015372 | -0.012634 | -0.047838 | -0.013739 | 0.012634 | south | Y | 0.015372 | 0
247 | BOSQUESW | 2 | 153 | -0.010896 | north | Y | -0.0095266 | -0.0067885 | -0.041993 | -0.0078939 | 0.0067885 | south | Y | 0.0095266 | 0.41892
251 | BOSQUESW | 2 | 150 | -0.015486 | north | Y | -0.014117 | -0.011379 | -0.046583 | -0.012484 | 0.011379 | south | Y | 0.014117 | 0.41071
253 | BOSQUESW | 2 | 80 | -0.015486 | north | Y | -0.014117 | -0.011379 | -0.046583 | -0.012484 | 0.011379 | south | Y | 0.014117 | 0.21904
332 | RWMILLER | 1 | 73 | -0.044977 | north | Y | -0.043608 | -0.04087 | -0.076074 | -0.041975 | 0.04087 | south | Y | 0.043608 | 0.19988
333 | RWMILLER | 2 | 119 | -0.044977 | north | Y | -0.043608 | -0.04087 | -0.076074 | -0.041975 | 0.04087 | south | Y | 0.043608 | 0.32583
334 | RWMILLER | 3 | 205 | -0.044977 | north | Y | -0.043608 | -0.04087 | -0.076074 | -0.041975 | 0.04087 | south | Y | 0.043608 | 0.5613
335 | RWMILLER | 4 | 102 | -0.044977 | north | Y | -0.043608 | -0.04087 | -0.076074 | -0.041975 | 0.04087 | south | Y | 0.043608 | 0.27928
336 | RWMILLER | 5 | 96 | -0.044977 | north | Y | -0.043608 | -0.04087 | -0.076074 | -0.041975 | 0.04087 | south | Y | 0.043608 | 0.26285
344 | MRSSHPRD | 1 | 12 | 0.01221 | north | N | 0.013579 | 0.016317 | -0.018887 | 0.015212 | 0.013579 | North | N | 0.013579 | 0
345 | MRSSHPRD | 2 | 12 | 0.01221 | north | N | 0.013579 | 0.016317 | -0.018887 | 0.015212 | 0.013579 | North | N | 0.013579 | 0
366 | JNSNCNTY | 1 | 168 | -0.009406 | north | Y | -0.0080366 | -0.0052985 | -0.040503 | -0.0064039 | 0.0052985 | south | Y | 0.0080366 | 0.45999
367 | JNSNCNTY | 2 | 90 | -0.009406 | north | Y | -0.0080366 | -0.0052985 | -0.040503 | -0.0064039 | 0.0052985 | south | Y | 0.0080366 | 0.24642
503 | NTHTEXAS | 1 | 18 | -0.013991 | north | Y | -0.012622 | -0.0098835 | -0.045088 | -0.010989 | 0.0098835 | south | Y | 0.012622 | 0.049285
504 | NTHTEXAS | 2 | 18 | -0.013991 | north | Y | -0.012622 | -0.0098835 | -0.045088 | -0.010989 | 0.0098835 | south | Y | 0.012622 | 0.049285
505 | NTHTEXAS | 3 | 38 | -0.013991 | north | Y | -0.012622 | -0.0098835 | -0.045088 | -0.010989 | 0.0098835 | south | Y | 0.012622 | 0.10405
580 | JCKCNTY8 | 1 | 288 | -0.002845 | north | Y | -0.0014756 | 0.0012625 | -0.033942 | 0.00015706 | 0.00015706 | houston | Y | 0.0014756 | 0.37973
581 | JCKCNTY8 | 2 | 147 | -0.002845 | north | Y | -0.0014756 | 0.0012625 | -0.033942 | 0.00015706 | 0.00015706 | houston | Y | 0.0014756 | 0.19382
582 | JCKCNTY8 | 3 | 147 | -0.002845 | north | Y | -0.0014756 | 0.0012625 | -0.033942 | 0.00015706 | 0.00015706 | houston | Y | 0.0014756 | 0.19382
728 | WOLFRIDG | 1 | 112.5 | 0.004079 | north | Y | 0.0054484 | 0.0081865 | -0.027018 | 0.0070811 | 0.0054484 | North | N | 0.0054484 | 0
837 | NEWMAN_G | 1 | 40 | 0.001096 | north | Y | 0.0024654 | 0.0052035 | -0.030001 | 0.0040981 | 0.0024654 | North | N | 0.0024654 | 0
842 | OLINGER_ | 1 | 79 | 0.001163 | north | Y | 0.0025324 | 0.0052705 | -0.029934 | 0.0041651 | 0.0025324 | North | N | 0.0025324 | 0
843 | OLINGER_ | 1 | 106 | 0.001163 | north | Y | 0.0025324 | 0.0052705 | -0.029934 | 0.0041651 | 0.0025324 | North | N | 0.0025324 | 0
844 | OLINGER_ | 1 | 146 | 0.001163 | north | Y | 0.0025324 | 0.0052705 | -0.029934 | 0.0041651 | 0.0025324 | North | N | 0.0025324 | 0
845 | OLINGER_ | 1 | 76 | 0.001163 | north | Y | 0.0025324 | 0.0052705 | -0.029934 | 0.0041651 | 0.0025324 | North | N | 0.0025324 | 0
923 | SPENCER_ | 1 | 60 | 0.00375 | north | Y | 0.0051194 | 0.0078575 | -0.027347 | 0.0067521 | 0.0051194 | North | N | 0.0051194 | 0
924 | SPENCER_ | 1 | 63 | 0.00375 | north | Y | 0.0051194 | 0.0078575 | -0.027347 | 0.0067521 | 0.0051194 | North | N | 0.0051194 | 0
948 | STEAM1 | 1 | 20 | 0.00111 | north | Y | 0.0024794 | 0.0052175 | -0.029987 | 0.0041121 | 0.0024794 | North | N | 0.0024794 | 0
949 | STEAM2 | 1 | 25 | 0.00111 | north | Y | 0.0024794 | 0.0052175 | -0.029987 | 0.0041121 | 0.0024794 | North | N | 0.0024794 | 0
950 | STEAM3 | 1 | 41 | 0.00111 | north | Y | 0.0024794 | 0.0052175 | -0.029987 | 0.0041121 | 0.0024794 | North | N | 0.0024794 | 0
990 | GIBN_CRE | 1 | 463 | -0.002303 | north | Y | -0.00093356 | 0.0018045 | -0.0334 | 0.00069906 | 0.00069906 | houston | Y | 0.00093356 | 0.10857
1002 | PBCTAGE_ | A | 66 | 0.030307 | west | Y | 0.031676 | 0.034414 | -0.00078993 | 0.033309 | 0.00078993 | west | N | 0.00078993 | 0
1003 | PBCTBGE_ | B | 65 | 0.030307 | west | Y | 0.031676 | 0.034414 | -0.00078993 | 0.033309 | 0.00078993 | west | N | 0.00078993 | 0
1004 | PBCTCGE_ | C | 67 | 0.030307 | west | Y | 0.031676 | 0.034414 | -0.00078993 | 0.033309 | 0.00078993 | west | N | 0.00078993 | 0
1005 | PBCTDGE_ | D | 67 | 0.030307 | west | Y | 0.031676 | 0.034414 | -0.00078993 | 0.033309 | 0.00078993 | west | N | 0.00078993 | 0
1006 | PBCTEGE_ | E | 67 | 0.030307 | west | Y | 0.031676 | 0.034414 | -0.00078993 | 0.033309 | 0.00078993 | west | N | 0.00078993 | 0
1007 | PB5GEN_6 | MB | 114 | 0.030307 | west | Y | 0.031676 | 0.034414 | -0.00078993 | 0.033309 | 0.00078993 | west | N | 0.00078993 | 0
1008 | PB6GEN_7 | MB | 515 | 0.030307 | west | Y | 0.031676 | 0.034414 | -0.00078993 | 0.033309 | 0.00078993 | west | N | 0.00078993 | 0
1039 | MRGNAG_1 | A | 66 | 0.032504 | west | Y | 0.033873 | 0.036611 | 0.0014071 | 0.035506 | 0.0014071 | west | N | 0.0014071 | 0
1040 | MRGNBG_2 | B | 69 | 0.032504 | west | Y | 0.033873 | 0.036611 | 0.0014071 | 0.035506 | 0.0014071 | west | N | 0.0014071 | 0
1041 | MRGNCG_3 | C | 69 | 0.032504 | west | Y | 0.033873 | 0.036611 | 0.0014071 | 0.035506 | 0.0014071 | west | N | 0.0014071 | 0
1042 | MRGNDG_4 | D | 67 | 0.032504 | west | Y | 0.033873 | 0.036611 | 0.0014071 | 0.035506 | 0.0014071 | west | N | 0.0014071 | 0
1043 | MRGNEG_5 | E | 67 | 0.032504 | west | Y | 0.033873 | 0.036611 | 0.0014071 | 0.035506 | 0.0014071 | west | N | 0.0014071 | 0
1044 | MRGNFG_6 | F | 65 | 0.032504 | west | Y | 0.033873 | 0.036611 | 0.0014071 | 0.035506 | 0.0014071 | west | N | 0.0014071 | 0
1045 | CALENG1G | 1 | 70 | 0.030468 | west | N | 0.031837 | 0.034575 | -0.00062893 | 0.03347 | 0.00062893 | west | N | 0.00062893 | 0
1046 | CALENG2G | 2 | 73.4 | 0.030468 | west | N | 0.031837 | 0.034575 | -0.00062893 | 0.03347 | 0.00062893 | west | N | 0.00062893 | 0
1047 | CALENG3G | 3 | 70.4 | 0.030468 | west | N | 0.031837 | 0.034575 | -0.00062893 | 0.03347 | 0.00062893 | west | N | 0.00062893 | 0
1058 | LONGSHOR | 1 | 150 | 0.030449 | west | Y | 0.031818 | 0.034556 | -0.00064793 | 0.033451 | 0.00064793 | west | N | 0.00064793 | 0
1058 | LONGSHOR | 2 | 220 | 0.030449 | west | Y | 0.031818 | 0.034556 | -0.00064793 | 0.033451 | 0.00064793 | west | N | 0.00064793 | 0
1061 | CIELOGEN | 1 | 99 | 0.034617 | west | Y | 0.035986 | 0.038724 | 0.0035201 | 0.037619 | 0.0035201 | west | N | 0.0035201 | 0
1062 | CIELOGEN | 1 | 61 | 0.034617 | west | Y | 0.035986 | 0.038724 | 0.0035201 | 0.037619 | 0.0035201 | west | N | 0.0035201 | 0
1068 | SCURRYCW | 1 | 141 | 0.034552 | west | Y | 0.035921 | 0.038659 | 0.0034551 | 0.037554 | 0.0034551 | west | N | 0.0034551 | 0
1069 | KINDERMG | 1 | 25 | 0.034617 | west | N | 0.035986 | 0.038724 | 0.0035201 | 0.037619 | 0.0035201 | west | N | 0.0035201 | 0
1070 | KINDERMG | 1 | 45.7 | 0.034617 | west | N | 0.035986 | 0.038724 | 0.0035201 | 0.037619 | 0.0035201 | west | N | 0.0035201 | 0
1071 | KINDERMG | 1 | 45.7 | 0.034617 | west | N | 0.035986 | 0.038724 | 0.0035201 | 0.037619 | 0.0035201 | west | N | 0.0035201 | 0
1073 | SCURRYCW | 2 | 120 | 0.034552 | west | Y | 0.035921 | 0.038659 | 0.0034551 | 0.037554 | 0.0034551 | west | N | 0.0034551 | 0
1320 | BSP 1 | 1 | 25.8 | 0.032305 | west | N | 0.033674 | 0.036412 | 0.0012081 | 0.035307 | 0.0012081 | west | N | 0.0012081 | 0
1326 | STANTONW | 1 | 100.5 | 0.031303 | west | Y | 0.032672 | 0.03541 | 0.00020607 | 0.034305 | 0.00020607 | west | N | 0.00020607 | 0
1327 | WILDHRSE | 1 | 120 | 0.032566 | west | Y | 0.033935 | 0.036673 | 0.0014691 | 0.035568 | 0.0014691 | west | N | 0.0014691 | 0
1328 | OCOTILLO | 1 | 58 | 0.031499 | west | Y | 0.032868 | 0.035606 | 0.00040207 | 0.034501 | 0.00040207 | west | N | 0.00040207 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.03164 | west | Y | 0.033009 | 0.035747 | 0.00054307 | 0.034642 | 0.00054307 | west | N | 0.00054307 | 0
1343 | TRENTIPP | 1 | 150 | 0.047455 | west | Y | 0.048824 | 0.051562 | 0.016358 | 0.050457 | 0.016358 | west | N | 0.016358 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.031641 | west | Y | 0.03301 | 0.035748 | 0.00054407 | 0.034643 | 0.00054407 | west | N | 0.00054407 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.031641 | west | Y | 0.03301 | 0.035748 | 0.00054407 | 0.034643 | 0.00054407 | west | N | 0.00054407 | 0
1354 | AEPWIND_ | 1 | 101 | 0.047455 | west | Y | 0.048824 | 0.051562 | 0.016358 | 0.050457 | 0.016358 | west | N | 0.016358 | 0
1360 | GUNSIGHT | 1 | 120 | 0.032763 | west | Y | 0.034132 | 0.03687 | 0.0016661 | 0.035765 | 0.0016661 | west | N | 0.0016661 | 0
1432 | GRHAMSES | 2 | 366 | 0.022615 | north | Y | 0.023984 | 0.026722 | -0.0084819 | 0.025617 | 0.0084819 | west | Y | 0.023984 | 5.6739
1433 | GRHAMSES | 1 | 242 | 0.059966 | north | Y | 0.061335 | 0.064073 | 0.028869 | 0.062968 | 0.028869 | west | Y | 0.061335 | 7.8569
1437 | MESQUITW | 1 | 400 | 0.028705 | west | Y | 0.030074 | 0.032812 | -0.0023919 | 0.031707 | 0.0023919 | west | N | 0.0023919 | 0
1438 | MESQUITW | 1 | 236 | 0.028688 | west | Y | 0.030057 | 0.032795 | -0.0024089 | 0.03169 | 0.0024089 | west | N | 0.0024089 | 0
1442 | COKFIELD | 1 | 165 | 0.027231 | west | Y | 0.0286 | 0.031338 | -0.0038659 | 0.030233 | 0.0038659 | west | N | 0.0038659 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.013293 | north | Y | 0.014662 | 0.0174 | -0.017804 | 0.016295 | 0.014662 | North | N | 0.014662 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.013293 | north | Y | 0.014662 | 0.0174 | -0.017804 | 0.016295 | 0.014662 | North | N | 0.014662 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.013293 | north | Y | 0.014662 | 0.0174 | -0.017804 | 0.016295 | 0.014662 | North | N | 0.014662 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.028299 | west | Y | 0.029668 | 0.032406 | -0.0027979 | 0.031301 | 0.0027979 | west | N | 0.0027979 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.028299 | west | Y | 0.029668 | 0.032406 | -0.0027979 | 0.031301 | 0.0027979 | west | N | 0.0027979 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.028299 | west | Y | 0.029668 | 0.032406 | -0.0027979 | 0.031301 | 0.0027979 | west | N | 0.0027979 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.028299 | west | Y | 0.029668 | 0.032406 | -0.0027979 | 0.031301 | 0.0027979 | west | N | 0.0027979 | 0
1600 | BARTNWND | 1 | 120 | 0.019725 | north | Y | 0.021094 | 0.023832 | -0.011372 | 0.022727 | 0.011372 | west | Y | 0.021094 | 1.1667
1643 | SLSTR1PP | 1 | 60 | -0.32207 | north | Y | -0.3207 | -0.31796 | -0.35317 | -0.31907 | 0.31796 | south | Y | 0.3207 | 0.16428
1675 | PEC_1G | 1 | 75 | 0.00144 | north | N | 0.0028094 | 0.0055475 | -0.029657 | 0.0044421 | 0.0028094 | North | N | 0.0028094 | 0
1676 | PEC_2G | 2 | 79.6 | 0.00144 | north | N | 0.0028094 | 0.0055475 | -0.029657 | 0.0044421 | 0.0028094 | North | N | 0.0028094 | 0
1677 | PEC_3G | 3 | 88.4 | 0.00144 | north | N | 0.0028094 | 0.0055475 | -0.029657 | 0.0044421 | 0.0028094 | North | N | 0.0028094 | 0
1678 | LAMARPWR | 1 | 160 | 0.001471 | north | Y | 0.0028404 | 0.0055785 | -0.029626 | 0.0044731 | 0.0028404 | North | N | 0.0028404 | 0
1679 | LAMARPWR | 2 | 156 | 0.001471 | north | Y | 0.0028404 | 0.0055785 | -0.029626 | 0.0044731 | 0.0028404 | North | N | 0.0028404 | 0
1680 | LAMARPWR | 3 | 196 | 0.001471 | north | Y | 0.0028404 | 0.0055785 | -0.029626 | 0.0044731 | 0.0028404 | North | N | 0.0028404 | 0
1681 | LAMARPWR | 4 | 156 | 0.001471 | north | Y | 0.0028404 | 0.0055785 | -0.029626 | 0.0044731 | 0.0028404 | North | N | 0.0028404 | 0
1682 | LAMARPWR | 5 | 157 | 0.001471 | north | Y | 0.0028404 | 0.0055785 | -0.029626 | 0.0044731 | 0.0028404 | North | N | 0.0028404 | 0
1683 | LAMARPWR | 6 | 198 | 0.001471 | north | Y | 0.0028404 | 0.0055785 | -0.029626 | 0.0044731 | 0.0028404 | North | N | 0.0028404 | 0
1687 | VALLEY_1 | 1 | 170 | 0.001608 | north | Y | 0.0029774 | 0.0057155 | -0.029489 | 0.0046101 | 0.0029774 | North | N | 0.0029774 | 0
1688 | VALLEY_2 | 2 | 520 | 0.001608 | north | Y | 0.0029774 | 0.0057155 | -0.029489 | 0.0046101 | 0.0029774 | North | N | 0.0029774 | 0
1689 | VALLEY_3 | 3 | 370 | 0.001516 | north | Y | 0.0028854 | 0.0056235 | -0.029581 | 0.0045181 | 0.0028854 | North | N | 0.0028854 | 0
1701 | MOSES_1G | 1 | 558 | 0.001392 | north | Y | 0.0027614 | 0.0054995 | -0.029705 | 0.0043941 | 0.0027614 | North | N | 0.0027614 | 0
1702 | MOSES_2G | 2 | 579 | 0.001392 | north | Y | 0.0027614 | 0.0054995 | -0.029705 | 0.0043941 | 0.0027614 | North | N | 0.0027614 | 0
1703 | MOSES_3G | 3 | 808 | 0.001392 | north | Y | 0.0027614 | 0.0054995 | -0.029705 | 0.0043941 | 0.0027614 | North | N | 0.0027614 | 0
1861 | EAGLEMNT | MB | 112 | 0.002849 | north | Y | 0.0042184 | 0.0069565 | -0.028248 | 0.0058511 | 0.0042184 | North | N | 0.0042184 | 0
1862 | EAGLEMNT | MB | 100 | 0.002849 | north | Y | 0.0042184 | 0.0069565 | -0.028248 | 0.0058511 | 0.0042184 | North | N | 0.0042184 | 0
1863 | EAGLEMNT | MB | 378 | 0.002849 | north | Y | 0.0042184 | 0.0069565 | -0.028248 | 0.0058511 | 0.0042184 | North | N | 0.0042184 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.001065 | north | Y | 0.0024344 | 0.0051725 | -0.030032 | 0.0040671 | 0.0024344 | North | N | 0.0024344 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.001065 | north | Y | 0.0024344 | 0.0051725 | -0.030032 | 0.0040671 | 0.0024344 | North | N | 0.0024344 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.001065 | north | Y | 0.0024344 | 0.0051725 | -0.030032 | 0.0040671 | 0.0024344 | North | N | 0.0024344 | 0
1889 | DECRDOVA | MB | 770 | -0.00096 | north | Y | 0.00040944 | 0.0031475 | -0.032057 | 0.0020421 | 0.00040944 | North | N | 0.00040944 | 0
1892 | DECRDOVA | A | 70 | -0.020261 | north | Y | -0.018892 | -0.016154 | -0.051358 | -0.017259 | 0.016154 | south | Y | 0.018892 | 0.19166
1893 | DECRDOVA | B | 69 | -0.020261 | north | Y | -0.018892 | -0.016154 | -0.051358 | -0.017259 | 0.016154 | south | Y | 0.018892 | 0.18892
1894 | DECRDOVA | C | 69 | -0.020261 | north | Y | -0.018892 | -0.016154 | -0.051358 | -0.017259 | 0.016154 | south | Y | 0.018892 | 0.18892
1895 | DECRDOVA | D | 68 | -0.020261 | north | Y | -0.018892 | -0.016154 | -0.051358 | -0.017259 | 0.016154 | south | Y | 0.018892 | 0.18619
1898 | COMCHEPK | 1 | 1157 | 0.001106 | north | N | 0.0024754 | 0.0052135 | -0.029991 | 0.0041081 | 0.0024754 | North | N | 0.0024754 | 0
1899 | COMCHEPK | 2 | 1158 | 0.001106 | north | N | 0.0024754 | 0.0052135 | -0.029991 | 0.0041081 | 0.0024754 | North | N | 0.0024754 | 0
1937 | MDLTHELP | 5 | 224 | -0.00066 | north | Y | 0.00070944 | 0.0034475 | -0.031757 | 0.0023421 | 0.00070944 | North | N | 0.00070944 | 0
1938 | MDLTHELP | 6 | 226 | -0.00066 | north | Y | 0.00070944 | 0.0034475 | -0.031757 | 0.0023421 | 0.00070944 | North | N | 0.00070944 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.000191 | north | Y | 0.0011784 | 0.0039165 | -0.031288 | 0.0028111 | 0.0011784 | North | N | 0.0011784 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.000191 | north | Y | 0.0011784 | 0.0039165 | -0.031288 | 0.0028111 | 0.0011784 | North | N | 0.0011784 | 0
1943 | MDLTHELP | 3 | 212 | -0.00066 | north | Y | 0.00070944 | 0.0034475 | -0.031757 | 0.0023421 | 0.00070944 | North | N | 0.00070944 | 0
1944 | MDLTHELP | 4 | 211 | -0.00066 | north | Y | 0.00070944 | 0.0034475 | -0.031757 | 0.0023421 | 0.00070944 | North | N | 0.00070944 | 0
1947 | HANDLEY_ | 3 | 395 | 0.001234 | north | Y | 0.0026034 | 0.0053415 | -0.029863 | 0.0042361 | 0.0026034 | North | N | 0.0026034 | 0
1948 | HANDLEY_ | 4 | 435 | 0.001108 | north | Y | 0.0024774 | 0.0052155 | -0.029989 | 0.0041101 | 0.0024774 | North | N | 0.0024774 | 0
1949 | HANDLEY_ | 5 | 435 | 0.001234 | north | Y | 0.0026034 | 0.0053415 | -0.029863 | 0.0042361 | 0.0026034 | North | N | 0.0026034 | 0
2371 | COLLIN_1 | MB | 138 | 0.002008 | north | Y | 0.0033774 | 0.0061155 | -0.029089 | 0.0050101 | 0.0033774 | North | N | 0.0033774 | 0
2413 | MTCK6_G | 6 | 118 | 0.000556 | north | Y | 0.0019254 | 0.0046635 | -0.030541 | 0.0035581 | 0.0019254 | North | N | 0.0019254 | 0
2414 | MTCK7_G | 7 | 115 | 0.000556 | north | Y | 0.0019254 | 0.0046635 | -0.030541 | 0.0035581 | 0.0019254 | North | N | 0.0019254 | 0
2417 | MTCK8_G | 8 | 556 | 0.000556 | north | Y | 0.0019254 | 0.0046635 | -0.030541 | 0.0035581 | 0.0019254 | North | N | 0.0019254 | 0
2451 | LKHB1_G | 1 | 388 | 0.000877 | north | Y | 0.0022464 | 0.0049845 | -0.03022 | 0.0038791 | 0.0022464 | North | N | 0.0022464 | 0
2452 | LKHB2_G | 2 | 515 | 0.000877 | north | Y | 0.0022464 | 0.0049845 | -0.03022 | 0.0038791 | 0.0022464 | North | N | 0.0022464 | 0
3097 | MARTLAKE | 1 | 785 | 8.5e-05 | north | Y | 0.0014544 | 0.0041925 | -0.031012 | 0.0030871 | 0.0014544 | North | N | 0.0014544 | 0
3098 | MARTLAKE | 2 | 795 | 8.5e-05 | north | Y | 0.0014544 | 0.0041925 | -0.031012 | 0.0030871 | 0.0014544 | North | N | 0.0014544 | 0
3099 | MARTLAKE | 3 | 780 | 8.5e-05 | north | Y | 0.0014544 | 0.0041925 | -0.031012 | 0.0030871 | 0.0014544 | North | N | 0.0014544 | 0
3107 | STRYKER_ | 1 | 182 | -0.000136 | north | Y | 0.0012334 | 0.0039715 | -0.031233 | 0.0028661 | 0.0012334 | North | N | 0.0012334 | 0
3108 | STRYKER_ | 2 | 484 | -0.000136 | north | Y | 0.0012334 | 0.0039715 | -0.031233 | 0.0028661 | 0.0012334 | North | N | 0.0012334 | 0
3126 | TRINIDAD | 1 | 224 | -0.001579 | north | Y | -0.00020956 | 0.0025285 | -0.032676 | 0.0014231 | 0.00020956 | North | N | 0.00020956 | 0
3309 | ASPN_G | 1 | 50 | -0.000102 | north | Y | 0.0012674 | 0.0040055 | -0.031199 | 0.0029001 | 0.0012674 | North | N | 0.0012674 | 0
3348 | CHAMPION | MB | 42 | -9.4e-05 | north | N | 0.0012754 | 0.0040135 | -0.031191 | 0.0029081 | 0.0012754 | North | N | 0.0012754 | 0
3381 | BBRN_1G | 1 | 615 | -0.001029 | north | Y | 0.00034044 | 0.0030785 | -0.032126 | 0.0019731 | 0.00034044 | North | N | 0.00034044 | 0
3382 | BBRN_2G | 2 | 587 | -0.001029 | north | Y | 0.00034044 | 0.0030785 | -0.032126 | 0.0019731 | 0.00034044 | North | N | 0.00034044 | 0
3403 | THOUSE_1 | MB | 537 | -0.005165 | north | Y | -0.0037956 | -0.0010575 | -0.036262 | -0.0021629 | 0.0010575 | south | Y | 0.0037956 | 0
3404 | THOUSE_2 | 2 | 787 | -0.005165 | north | Y | -0.0037956 | -0.0010575 | -0.036262 | -0.0021629 | 0.0010575 | south | Y | 0.0037956 | 2.1548
3416 | LAKE_CRK | MB | 75 | -0.005771 | north | Y | -0.0044016 | -0.0016635 | -0.036868 | -0.0027689 | 0.0016635 | south | Y | 0.0044016 | 0
3417 | LAKE_CRK | MB | 222 | -0.005771 | north | Y | -0.0044016 | -0.0016635 | -0.036868 | -0.0027689 | 0.0016635 | south | Y | 0.0044016 | 0
3432 | SANDOW_4 | 4 | 569 | -0.005028 | south | Y | -0.0036586 | -0.00092052 | -0.036125 | -0.0020259 | 0.00092052 | south | N | 0.00092052 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.003872 | south | Y | -0.0025026 | 0.00023548 | -0.034969 | -0.00086994 | 0.00023548 | south | N | 0.00023548 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.003872 | south | Y | -0.0025026 | 0.00023548 | -0.034969 | -0.00086994 | 0.00023548 | south | N | 0.00023548 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.00386 | south | Y | -0.0024906 | 0.00024748 | -0.034957 | -0.00085794 | 0.00024748 | south | N | 0.00024748 | 0
5031 | BRA_VHBC | 1 | 46 | -0.003872 | south | Y | -0.0025026 | 0.00023548 | -0.034969 | -0.00086994 | 0.00023548 | south | N | 0.00023548 | 0
5032 | BRA_VHBC | 2 | 47 | -0.003872 | south | Y | -0.0025026 | 0.00023548 | -0.034969 | -0.00086994 | 0.00023548 | south | N | 0.00023548 | 0
5033 | BRA_VHBC | 3 | 46 | -0.003872 | south | Y | -0.0025026 | 0.00023548 | -0.034969 | -0.00086994 | 0.00023548 | south | N | 0.00023548 | 0
5034 | BRA_VHBC | 4 | 46 | -0.003872 | south | Y | -0.0025026 | 0.00023548 | -0.034969 | -0.00086994 | 0.00023548 | south | N | 0.00023548 | 0
5111 | CALAVER_ | 1 | 424 | -0.003888 | south | Y | -0.0025186 | 0.00021948 | -0.034985 | -0.00088594 | 0.00021948 | south | N | 0.00021948 | 0
5112 | CALAVER_ | 2 | 425 | -0.003888 | south | Y | -0.0025186 | 0.00021948 | -0.034985 | -0.00088594 | 0.00021948 | south | N | 0.00021948 | 0
5264 | LEON_LCP | 3 | 58 | -0.003799 | south | Y | -0.0024296 | 0.00030848 | -0.034896 | -0.00079694 | 0.00030848 | south | N | 0.00030848 | 0
5265 | LEON_LCP | 4 | 89 | -0.003799 | south | Y | -0.0024296 | 0.00030848 | -0.034896 | -0.00079694 | 0.00030848 | south | N | 0.00030848 | 0
5266 | LEON_LCP | 1 | 44 | -0.003799 | south | Y | -0.0024296 | 0.00030848 | -0.034896 | -0.00079694 | 0.00030848 | south | N | 0.00030848 | 0
5267 | LEON_LCP | 2 | 44 | -0.003799 | south | Y | -0.0024296 | 0.00030848 | -0.034896 | -0.00079694 | 0.00030848 | south | N | 0.00030848 | 0
5268 | LEON_LCP | 3 | 43 | -0.003799 | south | Y | -0.0024296 | 0.00030848 | -0.034896 | -0.00079694 | 0.00030848 | south | N | 0.00030848 | 0
5269 | LEON_LCP | 4 | 45 | -0.003799 | south | Y | -0.0024296 | 0.00030848 | -0.034896 | -0.00079694 | 0.00030848 | south | N | 0.00030848 | 0
5396 | CALAVER_ | 1 | 412 | -0.003876 | south | Y | -0.0025066 | 0.00023148 | -0.034973 | -0.00087394 | 0.00023148 | south | N | 0.00023148 | 0
5397 | CALAVER_ | 2 | 400 | -0.003876 | south | Y | -0.0025066 | 0.00023148 | -0.034973 | -0.00087394 | 0.00023148 | south | N | 0.00023148 | 0
5401 | CALAVER_ | 1 | 546 | -0.003918 | south | Y | -0.0025486 | 0.00018948 | -0.035015 | -0.00091594 | 0.00018948 | south | N | 0.00018948 | 0
5402 | CALAVER_ | 2 | 750 | -0.003918 | south | Y | -0.0025486 | 0.00018948 | -0.035015 | -0.00091594 | 0.00018948 | south | N | 0.00018948 | 0
5436 | TUTTL_WB | MB | 61 | -0.003922 | south | Y | -0.0025526 | 0.00018548 | -0.035019 | -0.00091994 | 0.00018548 | south | N | 0.00018548 | 0
5438 | TUTTL_WB | MB | 95 | -0.003922 | south | Y | -0.0025526 | 0.00018548 | -0.035019 | -0.00091994 | 0.00018548 | south | N | 0.00018548 | 0
5439 | TUTTL_WB | MB | 151 | -0.003922 | south | Y | -0.0025526 | 0.00018548 | -0.035019 | -0.00091994 | 0.00018548 | south | N | 0.00018548 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.003925 | south | Y | -0.0025556 | 0.00018248 | -0.035022 | -0.00092294 | 0.00018248 | south | N | 0.00018248 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.003925 | south | Y | -0.0025556 | 0.00018248 | -0.035022 | -0.00092294 | 0.00018248 | south | N | 0.00018248 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.003925 | south | Y | -0.0025556 | 0.00018248 | -0.035022 | -0.00092294 | 0.00018248 | south | N | 0.00018248 | 0
5503 | RAYBURNG | 1 | 22 | -0.00358 | south | Y | -0.0022106 | 0.00052748 | -0.034677 | -0.00057794 | 0.00052748 | south | N | 0.00052748 | 0
5505 | RAYBURNG | 1 | 11 | -0.00358 | south | Y | -0.0022106 | 0.00052748 | -0.034677 | -0.00057794 | 0.00052748 | south | N | 0.00052748 | 0
5506 | RAYBURNG | 1 | 11 | -0.00358 | south | Y | -0.0022106 | 0.00052748 | -0.034677 | -0.00057794 | 0.00052748 | south | N | 0.00052748 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.003617 | south | Y | -0.0022476 | 0.00049048 | -0.034714 | -0.00061494 | 0.00049048 | south | N | 0.00049048 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.003617 | south | Y | -0.0022476 | 0.00049048 | -0.034714 | -0.00061494 | 0.00049048 | south | N | 0.00049048 | 0
5511 | RAYBURNC | 1 | 46 | -0.003617 | south | Y | -0.0022476 | 0.00049048 | -0.034714 | -0.00061494 | 0.00049048 | south | N | 0.00049048 | 0
5512 | RAYBURNC | 1 | 48 | -0.003617 | south | Y | -0.0022476 | 0.00049048 | -0.034714 | -0.00061494 | 0.00049048 | south | N | 0.00049048 | 0
5728 | FALCONHY | 2 | 12 | -0.003306 | south | N | -0.0019366 | 0.00080148 | -0.034403 | -0.00030394 | 0.00030394 | houston | Y | 0.00080148 | 0
5729 | FALCONHY | 3 | 11 | -0.003306 | south | N | -0.0019366 | 0.00080148 | -0.034403 | -0.00030394 | 0.00030394 | houston | Y | 0.00080148 | 0
5890 | PEARSALL | 1 | 24 | -0.002531 | south | Y | -0.0011616 | 0.0015765 | -0.033628 | 0.00047106 | 0.00047106 | houston | Y | 0.0015765 | 0.02653
5891 | PEARSALL | 1 | 24 | -0.002531 | south | Y | -0.0011616 | 0.0015765 | -0.033628 | 0.00047106 | 0.00047106 | houston | Y | 0.0015765 | 0.02653
5892 | PEARSALL | 1 | 23 | -0.002531 | south | Y | -0.0011616 | 0.0015765 | -0.033628 | 0.00047106 | 0.00047106 | houston | Y | 0.0015765 | 0.025425
5903 | SANMIGUE | 1 | 396 | -0.003683 | south | Y | -0.0023136 | 0.00042448 | -0.03478 | -0.00068094 | 0.00042448 | south | N | 0.00042448 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.003373 | houston | N | -0.0020036 | 0.00073448 | -0.03447 | -0.00037094 | 0.00037094 | houston | N | 0.00037094 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.003373 | houston | N | -0.0020036 | 0.00073448 | -0.03447 | -0.00037094 | 0.00037094 | houston | N | 0.00037094 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | N | 0.0013694 | 0
5932 | SI_RAY9 | 9 | 38 | -0.003554 | south | Y | -0.0021846 | 0.00055348 | -0.034651 | -0.00055194 | 0.00055194 | houston | Y | 0.00055348 | 5.8513e-05
5933 | SI_RAY6 | 6 | 19.3 | -0.003554 | south | Y | -0.0021846 | 0.00055348 | -0.034651 | -0.00055194 | 0.00055194 | houston | Y | 0.00055348 | 2.9718e-05
5934 | SI_RAY5 | 5 | 15 | -0.003554 | south | Y | -0.0021846 | 0.00055348 | -0.034651 | -0.00055194 | 0.00055194 | houston | Y | 0.00055348 | 2.3097e-05
5935 | SI_RAY10 | 10 | 47 | -0.003554 | south | Y | -0.0021846 | 0.00055348 | -0.034651 | -0.00055194 | 0.00055194 | houston | Y | 0.00055348 | 7.2371e-05
6016 | SWMESA | 1 | 75 | 0.028471 | west | Y | 0.02984 | 0.032578 | -0.0026259 | 0.031473 | 0.0026259 | west | N | 0.0026259 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.031097 | 0
6144 | MCADOO1A | 1 | 150 | 0.040971 | west | Y | 0.04234 | 0.045078 | 0.0098741 | 0.043973 | 0.0098741 | west | N | 0.0098741 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.033018 | west | Y | 0.034387 | 0.037125 | 0.0019211 | 0.03602 | 0.0019211 | west | N | 0.0019211 | 0
6476 | LANGFORD | 1 | 150 | 0.020878 | west | Y | 0.022247 | 0.024985 | -0.010219 | 0.02388 | 0.010219 | west | N | 0.010219 | 0
6637 | SNYDERW1 | 1 | 63 | 0.034374 | west | Y | 0.035743 | 0.038481 | 0.0032771 | 0.037376 | 0.0032771 | west | N | 0.0032771 | 0
6752 | OKLA0A | 1 | 649.7 | 0.02855 | west | Y | 0.029919 | 0.032657 | -0.0025469 | 0.031552 | 0.0025469 | west | N | 0.0025469 | 0
6948 | DENISNDM | 1 | 40 | 0.001682 | north | N | 0.0030514 | 0.0057895 | -0.029415 | 0.0046841 | 0.0030514 | North | N | 0.0030514 | 0
6948 | DENISNDM | 2 | 40 | 0.001682 | north | N | 0.0030514 | 0.0057895 | -0.029415 | 0.0046841 | 0.0030514 | North | N | 0.0030514 | 0
7000 | L_FERGUS | 1 | 422 | -0.006615 | south | Y | -0.0052456 | -0.0025075 | -0.037712 | -0.0036129 | 0.0025075 | south | N | 0.0025075 | 0
7004 | L_SIMGID | 1 | 132 | -0.004743 | south | Y | -0.0033736 | -0.00063552 | -0.03584 | -0.0017409 | 0.00063552 | south | N | 0.00063552 | 0
7005 | L_SIMGID | 2 | 134 | -0.004743 | south | Y | -0.0033736 | -0.00063552 | -0.03584 | -0.0017409 | 0.00063552 | south | N | 0.00063552 | 0
7006 | L_SIMGID | 3 | 323 | -0.004743 | south | Y | -0.0033736 | -0.00063552 | -0.03584 | -0.0017409 | 0.00063552 | south | N | 0.00063552 | 0
7007 | L_LOSTPI | 1 | 158 | -0.004592 | south | Y | -0.0032226 | -0.00048452 | -0.035689 | -0.0015899 | 0.00048452 | south | N | 0.00048452 | 0
7008 | L_LOSTPI | 2 | 160 | -0.004592 | south | Y | -0.0032226 | -0.00048452 | -0.035689 | -0.0015899 | 0.00048452 | south | N | 0.00048452 | 0
7009 | L_LOSTPI | 3 | 175 | -0.004592 | south | Y | -0.0032226 | -0.00048452 | -0.035689 | -0.0015899 | 0.00048452 | south | N | 0.00048452 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.00439 | south | Y | -0.0030206 | -0.00028252 | -0.035487 | -0.0013879 | 0.00028252 | south | N | 0.00028252 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.00439 | south | Y | -0.0030206 | -0.00028252 | -0.035487 | -0.0013879 | 0.00028252 | south | N | 0.00028252 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.004388 | south | Y | -0.0030186 | -0.00028052 | -0.035485 | -0.0013859 | 0.00028052 | south | N | 0.00028052 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.004235 | south | Y | -0.0028656 | -0.00012752 | -0.035332 | -0.0012329 | 0.00012752 | south | N | 0.00012752 | 0
7015 | L_HAYSEN | 2 | 225 | -0.004235 | south | Y | -0.0028656 | -0.00012752 | -0.035332 | -0.0012329 | 0.00012752 | south | N | 0.00012752 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.004235 | south | Y | -0.0028656 | -0.00012752 | -0.035332 | -0.0012329 | 0.00012752 | south | N | 0.00012752 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.004235 | south | Y | -0.0028656 | -0.00012752 | -0.035332 | -0.0012329 | 0.00012752 | south | N | 0.00012752 | 0
7020 | L_AUSTPL | 1 | 8 | -0.00504 | south | N | -0.0036706 | -0.00093252 | -0.036137 | -0.0020379 | 0.00093252 | south | N | 0.00093252 | 0
7020 | L_AUSTPL | 2 | 8 | -0.00504 | south | N | -0.0036706 | -0.00093252 | -0.036137 | -0.0020379 | 0.00093252 | south | N | 0.00093252 | 0
7022 | L_BUCHAN | 1 | 18 | -0.008685 | south | N | -0.0073156 | -0.0045775 | -0.039782 | -0.0056829 | 0.0045775 | south | N | 0.0045775 | 0
7023 | L_BUCHAN | 2 | 18 | -0.008685 | south | N | -0.0073156 | -0.0045775 | -0.039782 | -0.0056829 | 0.0045775 | south | N | 0.0045775 | 0
7024 | L_BUCHAN | 3 | 15 | -0.008685 | south | N | -0.0073156 | -0.0045775 | -0.039782 | -0.0056829 | 0.0045775 | south | N | 0.0045775 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.007305 | south | N | -0.0059356 | -0.0031975 | -0.038402 | -0.0043029 | 0.0031975 | south | N | 0.0031975 | 0
7028 | L_MARBFA | 1 | 18 | -0.006284 | south | N | -0.0049146 | -0.0021765 | -0.037381 | -0.0032819 | 0.0021765 | south | N | 0.0021765 | 0
7029 | L_MARBFA | 2 | 18 | -0.006284 | south | N | -0.0049146 | -0.0021765 | -0.037381 | -0.0032819 | 0.0021765 | south | N | 0.0021765 | 0
7031 | L_MARSFO | 1 | 35 | -0.005534 | south | N | -0.0041646 | -0.0014265 | -0.036631 | -0.0025319 | 0.0014265 | south | N | 0.0014265 | 0
7032 | L_MARSFO | 2 | 34 | -0.005534 | south | N | -0.0041646 | -0.0014265 | -0.036631 | -0.0025319 | 0.0014265 | south | N | 0.0014265 | 0
7033 | L_MARSFO | 3 | 35 | -0.005534 | south | N | -0.0041646 | -0.0014265 | -0.036631 | -0.0025319 | 0.0014265 | south | N | 0.0014265 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.006767 | south | N | -0.0053976 | -0.0026595 | -0.037864 | -0.0037649 | 0.0026595 | south | N | 0.0026595 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.006767 | south | N | -0.0053976 | -0.0026595 | -0.037864 | -0.0037649 | 0.0026595 | south | N | 0.0026595 | 0
7038 | L_DELAWA | 1 | 35 | 0.030419 | west | Y | 0.031788 | 0.034526 | -0.00067793 | 0.033421 | 0.00067793 | west | N | 0.00067793 | 0
7038 | L_DELAWA | 2 | 30 | 0.030419 | west | Y | 0.031788 | 0.034526 | -0.00067793 | 0.033421 | 0.00067793 | west | N | 0.00067793 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.004482 | south | Y | -0.0031126 | -0.00037452 | -0.035579 | -0.0014799 | 0.00037452 | south | N | 0.00037452 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.004482 | south | Y | -0.0031126 | -0.00037452 | -0.035579 | -0.0014799 | 0.00037452 | south | N | 0.00037452 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.004482 | south | Y | -0.0031126 | -0.00037452 | -0.035579 | -0.0014799 | 0.00037452 | south | N | 0.00037452 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.004482 | south | Y | -0.0031126 | -0.00037452 | -0.035579 | -0.0014799 | 0.00037452 | south | N | 0.00037452 | 0
7487 | L_CANYHY | 1 | 6 | -0.004431 | south | N | -0.0030616 | -0.00032352 | -0.035528 | -0.0014289 | 0.00032352 | south | N | 0.00032352 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.004183 | south | N | -0.0028136 | -7.5517e-05 | -0.03528 | -0.0011809 | 7.5517e-05 | south | N | 7.5517e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.004183 | south | N | -0.0028136 | -7.5517e-05 | -0.03528 | -0.0011809 | 7.5517e-05 | south | N | 7.5517e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.004183 | south | N | -0.0028136 | -7.5517e-05 | -0.03528 | -0.0011809 | 7.5517e-05 | south | N | 7.5517e-05 | 0
7609 | L_SCHUMA | 1 | 4 | -0.004111 | south | N | -0.0027416 | -3.5173e-06 | -0.035208 | -0.0011089 | 3.5173e-06 | south | N | 3.5173e-06 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.004173 | south | N | -0.0028036 | -6.5517e-05 | -0.03527 | -0.0011709 | 6.5517e-05 | south | N | 6.5517e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.004173 | south | N | -0.0028036 | -6.5517e-05 | -0.03527 | -0.0011709 | 6.5517e-05 | south | N | 6.5517e-05 | 0
7800 | L_GUADGE | 1 | 147 | -0.004037 | south | Y | -0.0026676 | 7.0483e-05 | -0.035134 | -0.0010349 | 7.0483e-05 | south | N | 7.0483e-05 | 0
7801 | L_GUADGE | 2 | 138 | -0.004037 | south | Y | -0.0026676 | 7.0483e-05 | -0.035134 | -0.0010349 | 7.0483e-05 | south | N | 7.0483e-05 | 0
7802 | L_GUADGE | 3 | 140 | -0.004037 | south | Y | -0.0026676 | 7.0483e-05 | -0.035134 | -0.0010349 | 7.0483e-05 | south | N | 7.0483e-05 | 0
7803 | L_GUADGE | 4 | 147 | -0.004037 | south | Y | -0.0026676 | 7.0483e-05 | -0.035134 | -0.0010349 | 7.0483e-05 | south | N | 7.0483e-05 | 0
7804 | L_GUADGE | 5 | 182 | -0.004037 | south | Y | -0.0026676 | 7.0483e-05 | -0.035134 | -0.0010349 | 7.0483e-05 | south | N | 7.0483e-05 | 0
7805 | L_GUADGE | 6 | 198 | -0.004037 | south | Y | -0.0026676 | 7.0483e-05 | -0.035134 | -0.0010349 | 7.0483e-05 | south | N | 7.0483e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.004636 | south | Y | -0.0032666 | -0.00052852 | -0.035733 | -0.0016339 | 0.00052852 | south | N | 0.00052852 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.004636 | south | Y | -0.0032666 | -0.00052852 | -0.035733 | -0.0016339 | 0.00052852 | south | N | 0.00052852 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.004636 | south | Y | -0.0032666 | -0.00052852 | -0.035733 | -0.0016339 | 0.00052852 | south | N | 0.00052852 | 0
7810 | L_RIONOG | 1 | 142 | -0.004135 | south | Y | -0.0027656 | -2.7517e-05 | -0.035232 | -0.0011329 | 2.7517e-05 | south | N | 2.7517e-05 | 0
7811 | L_RIONOG | 2 | 145 | -0.004135 | south | Y | -0.0027656 | -2.7517e-05 | -0.035232 | -0.0011329 | 2.7517e-05 | south | N | 2.7517e-05 | 0
7812 | L_RIONOG | 3 | 151 | -0.004135 | south | Y | -0.0027656 | -2.7517e-05 | -0.035232 | -0.0011329 | 2.7517e-05 | south | N | 2.7517e-05 | 0
7813 | L_RIONOG | 4 | 290 | -0.004135 | south | Y | -0.0027656 | -2.7517e-05 | -0.035232 | -0.0011329 | 2.7517e-05 | south | N | 2.7517e-05 | 0
8032 | AMISTADH | 1 | 33 | 0.005582 | south | N | 0.0069514 | 0.0096895 | -0.025515 | 0.0085841 | 0.0069514 | North | Y | 0.0096895 | 0
8033 | AMISTADH | 2 | 25 | 0.005582 | south | N | 0.0069514 | 0.0096895 | -0.025515 | 0.0085841 | 0.0069514 | North | Y | 0.0096895 | 0
8048 | FALCONHY | 1 | 12 | -0.003306 | south | N | -0.0019366 | 0.00080148 | -0.034403 | -0.00030394 | 0.00030394 | houston | Y | 0.00080148 | 0
8066 | DUP1V#1 | 1 | 73 | -0.00364 | south | N | -0.0022706 | 0.00046748 | -0.034737 | -0.00063794 | 0.00046748 | south | N | 0.00046748 | 0
8134 | FOR69CG0 | 1 | 79 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
8138 | FOR69CG0 | 2 | 81 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8147 | UCAR #2 | 10 | 28 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
8148 | UCAR #1 | 2 | 7 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
8153 | FOR69CG0 | 3 | 79 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
8154 | FOR69CG0 | 4 | 80 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
8156 | FOR69CG0 | 6 | 25 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
8157 | FOR69CG0 | 7 | 46 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
8161 | COLETOU1 | 1 | 629 | -0.003659 | south | Y | -0.0022896 | 0.00044848 | -0.034756 | -0.00065694 | 0.00044848 | south | N | 0.00044848 | 0
8173 | VICEC51A | 5 | 144 | -0.003651 | south | Y | -0.0022816 | 0.00045648 | -0.034748 | -0.00064894 | 0.00045648 | south | N | 0.00045648 | 0
8174 | VICEC61A | 6 | 188 | -0.003651 | south | Y | -0.0022816 | 0.00045648 | -0.034748 | -0.00064894 | 0.00045648 | south | N | 0.00045648 | 0
8189 | CUERO 2 | 1 | 12 | -0.004014 | south | N | -0.0026446 | 9.3483e-05 | -0.035111 | -0.0010119 | 9.3483e-05 | south | N | 9.3483e-05 | 0
8262 | ELPS | 1 | 6 | 0.003011 | south | N | 0.0043804 | 0.0071185 | -0.028086 | 0.0060131 | 0.0043804 | North | Y | 0.0071185 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8442 | NBEC71A | 1 | 336 | -0.003572 | south | Y | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | 0.0013694 | 0.0041075 | -0.031097 | 0.0030021 | 0.0013694 | North | Y | 0.0041075 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.003572 | south | Y | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.003572 | south | Y | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.003569 | south | N | -0.0021996 | 0.00053848 | -0.034666 | -0.00056694 | 0.00053848 | south | N | 0.00053848 | 0
8506 | VAL #1 | 1 | 25 | -0.00357 | south | N | -0.0022006 | 0.00053748 | -0.034667 | -0.00056794 | 0.00053748 | south | N | 0.00053748 | 0
8507 | VAL #2 | 2 | 25 | -0.00357 | south | N | -0.0022006 | 0.00053748 | -0.034667 | -0.00056794 | 0.00053748 | south | N | 0.00053748 | 0
8511 | OXY_CC0A | 1 | 38 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8517 | CELANEBI | 1 | 29 | -0.003568 | south | N | -0.0021986 | 0.00053948 | -0.034665 | -0.00056594 | 0.00053948 | south | N | 0.00053948 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8562 | CNOPST1 | 3 | 153 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8926 | LGE_GT10 | 1 | 158 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8927 | LGE_GT20 | 2 | 153 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8928 | LGE_STG0 | 3 | 100 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8930 | ICPGN10A | 1 | 145 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8931 | ICPGN20A | 2 | 147 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8932 | ICPGN30A | 3 | 127 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.003503 | south | Y | -0.0021336 | 0.00060448 | -0.0346 | -0.00050094 | 0.00050094 | houston | Y | 0.00060448 | 0.015169
8934 | FGNTS101 | 2 | 147.9 | -0.003503 | south | Y | -0.0021336 | 0.00060448 | -0.0346 | -0.00050094 | 0.00050094 | houston | Y | 0.00060448 | 0.015314
8935 | FGNTS201 | 3 | 173 | -0.003503 | south | Y | -0.0021336 | 0.00060448 | -0.0346 | -0.00050094 | 0.00050094 | houston | Y | 0.00060448 | 0.017912
8936 | MVGN#1 | 1 | 207 | -0.003535 | south | Y | -0.0021656 | 0.00057248 | -0.034632 | -0.00053294 | 0.00053294 | houston | Y | 0.00057248 | 0.0081847
8937 | MVGN#2 | 2 | 216.7 | -0.003535 | south | Y | -0.0021656 | 0.00057248 | -0.034632 | -0.00053294 | 0.00053294 | houston | Y | 0.00057248 | 0.0085683
8938 | MVGN#3 | 3 | 242 | -0.003535 | south | Y | -0.0021656 | 0.00057248 | -0.034632 | -0.00053294 | 0.00053294 | houston | Y | 0.00057248 | 0.0095686
8981 | HECN1 | 1 | 144 | -0.003535 | south | Y | -0.0021656 | 0.00057248 | -0.034632 | -0.00053294 | 0.00053294 | houston | Y | 0.00057248 | 0.0056937
8982 | HECN2 | 2 | 144 | -0.003535 | south | Y | -0.0021656 | 0.00057248 | -0.034632 | -0.00053294 | 0.00053294 | houston | Y | 0.00057248 | 0.0056937
8983 | HECN3 | 3 | 171 | -0.003535 | south | Y | -0.0021656 | 0.00057248 | -0.034632 | -0.00053294 | 0.00053294 | houston | Y | 0.00057248 | 0.0067613
9000 | DECKR_G1 | 1 | 310 | -0.004999 | south | Y | -0.0036296 | -0.00089152 | -0.036096 | -0.0019969 | 0.00089152 | south | N | 0.00089152 | 0
9001 | DECKR_G2 | 2 | 413 | -0.004999 | south | Y | -0.0036296 | -0.00089152 | -0.036096 | -0.0019969 | 0.00089152 | south | N | 0.00089152 | 0
9002 | DECKR_G3 | 3 | 42 | -0.005006 | south | Y | -0.0036366 | -0.00089852 | -0.036103 | -0.0020039 | 0.00089852 | south | N | 0.00089852 | 0
9003 | DECKR_G4 | 4 | 44 | -0.005006 | south | Y | -0.0036366 | -0.00089852 | -0.036103 | -0.0020039 | 0.00089852 | south | N | 0.00089852 | 0
9004 | DECKR_G5 | 5 | 44 | -0.005006 | south | Y | -0.0036366 | -0.00089852 | -0.036103 | -0.0020039 | 0.00089852 | south | N | 0.00089852 | 0
9005 | DECKR_G6 | 6 | 47 | -0.005006 | south | Y | -0.0036366 | -0.00089852 | -0.036103 | -0.0020039 | 0.00089852 | south | N | 0.00089852 | 0
9016 | SANDH_G1 | 1 | 49 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
9017 | SANDH_G2 | 2 | 46 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
9018 | SANDH_G3 | 3 | 46 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
9019 | SANDH_G4 | 4 | 47 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
9020 | SANDHG5A | 5A | 154 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
9021 | SANDHG5C | 5C | 148 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
9022 | SANDH_G6 | 6 | 48 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
9023 | SANDH_G7 | 7 | 48 | -0.00495 | south | Y | -0.0035806 | -0.00084252 | -0.036047 | -0.0019479 | 0.00084252 | south | N | 0.00084252 | 0
11001 | NAV1CT | 1 | 70 | 0.03039 | west | Y | 0.031759 | 0.034497 | -0.00070693 | 0.033392 | 0.00070693 | west | N | 0.00070693 | 0
11009 | NAV2CT | 1 | 70 | 0.03039 | west | Y | 0.031759 | 0.034497 | -0.00070693 | 0.033392 | 0.00070693 | west | N | 0.00070693 | 0
11011 | NAV3ST | 1 | 92.8 | 0.03039 | west | Y | 0.031759 | 0.034497 | -0.00070693 | 0.033392 | 0.00070693 | west | N | 0.00070693 | 0
11012 | NAV4CT | 1 | 80 | 0.03039 | west | Y | 0.031759 | 0.034497 | -0.00070693 | 0.033392 | 0.00070693 | west | N | 0.00070693 | 0
11013 | NAV5CT | 1 | 80 | 0.03039 | west | Y | 0.031759 | 0.034497 | -0.00070693 | 0.033392 | 0.00070693 | west | N | 0.00070693 | 0
11014 | NAV6ST | 1 | 115 | 0.03039 | west | Y | 0.031759 | 0.034497 | -0.00070693 | 0.033392 | 0.00070693 | west | N | 0.00070693 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.030389 | west | Y | 0.031758 | 0.034496 | -0.00070793 | 0.033391 | 0.00070793 | west | N | 0.00070793 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.030389 | west | Y | 0.031758 | 0.034496 | -0.00070793 | 0.033391 | 0.00070793 | west | N | 0.00070793 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.030389 | west | Y | 0.031758 | 0.034496 | -0.00070793 | 0.033391 | 0.00070793 | west | N | 0.00070793 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.030389 | west | Y | 0.031758 | 0.034496 | -0.00070793 | 0.033391 | 0.00070793 | west | N | 0.00070793 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.030389 | west | Y | 0.031758 | 0.034496 | -0.00070793 | 0.033391 | 0.00070793 | west | N | 0.00070793 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.030389 | west | Y | 0.031758 | 0.034496 | -0.00070793 | 0.033391 | 0.00070793 | west | N | 0.00070793 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.029444 | west | Y | 0.030813 | 0.033551 | -0.0016529 | 0.032446 | 0.0016529 | west | N | 0.0016529 | 0
11057 | CHAMPION | 1 | 126.5 | 0.029444 | west | Y | 0.030813 | 0.033551 | -0.0016529 | 0.032446 | 0.0016529 | west | N | 0.0016529 | 0
11058 | PYRON_1G | 1 | 249 | 0.029444 | west | Y | 0.030813 | 0.033551 | -0.0016529 | 0.032446 | 0.0016529 | west | N | 0.0016529 | 0
11059 | INADALE_ | 1 | 197 | 0.029444 | west | Y | 0.030813 | 0.033551 | -0.0016529 | 0.032446 | 0.0016529 | west | N | 0.0016529 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.030449 | west | Y | 0.031818 | 0.034556 | -0.00064793 | 0.033451 | 0.00064793 | west | N | 0.00064793 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.030449 | west | Y | 0.031818 | 0.034556 | -0.00064793 | 0.033451 | 0.00064793 | west | N | 0.00064793 | 0
11147 | NOTREES_ | 1 | 149 | 0.030686 | west | Y | 0.032055 | 0.034793 | -0.00041093 | 0.033688 | 0.00041093 | west | N | 0.00041093 | 0
11309 | BULLCREK | 1 | 180 | 0.033455 | west | Y | 0.034824 | 0.037562 | 0.0023581 | 0.036457 | 0.0023581 | west | N | 0.0023581 | 0
11310 | BULLCREK | 1 | 180 | 0.033455 | west | Y | 0.034824 | 0.037562 | 0.0023581 | 0.036457 | 0.0023581 | west | N | 0.0023581 | 0
11320 | COYOTE_1 | 1 | 225 | 0.033348 | west | Y | 0.034717 | 0.037455 | 0.0022511 | 0.03635 | 0.0022511 | west | N | 0.0022511 | 0
11415 | LORAINE_ | 1 | 125 | 0.030257 | west | Y | 0.031626 | 0.034364 | -0.00083993 | 0.033259 | 0.00083993 | west | N | 0.00083993 | 0
11416 | LORAINE_ | 1 | 125 | 0.030257 | west | Y | 0.031626 | 0.034364 | -0.00083993 | 0.033259 | 0.00083993 | west | N | 0.00083993 | 0
11691 | KMICHICT | 1 | 140 | 0.001516 | north | N | 0.0028854 | 0.0056235 | -0.029581 | 0.0045181 | 0.0028854 | North | N | 0.0028854 | 0
11692 | KMICHICT | 2 | 141 | 0.001516 | north | N | 0.0028854 | 0.0056235 | -0.029581 | 0.0045181 | 0.0028854 | North | N | 0.0028854 | 0
11693 | KMICHIST | 3 | 309 | 0.001516 | north | N | 0.0028854 | 0.0056235 | -0.029581 | 0.0045181 | 0.0028854 | North | N | 0.0028854 | 0
11694 | KMICHICT | 4 | 143 | 0.001516 | north | N | 0.0028854 | 0.0056235 | -0.029581 | 0.0045181 | 0.0028854 | North | N | 0.0028854 | 0
11695 | KMICHICT | 5 | 144 | 0.001516 | north | N | 0.0028854 | 0.0056235 | -0.029581 | 0.0045181 | 0.0028854 | North | N | 0.0028854 | 0
11696 | KMICHIST | 6 | 310 | 0.001516 | north | N | 0.0028854 | 0.0056235 | -0.029581 | 0.0045181 | 0.0028854 | North | N | 0.0028854 | 0
12322 | ENNSTRAC | 1 | 196 | -0.001622 | north | Y | -0.00025256 | 0.0024855 | -0.032719 | 0.0013801 | 0.00025256 | North | N | 0.00025256 | 0
12323 | ENNSTRAC | 2 | 111 | -0.001622 | north | Y | -0.00025256 | 0.0024855 | -0.032719 | 0.0013801 | 0.00025256 | North | N | 0.00025256 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.001681 | north | N | 0.0030504 | 0.0057885 | -0.029416 | 0.0046831 | 0.0030504 | North | N | 0.0030504 | 0
12411 | FPLEFR1A | 1 | 161 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12412 | FPLEFR1B | 2 | 164 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12413 | FPLEFR1C | 3 | 164 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12414 | FPLEFR1S | 4 | 414 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12421 | FPLEFR2A | 1 | 162 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12422 | FPLEFR2B | 2 | 161 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12423 | FPLEFR2C | 3 | 163 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12424 | FPLEFR2S | 4 | 409 | 0.000829 | north | Y | 0.0021984 | 0.0049365 | -0.030268 | 0.0038311 | 0.0021984 | North | N | 0.0021984 | 0
12440 | PARKD_1S | 1 | 0 | 0.000802 | north | N | 0.0021714 | 0.0049095 | -0.030295 | 0.0038041 | 0.0021714 | North | N | 0.0021714 | 0
12449 | PARKD_2S | 1 | 0 | 0.000802 | north | N | 0.0021714 | 0.0049095 | -0.030295 | 0.0038041 | 0.0021714 | North | N | 0.0021714 | 0
13116 | TGATEWAY | 1 | 148 | -1.4e-05 | north | N | 0.0013554 | 0.0040935 | -0.031111 | 0.0029881 | 0.0013554 | North | N | 0.0013554 | 0
13117 | TGATEWAY | 2 | 130 | -1.4e-05 | north | N | 0.0013554 | 0.0040935 | -0.031111 | 0.0029881 | 0.0013554 | North | N | 0.0013554 | 0
13118 | TGATEWAY | 3 | 145 | -1.4e-05 | north | N | 0.0013554 | 0.0040935 | -0.031111 | 0.0029881 | 0.0013554 | North | N | 0.0013554 | 0
13119 | TGATEWAY | 4 | 399 | -1.4e-05 | north | N | 0.0013554 | 0.0040935 | -0.031111 | 0.0029881 | 0.0013554 | North | N | 0.0013554 | 0
13131 | CALFREST | 1 | 150.7 | -0.000877 | north | Y | 0.00049244 | 0.0032305 | -0.031974 | 0.0021251 | 0.00049244 | North | N | 0.00049244 | 0
13132 | CALFREST | 2 | 151 | -0.000877 | north | Y | 0.00049244 | 0.0032305 | -0.031974 | 0.0021251 | 0.00049244 | North | N | 0.00049244 | 0
13133 | CALFREST | 3 | 177.4 | -0.000877 | north | Y | 0.00049244 | 0.0032305 | -0.031974 | 0.0021251 | 0.00049244 | North | N | 0.00049244 | 0
13134 | CALFREST | 4 | 151.5 | -0.000863 | north | Y | 0.00050644 | 0.0032445 | -0.03196 | 0.0021391 | 0.00050644 | North | N | 0.00050644 | 0
13135 | CALFREST | 5 | 152.3 | -0.000863 | north | Y | 0.00050644 | 0.0032445 | -0.03196 | 0.0021391 | 0.00050644 | North | N | 0.00050644 | 0
13136 | CALFREST | 6 | 177.5 | -0.000863 | north | Y | 0.00050644 | 0.0032445 | -0.03196 | 0.0021391 | 0.00050644 | North | N | 0.00050644 | 0
13432 | SANDOW_5 | 5 | 581 | -0.005028 | south | Y | -0.0036586 | -0.00092052 | -0.036125 | -0.0020259 | 0.00092052 | south | N | 0.00092052 | 0
13691 | OAKGROVE | 1 | 855 | -0.001924 | north | Y | -0.00055456 | 0.0021835 | -0.033021 | 0.0010781 | 0.00055456 | North | N | 0.00055456 | 0
13692 | OAKGROVE | 2 | 855 | -0.001924 | north | Y | -0.00055456 | 0.0021835 | -0.033021 | 0.0010781 | 0.00055456 | North | N | 0.00055456 | 0
32798 | BRYN_TAM | 1 | 32 | -0.002431 | north | N | -0.0010616 | 0.0016765 | -0.033528 | 0.00057106 | 0.00057106 | houston | Y | 0.0010616 | 0
32883 | BRYN_DNS | 1 | 48 | -0.002483 | north | Y | -0.0011136 | 0.0016245 | -0.03358 | 0.00051906 | 0.00051906 | houston | Y | 0.0011136 | 0.028536
32884 | BRYN_DNS | 1 | 46 | -0.002483 | north | Y | -0.0011136 | 0.0016245 | -0.03358 | 0.00051906 | 0.00051906 | houston | Y | 0.0011136 | 0.027347
32886 | BRYN_ATK | MB | 12 | -0.002431 | north | Y | -0.0010616 | 0.0016765 | -0.033528 | 0.00057106 | 0.00057106 | houston | Y | 0.0010616 | 0
32887 | BRYN_ATK | MB | 51 | -0.002431 | north | Y | -0.0010616 | 0.0016765 | -0.033528 | 0.00057106 | 0.00057106 | houston | Y | 0.0010616 | 0
32888 | BRYN_ATK | 1 | 17 | -0.002431 | north | Y | -0.0010616 | 0.0016765 | -0.033528 | 0.00057106 | 0.00057106 | houston | Y | 0.0010616 | 0.0083385
32890 | BRYN_ATK | MB | 22 | -0.002431 | north | Y | -0.0010616 | 0.0016765 | -0.033528 | 0.00057106 | 0.00057106 | houston | Y | 0.0010616 | 0
32891 | BRYN_ATK | MB | 25 | -0.002431 | north | Y | -0.0010616 | 0.0016765 | -0.033528 | 0.00057106 | 0.00057106 | houston | Y | 0.0010616 | 0
32892 | BRYN_DNS | 1 | 105 | -0.002483 | north | Y | -0.0011136 | 0.0016245 | -0.03358 | 0.00051906 | 0.00051906 | houston | Y | 0.0011136 | 0.062423
36998 | RDCNYNG1 | 1 | 84 | 0.035797 | west | Y | 0.037166 | 0.039904 | 0.0047001 | 0.038799 | 0.0047001 | west | N | 0.0047001 | 0
38332 | WDWRDU2 | 1 | 80 | 0.028441 | west | Y | 0.02981 | 0.032548 | -0.0026559 | 0.031443 | 0.0026559 | west | N | 0.0026559 | 0
38437 | TNSRBNMS | 1 | 150 | 0.028424 | west | Y | 0.029793 | 0.032531 | -0.0026729 | 0.031426 | 0.0026729 | west | N | 0.0026729 | 0
38438 | TNSRBNMS | 1 | 150 | 0.028424 | west | Y | 0.029793 | 0.032531 | -0.0026729 | 0.031426 | 0.0026729 | west | N | 0.0026729 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38600 | TNBP_CGN | 5 | 53 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38614 | TNBPAMCG | 4 | 96 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38615 | TNBPAMCG | 1 | 244 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38690 | TNBP_CGN | 3 | 40 | -0.003017 | houston | N | -0.0016476 | 0.0010905 | -0.034114 | -1.4943e-05 | 1.4943e-05 | houston | N | 1.4943e-05 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.003018 | houston | N | -0.0016486 | 0.0010895 | -0.034115 | -1.5943e-05 | 1.5943e-05 | houston | N | 1.5943e-05 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.003018 | houston | N | -0.0016486 | 0.0010895 | -0.034115 | -1.5943e-05 | 1.5943e-05 | houston | N | 1.5943e-05 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.003018 | houston | N | -0.0016486 | 0.0010895 | -0.034115 | -1.5943e-05 | 1.5943e-05 | houston | N | 1.5943e-05 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.003018 | houston | N | -0.0016486 | 0.0010895 | -0.034115 | -1.5943e-05 | 1.5943e-05 | houston | N | 1.5943e-05 | 0
39470 | TNDOWCGN | 1 | 32 | -0.003018 | houston | N | -0.0016486 | 0.0010895 | -0.034115 | -1.5943e-05 | 1.5943e-05 | houston | N | 1.5943e-05 | 0
39480 | TNDOWCGN | 1 | 30 | -0.003018 | houston | N | -0.0016486 | 0.0010895 | -0.034115 | -1.5943e-05 | 1.5943e-05 | houston | N | 1.5943e-05 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.003161 | houston | N | -0.0017916 | 0.00094648 | -0.034258 | -0.00015894 | 0.00015894 | houston | N | 0.00015894 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.003161 | houston | N | -0.0017916 | 0.00094648 | -0.034258 | -0.00015894 | 0.00015894 | houston | N | 0.00015894 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.003161 | houston | N | -0.0017916 | 0.00094648 | -0.034258 | -0.00015894 | 0.00015894 | houston | N | 0.00015894 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.003161 | houston | N | -0.0017916 | 0.00094648 | -0.034258 | -0.00015894 | 0.00015894 | houston | N | 0.00015894 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.001924 | north | Y | -0.00055456 | 0.0021835 | -0.033021 | 0.0010781 | 0.00055456 | North | N | 0.00055456 | 0
39970 | TNTNPONE | 1 | 153 | -0.001924 | north | Y | -0.00055456 | 0.0021835 | -0.033021 | 0.0010781 | 0.00055456 | North | N | 0.00055456 | 0
48500 | APD_GT1_ | 1 | 136 | -0.002929 | houston | N | -0.0015596 | 0.0011785 | -0.034026 | 7.3057e-05 | 7.3057e-05 | houston | N | 7.3057e-05 | 0
48510 | AK_GT1__ | 1 | 33 | -0.003065 | houston | N | -0.0016956 | 0.0010425 | -0.034162 | -6.2943e-05 | 6.2943e-05 | houston | N | 6.2943e-05 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.002928 | houston | Y | -0.0015586 | 0.0011795 | -0.034025 | 7.4057e-05 | 7.4057e-05 | houston | N | 7.4057e-05 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.002928 | houston | Y | -0.0015586 | 0.0011795 | -0.034025 | 7.4057e-05 | 7.4057e-05 | houston | N | 7.4057e-05 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.002928 | houston | Y | -0.0015586 | 0.0011795 | -0.034025 | 7.4057e-05 | 7.4057e-05 | houston | N | 7.4057e-05 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.002928 | houston | Y | -0.0015586 | 0.0011795 | -0.034025 | 7.4057e-05 | 7.4057e-05 | houston | N | 7.4057e-05 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.003183 | houston | N | -0.0018136 | 0.00092448 | -0.03428 | -0.00018094 | 0.00018094 | houston | N | 0.00018094 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.003183 | houston | N | -0.0018136 | 0.00092448 | -0.03428 | -0.00018094 | 0.00018094 | houston | N | 0.00018094 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.003077 | houston | N | -0.0017076 | 0.0010305 | -0.034174 | -7.4943e-05 | 7.4943e-05 | houston | N | 7.4943e-05 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.003077 | houston | N | -0.0017076 | 0.0010305 | -0.034174 | -7.4943e-05 | 7.4943e-05 | houston | N | 7.4943e-05 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.003077 | houston | N | -0.0017076 | 0.0010305 | -0.034174 | -7.4943e-05 | 7.4943e-05 | houston | N | 7.4943e-05 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.002962 | houston | N | -0.0015926 | 0.0011455 | -0.034059 | 4.0057e-05 | 4.0057e-05 | houston | N | 4.0057e-05 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.002962 | houston | N | -0.0015926 | 0.0011455 | -0.034059 | 4.0057e-05 | 4.0057e-05 | houston | N | 4.0057e-05 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.002962 | houston | N | -0.0015926 | 0.0011455 | -0.034059 | 4.0057e-05 | 4.0057e-05 | houston | N | 4.0057e-05 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.002962 | houston | N | -0.0015926 | 0.0011455 | -0.034059 | 4.0057e-05 | 4.0057e-05 | houston | N | 4.0057e-05 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.00294 | houston | N | -0.0015706 | 0.0011675 | -0.034037 | 6.2057e-05 | 6.2057e-05 | houston | N | 6.2057e-05 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.00294 | houston | N | -0.0015706 | 0.0011675 | -0.034037 | 6.2057e-05 | 6.2057e-05 | houston | N | 6.2057e-05 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.002968 | houston | N | -0.0015986 | 0.0011395 | -0.034065 | 3.4057e-05 | 3.4057e-05 | houston | N | 3.4057e-05 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.002968 | houston | N | -0.0015986 | 0.0011395 | -0.034065 | 3.4057e-05 | 3.4057e-05 | houston | N | 3.4057e-05 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.002968 | houston | N | -0.0015986 | 0.0011395 | -0.034065 | 3.4057e-05 | 3.4057e-05 | houston | N | 3.4057e-05 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.002968 | houston | N | -0.0015986 | 0.0011395 | -0.034065 | 3.4057e-05 | 3.4057e-05 | houston | N | 3.4057e-05 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.002968 | houston | N | -0.0015986 | 0.0011395 | -0.034065 | 3.4057e-05 | 3.4057e-05 | houston | N | 3.4057e-05 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.0029 | houston | Y | -0.0015306 | 0.0012075 | -0.033997 | 0.00010206 | 0.00010206 | houston | N | 0.00010206 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.002912 | houston | Y | -0.0015426 | 0.0011955 | -0.034009 | 9.0057e-05 | 9.0057e-05 | houston | N | 9.0057e-05 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.002897 | houston | Y | -0.0015276 | 0.0012105 | -0.033994 | 0.00010506 | 0.00010506 | houston | N | 0.00010506 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.002897 | houston | Y | -0.0015276 | 0.0012105 | -0.033994 | 0.00010506 | 0.00010506 | houston | N | 0.00010506 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.002897 | houston | Y | -0.0015276 | 0.0012105 | -0.033994 | 0.00010506 | 0.00010506 | houston | N | 0.00010506 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.002835 | houston | N | -0.0014656 | 0.0012725 | -0.033932 | 0.00016706 | 0.00016706 | houston | N | 0.00016706 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.002926 | houston | N | -0.0015566 | 0.0011815 | -0.034023 | 7.6057e-05 | 7.6057e-05 | houston | N | 7.6057e-05 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.002926 | houston | N | -0.0015566 | 0.0011815 | -0.034023 | 7.6057e-05 | 7.6057e-05 | houston | N | 7.6057e-05 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.002889 | houston | N | -0.0015196 | 0.0012185 | -0.033986 | 0.00011306 | 0.00011306 | houston | N | 0.00011306 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.002889 | houston | N | -0.0015196 | 0.0012185 | -0.033986 | 0.00011306 | 0.00011306 | houston | N | 0.00011306 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.002889 | houston | N | -0.0015196 | 0.0012185 | -0.033986 | 0.00011306 | 0.00011306 | houston | N | 0.00011306 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.002889 | houston | N | -0.0015196 | 0.0012185 | -0.033986 | 0.00011306 | 0.00011306 | houston | N | 0.00011306 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.002946 | houston | N | -0.0015766 | 0.0011615 | -0.034043 | 5.6057e-05 | 5.6057e-05 | houston | N | 5.6057e-05 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.002946 | houston | N | -0.0015766 | 0.0011615 | -0.034043 | 5.6057e-05 | 5.6057e-05 | houston | N | 5.6057e-05 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.002946 | houston | N | -0.0015766 | 0.0011615 | -0.034043 | 5.6057e-05 | 5.6057e-05 | houston | N | 5.6057e-05 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.002946 | houston | N | -0.0015766 | 0.0011615 | -0.034043 | 5.6057e-05 | 5.6057e-05 | houston | N | 5.6057e-05 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.002946 | houston | N | -0.0015766 | 0.0011615 | -0.034043 | 5.6057e-05 | 5.6057e-05 | houston | N | 5.6057e-05 | 0
48651 | EP_1_2 | 1 | 5 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48651 | EP_1_2 | 2 | 21 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.002396 | north | N | -0.0010266 | 0.0017115 | -0.033493 | 0.00060606 | 0.00060606 | houston | Y | 0.0010266 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.002396 | north | N | -0.0010266 | 0.0017115 | -0.033493 | 0.00060606 | 0.00060606 | houston | Y | 0.0010266 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.002396 | north | N | -0.0010266 | 0.0017115 | -0.033493 | 0.00060606 | 0.00060606 | houston | Y | 0.0010266 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.002396 | north | N | -0.0010266 | 0.0017115 | -0.033493 | 0.00060606 | 0.00060606 | houston | Y | 0.0010266 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.002887 | houston | Y | -0.0015176 | 0.0012205 | -0.033984 | 0.00011506 | 0.00011506 | houston | N | 0.00011506 | 0
48691 | GBY_7374 | A | 46 | -0.002953 | houston | Y | -0.0015836 | 0.0011545 | -0.03405 | 4.9057e-05 | 4.9057e-05 | houston | N | 4.9057e-05 | 0
48691 | GBY_7374 | B | 46 | -0.002953 | houston | Y | -0.0015836 | 0.0011545 | -0.03405 | 4.9057e-05 | 4.9057e-05 | houston | N | 4.9057e-05 | 0
48692 | GBY_8182 | C | 46 | -0.002953 | houston | Y | -0.0015836 | 0.0011545 | -0.03405 | 4.9057e-05 | 4.9057e-05 | houston | N | 4.9057e-05 | 0
48692 | GBY_8182 | D | 55 | -0.002953 | houston | Y | -0.0015836 | 0.0011545 | -0.03405 | 4.9057e-05 | 4.9057e-05 | houston | N | 4.9057e-05 | 0
48693 | GBY_8384 | E | 55 | -0.002953 | houston | Y | -0.0015836 | 0.0011545 | -0.03405 | 4.9057e-05 | 4.9057e-05 | houston | N | 4.9057e-05 | 0
48693 | GBY_8384 | F | 54 | -0.002953 | houston | Y | -0.0015836 | 0.0011545 | -0.03405 | 4.9057e-05 | 4.9057e-05 | houston | N | 4.9057e-05 | 0
48721 | LEG_1___ | 1 | 827 | -0.001774 | north | Y | -0.00040456 | 0.0023335 | -0.032871 | 0.0012281 | 0.00040456 | North | N | 0.00040456 | 0
48722 | LEG_2___ | 2 | 819 | -0.001774 | north | Y | -0.00040456 | 0.0023335 | -0.032871 | 0.0012281 | 0.00040456 | North | N | 0.00040456 | 0
48730 | MNS_GT | 1 | 46.1 | -0.003078 | houston | N | -0.0017086 | 0.0010295 | -0.034175 | -7.5943e-05 | 7.5943e-05 | houston | N | 7.5943e-05 | 0
48731 | CBE_GT1 | 1 | 76 | -0.003374 | houston | Y | -0.0020046 | 0.00073348 | -0.034471 | -0.00037194 | 0.00037194 | houston | N | 0.00037194 | 0
48732 | CBE_GT2 | 1 | 76 | -0.003374 | houston | Y | -0.0020046 | 0.00073348 | -0.034471 | -0.00037194 | 0.00037194 | houston | N | 0.00037194 | 0
48733 | CBE_ST12 | 1 | 105 | -0.003374 | houston | Y | -0.0020046 | 0.00073348 | -0.034471 | -0.00037194 | 0.00037194 | houston | N | 0.00037194 | 0
48734 | CBE_GT3 | 1 | 74 | -0.003374 | houston | Y | -0.0020046 | 0.00073348 | -0.034471 | -0.00037194 | 0.00037194 | houston | N | 0.00037194 | 0
48735 | CBE_GT4 | 1 | 74 | -0.003374 | houston | Y | -0.0020046 | 0.00073348 | -0.034471 | -0.00037194 | 0.00037194 | houston | N | 0.00037194 | 0
48736 | CBE_ST34 | 1 | 102 | -0.003374 | houston | Y | -0.0020046 | 0.00073348 | -0.034471 | -0.00037194 | 0.00037194 | houston | N | 0.00037194 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48761 | PR_GT1__ | 1 | 35 | -0.002944 | houston | N | -0.0015746 | 0.0011635 | -0.034041 | 5.8057e-05 | 5.8057e-05 | houston | N | 5.8057e-05 | 0
48772 | PHR_GN2_ | MB | 459 | -0.002985 | houston | Y | -0.0016156 | 0.0011225 | -0.034082 | 1.7057e-05 | 1.7057e-05 | houston | N | 1.7057e-05 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.002901 | houston | N | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.002835 | houston | N | -0.0014656 | 0.0012725 | -0.033932 | 0.00016706 | 0.00016706 | houston | N | 0.00016706 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.002835 | houston | N | -0.0014656 | 0.0012725 | -0.033932 | 0.00016706 | 0.00016706 | houston | N | 0.00016706 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.002835 | houston | N | -0.0014656 | 0.0012725 | -0.033932 | 0.00016706 | 0.00016706 | houston | N | 0.00016706 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.002835 | houston | N | -0.0014656 | 0.0012725 | -0.033932 | 0.00016706 | 0.00016706 | houston | N | 0.00016706 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.002899 | houston | N | -0.0015296 | 0.0012085 | -0.033996 | 0.00010306 | 0.00010306 | houston | N | 0.00010306 | 0
48820 | SHELLG1_ | 1 | 71 | -0.002935 | houston | N | -0.0015656 | 0.0011725 | -0.034032 | 6.7057e-05 | 6.7057e-05 | houston | N | 6.7057e-05 | 0
48821 | SHELLG2 | 2 | 72 | -0.002935 | houston | N | -0.0015656 | 0.0011725 | -0.034032 | 6.7057e-05 | 6.7057e-05 | houston | N | 6.7057e-05 | 0
48822 | SHELLG3_ | 1 | 39 | -0.002935 | houston | N | -0.0015656 | 0.0011725 | -0.034032 | 6.7057e-05 | 6.7057e-05 | houston | N | 6.7057e-05 | 0
48822 | SHELLG3_ | 2 | 30 | -0.002935 | houston | N | -0.0015656 | 0.0011725 | -0.034032 | 6.7057e-05 | 6.7057e-05 | houston | N | 6.7057e-05 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.002949 | houston | N | -0.0015796 | 0.0011585 | -0.034046 | 5.3057e-05 | 5.3057e-05 | houston | N | 5.3057e-05 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.002949 | houston | N | -0.0015796 | 0.0011585 | -0.034046 | 5.3057e-05 | 5.3057e-05 | houston | N | 5.3057e-05 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.002939 | houston | N | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.00294 | houston | Y | -0.0015706 | 0.0011675 | -0.034037 | 6.2057e-05 | 6.2057e-05 | houston | N | 6.2057e-05 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.00294 | houston | Y | -0.0015706 | 0.0011675 | -0.034037 | 6.2057e-05 | 6.2057e-05 | houston | N | 6.2057e-05 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.002939 | houston | Y | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.002939 | houston | Y | -0.0015696 | 0.0011685 | -0.034036 | 6.3057e-05 | 6.3057e-05 | houston | N | 6.3057e-05 | 0
48855 | SRB_GT21 | B2 | 12 | -0.002941 | houston | Y | -0.0015716 | 0.0011665 | -0.034038 | 6.1057e-05 | 6.1057e-05 | houston | N | 6.1057e-05 | 0
48855 | SRB_GT21 | MB | 18 | -0.002941 | houston | Y | -0.0015716 | 0.0011665 | -0.034038 | 6.1057e-05 | 6.1057e-05 | houston | N | 6.1057e-05 | 0
48865 | TECO_GT1 | 1 | 50 | -0.003 | houston | Y | -0.0016306 | 0.0011075 | -0.034097 | 2.0571e-06 | 2.0571e-06 | houston | N | 2.0571e-06 | 0
48873 | THW_ST3_ | 3 | 104 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48874 | THW_ST4_ | 4 | 104 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48875 | THW_3132 | A | 54 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48875 | THW_3132 | B | 53 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48877 | THW_3334 | C | 54 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48877 | THW_3334 | D | 57 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48879 | THW_4142 | E | 54 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48879 | THW_4142 | F | 54 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48881 | THW_4344 | G | 58 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48881 | THW_4344 | H | 58 | -0.002916 | houston | Y | -0.0015466 | 0.0011915 | -0.034013 | 8.6057e-05 | 8.6057e-05 | houston | N | 8.6057e-05 | 0
48883 | THW_GT1_ | B2 | 12 | -0.002906 | houston | Y | -0.0015366 | 0.0012015 | -0.034003 | 9.6057e-05 | 9.6057e-05 | houston | N | 9.6057e-05 | 0
48885 | THW_5152 | A | 56 | -0.002882 | houston | Y | -0.0015126 | 0.0012255 | -0.033979 | 0.00012006 | 0.00012006 | houston | N | 0.00012006 | 0
48885 | THW_5152 | B | 59 | -0.002882 | houston | Y | -0.0015126 | 0.0012255 | -0.033979 | 0.00012006 | 0.00012006 | houston | N | 0.00012006 | 0
48886 | THW_5354 | C | 56 | -0.002882 | houston | Y | -0.0015126 | 0.0012255 | -0.033979 | 0.00012006 | 0.00012006 | houston | N | 0.00012006 | 0
48886 | THW_5354 | D | 56 | -0.002882 | houston | Y | -0.0015126 | 0.0012255 | -0.033979 | 0.00012006 | 0.00012006 | houston | N | 0.00012006 | 0
48887 | THW_5556 | E | 59 | -0.002882 | houston | Y | -0.0015126 | 0.0012255 | -0.033979 | 0.00012006 | 0.00012006 | houston | N | 0.00012006 | 0
48887 | THW_5556 | F | 56 | -0.002882 | houston | Y | -0.0015126 | 0.0012255 | -0.033979 | 0.00012006 | 0.00012006 | houston | N | 0.00012006 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.003327 | houston | Y | -0.0019576 | 0.00078048 | -0.034424 | -0.00032494 | 0.00032494 | houston | N | 0.00032494 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.003065 | houston | Y | -0.0016956 | 0.0010425 | -0.034162 | -6.2943e-05 | 6.2943e-05 | houston | N | 6.2943e-05 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.003065 | houston | Y | -0.0016956 | 0.0010425 | -0.034162 | -6.2943e-05 | 6.2943e-05 | houston | N | 6.2943e-05 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.003065 | houston | Y | -0.0016956 | 0.0010425 | -0.034162 | -6.2943e-05 | 6.2943e-05 | houston | N | 6.2943e-05 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.003065 | houston | Y | -0.0016956 | 0.0010425 | -0.034162 | -6.2943e-05 | 6.2943e-05 | houston | N | 6.2943e-05 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.003065 | houston | N | -0.0016956 | 0.0010425 | -0.034162 | -6.2943e-05 | 6.2943e-05 | houston | N | 6.2943e-05 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.003077 | houston | Y | -0.0017076 | 0.0010305 | -0.034174 | -7.4943e-05 | 7.4943e-05 | houston | N | 7.4943e-05 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.003077 | houston | Y | -0.0017076 | 0.0010305 | -0.034174 | -7.4943e-05 | 7.4943e-05 | houston | N | 7.4943e-05 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.003077 | houston | Y | -0.0017076 | 0.0010305 | -0.034174 | -7.4943e-05 | 7.4943e-05 | houston | N | 7.4943e-05 | 0
48929 | WAPGT21_ | B1 | 13 | -0.003065 | houston | Y | -0.0016956 | 0.0010425 | -0.034162 | -6.2943e-05 | 6.2943e-05 | houston | N | 6.2943e-05 | 0
48940 | WARVUE_G | G1 | 12 | -0.002901 | houston | Y | -0.0015316 | 0.0012065 | -0.033998 | 0.00010106 | 0.00010106 | houston | N | 0.00010106 | 0
49803 | EXN_15GT | 1 | 34 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49826 | EXN938GT | 5 | 45.9 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49828 | EXN941GT | 10 | 17.7 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49829 | EXN942GT | 11 | 20.4 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49830 | EXN943GT | 12 | 19.9 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49831 | EXN944GT | 13 | 35 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49832 | EXN945GT | 9 | 18 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49837 | EXN_GT | 4 | 85.4 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49838 | EXN_14GT | 14 | 148 | -0.002909 | houston | N | -0.0015396 | 0.0011985 | -0.034006 | 9.3057e-05 | 9.3057e-05 | houston | N | 9.3057e-05 | 0
49851 | DOW17000 | 37 | 62 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49858 | DOW38100 | 31 | 71.4 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49859 | DOW38200 | 33 | 45 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49860 | DOW38300 | 32 | 101 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49862 | DOW39100 | 36 | 86 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49863 | DOW39200 | 35 | 88 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49865 | DOW41000 | 41 | 50 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49866 | DOW42000 | 42 | 18 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49869 | DOW49000 | 45 | 94 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49870 | DOW61000 | 61 | 70 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49871 | DOW62000 | 62 | 63 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49872 | DOW63000 | 63 | 72 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49873 | DOW64000 | 64 | 64.8 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49876 | DOW65000 | 65 | 101 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49877 | DOW66000 | 66 | 97 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49878 | DOW67000 | 67 | 103 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49882 | DOW81000 | 81 | 76 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49884 | DOW82000 | 82 | 80 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49885 | DOW83000 | 83 | 80 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
49886 | DOW84000 | 84 | 171 | -0.003212 | houston | N | -0.0018426 | 0.00089548 | -0.034309 | -0.00020994 | 0.00020994 | houston | N | 0.00020994 | 0
58909 | PEARSALL | 1 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58909 | PEARSALL | 2 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58909 | PEARSALL | 3 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58909 | PEARSALL | 4 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58909 | PEARSALL | 5 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58909 | PEARSALL | 6 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58919 | PEARSALL | 1 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58919 | PEARSALL | 2 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58919 | PEARSALL | 3 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58919 | PEARSALL | 4 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58919 | PEARSALL | 5 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58919 | PEARSALL | 6 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58929 | PEARSALL | 1 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58929 | PEARSALL | 2 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58929 | PEARSALL | 3 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58929 | PEARSALL | 4 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58929 | PEARSALL | 5 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58929 | PEARSALL | 6 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58949 | PEARSALL | 1 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58949 | PEARSALL | 2 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58949 | PEARSALL | 3 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58949 | PEARSALL | 4 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58949 | PEARSALL | 5 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
58949 | PEARSALL | 6 | 8.4 | -0.002291 | south | Y | -0.00092156 | 0.0018165 | -0.033388 | 0.00071106 | 0.00071106 | houston | Y | 0.0018165 | 0.0092856
60000 | DSKY2 | 1 | 76.5 | 0.027621 | west | Y | 0.02899 | 0.031728 | -0.0034759 | 0.030623 | 0.0034759 | west | N | 0.0034759 | 0
60003 | KING_NE1 | 1 | 80 | 0.028471 | west | Y | 0.02984 | 0.032578 | -0.0026259 | 0.031473 | 0.0026259 | west | N | 0.0026259 | 0
60005 | KING_SE1 | 1 | 40 | 0.028471 | west | Y | 0.02984 | 0.032578 | -0.0026259 | 0.031473 | 0.0026259 | west | N | 0.0026259 | 0
60007 | KING_SW1 | 1 | 80 | 0.028597 | west | Y | 0.029966 | 0.032704 | -0.0024999 | 0.031599 | 0.0024999 | west | N | 0.0024999 | 0
60016 | WOODWRD1 | 1 | 80 | 0.028445 | west | Y | 0.029814 | 0.032552 | -0.0026519 | 0.031447 | 0.0026519 | west | N | 0.0026519 | 0
60017 | ORNNWP1 | 1 | 80 | 0.02778 | west | Y | 0.029149 | 0.031887 | -0.0033169 | 0.030782 | 0.0033169 | west | N | 0.0033169 | 0
60018 | DSKY1 | 1 | 84 | 0.027563 | west | Y | 0.028932 | 0.03167 | -0.0035339 | 0.030565 | 0.0035339 | west | N | 0.0035339 | 0
60019 | KING_NW1 | 1 | 80 | 0.028597 | west | Y | 0.029966 | 0.032704 | -0.0024999 | 0.031599 | 0.0024999 | west | N | 0.0024999 | 0
60057 | CALLAHAN | 1 | 114 | -0.00407 | south | Y | -0.0027006 | 3.7483e-05 | -0.035167 | -0.0010679 | 3.7483e-05 | south | N | 3.7483e-05 | 0
60058 | BUFF_GAP | 1 | 120 | 0.035259 | west | Y | 0.036628 | 0.039366 | 0.0041621 | 0.038261 | 0.0041621 | west | N | 0.0041621 | 0
60060 | CIRELLO | 1 | 233 | 0.035259 | west | Y | 0.036628 | 0.039366 | 0.0041621 | 0.038261 | 0.0041621 | west | N | 0.0041621 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.035259 | west | Y | 0.036628 | 0.039366 | 0.0041621 | 0.038261 | 0.0041621 | west | N | 0.0041621 | 0
60066 | H_HOLLOW | 1 | 222 | -0.00407 | south | Y | -0.0027006 | 3.7483e-05 | -0.035167 | -0.0010679 | 3.7483e-05 | south | N | 3.7483e-05 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.00407 | south | Y | -0.0027006 | 3.7483e-05 | -0.035167 | -0.0010679 | 3.7483e-05 | south | N | 3.7483e-05 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.00407 | south | Y | -0.0027006 | 3.7483e-05 | -0.035167 | -0.0010679 | 3.7483e-05 | south | N | 3.7483e-05 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.00407 | south | Y | -0.0027006 | 3.7483e-05 | -0.035167 | -0.0010679 | 3.7483e-05 | south | N | 3.7483e-05 | 0
60074 | HORSH5 | 1 | 100 | -0.00407 | south | Y | -0.0027006 | 3.7483e-05 | -0.035167 | -0.0010679 | 3.7483e-05 | south | N | 3.7483e-05 | 0
60081 | WHRLWIND | 1 | 60 | 0.043174 | west | Y | 0.044543 | 0.047281 | 0.012077 | 0.046176 | 0.012077 | west | N | 0.012077 | 0
60201 | RIO DRCS | F | 0 | 0.004475 | south | N | 0.0058444 | 0.0085825 | -0.026622 | 0.0074771 | 0.0058444 | North | Y | 0.0085825 | 0
60202 | FRIEND_R | F | 0 | 0.024129 | west | N | 0.025498 | 0.028236 | -0.0069679 | 0.027131 | 0.0069679 | west | N | 0.0069679 | 0
60203 | PRES0A | BT | 4.8 | 0.029105 | west | N | 0.030474 | 0.033212 | -0.0019919 | 0.032107 | 0.0019919 | west | N | 0.0019919 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.031635 | west | Y | 0.033004 | 0.035742 | 0.00053807 | 0.034637 | 0.00053807 | west | N | 0.00053807 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.031635 | west | Y | 0.033004 | 0.035742 | 0.00053807 | 0.034637 | 0.00053807 | west | N | 0.00053807 | 0
71057 | L_SWEETW | W1 | 135 | 0.031635 | west | Y | 0.033004 | 0.035742 | 0.00053807 | 0.034637 | 0.00053807 | west | N | 0.00053807 | 0
71059 | L_SWEETW | W1 | 119 | 0.031635 | west | Y | 0.033004 | 0.035742 | 0.00053807 | 0.034637 | 0.00053807 | west | N | 0.00053807 | 0
71060 | L_SWEETW | W1 | 105 | 0.031635 | west | Y | 0.033004 | 0.035742 | 0.00053807 | 0.034637 | 0.00053807 | west | N | 0.00053807 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.031635 | west | Y | 0.033004 | 0.035742 | 0.00053807 | 0.034637 | 0.00053807 | west | N | 0.00053807 | 0
76031 | L_GASCCR | W1 | 150 | 0.029123 | west | Y | 0.030492 | 0.03323 | -0.0019739 | 0.032125 | 0.0019739 | west | N | 0.0019739 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.028862 | west | Y | 0.030231 | 0.032969 | -0.0022349 | 0.031864 | 0.0022349 | west | N | 0.0022349 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.028862 | west | Y | 0.030231 | 0.032969 | -0.0022349 | 0.031864 | 0.0022349 | west | N | 0.0022349 | 0
76096 | L_CAPRSI | W1 | 186 | 0.028862 | west | Y | 0.030231 | 0.032969 | -0.0022349 | 0.031864 | 0.0022349 | west | N | 0.0022349 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.028862 | west | Y | 0.030231 | 0.032969 | -0.0022349 | 0.031864 | 0.0022349 | west | N | 0.0022349 | 0
80003 | MILHWYS | F | 0 | -0.003554 | south | N | -0.0021846 | 0.00055348 | -0.034651 | -0.00055194 | 0.00055194 | houston | Y | 0.00055348 | 0
80010 | EPLVT1 | F | 0 | 0.002413 | south | N | 0.0037824 | 0.0065205 | -0.028684 | 0.0054151 | 0.0037824 | North | Y | 0.0065205 | 0
80012 | LAR | F | 0 | -0.002928 | south | N | -0.0015586 | 0.0011795 | -0.034025 | 7.4057e-05 | 7.4057e-05 | houston | Y | 0.0011795 | 0
80051 | FORPVCM0 | 8 | 28 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
80053 | FOR69CG0 | 10 | 74 | -0.003587 | south | N | -0.0022176 | 0.00052048 | -0.034684 | -0.00058494 | 0.00052048 | south | N | 0.00052048 | 0
80080 | GWINDT11 | 1 | 94 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80080 | GWINDT11 | 2 | 41 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80080 | GWINDT11 | 3 | 38 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80080 | GWINDT11 | 4 | 19 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80081 | GWINDT21 | 1 | 94 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80081 | GWINDT21 | 2 | 36 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80081 | GWINDT21 | 3 | 43 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80081 | GWINDT21 | 4 | 22 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80137 | CSDR89 | 8 | 39 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
80137 | CSDR89 | 9 | 15 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
80138 | CSDR7 | 7 | 7 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
80139 | CSDR56 | 5 | 15 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
80139 | CSDR56 | 6 | 39 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
80140 | CSDR11 | 11 | 39 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
80180 | PNSCALT1 | 1 | 148 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80180 | PNSCALT1 | 2 | 50 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80181 | PNSCALT2 | 1 | 55 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80181 | PNSCALT2 | 2 | 50 | -0.003561 | south | Y | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
80223 | REYSHR G | 1 | 12 | -0.003572 | south | N | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
80224 | VISTRONG | 1 | 15 | -0.003617 | south | N | -0.0022476 | 0.00049048 | -0.034714 | -0.00061494 | 0.00049048 | south | N | 0.00049048 | 0
80225 | VISTRONG | 2 | 23 | -0.003617 | south | N | -0.0022476 | 0.00049048 | -0.034714 | -0.00061494 | 0.00049048 | south | N | 0.00049048 | 0
80226 | ALCOA G | 1 | 48 | -0.003593 | south | N | -0.0022236 | 0.00051448 | -0.03469 | -0.00059094 | 0.00051448 | south | N | 0.00051448 | 0
80227 | AIRCO G | 1 | 8 | -0.003606 | south | N | -0.0022366 | 0.00050148 | -0.034703 | -0.00060394 | 0.00050148 | south | N | 0.00050148 | 0
80261 | NBEC81A | 1 | 180 | -0.003572 | south | Y | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
80262 | NBEC91A | 1 | 180 | -0.003572 | south | Y | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.003572 | south | Y | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.003572 | south | Y | -0.0022026 | 0.00053548 | -0.034669 | -0.00056994 | 0.00053548 | south | N | 0.00053548 | 0
80265 | LARECU40 | 4 | 100 | -0.002929 | south | Y | -0.0015596 | 0.0011785 | -0.034026 | 7.3057e-05 | 7.3057e-05 | houston | Y | 0.0011785 | 0.11054
80266 | LARECU50 | 5 | 100 | -0.002929 | south | Y | -0.0015596 | 0.0011785 | -0.034026 | 7.3057e-05 | 7.3057e-05 | houston | Y | 0.0011785 | 0.11054
80291 | PAPALOTE | 1 | 25 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
80291 | PAPALOTE | 2 | 25 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
80291 | PAPALOTE | 3 | 25 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
80291 | PAPALOTE | 4 | 16 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
80294 | PAPALOTE | 5 | 25 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
80294 | PAPALOTE | 6 | 25 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
80294 | PAPALOTE | 7 | 25 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
80294 | PAPALOTE | 8 | 15 | -0.003571 | south | Y | -0.0022016 | 0.00053648 | -0.034668 | -0.00056894 | 0.00053648 | south | N | 0.00053648 | 0
86104 | CID-138 | EQ | 0 | -0.002929 | south | N | -0.0015596 | 0.0011785 | -0.034026 | 7.3057e-05 | 7.3057e-05 | houston | Y | 0.0011785 | 0
86105 | CID-230 | EQ | 500 | -0.002929 | south | N | -0.0015596 | 0.0011785 | -0.034026 | 7.3057e-05 | 7.3057e-05 | houston | Y | 0.0011785 | 0
86106 | CUF-230 | EQ | 500 | -0.002929 | south | N | -0.0015596 | 0.0011785 | -0.034026 | 7.3057e-05 | 7.3057e-05 | houston | Y | 0.0011785 | 0
86107 | CUF-138 | EQ | 0 | -0.002929 | south | N | -0.0015596 | 0.0011785 | -0.034026 | 7.3057e-05 | 7.3057e-05 | houston | Y | 0.0011785 | 0
88198 | BEEVILLE | F | 0 | -0.003561 | south | N | -0.0021916 | 0.00054648 | -0.034658 | -0.00055894 | 0.00054648 | south | N | 0.00054648 | 0
88253 | HAMILTON | F | 0 | 0.005582 | south | N | 0.0069514 | 0.0096895 | -0.025515 | 0.0085841 | 0.0069514 | North | Y | 0.0096895 | 0
88299 | ZAPATA | F | 0 | -0.003118 | south | N | -0.0017486 | 0.00098948 | -0.034215 | -0.00011594 | 0.00011594 | houston | Y | 0.00098948 | 0
88508 | FALFURRI | F | 0 | -0.003481 | south | N | -0.0021116 | 0.00062648 | -0.034578 | -0.00047894 | 0.00047894 | houston | Y | 0.00062648 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:Leon Switch - Flatcreek 138kV 1624-1642 C:Comanchee SS Auto 1440-1441 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.059966 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.5118 | 242 | 0.060787 | 14.7105 | 242 | 14.7105
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.047455 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1182 | 150 | 0.048276 | 7.2414
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.047455 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.793 | 101 | 0.048276 | 4.8759
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.043174 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5904 | 60 | 0.043995 | 2.6397 |  |  | Weighted Shift Factors
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.040971 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1456 | 150 | 0.041792 | 6.2688 |  |  | West | 0.031097
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.035797 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0069 | 84 | 0.036618 | 3.0759 |  |  | North | -0.0008211
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2311 | 120 | 0.03608 | 4.3296 |  |  |  | 0.031918
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2153 | 233 | 0.03608 | 8.4067
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0011 | 170.2 | 0.03608 | 6.1408 |  |  | Line Rating | 96.8
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.034617 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4271 | 99 | 0.035438 | 3.5084 |  |  | Conc Gen | 242
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.034617 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1116 | 61 | 0.035438 | 2.1617 |  |  | Weighted Imp. | 14.7105
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 1 | 0.86542 | 0 | 0.035438 | 0 |  |  | PTDF | 0.060787
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 1 | 1.582 | 0 | 0.035438 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 1 | 1.582 | 0 | 0.035438 | 0 |  |  | Concentration | 1.9045
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.034552 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8718 | 141 | 0.035373 | 4.9876
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.034552 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1462 | 120 | 0.035373 | 4.2448
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.034374 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1656 | 63 | 0.035195 | 2.2173
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.033455 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0219 | 180 | 0.034276 | 6.1697
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.033455 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0219 | 180 | 0.034276 | 6.1697
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.033348 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5033 | 225 | 0.034169 | 7.688
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.033018 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5966 | 169.5 | 0.033839 | 5.7357
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.032763 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9316 | 120 | 0.033584 | 4.0301
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.032566 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9079 | 120 | 0.033387 | 4.0065
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1453 | 66 | 0.033325 | 2.1995
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2428 | 69 | 0.033325 | 2.2994
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2428 | 69 | 0.033325 | 2.2994
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1778 | 67 | 0.033325 | 2.2328
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1778 | 67 | 0.033325 | 2.2328
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1128 | 65 | 0.033325 | 2.1661
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.032305 | west | 8 | N | N | Nwest | Nwest | 1 | 0.83347 | 0 | 0.033126 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.031641 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20883 | 6.6 | 0.032462 | 0.21425
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.031641 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0853 | 34.3 | 0.032462 | 1.1135
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.03164 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7773 | 214.2 | 0.032461 | 6.9532
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1863 | 37.5 | 0.032456 | 1.2171
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4008 | 107.5 | 0.032456 | 3.489
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2707 | 135 | 0.032456 | 4.3816
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7646 | 119 | 0.032456 | 3.8623
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3217 | 105 | 0.032456 | 3.4079
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5466 | 80.5 | 0.032456 | 2.6127
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.031499 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8269 | 58 | 0.03232 | 1.8746
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.031303 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.146 | 100.5 | 0.032124 | 3.2285
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.030686 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5722 | 149 | 0.031507 | 4.6946
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1328 | 0 | 0.031289 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 1 | 2.2364 | 0 | 0.031289 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1449 | 0 | 0.031289 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5674 | 150 | 0.03127 | 4.6905
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6988 | 220 | 0.03127 | 6.8794
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0898 | 200 | 0.03127 | 6.254
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7117 | 121.9 | 0.03127 | 3.8118
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.030419 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0647 | 35 | 0.03124 | 1.0934
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.030419 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.91257 | 30 | 0.03124 | 0.9372
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1273 | 70 | 0.031211 | 2.1848
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1273 | 70 | 0.031211 | 2.1848
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8202 | 92.8 | 0.031211 | 2.8964
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4312 | 80 | 0.031211 | 2.4969
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4312 | 80 | 0.031211 | 2.4969
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4949 | 115 | 0.031211 | 3.5893
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.327 | 208.2 | 0.03121 | 6.4979
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3183 | 142.1 | 0.03121 | 4.435
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.0235 | 132.4 | 0.03121 | 4.1322
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.1329 | 136 | 0.03121 | 4.2446
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.4672 | 147 | 0.03121 | 4.5879
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.3817 | 210 | 0.03121 | 6.5541
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0003 | 66 | 0.031128 | 2.0545
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.97 | 65 | 0.031128 | 2.0233
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0306 | 67 | 0.031128 | 2.0856
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0306 | 67 | 0.031128 | 2.0856
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0306 | 67 | 0.031128 | 2.0856
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.030307 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.031128 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.030307 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.031128 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.030257 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7821 | 125 | 0.031078 | 3.8848
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.030257 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7821 | 125 | 0.031078 | 3.8848
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1538 | 209 | 0.030265 | 6.3254
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7247 | 126.5 | 0.030265 | 3.8285
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3316 | 249 | 0.030265 | 7.536
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8005 | 197 | 0.030265 | 5.9622
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.029123 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3685 | 150 | 0.029944 | 4.4916
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.029105 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.1397 | 0 | 0.029926 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.247 | 112.5 | 0.029683 | 3.3393
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3149 | 149.5 | 0.029683 | 4.4376
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3683 | 186 | 0.029683 | 5.5211
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1909 | 214.5 | 0.029683 | 6.367
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.028705 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.482 | 400 | 0.029526 | 11.8104
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.028688 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7704 | 236 | 0.029509 | 6.9641
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028597 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2878 | 80 | 0.029418 | 2.3534
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028597 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2878 | 80 | 0.029418 | 2.3534
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.02855 | west | 4 | Y | N | Ywest | Nwest | 1 | 18.5489 | 649.7 | 0.029371 | 19.0824
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1353 | 75 | 0.029292 | 2.1969
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2777 | 80 | 0.029292 | 2.3434
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1388 | 40 | 0.029292 | 1.1717
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028445 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2756 | 80 | 0.029266 | 2.3413
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.028441 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2753 | 80 | 0.029262 | 2.341
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.028424 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2636 | 150 | 0.029245 | 4.3868
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.028424 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2636 | 150 | 0.029245 | 4.3868
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.56598 | 20 | 0.02912 | 0.5824
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.56598 | 20 | 0.02912 | 0.5824
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.56598 | 20 | 0.02912 | 0.5824
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48108 | 17 | 0.02912 | 0.49504
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02778 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2224 | 80 | 0.028601 | 2.2881
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.027621 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.113 | 76.5 | 0.028442 | 2.1758
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.027563 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3153 | 84 | 0.028384 | 2.3843
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.027231 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4931 | 165 | 0.028052 | 4.6286
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.024129 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.02495 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.022615 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.2771 | 366 | 0.023436 | 8.5776
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.020878 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1317 | 150 | 0.021699 | 3.2549
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.019725 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.367 | 120 | 0.020546 | 2.4655
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7118 | 204 | 0.014114 | 2.8793
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6719 | 201 | 0.014114 | 2.8369
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2169 | 242 | 0.014114 | 3.4156
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.01221 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14652 | 0 | 0.013031 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.01221 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14652 | 0 | 0.013031 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.004475 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.0052961 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.004079 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.45889 | 112.5 | 0.0049001 | 0.55126
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.00375 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.225 | 60 | 0.0045711 | 0.27427
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.00375 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.23625 | 63 | 0.0045711 | 0.28798
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.002849 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0036701 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.002849 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0036701 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.002849 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0036701 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.002008 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028291 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.001682 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06728 | 0 | 0.0025031 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.001682 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06728 | 0 | 0.0025031 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.001681 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0025021 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.001608 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.27336 | 170 | 0.0024291 | 0.41295
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.001608 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.83616 | 520 | 0.0024291 | 1.2631
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.001516 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.56092 | 370 | 0.0023371 | 0.86473
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.21224 | 0 | 0.0023371 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.21376 | 0 | 0.0023371 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.46844 | 0 | 0.0023371 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.21679 | 0 | 0.0023371 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2183 | 0 | 0.0023371 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.46996 | 0 | 0.0023371 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.23536 | 160 | 0.0022921 | 0.36674
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.22948 | 156 | 0.0022921 | 0.35757
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.28832 | 196 | 0.0022921 | 0.44925
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.22948 | 156 | 0.0022921 | 0.35757
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.23095 | 157 | 0.0022921 | 0.35986
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.29126 | 198 | 0.0022921 | 0.45384
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.108 | 0 | 0.0022611 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.11462 | 0 | 0.0022611 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.1273 | 0 | 0.0022611 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.77674 | 558 | 0.0022131 | 1.2349
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.80597 | 579 | 0.0022131 | 1.2814
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1247 | 808 | 0.0022131 | 1.7882
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.001234 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.48743 | 395 | 0.0020551 | 0.81177
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.001234 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.53679 | 435 | 0.0020551 | 0.89397
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.091877 | 79 | 0.0019841 | 0.15674
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.12328 | 106 | 0.0019841 | 0.21032
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1698 | 146 | 0.0019841 | 0.28968
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.001163 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.088388 | 76 | 0.0019841 | 0.15079
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0222 | 20 | 0.0019311 | 0.038622
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.02775 | 25 | 0.0019311 | 0.048278
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04551 | 41 | 0.0019311 | 0.079175
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.001108 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.48198 | 435 | 0.0019291 | 0.83916
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.001106 | north | 3 | N | N | Nnorth | Nnorth | 1 | 1.2796 | 0 | 0.0019271 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.001106 | north | 3 | N | N | Nnorth | Nnorth | 1 | 1.2807 | 0 | 0.0019271 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.001096 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04384 | 40 | 0.0019171 | 0.076684
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.23142 | 217.3 | 0.0018861 | 0.40985
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.21832 | 205 | 0.0018861 | 0.38665
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.29011 | 272.4 | 0.0018861 | 0.51377
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.000877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.34028 | 388 | 0.0016981 | 0.65886
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.000877 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.45165 | 515 | 0.0016981 | 0.87452
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13347 | 161 | 0.0016501 | 0.26567
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13596 | 164 | 0.0016501 | 0.27062
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13596 | 164 | 0.0016501 | 0.27062
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.34321 | 414 | 0.0016501 | 0.68314
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.1343 | 162 | 0.0016501 | 0.26732
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13347 | 161 | 0.0016501 | 0.26567
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13513 | 163 | 0.0016501 | 0.26897
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.33906 | 409 | 0.0016501 | 0.67489
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000802 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0016231 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000802 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0016231 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.000556 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.065608 | 118 | 0.0013771 | 0.1625
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.000556 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.06394 | 115 | 0.0013771 | 0.15837
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.000556 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.30914 | 556 | 0.0013771 | 0.76567
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.066725 | 785 | 0.0009061 | 0.71129
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.067575 | 795 | 0.0009061 | 0.72035
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.0663 | 780 | 0.0009061 | 0.70676
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0008211 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0008211 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.002072 | 0 | 0.0008071 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00182 | 0 | 0.0008071 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00203 | 0 | 0.0008071 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.005586 | 0 | 0.0008071 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -9.4e-05 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0007271 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.000102 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.0051 | 50 | 0.0007191 | 0.035955
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.000136 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.024752 | 182 | 0.0006851 | 0.12469
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.000136 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.065824 | 484 | 0.0006851 | 0.33159
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.000191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.041332 | 216.4 | 0.0006301 | 0.13635
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.000191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.041275 | 216.1 | 0.0006301 | 0.13617
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.14784 | 224 | 0.0001611 | 0.036087
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.14916 | 226 | 0.0001611 | 0.03641
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13992 | 212 | 0.0001611 | 0.034154
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13926 | 211 | 0.0001611 | 0.033993
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13074 | 151.5 | -4.1896e-05 | -0.0063472
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13143 | 152.3 | -4.1896e-05 | -0.0063807
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.15318 | 177.5 | -4.1896e-05 | -0.0074365
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13216 | 150.7 | -5.5896e-05 | -0.0084235
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13243 | 151 | -5.5896e-05 | -0.0084403
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.15558 | 177.4 | -5.5896e-05 | -0.0099159
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.00096 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0001389 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.001029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.63284 | 615 | -0.0002079 | -0.12786
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.001029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.60402 | 587 | -0.0002079 | -0.12203
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.001579 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.3537 | 224 | -0.0007579 | -0.16977
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.001622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.31791 | 196 | -0.0008009 | -0.15698
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.001622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.18004 | 111 | -0.0008009 | -0.088899
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.001774 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.4671 | 827 | -0.0009529 | -0.78804
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.001774 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.4529 | 819 | -0.0009529 | -0.78042
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.645 | 855 | -0.0011029 | -0.94298
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.645 | 855 | -0.0011029 | -0.94298
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.29303 | 152.3 | -0.0011029 | -0.16797
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.29437 | 153 | -0.0011029 | -0.16874
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.002303 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.0663 | 463 | -0.0014819 | -0.68612
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.36946 | 0 | -0.0015749 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.37378 | 0 | -0.0015749 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.37378 | 0 | -0.0015749 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.91048 | 0 | -0.0015749 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.002431 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.077792 | 0 | -0.0016099 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.002431 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.041327 | 17 | -0.0016099 | -0.027368
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.002483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11918 | 48 | -0.0016619 | -0.079771
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.002483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11422 | 46 | -0.0016619 | -0.076447
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.002483 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.26071 | 105 | -0.0016619 | -0.1745
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.81936 | 288 | -0.0020239 | -0.58288
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41822 | 147 | -0.0020239 | -0.29751
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41822 | 147 | -0.0020239 | -0.29751
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.407 | 100 | -0.0032489 | -0.32489
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.005165 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0043439 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.005165 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.0649 | 787 | -0.0043439 | -3.4186
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.005771 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0049499 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.005771 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0049499 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.009406 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.5802 | 168 | -0.0085849 | -1.4423
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.009406 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.84654 | 90 | -0.0085849 | -0.77264
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.010896 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7785 | 255 | -0.010075 | -2.5691
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.010896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6235 | 149 | -0.010075 | -1.5012
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.010896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6671 | 153 | -0.010075 | -1.5415
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.25184 | 18 | -0.01317 | -0.23706
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.25184 | 18 | -0.01317 | -0.23706
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.53166 | 38 | -0.01317 | -0.50046
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.015486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3229 | 150 | -0.014665 | -2.1997
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.015486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2389 | 80 | -0.014665 | -1.1732
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.016741 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.25111 | 0 | -0.01592 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.016741 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.25111 | 0 | -0.01592 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4183 | 70 | -0.01944 | -1.3608
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.398 | 69 | -0.01944 | -1.3414
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.398 | 69 | -0.01944 | -1.3414
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.3777 | 68 | -0.01944 | -1.3219
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.005582 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18421 | 0 | -0.025515 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.005582 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13955 | 0 | -0.025515 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.005582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.025515 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.003011 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018066 | 0 | -0.028086 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.002413 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.028684 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031097 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031097 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002531 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.060744 | 24 | -0.033628 | -0.80707
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002531 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.060744 | 24 | -0.033628 | -0.80707
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.002531 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.058213 | 23 | -0.033628 | -0.77344
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49045 | 0 | -0.033932 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.44226 | 0 | -0.033932 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.43659 | 0 | -0.033932 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.43659 | 0 | -0.033932 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.002835 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45927 | 0 | -0.033932 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17004 | 59 | -0.033979 | -2.0048
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17004 | 59 | -0.033979 | -2.0048
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.002887 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.149 | 398 | -0.033984 | -13.5256
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47033 | 0 | -0.033986 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46628 | 0 | -0.033986 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45906 | 0 | -0.033986 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77772 | 0 | -0.033986 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49828 | 172 | -0.033994 | -5.847
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49828 | 172 | -0.033994 | -5.847
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49828 | 172 | -0.033994 | -5.847
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002899 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45514 | 0 | -0.033996 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.0029 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.1547 | 743 | -0.033997 | -25.2597
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002901 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.034812 | 12 | -0.033998 | -0.40798
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18857 | 0 | -0.033998 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19147 | 0 | -0.033998 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20307 | 0 | -0.033998 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18276 | 0 | -0.033998 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17986 | 0 | -0.033998 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3017 | 0 | -0.033998 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17116 | 0 | -0.033998 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.014505 | 0 | -0.033998 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.060921 | 0 | -0.033998 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.034872 | 12 | -0.034003 | -0.40804
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.098906 | 0 | -0.034006 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10094 | 0 | -0.034006 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.095124 | 0 | -0.034006 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13352 | 0 | -0.034006 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051489 | 0 | -0.034006 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059344 | 0 | -0.034006 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057889 | 0 | -0.034006 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10182 | 0 | -0.034006 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052362 | 0 | -0.034006 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24843 | 0 | -0.034006 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43053 | 0 | -0.034006 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002912 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.1403 | 735 | -0.034009 | -24.9966
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30326 | 104 | -0.034013 | -3.5373
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30326 | 104 | -0.034013 | -3.5373
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15455 | 53 | -0.034013 | -1.8027
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16621 | 57 | -0.034013 | -1.9387
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16913 | 58 | -0.034013 | -1.9727
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16913 | 58 | -0.034013 | -1.9727
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002926 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5062 | 0 | -0.034023 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002926 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39501 | 0 | -0.034023 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.002928 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034025 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12298 | 42 | -0.034025 | -1.429
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12298 | 42 | -0.034025 | -1.429
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11126 | 38 | -0.034025 | -1.2929
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11126 | 38 | -0.034025 | -1.2929
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.002929 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2929 | 100 | -0.034026 | -3.4026
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.002929 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2929 | 100 | -0.034026 | -3.4026
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002929 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39834 | 0 | -0.034026 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20838 | 0 | -0.034032 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21132 | 0 | -0.034032 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11446 | 0 | -0.034032 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.08805 | 0 | -0.034032 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.52902 | 0 | -0.034036 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46613 | 0 | -0.034036 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46142 | 0 | -0.034036 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.002939 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.67009 | 228 | -0.034036 | -7.7602
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1881 | 0 | -0.034036 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18574 | 0 | -0.034036 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24276 | 0 | -0.034036 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21631 | 0 | -0.034036 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.047612 | 0 | -0.034036 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.002939 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.62601 | 213 | -0.034036 | -7.2497
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00294 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43806 | 0 | -0.034037 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00294 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19139 | 0 | -0.034037 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.00294 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.4851 | 165 | -0.034037 | -5.6161
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00294 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.49686 | 169 | -0.034037 | -5.7522
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002941 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.035292 | 12 | -0.034038 | -0.40846
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.002941 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.034038 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.002944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10304 | 0 | -0.034041 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48079 | 0 | -0.034043 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46282 | 0 | -0.034043 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46399 | 0 | -0.034043 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46252 | 0 | -0.034043 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79247 | 0 | -0.034043 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.002949 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23002 | 0 | -0.034046 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.002949 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23592 | 0 | -0.034046 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13584 | 46 | -0.03405 | -1.5663
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13584 | 46 | -0.03405 | -1.5663
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13584 | 46 | -0.03405 | -1.5663
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16242 | 55 | -0.03405 | -1.8727
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16242 | 55 | -0.03405 | -1.8727
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.15946 | 54 | -0.03405 | -1.8387
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19253 | 0 | -0.034059 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.17772 | 0 | -0.034059 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19253 | 0 | -0.034059 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19253 | 0 | -0.034059 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27009 | 0 | -0.034065 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26 | 0 | -0.034065 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25822 | 0 | -0.034065 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16176 | 0 | -0.034065 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03621 | 0 | -0.034065 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.002985 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.034082 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.003 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15 | 50 | -0.034097 | -1.7048
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2136 | 0 | -0.034114 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20123 | 0 | -0.034114 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1599 | 0 | -0.034114 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4622 | 0 | -0.034114 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46311 | 0 | -0.034114 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45949 | 0 | -0.034114 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.28963 | 0 | -0.034114 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73615 | 0 | -0.034114 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12068 | 0 | -0.034114 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.003018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096576 | 0 | -0.034115 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.003018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09054 | 0 | -0.034115 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30271 | 0 | -0.034115 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.28037 | 0 | -0.034115 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30995 | 0 | -0.034115 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30784 | 0 | -0.034115 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10114 | 0 | -0.034162 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.49346 | 161 | -0.034162 | -5.5001
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.50879 | 166 | -0.034162 | -5.6709
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.76012 | 248 | -0.034162 | -8.4722
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.003065 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.6735 | 546 | -0.034162 | -18.6524
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.003065 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -1.9708 | 0 | -0.034162 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.003065 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.039845 | 13 | -0.034162 | -0.44411
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50155 | 0 | -0.034174 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50155 | 0 | -0.034174 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75387 | 0 | -0.034174 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -2.0031 | 651 | -0.034174 | -22.2472
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.7354 | 564 | -0.034174 | -19.2741
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.8462 | 600 | -0.034174 | -20.5044
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.003078 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1419 | 0 | -0.034175 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003118 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034215 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35087 | 0 | -0.034258 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35087 | 0 | -0.034258 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.37616 | 0 | -0.034258 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.34613 | 0 | -0.034258 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.003183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22599 | 0 | -0.03428 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.003183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03183 | 0 | -0.03428 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19914 | 0 | -0.034309 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22934 | 0 | -0.034309 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14454 | 0 | -0.034309 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32441 | 0 | -0.034309 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27623 | 0 | -0.034309 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28266 | 0 | -0.034309 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1606 | 0 | -0.034309 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057816 | 0 | -0.034309 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30193 | 0 | -0.034309 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22484 | 0 | -0.034309 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20236 | 0 | -0.034309 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23126 | 0 | -0.034309 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20814 | 0 | -0.034309 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32441 | 0 | -0.034309 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31156 | 0 | -0.034309 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33084 | 0 | -0.034309 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24411 | 0 | -0.034309 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25696 | 0 | -0.034309 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25696 | 0 | -0.034309 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54925 | 0 | -0.034309 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039672 | 0 | -0.034403 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036366 | 0 | -0.034403 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039672 | 0 | -0.034403 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.21958 | 66 | -0.034424 | -2.272
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.003373 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -4.4962 | 0 | -0.03447 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.003373 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -4.4793 | 0 | -0.03447 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.25642 | 76 | -0.034471 | -2.6198
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.25642 | 76 | -0.034471 | -2.6198
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35427 | 105 | -0.034471 | -3.6194
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24968 | 74 | -0.034471 | -2.5508
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24968 | 74 | -0.034471 | -2.5508
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.34415 | 102 | -0.034471 | -3.516
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.003481 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034578 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.51319 | 146.5 | -0.0346 | -5.0689
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.51809 | 147.9 | -0.0346 | -5.1173
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60602 | 173 | -0.0346 | -5.9858
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.50904 | 144 | -0.034632 | -4.987
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.50904 | 144 | -0.034632 | -4.987
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60449 | 171 | -0.034632 | -5.9221
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73174 | 207 | -0.034632 | -7.1688
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76603 | 216.7 | -0.034632 | -7.5047
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.85547 | 242 | -0.034632 | -8.3809
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.003554 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034651 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.13505 | 38 | -0.034651 | -1.3167
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.068592 | 19.3 | -0.034651 | -0.66876
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.05331 | 15 | -0.034651 | -0.51976
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.003554 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16704 | 47 | -0.034651 | -1.6286
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.003561 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034658 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.33473 | 94 | -0.034658 | -3.2578
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.146 | 41 | -0.034658 | -1.421
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.13532 | 38 | -0.034658 | -1.317
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.067659 | 19 | -0.034658 | -0.6585
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.33473 | 94 | -0.034658 | -3.2578
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1282 | 36 | -0.034658 | -1.2477
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.15312 | 43 | -0.034658 | -1.4903
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.078342 | 22 | -0.034658 | -0.76247
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52703 | 148 | -0.034658 | -5.1294
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.17805 | 50 | -0.034658 | -1.7329
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19586 | 55 | -0.034658 | -1.9062
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.17805 | 50 | -0.034658 | -1.7329
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.003568 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10347 | 0 | -0.034665 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.003569 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13562 | 0 | -0.034666 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.08925 | 0 | -0.034667 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.08925 | 0 | -0.034667 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 25 | -0.034668 | -0.8667
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 25 | -0.034668 | -0.8667
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 25 | -0.034668 | -0.8667
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.057136 | 16 | -0.034668 | -0.55469
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 25 | -0.034668 | -0.8667
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 25 | -0.034668 | -0.8667
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 25 | -0.034668 | -0.8667
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.053565 | 15 | -0.034668 | -0.52002
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.003572 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13574 | 0 | -0.034669 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.003572 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.193 | 334 | -0.034669 | -11.5794
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.003572 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2145 | 340 | -0.034669 | -11.7874
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2002 | 336 | -0.034669 | -11.6488
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.52973 | 0 | -0.034669 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.5308 | 0 | -0.034669 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.54652 | 0 | -0.034669 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.56438 | 0 | -0.034669 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.54652 | 0 | -0.034669 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.3572 | 0 | -0.034669 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.51794 | 0 | -0.034669 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.52508 | 0 | -0.034669 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.45364 | 0 | -0.034669 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.003572 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.042864 | 0 | -0.034669 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.00358 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.07876 | 22 | -0.034677 | -0.76289
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.00358 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.03938 | 11 | -0.034677 | -0.38145
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.00358 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.03938 | 11 | -0.034677 | -0.38145
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28337 | 0 | -0.034684 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.29055 | 0 | -0.034684 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28337 | 0 | -0.034684 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28696 | 0 | -0.034684 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28122 | 0 | -0.034684 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.089675 | 0 | -0.034684 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.165 | 0 | -0.034684 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10044 | 0 | -0.034684 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.15639 | 0 | -0.034684 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26544 | 0 | -0.034684 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.17246 | 0 | -0.03469 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.028848 | 0 | -0.034703 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10097 | 0 | -0.034703 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.025242 | 0 | -0.034703 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14063 | 0 | -0.034703 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.05409 | 0 | -0.034703 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.025242 | 0 | -0.034703 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.05409 | 0 | -0.034703 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14063 | 0 | -0.034703 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14063 | 0 | -0.034703 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.17253 | 47.7 | -0.034714 | -1.6559
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13491 | 37.3 | -0.034714 | -1.2948
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16638 | 46 | -0.034714 | -1.5968
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.17362 | 48 | -0.034714 | -1.6663
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.003617 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.054255 | 0 | -0.034714 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.003617 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.083191 | 0 | -0.034714 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.00364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26572 | 0 | -0.034737 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.003651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.52574 | 144 | -0.034748 | -5.0037
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.003651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.68639 | 188 | -0.034748 | -6.5326
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.003659 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.3015 | 629 | -0.034756 | -21.8615
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.003683 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.4585 | 396 | -0.03478 | -13.7729
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.003799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.22034 | 58 | -0.034896 | -2.024
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.003799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.33811 | 89 | -0.034896 | -3.1057
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16716 | 44 | -0.034896 | -1.5354
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16716 | 44 | -0.034896 | -1.5354
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16336 | 43 | -0.034896 | -1.5005
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17095 | 45 | -0.034896 | -1.5703
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.00386 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.571 | 407 | -0.034957 | -14.2275
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.003872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.80925 | 209 | -0.034969 | -7.3085
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.003872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.83635 | 216 | -0.034969 | -7.5533
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17811 | 46 | -0.034969 | -1.6086
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.18198 | 47 | -0.034969 | -1.6435
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17811 | 46 | -0.034969 | -1.6086
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17811 | 46 | -0.034969 | -1.6086
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.003876 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5969 | 412 | -0.034973 | -14.4088
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.003876 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5504 | 400 | -0.034973 | -13.9892
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.003888 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6485 | 424 | -0.034985 | -14.8336
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.003888 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6524 | 425 | -0.034985 | -14.8686
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.003918 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.1392 | 546 | -0.035015 | -19.1181
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.003918 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.9385 | 750 | -0.035015 | -26.2612
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.035019 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.035019 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.035019 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60837 | 155 | -0.035022 | -5.4284
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.66725 | 170 | -0.035022 | -5.9537
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60837 | 155 | -0.035022 | -5.4284
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.004014 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.048168 | 0 | -0.035111 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59344 | 147 | -0.035134 | -5.1647
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.55711 | 138 | -0.035134 | -4.8485
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.56518 | 140 | -0.035134 | -4.9187
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59344 | 147 | -0.035134 | -5.1647
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73473 | 182 | -0.035134 | -6.3944
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.79933 | 198 | -0.035134 | -6.9565
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46398 | 114 | -0.035167 | -4.009
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.90354 | 222 | -0.035167 | -7.8071
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.74888 | 184 | -0.035167 | -6.4707
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91168 | 224 | -0.035167 | -7.8774
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46805 | 115 | -0.035167 | -4.0442
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.004111 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.016444 | 0 | -0.035208 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.58717 | 142 | -0.035232 | -5.0029
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59957 | 145 | -0.035232 | -5.1086
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.62438 | 151 | -0.035232 | -5.32
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1991 | 290 | -0.035232 | -10.2173
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.004173 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010015 | 0 | -0.03527 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.004173 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010015 | 0 | -0.03527 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010039 | 0 | -0.03528 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010039 | 0 | -0.03528 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.011712 | 0 | -0.03528 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94822 | 223.9 | -0.035332 | -7.9108
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.95288 | 225 | -0.035332 | -7.9497
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.95118 | 224.6 | -0.035332 | -7.9356
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.96007 | 226.7 | -0.035332 | -8.0097
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.004388 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.9 | 433 | -0.035485 | -15.365
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.00439 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.5638 | 584 | -0.035487 | -20.7244
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.00439 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.612 | 595 | -0.035487 | -21.1147
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.004431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.026586 | 0 | -0.035528 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.72554 | 158 | -0.035689 | -5.6389
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73472 | 160 | -0.035689 | -5.7102
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8036 | 175 | -0.035689 | -6.2456
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.70699 | 152.5 | -0.035733 | -5.4493
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.69308 | 149.5 | -0.035733 | -5.3421
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0783 | 232.6 | -0.035733 | -8.3115
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.62608 | 132 | -0.03584 | -4.7309
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.63556 | 134 | -0.03584 | -4.8026
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.532 | 323 | -0.03584 | -11.5763
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24255 | 49 | -0.036047 | -1.7663
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2277 | 46 | -0.036047 | -1.6582
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2277 | 46 | -0.036047 | -1.6582
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23265 | 47 | -0.036047 | -1.6942
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.00495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7623 | 154 | -0.036047 | -5.5512
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.00495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7326 | 148 | -0.036047 | -5.3349
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2376 | 48 | -0.036047 | -1.7303
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2376 | 48 | -0.036047 | -1.7303
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.004999 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5497 | 310 | -0.036096 | -11.1897
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.004999 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0646 | 413 | -0.036096 | -14.9076
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.21025 | 42 | -0.036103 | -1.5163
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22026 | 44 | -0.036103 | -1.5885
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22026 | 44 | -0.036103 | -1.5885
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23528 | 47 | -0.036103 | -1.6968
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.005028 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.8609 | 569 | -0.036125 | -20.5551
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.005028 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.9213 | 581 | -0.036125 | -20.9886
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.00504 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04032 | 0 | -0.036137 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.00504 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04032 | 0 | -0.036137 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.19369 | 0 | -0.036631 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18816 | 0 | -0.036631 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.19369 | 0 | -0.036631 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.006284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11311 | 0 | -0.037381 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.006284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11311 | 0 | -0.037381 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.006615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7915 | 422 | -0.037712 | -15.9144
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.006767 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18948 | 0 | -0.037864 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.006767 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.19624 | 0 | -0.037864 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.007305 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10008 | 0 | -0.038402 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15633 | 0 | -0.039782 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15633 | 0 | -0.039782 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13028 | 0 | -0.039782 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.044977 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -3.2833 | 73 | -0.044156 | -3.2234
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.044977 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.3523 | 119 | -0.044156 | -5.2546
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.044977 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2203 | 205 | -0.044156 | -9.052
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.044977 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.5877 | 102 | -0.044156 | -4.5039
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.044977 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.3178 | 96 | -0.044156 | -4.239
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.32207 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -19.3243 | 60 | -0.32125 | -19.275

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:Leon Switch - Flatcreek 138kV 1624-1642 C:Comanchee SS Auto 1440-1441 | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.32207 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -19.3243 | 0 | -0.32125 | 0 | 0 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.044977 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -3.2833 | 73 | -0.044156 | -3.2234 | 73 | 3.2234
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.044977 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -5.3523 | 119 | -0.044156 | -5.2546 | 192 | 8.4779
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.044977 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -9.2203 | 205 | -0.044156 | -9.052 |  |  | Weighted Shift Factors
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.044977 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.5877 | 102 | -0.044156 | -4.5039 |  |  | West | 0.031097
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.044977 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -4.3178 | 96 | -0.044156 | -4.239 |  |  | North | -0.0008211
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15633 | 0 | -0.039782 | 0 |  |  |  | 0.031918
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.15633 | 0 | -0.039782 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.008685 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13028 | 0 | -0.039782 | 0 |  |  | Line Rating | 96.8
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.007305 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.10008 | 0 | -0.038402 | 0 |  |  | Conc Gen | 192
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.006767 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18948 | 0 | -0.037864 | 0 |  |  | Weighted Imp. | 8.4779
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.006767 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.19624 | 0 | -0.037864 | 0 |  |  | PTDF | 0.044156
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.006615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.7915 | 422 | -0.037712 | -15.9144
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.006284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11311 | 0 | -0.037381 | 0 |  |  | Concentration | 1.3834
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.006284 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.11311 | 0 | -0.037381 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.19369 | 0 | -0.036631 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.18816 | 0 | -0.036631 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.005534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.19369 | 0 | -0.036631 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.00504 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04032 | 0 | -0.036137 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.00504 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.04032 | 0 | -0.036137 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.005028 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.8609 | 0 | -0.036125 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.005028 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.9213 | 0 | -0.036125 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.21025 | 42 | -0.036103 | -1.5163
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22026 | 44 | -0.036103 | -1.5885
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22026 | 44 | -0.036103 | -1.5885
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.005006 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23528 | 47 | -0.036103 | -1.6968
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.004999 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5497 | 310 | -0.036096 | -11.1897
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.004999 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.0646 | 413 | -0.036096 | -14.9076
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24255 | 49 | -0.036047 | -1.7663
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2277 | 46 | -0.036047 | -1.6582
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2277 | 46 | -0.036047 | -1.6582
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23265 | 47 | -0.036047 | -1.6942
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.00495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7623 | 154 | -0.036047 | -5.5512
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.00495 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.7326 | 148 | -0.036047 | -5.3349
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2376 | 48 | -0.036047 | -1.7303
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.00495 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2376 | 48 | -0.036047 | -1.7303
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.62608 | 132 | -0.03584 | -4.7309
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.63556 | 134 | -0.03584 | -4.8026
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.004743 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.532 | 323 | -0.03584 | -11.5763
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.70699 | 152.5 | -0.035733 | -5.4493
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.69308 | 149.5 | -0.035733 | -5.3421
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.004636 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.0783 | 232.6 | -0.035733 | -8.3115
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.72554 | 158 | -0.035689 | -5.6389
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73472 | 160 | -0.035689 | -5.7102
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.004592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.8036 | 175 | -0.035689 | -6.2456
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.004482 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2241 | 50 | -0.035579 | -1.7789
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.004431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.026586 | 0 | -0.035528 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.00439 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.5638 | 0 | -0.035487 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.00439 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.612 | 0 | -0.035487 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.004388 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.9 | 0 | -0.035485 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.94822 | 223.9 | -0.035332 | -7.9108
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.95288 | 225 | -0.035332 | -7.9497
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.95118 | 224.6 | -0.035332 | -7.9356
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.004235 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.96007 | 226.7 | -0.035332 | -8.0097
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010039 | 0 | -0.03528 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010039 | 0 | -0.03528 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.004183 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.011712 | 0 | -0.03528 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.004173 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010015 | 0 | -0.03527 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.004173 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.010015 | 0 | -0.03527 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.58717 | 142 | -0.035232 | -5.0029
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59957 | 145 | -0.035232 | -5.1086
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.62438 | 151 | -0.035232 | -5.32
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.004135 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.1991 | 290 | -0.035232 | -10.2173
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.004111 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.016444 | 0 | -0.035208 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46398 | 0 | -0.035167 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.90354 | 0 | -0.035167 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.74888 | 0 | -0.035167 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91168 | 0 | -0.035167 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.46805 | 0 | -0.035167 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59344 | 147 | -0.035134 | -5.1647
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.55711 | 138 | -0.035134 | -4.8485
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.56518 | 140 | -0.035134 | -4.9187
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.59344 | 147 | -0.035134 | -5.1647
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73473 | 182 | -0.035134 | -6.3944
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.004037 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.79933 | 198 | -0.035134 | -6.9565
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.004014 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.048168 | 0 | -0.035111 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60837 | 155 | -0.035022 | -5.4284
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.66725 | 170 | -0.035022 | -5.9537
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.003925 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60837 | 155 | -0.035022 | -5.4284
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.035019 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.035019 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.003922 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.035019 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.003918 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.1392 | 0 | -0.035015 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.003918 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.9385 | 0 | -0.035015 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.003888 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6485 | 0 | -0.034985 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.003888 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.6524 | 0 | -0.034985 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.003876 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5969 | 412 | -0.034973 | -14.4088
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.003876 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5504 | 400 | -0.034973 | -13.9892
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.003872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.80925 | 209 | -0.034969 | -7.3085
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.003872 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.83635 | 216 | -0.034969 | -7.5533
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17811 | 46 | -0.034969 | -1.6086
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.18198 | 47 | -0.034969 | -1.6435
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17811 | 46 | -0.034969 | -1.6086
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.003872 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17811 | 46 | -0.034969 | -1.6086
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.00386 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.571 | 407 | -0.034957 | -14.2275
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.003799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.22034 | 58 | -0.034896 | -2.024
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.003799 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.33811 | 89 | -0.034896 | -3.1057
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16716 | 44 | -0.034896 | -1.5354
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16716 | 44 | -0.034896 | -1.5354
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16336 | 43 | -0.034896 | -1.5005
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.003799 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.17095 | 45 | -0.034896 | -1.5703
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.003683 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -1.4585 | 0 | -0.03478 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.003659 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -2.3015 | 0 | -0.034756 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.003651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.52574 | 144 | -0.034748 | -5.0037
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.003651 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.68639 | 188 | -0.034748 | -6.5326
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.00364 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26572 | 0 | -0.034737 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.003617 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.054255 | 0 | -0.034714 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.003617 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.083191 | 0 | -0.034714 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.17253 | 47.7 | -0.034714 | -1.6559
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.13491 | 37.3 | -0.034714 | -1.2948
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.16638 | 46 | -0.034714 | -1.5968
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.003617 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.17362 | 48 | -0.034714 | -1.6663
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10097 | 0 | -0.034703 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.025242 | 0 | -0.034703 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14063 | 0 | -0.034703 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.05409 | 0 | -0.034703 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.025242 | 0 | -0.034703 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.05409 | 0 | -0.034703 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14063 | 0 | -0.034703 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.14063 | 0 | -0.034703 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.003606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.028848 | 0 | -0.034703 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.003593 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.17246 | 0 | -0.03469 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28337 | 0 | -0.034684 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.29055 | 0 | -0.034684 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28337 | 0 | -0.034684 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28696 | 0 | -0.034684 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.28122 | 0 | -0.034684 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.089675 | 0 | -0.034684 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.165 | 0 | -0.034684 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10044 | 0 | -0.034684 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.15639 | 0 | -0.034684 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.003587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.26544 | 0 | -0.034684 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.00358 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.07876 | 22 | -0.034677 | -0.76289
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.00358 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.03938 | 11 | -0.034677 | -0.38145
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.00358 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.03938 | 11 | -0.034677 | -0.38145
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.56438 | 0 | -0.034669 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.54652 | 0 | -0.034669 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.3572 | 0 | -0.034669 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.51794 | 0 | -0.034669 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.52508 | 0 | -0.034669 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.45364 | 0 | -0.034669 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.003572 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.042864 | 0 | -0.034669 | 0
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.52973 | 0 | -0.034669 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.5308 | 0 | -0.034669 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.003572 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.54652 | 0 | -0.034669 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.2002 | 336 | -0.034669 | -11.6488
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.003572 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.193 | 334 | -0.034669 | -11.5794
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.003572 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2145 | 340 | -0.034669 | -11.7874
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.003572 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.64296 | 180 | -0.034669 | -6.2404
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.003572 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13574 | 0 | -0.034669 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 0 | -0.034668 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 0 | -0.034668 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 0 | -0.034668 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.057136 | 0 | -0.034668 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 0 | -0.034668 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 0 | -0.034668 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.089275 | 0 | -0.034668 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.003571 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.053565 | 0 | -0.034668 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.08925 | 0 | -0.034667 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.00357 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.08925 | 0 | -0.034667 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.003569 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.13562 | 0 | -0.034666 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.003568 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.10347 | 0 | -0.034665 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.33473 | 0 | -0.034658 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.146 | 0 | -0.034658 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.13532 | 0 | -0.034658 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.067659 | 0 | -0.034658 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.33473 | 0 | -0.034658 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.1282 | 0 | -0.034658 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.15312 | 0 | -0.034658 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.078342 | 0 | -0.034658 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.52703 | 0 | -0.034658 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.17805 | 0 | -0.034658 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.19586 | 0 | -0.034658 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.003561 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.17805 | 0 | -0.034658 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.003561 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034658 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.13505 | 38 | -0.034651 | -1.3167
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.068592 | 19.3 | -0.034651 | -0.66876
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.003554 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.05331 | 15 | -0.034651 | -0.51976
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.003554 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.16704 | 47 | -0.034651 | -1.6286
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.003554 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034651 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.73174 | 207 | -0.034632 | -7.1688
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.76603 | 216.7 | -0.034632 | -7.5047
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.85547 | 242 | -0.034632 | -8.3809
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.50904 | 144 | -0.034632 | -4.987
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.50904 | 144 | -0.034632 | -4.987
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.003535 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60449 | 171 | -0.034632 | -5.9221
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.51319 | 146.5 | -0.0346 | -5.0689
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.51809 | 147.9 | -0.0346 | -5.1173
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.003503 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.60602 | 173 | -0.0346 | -5.9858
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.003481 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034578 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.25642 | 76 | -0.034471 | -2.6198
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.25642 | 76 | -0.034471 | -2.6198
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.35427 | 105 | -0.034471 | -3.6194
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24968 | 74 | -0.034471 | -2.5508
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.24968 | 74 | -0.034471 | -2.5508
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.003374 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.34415 | 102 | -0.034471 | -3.516
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.003373 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -4.4962 | 0 | -0.03447 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.003373 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -4.4793 | 0 | -0.03447 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.003327 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.21958 | 66 | -0.034424 | -2.272
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039672 | 0 | -0.034403 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036366 | 0 | -0.034403 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.003306 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.039672 | 0 | -0.034403 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19914 | 0 | -0.034309 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22934 | 0 | -0.034309 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.14454 | 0 | -0.034309 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32441 | 0 | -0.034309 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27623 | 0 | -0.034309 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.28266 | 0 | -0.034309 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1606 | 0 | -0.034309 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057816 | 0 | -0.034309 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30193 | 0 | -0.034309 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22484 | 0 | -0.034309 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20236 | 0 | -0.034309 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.23126 | 0 | -0.034309 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20814 | 0 | -0.034309 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.32441 | 0 | -0.034309 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.31156 | 0 | -0.034309 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.33084 | 0 | -0.034309 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24411 | 0 | -0.034309 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25696 | 0 | -0.034309 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25696 | 0 | -0.034309 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.003212 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.54925 | 0 | -0.034309 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.003183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.22599 | 0 | -0.03428 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.003183 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03183 | 0 | -0.03428 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35087 | 0 | -0.034258 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.35087 | 0 | -0.034258 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.37616 | 0 | -0.034258 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.003161 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.34613 | 0 | -0.034258 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003118 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034215 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.003078 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1419 | 0 | -0.034175 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -2.0031 | 0 | -0.034174 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.7354 | 0 | -0.034174 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.003077 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -1.8462 | 0 | -0.034174 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50155 | 0 | -0.034174 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.50155 | 0 | -0.034174 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.003077 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.75387 | 0 | -0.034174 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.49346 | 161 | -0.034162 | -5.5001
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.50879 | 166 | -0.034162 | -5.6709
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.003065 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.76012 | 248 | -0.034162 | -8.4722
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.003065 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -1.6735 | 546 | -0.034162 | -18.6524
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.003065 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -1.9708 | 0 | -0.034162 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.003065 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.039845 | 13 | -0.034162 | -0.44411
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.003065 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10114 | 0 | -0.034162 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30271 | 0 | -0.034115 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.28037 | 0 | -0.034115 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30995 | 0 | -0.034115 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.003018 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.30784 | 0 | -0.034115 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.003018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.096576 | 0 | -0.034115 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.003018 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.09054 | 0 | -0.034115 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.2136 | 0 | -0.034114 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20123 | 0 | -0.034114 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1599 | 0 | -0.034114 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.4622 | 0 | -0.034114 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46311 | 0 | -0.034114 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45949 | 0 | -0.034114 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.28963 | 0 | -0.034114 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.003017 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.73615 | 0 | -0.034114 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.003017 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.12068 | 0 | -0.034114 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.003 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15 | 50 | -0.034097 | -1.7048
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.002985 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.034082 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.27009 | 0 | -0.034065 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.26 | 0 | -0.034065 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.25822 | 0 | -0.034065 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.16176 | 0 | -0.034065 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.002968 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.03621 | 0 | -0.034065 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19253 | 0 | -0.034059 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.17772 | 0 | -0.034059 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19253 | 0 | -0.034059 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.002962 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.19253 | 0 | -0.034059 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13584 | 46 | -0.03405 | -1.5663
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13584 | 46 | -0.03405 | -1.5663
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.13584 | 46 | -0.03405 | -1.5663
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16242 | 55 | -0.03405 | -1.8727
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16242 | 55 | -0.03405 | -1.8727
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.002953 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.15946 | 54 | -0.03405 | -1.8387
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.002949 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23002 | 0 | -0.034046 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.002949 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.23592 | 0 | -0.034046 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.48079 | 0 | -0.034043 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46282 | 0 | -0.034043 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46399 | 0 | -0.034043 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46252 | 0 | -0.034043 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.002946 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.79247 | 0 | -0.034043 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.002944 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10304 | 0 | -0.034041 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002941 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.035292 | 12 | -0.034038 | -0.40846
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.002941 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.034038 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00294 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.49686 | 169 | -0.034037 | -5.7522
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.00294 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.4851 | 165 | -0.034037 | -5.6161
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00294 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43806 | 0 | -0.034037 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00294 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19139 | 0 | -0.034037 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.002939 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.62601 | 213 | -0.034036 | -7.2497
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.047612 | 0 | -0.034036 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.1881 | 0 | -0.034036 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18574 | 0 | -0.034036 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24276 | 0 | -0.034036 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.002939 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21631 | 0 | -0.034036 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.002939 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.67009 | 228 | -0.034036 | -7.7602
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.52902 | 0 | -0.034036 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46613 | 0 | -0.034036 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.002939 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.46142 | 0 | -0.034036 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20838 | 0 | -0.034032 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.21132 | 0 | -0.034032 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.11446 | 0 | -0.034032 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.002935 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.08805 | 0 | -0.034032 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.002929 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39834 | 0 | -0.034026 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.002929 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2929 | 100 | -0.034026 | -3.4026
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.002929 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.2929 | 100 | -0.034026 | -3.4026
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.002929 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034026 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12298 | 42 | -0.034025 | -1.429
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.12298 | 42 | -0.034025 | -1.429
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11126 | 38 | -0.034025 | -1.2929
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.002928 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.11126 | 38 | -0.034025 | -1.2929
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.002928 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.034025 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.002926 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.5062 | 0 | -0.034023 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.002926 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.39501 | 0 | -0.034023 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30326 | 104 | -0.034013 | -3.5373
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.30326 | 104 | -0.034013 | -3.5373
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15455 | 53 | -0.034013 | -1.8027
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16621 | 57 | -0.034013 | -1.9387
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.15746 | 54 | -0.034013 | -1.8367
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16913 | 58 | -0.034013 | -1.9727
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.002916 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.16913 | 58 | -0.034013 | -1.9727
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.002912 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.1403 | 735 | -0.034009 | -24.9966
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.098906 | 0 | -0.034006 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10094 | 0 | -0.034006 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.095124 | 0 | -0.034006 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.13352 | 0 | -0.034006 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051489 | 0 | -0.034006 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059344 | 0 | -0.034006 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.057889 | 0 | -0.034006 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10182 | 0 | -0.034006 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052362 | 0 | -0.034006 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.24843 | 0 | -0.034006 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.002909 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43053 | 0 | -0.034006 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.002906 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.034872 | 12 | -0.034003 | -0.40804
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.014505 | 0 | -0.033998 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.060921 | 0 | -0.033998 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18857 | 0 | -0.033998 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.19147 | 0 | -0.033998 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.20307 | 0 | -0.033998 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.18276 | 0 | -0.033998 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17986 | 0 | -0.033998 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.3017 | 0 | -0.033998 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.002901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17116 | 0 | -0.033998 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.002901 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.034812 | 0 | -0.033998 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.0029 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -2.1547 | 743 | -0.033997 | -25.2597
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.002899 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.45514 | 0 | -0.033996 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49828 | 172 | -0.033994 | -5.847
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49828 | 172 | -0.033994 | -5.847
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.002897 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.49828 | 172 | -0.033994 | -5.847
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.47033 | 0 | -0.033986 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.46628 | 0 | -0.033986 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45906 | 0 | -0.033986 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.002889 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.77772 | 0 | -0.033986 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.002887 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -1.149 | 398 | -0.033984 | -13.5256
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17004 | 59 | -0.033979 | -2.0048
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.17004 | 59 | -0.033979 | -2.0048
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.002882 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.16139 | 56 | -0.033979 | -1.9028
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.49045 | 0 | -0.033932 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.44226 | 0 | -0.033932 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.43659 | 0 | -0.033932 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.002835 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.43659 | 0 | -0.033932 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.002835 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.45927 | 0 | -0.033932 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002531 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.060744 | 24 | -0.033628 | -0.80707
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.002531 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.060744 | 24 | -0.033628 | -0.80707
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.002531 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.058213 | 23 | -0.033628 | -0.77344
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.002291 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.019244 | 8.4 | -0.033388 | -0.28046
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.031097 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031097 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.031097 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.002413 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.028684 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.003011 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.018066 | 0 | -0.028086 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.005582 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.18421 | 0 | -0.025515 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.005582 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13955 | 0 | -0.025515 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.005582 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.025515 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.4183 | 70 | -0.01944 | -1.3608
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.398 | 69 | -0.01944 | -1.3414
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.398 | 69 | -0.01944 | -1.3414
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.020261 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.3777 | 68 | -0.01944 | -1.3219
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.016741 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.25111 | 0 | -0.01592 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.016741 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.25111 | 0 | -0.01592 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.015486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.3229 | 150 | -0.014665 | -2.1997
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.015486 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.2389 | 80 | -0.014665 | -1.1732
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.25184 | 18 | -0.01317 | -0.23706
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.25184 | 18 | -0.01317 | -0.23706
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.013991 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.53166 | 38 | -0.01317 | -0.50046
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.010896 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -2.7785 | 255 | -0.010075 | -2.5691
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.010896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6235 | 149 | -0.010075 | -1.5012
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.010896 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -1.6671 | 153 | -0.010075 | -1.5415
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.009406 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -1.5802 | 168 | -0.0085849 | -1.4423
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.009406 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.84654 | 90 | -0.0085849 | -0.77264
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.005771 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0049499 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.005771 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0049499 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.005165 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0043439 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.005165 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -4.0649 | 787 | -0.0043439 | -3.4186
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.00407 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.407 | 0 | -0.0032489 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.81936 | 288 | -0.0020239 | -0.58288
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41822 | 147 | -0.0020239 | -0.29751
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -0.002845 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.41822 | 147 | -0.0020239 | -0.29751
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.002483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11918 | 48 | -0.0016619 | -0.079771
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.002483 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.11422 | 46 | -0.0016619 | -0.076447
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.002483 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.26071 | 105 | -0.0016619 | -0.1745
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.002431 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.041327 | 17 | -0.0016099 | -0.027368
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.002431 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0016099 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.002431 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.077792 | 0 | -0.0016099 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.36946 | 0 | -0.0015749 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.37378 | 0 | -0.0015749 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.37378 | 0 | -0.0015749 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.002396 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.91048 | 0 | -0.0015749 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.002303 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.0663 | 0 | -0.0014819 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.645 | 0 | -0.0011029 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.645 | 0 | -0.0011029 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.29303 | 0 | -0.0011029 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.001924 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.29437 | 0 | -0.0011029 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.001774 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.4671 | 0 | -0.0009529 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.001774 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -1.4529 | 0 | -0.0009529 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.001622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.31791 | 196 | -0.0008009 | -0.15698
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.001622 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.18004 | 111 | -0.0008009 | -0.088899
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.001579 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.3537 | 224 | -0.0007579 | -0.16977
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.001029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.63284 | 0 | -0.0002079 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.001029 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.60402 | 0 | -0.0002079 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.00096 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0001389 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13216 | 150.7 | -5.5896e-05 | -0.0084235
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13243 | 151 | -5.5896e-05 | -0.0084403
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.000877 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.15558 | 177.4 | -5.5896e-05 | -0.0099159
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13074 | 151.5 | -4.1896e-05 | -0.0063472
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13143 | 152.3 | -4.1896e-05 | -0.0063807
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.000863 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.15318 | 177.5 | -4.1896e-05 | -0.0074365
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.14784 | 224 | 0.0001611 | 0.036087
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.14916 | 226 | 0.0001611 | 0.03641
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13992 | 212 | 0.0001611 | 0.034154
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.00066 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13926 | 211 | 0.0001611 | 0.033993
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.000191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.041332 | 216.4 | 0.0006301 | 0.13635
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.000191 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.041275 | 216.1 | 0.0006301 | 0.13617
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.000136 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.024752 | 182 | 0.0006851 | 0.12469
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.000136 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.065824 | 484 | 0.0006851 | 0.33159
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.000102 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.0051 | 0 | 0.0007191 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -9.4e-05 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.0007271 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.002072 | 0 | 0.0008071 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00182 | 0 | 0.0008071 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00203 | 0 | 0.0008071 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -1.4e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.005586 | 0 | 0.0008071 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0008211 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.0008211 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.066725 | 0 | 0.0009061 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.067575 | 0 | 0.0009061 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 8.5e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.0663 | 0 | 0.0009061 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.000556 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.065608 | 118 | 0.0013771 | 0.1625
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.000556 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.06394 | 115 | 0.0013771 | 0.15837
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.000556 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.30914 | 556 | 0.0013771 | 0.76567
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000802 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0016231 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.000802 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0016231 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13347 | 161 | 0.0016501 | 0.26567
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13596 | 164 | 0.0016501 | 0.27062
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13596 | 164 | 0.0016501 | 0.27062
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.34321 | 414 | 0.0016501 | 0.68314
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.1343 | 162 | 0.0016501 | 0.26732
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13347 | 161 | 0.0016501 | 0.26567
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13513 | 163 | 0.0016501 | 0.26897
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.000829 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.33906 | 409 | 0.0016501 | 0.67489
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.000877 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.34028 | 388 | 0.0016981 | 0.65886
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.000877 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.45165 | 515 | 0.0016981 | 0.87452
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.23142 | 217.3 | 0.0018861 | 0.40985
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.21832 | 205 | 0.0018861 | 0.38665
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.001065 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.29011 | 272.4 | 0.0018861 | 0.51377
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.001096 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04384 | 40 | 0.0019171 | 0.076684
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.001106 | north | 3 | N | N | Nnorth | Nnorth | 1 | 1.2796 | 0 | 0.0019271 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.001106 | north | 3 | N | N | Nnorth | Nnorth | 1 | 1.2807 | 0 | 0.0019271 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.001108 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.48198 | 435 | 0.0019291 | 0.83916
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.0222 | 20 | 0.0019311 | 0.038622
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.02775 | 25 | 0.0019311 | 0.048278
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.00111 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.04551 | 41 | 0.0019311 | 0.079175
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.091877 | 79 | 0.0019841 | 0.15674
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.12328 | 106 | 0.0019841 | 0.21032
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.001163 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.1698 | 146 | 0.0019841 | 0.28968
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.001163 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.088388 | 76 | 0.0019841 | 0.15079
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.001234 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.48743 | 395 | 0.0020551 | 0.81177
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.001234 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.53679 | 435 | 0.0020551 | 0.89397
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.77674 | 0 | 0.0022131 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 0.80597 | 0 | 0.0022131 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.001392 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 1.1247 | 0 | 0.0022131 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.108 | 0 | 0.0022611 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.11462 | 0 | 0.0022611 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.00144 | north | 8 | N | N | Nnorth | Nnorth | 1 | 0.1273 | 0 | 0.0022611 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.23536 | 160 | 0.0022921 | 0.36674
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.22948 | 156 | 0.0022921 | 0.35757
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.28832 | 196 | 0.0022921 | 0.44925
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.22948 | 156 | 0.0022921 | 0.35757
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.23095 | 157 | 0.0022921 | 0.35986
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.001471 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.29126 | 198 | 0.0022921 | 0.45384
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.001516 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 0.56092 | 370 | 0.0023371 | 0.86473
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.21224 | 0 | 0.0023371 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.21376 | 0 | 0.0023371 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.46844 | 0 | 0.0023371 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.21679 | 0 | 0.0023371 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.2183 | 0 | 0.0023371 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.001516 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0.46996 | 0 | 0.0023371 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.001608 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.27336 | 170 | 0.0024291 | 0.41295
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.001608 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.83616 | 520 | 0.0024291 | 1.2631
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.001681 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.0025021 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.001682 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06728 | 0 | 0.0025031 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.001682 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.06728 | 0 | 0.0025031 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.002008 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0028291 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.002849 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0036701 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.002849 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0036701 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.002849 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0036701 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.00375 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.225 | 60 | 0.0045711 | 0.27427
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.00375 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.23625 | 63 | 0.0045711 | 0.28798
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.004079 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.45889 | 0 | 0.0049001 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.004475 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.0052961 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.01221 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14652 | 0 | 0.013031 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.01221 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.14652 | 0 | 0.013031 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.7118 | 204 | 0.014114 | 2.8793
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 2.6719 | 201 | 0.014114 | 2.8369
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.013293 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 3.2169 | 242 | 0.014114 | 3.4156
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.019725 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.367 | 0 | 0.020546 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.020878 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1317 | 0 | 0.021699 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.022615 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 8.2771 | 366 | 0.023436 | 8.5776
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.024129 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.02495 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.027231 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4931 | 0 | 0.028052 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.027563 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.3153 | 0 | 0.028384 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.027621 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.113 | 0 | 0.028442 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.02778 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2224 | 0 | 0.028601 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.56598 | 20 | 0.02912 | 0.5824
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.56598 | 20 | 0.02912 | 0.5824
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.56598 | 20 | 0.02912 | 0.5824
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.028299 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.48108 | 17 | 0.02912 | 0.49504
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.028424 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2636 | 0 | 0.029245 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.028424 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2636 | 0 | 0.029245 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.028441 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2753 | 0 | 0.029262 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028445 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2756 | 0 | 0.029266 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1353 | 0 | 0.029292 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2777 | 0 | 0.029292 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.028471 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1388 | 0 | 0.029292 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.02855 | west | 4 | Y | N | Ywest | Nwest | 1 | 18.5489 | 0 | 0.029371 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028597 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2878 | 0 | 0.029418 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.028597 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.2878 | 0 | 0.029418 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.028688 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7704 | 0 | 0.029509 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.028705 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.482 | 0 | 0.029526 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.247 | 0 | 0.029683 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3149 | 0 | 0.029683 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3683 | 0 | 0.029683 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.028862 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1909 | 0 | 0.029683 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.029105 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.1397 | 0 | 0.029926 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.029123 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3685 | 0 | 0.029944 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1538 | 0 | 0.030265 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7247 | 0 | 0.030265 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3316 | 0 | 0.030265 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.029444 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8005 | 0 | 0.030265 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.030257 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7821 | 0 | 0.031078 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.030257 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7821 | 0 | 0.031078 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0003 | 66 | 0.031128 | 2.0545
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 1.97 | 65 | 0.031128 | 2.0233
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0306 | 67 | 0.031128 | 2.0856
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0306 | 67 | 0.031128 | 2.0856
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.030307 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.0306 | 67 | 0.031128 | 2.0856
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.030307 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.031128 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.030307 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.031128 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.327 | 208.2 | 0.03121 | 6.4979
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.3183 | 142.1 | 0.03121 | 4.435
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.0235 | 132.4 | 0.03121 | 4.1322
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.1329 | 136 | 0.03121 | 4.2446
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.4672 | 147 | 0.03121 | 4.5879
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.030389 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.3817 | 210 | 0.03121 | 6.5541
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1273 | 70 | 0.031211 | 2.1848
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1273 | 70 | 0.031211 | 2.1848
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.8202 | 92.8 | 0.031211 | 2.8964
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4312 | 80 | 0.031211 | 2.4969
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.4312 | 80 | 0.031211 | 2.4969
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.03039 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.4949 | 115 | 0.031211 | 3.5893
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.030419 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0647 | 0 | 0.03124 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.030419 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.91257 | 0 | 0.03124 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5674 | 0 | 0.03127 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6988 | 0 | 0.03127 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0898 | 0 | 0.03127 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.030449 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7117 | 0 | 0.03127 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1328 | 0 | 0.031289 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 1 | 2.2364 | 0 | 0.031289 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.030468 | west | 8 | N | N | Nwest | Nwest | 1 | 2.1449 | 0 | 0.031289 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.030686 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5722 | 0 | 0.031507 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.031303 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.146 | 0 | 0.032124 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.031499 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8269 | 0 | 0.03232 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1863 | 0 | 0.032456 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4008 | 0 | 0.032456 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2707 | 0 | 0.032456 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7646 | 0 | 0.032456 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3217 | 0 | 0.032456 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.031635 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5466 | 0 | 0.032456 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.03164 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7773 | 0 | 0.032461 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.031641 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20883 | 0 | 0.032462 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.031641 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0853 | 0 | 0.032462 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.032305 | west | 8 | N | N | Nwest | Nwest | 1 | 0.83347 | 0 | 0.033126 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1453 | 66 | 0.033325 | 2.1995
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2428 | 69 | 0.033325 | 2.2994
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.2428 | 69 | 0.033325 | 2.2994
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1778 | 67 | 0.033325 | 2.2328
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1778 | 67 | 0.033325 | 2.2328
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.032504 | west | 13 | Y | Y | Ywest | Ywest | 1 | 2.1128 | 65 | 0.033325 | 2.1661
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.032566 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9079 | 0 | 0.033387 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.032763 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9316 | 0 | 0.033584 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.033018 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5966 | 0 | 0.033839 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.033348 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.5033 | 0 | 0.034169 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.033455 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0219 | 0 | 0.034276 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.033455 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0219 | 0 | 0.034276 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.034374 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1656 | 0 | 0.035195 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.034552 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.8718 | 0 | 0.035373 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.034552 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.1462 | 0 | 0.035373 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.034617 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4271 | 0 | 0.035438 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.034617 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.1116 | 0 | 0.035438 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 1 | 0.86542 | 0 | 0.035438 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 1 | 1.582 | 0 | 0.035438 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.034617 | west | 7 | N | N | Nwest | Nwest | 1 | 1.582 | 0 | 0.035438 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.2311 | 0 | 0.03608 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2153 | 0 | 0.03608 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.035259 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0011 | 0 | 0.03608 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.035797 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0069 | 0 | 0.036618 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.040971 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1456 | 0 | 0.041792 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.043174 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.5904 | 0 | 0.043995 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.047455 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.1182 | 0 | 0.048276 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.047455 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.793 | 0 | 0.048276 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.059966 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.5118 | 242 | 0.060787 | 14.7105

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown
| Degrees | Rating
| 20 | 105
| 25 | 105
| 30 | 105
| 35 | 105
| 40 | 105
| 45 | 105
| 50 | 105
| 55 | 105
| 60 | 103
| 65 | 102
| 70 | 99
| 75 | 97
| 80 | 95
| 85 | 93
| 90 | 91
| 95 | 88
| 100 | 86
| 105 | 83
| 110 | 81
| 115 | 78
| Max | 105
| Min | 78
| Avg | 96.8