| PRR Number | 824 | PRR Title | Primary Frequency Response from WGRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | September 17, 2009 |  |  |
| Protocol Sections Requiring Revision |  | 1.3.6, Exceptions 2.1, Definitions 5.9.1.1, Governor in Service 5.9.1.2, Reporting5.9.1.3, Wind-powered Generation Resource (WGR) Primary Frequency Response (new) 5.9.2, Primary Frequency Control Measurements 5.9.2.1, ERCOT Required Primary Frequency Response 6.5.3, Regulation Service (RGS) 6.5.4, Responsive Reserve Service 6.7.3, Deployment of Responsive Reserve Service 6.10.5.3, SCE Monitoring Criteria |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Revision Description |  | This Protocol Revision Request (PRR) adds a requirement for wind generator control systems to be programmed to respond to frequency deviations by controlling WGR real power output in a way that is similar to governor response for conventional generators. This PRR also proposes the addition of the new terms, Primary Frequency Response and Governor, and aligns the other sections of the Protocols with this terminology. |  |  |
| Overall Market Benefit |  | Maintain system frequency better with additional wind generation in the ERCOT Region, which shall allow greater utilization of wind generation and improve the reliability of the ERCOT System. |  |  |
| Overall Market Impact |  | Significant reduction in production costs since more wind generation can be allowed on the ERCOT System. |  |  |
| Consumer Impact |  | Reduced fuel costs. |  |  |
| Credit Impacts |  | To be determined. |  |  |
| Procedural History |  | - On 7/21/09, PRR824 was posted. - On 8/3/09, PUCT comments were posted. - On 8/14/09, BP Wind comments were posted. - On 8/24/09, the CEO Revision Request Review for PRR824 was posted. - On 8/25/09, Performance, Disturbance, Compliance Working Group (PDCWG) comments were posted. - On 8/25/09, PRS considered PRR824. - On 8/31/09, a second set of PUCT comments were posted. - On 9/10/09, a second set of PDCWG comments were posted. - On 9/11/09, a second set of BP Wind comments were posted. - On 9/16/09, PSEG TX comments were posted. - On 9/16/09, CPS Energy comments were posted. - On 9/17/09, PRS again considered PRR824. |  |  |
| PRS Decision |  | On 8/25/09, PRS unanimously voted to table PRR824 for one month. All Market Segments were present for the vote. On 9/17/09, PRS voted to recommend approval of PRR824 as amended by the 9/16/09 CPS Energy comments and as revised by PRS. There was one abstention from the Independent Generator Market Segment. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 8/25/09, PRS discussed the request from PDCWG to table PRR824 for one month to allow additional time for review of the definition for Primary Frequency Response. On 9/17/09, there was discussion regarding CPS Energy’s comments and the need for additional primary frequency response requirements for WGRs currently in the planning and development phases; however, additional review of the requirement for existing WGRs is needed. It was agreed that existing WGRs would be addressed by a subsequent PRR. There was also discussion regarding the need to address a contradiction related to the 5% droop to wind turbines and the need for additional clarification related to performance and compliance in the Operating Guides. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | WGR software and hardware. | Less than $500,000 per new WGR. |
|  | 2 | Lost production due to high frequency. | $1,000,000 to $100,000,000 plus, depending on implementation settings. |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Provides automatic response to frequency, primarily to high frequency excursions, in addition to the response from conventional generation units. Should help avoid excessive frequency excursions. | Monetary impact of frequency excursions is difficult to estimate. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| PUCT 080309 | Proposed language changes to add clarification of Primary Frequency Response. |
| BP Wind 081409 | Proposed language changes to revise the look back period in which older wind farms can be retrofitted. |
| PDCWG 082509 | Requested that PRS table PRR824 to allow additional time for review of the language and definition for Primary Frequency Response. |
| PUCT 083109 | Withdrew the comments submitted by the PUCT on August 3, 2009. |
| PDCWG 091009 | Proposed additional language revisions to clarify the meanings of Primary Frequency Response and Governor. |
| BP Wind 091109 | Proposed additional revisions to Section 5.9.1.3 and also withdrew the comments submitted by BP Wind on August 14, 2009. |
| PSEG TX 091609 | Addressed potential issues associated with the proposed changes to the language. |
| CPS Energy 091609 | Proposed to incorporate frequency response on WGRs on a forward looking basis and to delete the requirement on existing WGRs from PRR824. |

| Original Sponsor |  |
| --- | --- |
| Name | Rick Keetch on behalf of the Reliability and Operations Subcommittee (ROS) |
| Company | Reliant |
| Market Segment | Independent Retail Electric Provider (IREP) |

Proposed Protocol Language Revision

- 1.3.6	Exceptions

Receiving Party may, without violating this Section 1.3, Confidentiality, disclose certain Protected Information:

(1)	To governmental officials, Market Participants, the public, or others as required by any law, regulation, or order, or by these Protocols, provided that any Receiving Party must make reasonable efforts to restrict public access to the Disclosed Protected Information by protective order, by aggregating information, or otherwise if reasonably possible; or

(2)	If ERCOT is the Receiving Party and Disclosure to the PUCT of the Protected Information is required from ERCOT pursuant to applicable Protocol, law, regulation or order; or

(3)	If Disclosing Party that supplied the Protected Information to the Receiving Party has given its prior written consent to the Disclosure, which consent may be given or withheld in Disclosing Party’s sole discretion; or

(4)	If the Protected Information, before it is furnished to Receiving Party, is in the public domain; or

(5)	If the Protected Information, after it is furnished to Receiving Party, enters the public domain other than as a result of a breach by Receiving Party of its obligations under this Section 1.3, Confidentiality; or

(6)	If reasonably deemed by the disclosing Receiving Party to be required to be disclosed in connection with a dispute between Receiving Party and Disclosing Party; provided that the disclosing Receiving Party must make reasonable efforts to restrict public access to the disclosed Protected Information by protective order, by aggregating information, or otherwise if reasonably possible; or

(7)	To a TDSP engaged in transmission or distribution system planning and operating activities, provided that the TDSP has executed a confidentiality agreement with requirements substantially similar to those in Section 1.3, Confidentiality; or

(8)	To a vendor or prospective vendor of goods and services to ERCOT so long as such vendor or prospective vendor: (i) is not a Market Participant and (ii) agrees to abide by the terms of Section 1.3, Confidentiality, regarding management of Protected Information; or

(9)	To NERC if required for compliance with any applicable NERC requirement; or

(10)	To ERCOT and its consultants, and members of task forces and working groups of ERCOT engaged in performing analysis of abnormal system conditions, disturbances, unusual events, and abnormal system performance, provided that Ancillary Service Bid prices  or other competitively sensitive price or cost information shall not be disclosed, and further provided that the members of task forces and working groups execute a confidentiality agreement with requirements substantially similar to those in Section 1.3, Confidentiality.  Data to be disclosed under this exception shall be limited to clearly defined periods surrounding the relevant conditions, events, or performance under review and will be limited in scope to information pertinent to the condition or events under review and may include the following:

(a)	QSE base schedules;

(b)	QSE AS awards and deployments, in aggregate and by type of Resource;

(c)	Resource facility availability status, including the status of switching devices, auxiliary loads, and mechanical systems which had a material impact on Resource facility availability or an adverse impact on the transmission system operation;

(d)	Individual Resource information including, real power output, reactive output, and maximum/minimum generating capability;

(e)	Resource control mode and protective device settings and status;

(f)	QSE SCE and its components, including Primary Frequency Response, bias, and droop setting;

(g)	Load Imbalance;

(h)	Data from Resource Plans; and

(i)	Resource Outage schedule information.

Such information shall not be disclosed to other Market Participants prior to ten (10) days following the date(s) under review.

- 2.1	Definitions

Primary Frequency Response

The instantaneous proportional increase or decrease in real power output provided by a Generation Resource and the natural real power dampening response provided by load in response to system frequency deviations.  This response is in the direction that stabilizes frequency.

Governor

The electronic, digital, or mechanical device that implements Primary Frequency Response of a Generation Resource.

- 5.9.1.1	Governor in Service

At all times a Generation Resource is On-line its Governor shall remain in service and be allowed to respond to all changes in system frequency.  Generation Entities shall not reduce Primary Frequency Response on individual Resources during abnormal conditions without ERCOT’s consent (conveyed by way of the Generation Entity’s Qualified Scheduling Entity (QSE)) unless equipment damage is imminent.  All Generation Resources that have capacity available to either increase output or decrease output in Real Time must provide Primary Frequency Response, which may make use of that available capacity.  Only Generation Resources providing Regulation Service Up (RGSU), Regulation Service Down (RGSD), and Responsive Reserve Service (RRS), as specified in Section 6.5, Ancillary Services Selection and Requirements, shall be required to reserve capacity that may also be used to provide Primary Frequency Response.

- 5.9.1.2	Reporting

Generation Resources shall conduct applicable generating governor speed regulation tests on Resources as specified in the Operating Guides.  Test results and/or other relevant information shall be reported to ERCOT and ERCOT shall forward results to the appropriate TSPs.

Resource Governor modeling information required in the ERCOT Planning Criteria shall be determined from actual Resource testing described in the Operating Guides.  Within thirty (30) days of ERCOT’s request, the results of the latest test performed shall be supplied to ERCOT and the connected TSP.

When the Governor of a Generation Resource is blocked while the Resource is operating, the QSE shall promptly inform ERCOT.  The QSE shall also supply Governor status logs to ERCOT upon request.

Any short-term inability of a Generation Resource to supply Primary Frequency Response shall be immediately reported to ERCOT except as provided for in 5.9.1.1, Governor In Service.

If a Generation Resource trips Off-line due to Governor problems, the Generation Resources shall immediately report the change in the status of the Resource to ERCOT through its QSE.

- 5.9.1.3		Wind-powered Generation Resource (WGR) Primary Frequency Response

Wind-powered Generation Resources (WGRs) with Generation Interconnect Agreements signed after January 1, 2010 shall provide Primary Frequency Response to frequency deviations from 60.000 Hz.  The WGR automatic control system design shall have an adjustable dead band that can be set as specified in the ERCOT Operating Guides.  The Primary Frequency Response shall be similar to the droop characteristic of five-percent (5%) used by conventional generators.

- 5.9.2	Primary Frequency Response Measurements

For the purposes of this Section, the “A Point” is the last stable frequency value prior to a frequency disturbance.  For a decreasing frequency event with the last stable frequency value of 60.000 Hz or below, the actual frequency is used.  For a decreasing frequency event with the last stable frequency value between 60.000 and 60.036 Hz, 60.000 Hz will be used.  For a decreasing frequency event with the last stable frequency value above 60.036 Hz, actual frequency will be used.  For an increasing frequency event with the last stable frequency value of 60.000 or above, the actual frequency is used.  For an increasing frequency event with the last stable frequency between 59.964 and 60.000 Hz, 60.000 Hz will be used.  For an increasing frequency event with the last stable frequency value of 59.964 or below, the actual frequency is used.  ERCOT shall determine the A Point frequency for each event.

For the purposes of this Section, the “C Point” is the lowest frequency value during the first five (5) seconds of the event.

For the purposes of this Section, the “B Point” is the recovery frequency value after the C Point.   The B Point should occur after full Primary Frequency Response of the Resource has occurred, usually between ten (10) and thirty (30) seconds after the A Point, but not greater than sixty (60) seconds after the A Point.  ERCOT shall determine the B Point for each event.

B Point Plus Thirty (30) Seconds: At thirty seconds following the B Point, an analysis will be performed by ERCOT with the assistance of the appropriate TAC subcommittee to determine if Primary Frequency Response is sustained.

For the purposes of this Section, a “Measurable Event” is the sudden change in interconnection frequency that will be evaluated for performance compliance will have i) a frequency B Point between 59.700 Hz and 59.900 Hz or between 60.100 Hz and 60.300 Hz, and ii) a difference between the B Point and the A Point greater than or equal to +/- 0.100 Hz.

- 5.9.2.1	ERCOT Required Primary Frequency Response

The combined response of all Generation Resources interconnected in ERCOT to a Measurable Event shall be at least 420 MW / 0.1 Hz. This value should be reviewed on an annual basis by ERCOT and the appropriate TAC subcommittee for system interconnect reliability needs.

ERCOT will evaluate, with the assistance of the appropriate TAC subcommittee, Primary Frequency Response during Measurable Events.  The actual Generation Resource response will be compiled to determine if adequate Primary Frequency Response was provided.

ERCOT and the appropriate TAC subcommittee will review each Measurable Event, verifying the reasonableness of data.  Data that is in question may be requested from the QSE for comparison and/or individual Resource data may be retrieved from ERCOT’s database.

ERCOT’s performance will be averaged using the most recent six (6) Measurable Events to determine its rolling average contribution.

- 6.5.3	Regulation Service (RGS)

(1)	The QSE’s control system must be capable of receiving digital control signals from ERCOT’s control system, and of directing its Resources to respond to the control signals, in an upward and downward direction to balance Real Time Demand and Resources, consistent with established NERC and ERCOT operating criteria.

(2)	Any QSE providing RGS must provide for communications equipment to receive telemetered control deployments of power from ERCOT.

(3)	QSEs must demonstrate to ERCOT that they have the capability to switch control to constant frequency operation as specified in the Operating Guides using telemetry at the QSE’s control center.  ERCOT authorized operations of the QSE’s regulation control system on constant frequency will be considered a Dispatch Instruction to deviate from schedule energy.

(4)	QSEs providing RGS will be required to provide a feedback signal meeting the requirements of ERCOT.

(5)	The Resource providing RGS must be capable of delivering the full amount of regulating capacity offered to ERCOT within ten (10) minutes.

(6)	Load Resources providing RGS must be capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and provide Primary 
Frequency Response.

(7)	The minimum amount of RGS that may be offered to ERCOT is one (1) MW.

(8)	QSE’s bids will be in accordance with Section 4, Scheduling.

(9)	Regulation instructions will be included in a QSE’s Schedule Control Error (SCE) calculation as instructed deviations.

(10)	Each Resource providing RGS must meet additional technical requirements specified in Section 6.10, Ancillary Service Qualification, Testing and Performance Standards, of these Protocols.

(11)	Resources providing RGS must have their Governors in service.

(12)	RGS is deployed proportionately to all providers.

(13)	Resources providing RGS must have sufficient qualified Generation Resources that will be On-line and able to respond in the Operating Hour for which they have been selected to provide the Ancillary Service.

- 6.5.4	Responsive Reserve Service

(1)	Responsive Reserve Service (RRS) may be provided by:

(a) 	Unloaded Generation Resources that are On-line;

(b) 	Resources controlled by high-set under-frequency relays;

(c) 	Hydro Responsive Reserves;

(d) 	From DC Tie response that stops frequency decay or; and

(e) 	From Load Resources capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and provide Primary Frequency Response.

The minimum amount of RRS provided by Generation Resources and Load Resources capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and that provides Primary Frequency Response shall be as specified in the Operating Guides.  QSE’s Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten (10) minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.  The amount of RRS on an individual Generation Resource may be further limited by requirements of the Operating Guides.

(2)	A QSE’s Load acting as a Resource must be loaded and capable of unloading the scheduled amount of RRS within ten (10) minutes of instruction by ERCOT and must either be immediately responsive to system frequency or be interrupted by action of under-frequency relays as specified by the Operating Guides.

(3)	Any QSE providing RRS must provide communications equipment to receive ERCOT telemetered control deployments of power.

(4)	Generation Resources providing RRS must have their Governor in service.

(5)	Interruptible Loads acting as a Resource providing RRS must provide a telemetered output signal, including breaker status and status of the under-frequency relay.

(6)	The minimum amount of RRS that may be offered to ERCOT is one (1) MW.

(7)	QSEs that provide the Resource for Responsive Reserve Service must ensure that Resources providing the service must be able to respond in the Operating Hour for which they have been selected to provide the RRS.  Each Generation Resource and Load acting as a Resource and providing RRS must meet additional technical requirements specified in Section 6.10, Ancillary Service Qualification, Testing, and Performance Standards of these Protocols.

(8)	The amount of Resources on high-set under-frequency relays providing RRS will be limited to fifty percent (50 %) of the total ERCOT RRS requirement.  ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation to be deployed as prescribed in Section 6.4.1, Standards for Determining Ancillary Services Quantities.

(9)	The amount of RRS that a QSE can self-arrange using Load acting as a Resource is limited to the lower of:

(a) 	the fifty percent (50%) limit set by these Protocols; or,

(b) 	the limit established by ERCOT.  However, a QSE may bid additional Load acting as a Resource above the percentage limitation established by ERCOT for sale of RRS to other Market Participants.   The total amount of Responsive Reserve Service using Load acting as a Resource procured by ERCOT is also limited to the lesser of the fifty percent (50%) limit or the limit established by ERCOT.

(10)	QSE bids for RRS will be in accordance with Section 4, Scheduling.

(11)	A Load acting as a Resource has the option to request a Load bid to be deployed only as a complete block.  To the extent that ERCOT deploys a bid by a Load acting as a Resource that has chosen a block deployment option, ERCOT shall either deploy the entire bid or, if only partial deployment is possible, skip the bid by the Load acting as a Resource and proceed to deploy the next available bid.

(12)	The amount of RRS that a QSE can self-arrange using Load acting as a Resource is limited to the percentage amount of total RRS that the LaaR can provide as specified by ERCOT.  However, a QSE may bid additional Load acting as a Resource into the ERCOT RRS Ancillary Service market.

(13)	LaaRs providing the RRS requested shall return to their committed operating level for providing RRS as soon as practical considering process constraints. For LaaRs unable to return to their committed operating level within three (3) hours, their QSE may schedule the quantity of deficient Responsive Reserve Service Capacity from other uncommitted Generation or LaaR Resource(s) to fulfill their RRS obligation.

(14)	RRS bids from QSEs may include contributions from combined cycle Resources in Aggregated Units meeting the criteria in Section 6.8.2.4, Aggregating Units.  Thus, to determine if a combined cycle Aggregated Unit is capable of performing its RRS Obligation, all Resources On-line in the Aggregated Unit will be measured as on an aggregate capacity basis and will be calculated from the lower of the High Sustainable Limits specified in the Resource Plan or through telemetry, or the seasonal tested Net Dependable Capability.

- 6.7.3	Deployment of Responsive Reserve Service

(1)	Responsive Reserve energy shall be deployed as necessary to meet North American Electric Reliability Corporation (NERC) requirements.  This shall be accomplished by:

(a)	Primary Frequency Response;

(b)	Through use of an automatic signal and a Dispatch Instruction to deploy Responsive Reserve energy from Resources; and/or

(c)	By Dispatch Instructions for deployment of Responsive Reserve energy from interruptible Load acting as a Resource via an electronic Messaging System to providers.

(2)	Deployment of energy as a result of  Primary Frequency Response will not be considered as an Uninstructed Deviation.

(3)	ERCOT will deploy Responsive Reserve Service (RRS) in response to disturbance control assistance requirements as specified in the Operating Guides or after all the bids in the Balancing Energy Services Up Bid Stack have been depleted.  Energy from Responsive Reserve Resources will be deployed by ERCOT in accordance with Section 5.6, Emergency and Short Supply Operation.

(4)	ERCOT deployment of RRS Resources will be proportioned first between suppliers who provide RRS using Generation Resources until thirty-three percent (33%) of the total amount procured by ERCOT is deployed.  If deployment of more than thirty-three percent (33%) is required, ERCOT shall:

(a)	For frequency restoration caused by an event other than capacity insufficiency, issue an Emergency Notice for frequency restoration and deploy all or a portion of remaining RRS being provided by hydro Resources and by Loads acting as Resources (LaaRs).

(b)	For frequency restoration related to capacity insufficiency, declare the Energy Emergency Alert (EEA) in effect and follow emergency provisions in Section 5, Dispatch.

(5)	ERCOT will deploy Balancing Energy Service and Non-Spinning Service as soon a practicable to minimize the use of Responsive Reserve energy.

(6)	All providers of Responsive Reserve Resources will be required to provide feedback to ERCOT of their availability and level of deployment in Real Time.  Except in those instances where a significant frequency deviation has occurred and temporary deployment is necessary to meet NERC requirements, ERCOT shall deploy RRS according to Section 5.6.

(7)	Once RRS is deployed, the obligation to deliver energy shall remain until specifically instructed by ERCOT to stop providing energy from RRS, but not longer than the period of the service is scheduled.

(8)	The QSEs providing RRS shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Service Deployment Performance Measures.

[PRR496: Add paragraph (9) below to Section 6.7.3 upon system implementation.] (9) RRS procured from a LaaR block bid shall be deployed as a block.

- 6.10.5.3	SCE Monitoring Criteria

SCE Monitoring Criteria will be reviewed by the appropriate ERCOT TAC subcommittee and submitted into these Protocols upon approval.

Each QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the equivalent power requirement of any instructed Ancillary Services and other SCE Obligation terms including Primary Frequency Response.  Texas Regional Entity (TRE) shall calculate one (1) and ten (10) minute averages of each QSE’s SCE.  TRE shall also calculate each QSE’s participation factor as the ratio of the QSE’s Generation Resource scheduled change in the measurement period (one (1) or ten (10) minute) to the total ERCOT Generation Resource scheduled change in the same measurement period.  ERCOT shall limit the deployment of RGS to QSEs for each control cycle equal to one hundred twenty five percent (125%) of the total amount of RGS in ERCOT divided by the number of control cycles in ten (10) minutes.  Intervals where a QSE’s generation level is less than one (1) MW in the measurement period (one (1) or ten (10) minute) will not be included in the calculation of the SCE Monitoring Criteria.  Satisfactory control performance of the QSE shall be deemed acceptable when:

(1)	The one (1) minute averages of the QSE’s SCE meet the following criteria over the calendar month (commonly referred to as SCPS1), and

(2)	The ten (10) minute averages of the QSE’s SCE meet the following criteria for ninety percent (90%) of the ten (10) minute periods over the calendar month (commonly referred to as SCPS2).

Where:

SCE1 	is the one (1) minute average of SCE.

SCE10	is the ten (10) minute average of SCE.

Bias1 	is the one (1) minute average of the ERCOT total bias used in the ACE calculation.

F1 	is the one (1) minute average of frequency deviation from schedule.

Participation Factor	is determined by the ratio of the QSE’s generation scheduled change for the measurement period (one (1) or ten (10) minute) to total ERCOT generation schedule change for the measurement period (one (1) or ten (10) minute).  Generation schedule change per interval is defined as below:

{Absolute Value

[     (ResourceSchedule – ResourceSchedulePreviousInterval)

+ (BalancingDeployment – BalancingDeploymentPreviousInterval)  ]

+ RegulationUpSchedule

+ RegulationDownSchedule}

If this Participation Factor Calculation results in a value of less than one-percent (1%), then one-percent (1%) will be used.

 	is a constant derived from the targeted frequency bound.  It is the targeted root-mean score of one (1) minute average frequency error from a schedule based on frequency performance over a given year as established according to NERC performance requirements by ERCOT and the appropriate TAC subcommittee.

L10 	is a limit to recognize the desired performance of frequency for ERCOT as established according to NERC performance requirements by the appropriate TAC subcommittee.  As of July 2003, L10 is defined as (1.65 * E10 * 10 * Bias10) where E10 is 0.01315 Hz and Bias10 is the ten (10) minute average of the ERCOT total bias used in the ACE calculation.

K	is a constant currently set to .81 which is established by the appropriate TAC subcommittee.  K should initially be set to .81 to provide an ERCOT wide L10 equivalent to the ERCOT wide L10 currently used by Control Areas in ERCOT.  This constant can be adjusted to ensure correlation between passing the NERC CPS2 criteria and passing the SCE ten (10) minute control limit.

TRE shall determine the QSE SCE performance score on a monthly basis.  SCPS2 scores equal to or greater than ninety-percent (90%) will be considered to be in compliance with the SCE Monitoring Criteria.  A QSE shall not be in compliance for any month with its score less than ninety-percent (90%) and shall be subject to procedures for non-compliance consistent with Section 6.10.12, Actions for Non-Compliance of the SCE Monitoring Criteria, through Section 6.10.12.5, ERCOT Actions for Non-Compliance.

Forced Derates shall be communicated to ERCOT immediately by voice communication.  The QSE representing the Resource will also report any changes in Resource status to ERCOT in the Resource Plan by the beginning of the next hour following the change in status in accordance with Section 5.5.1, Changes in Resource Status.

Startup Loading Failures shall be communicated to ERCOT immediately by voice communication.  The QSE representing the Resource will also report any changes in Resource status to ERCOT in the Resource Plan by the beginning of the next hour following the change in status in accordance with Section 5.5.1.