| PRR Number | 835 | PRR Title | Reactive Capability Requirement |
| --- | --- | --- | --- |
| Date Posted |  | September 30, 2009 |  |
| Protocol Section(s) Requiring Revision (Include Section No. and Title) |  | 2.1, Definitions 2.2, Acronyms 6.5.7, Voltage Support Service 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability 6.5.7.4, Wind-powered Generation Resources Required to Provide VSS Installed Reactive Capability (new) 6.7.6, Deployment of Voltage Support Service |  |
| Requested Resolution (Normal or Urgent, and justification for Urgent status) |  | Urgent. Due to conflicting interpretations of Protocol Sections 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability and 6.7.6, Deployment of Voltage Support Service, ambiguity exists as to what the requirements are for existing and future Wind-powered Generation Resources (WGRs) in providing Reactive Power and Voltage Support Service (VSS). This Protocol Revision Request (PRR) clarifies the Reactive Power and VSS requirements for WGRs, and provides a means for maintaining and ensuring reliability without unnecessarily burdening existing and future WGRs with the cost of installing supplemental reactive capability in locations where it will have little or no value. This PRR requires existing WGRs interconnected after May 17, 2005 to provide +/- .95 power factor at the Point of Interconnection (POI) over the full output range of the Resource which is consistent with the interpretation and criteria applied by the Transmission Service Providers (TSPs) at the time these Resources were interconnected. This PRR differentiates Reactive Power and VSS requirements for WGRs from other non-wind types of Resources primarily because of the unique characteristics of the ERCOT Transmission Grid where the majority of the wind Resources currently are, and will be, interconnected. The Western zone of ERCOT has very little Load as compared to the magnitude of installed and planned WGRs and therefore has very different Reactive Power requirements from other regions of ERCOT. The imposition of a “one size for all” approach, as proposed in PRR830, Reactive Power Capability Requirement, to all generating Resources for ensuring reliability is not economically efficient in that it will necessitate the installation of reactive Resources at locations where, as a practical matter, grid reliability benefits will not be realized or ensured. This PRR also provides for the imposition of additional Reactive Power capability to support VSS by WGRs if the TSP shows, through the System Impact Study, that such capability is required to ensure grid safety or reliability. |  |
| Revision Description |  | This PRR clarifies the Reactive Power capability requirement for WGRs by specifying +/- 0.95 power factor criteria as the minimum requirement, and the Generation Resources Unit Reactive Limit (URL) criteria as the maximum requirement contingent upon a System Impact Study by the TSP. |  |
| Reason for Revision |  | Clarification of requirements for Resources. |  |
| Overall Market Benefit |  | This PRR provides additional clarity to the reactive requirements for wind generation to ensure grid safety and reliability while avoiding the cost of additional equipment where it is not justified. |  |
| Overall Market Impact |  | None. |  |
| Consumer Impact |  | This PRR may cause the cost of energy generation to increase for WGRs, however, it provides a responsible, economically efficient and technically justified option for consumers should Market Participants find that WGRs should provide additional Reactive Power. |  |
| Credit Implications (Yes or No, and summary of impact) |  | Unknown. |  |
| Relevance to Nodal Market (Yes or No, and summary of impact) |  | Yes. |  |
| Nodal Protocol Section(s) Requiring Revision (Include Section No. and Title, and submit NPRR if applicable) |  | To be determined based upon final resolution of this issue in the Zonal Protocols. |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Additional 10,000 MW of wind generation in Competitive Renewable Energy Zones (CREZs) and unknown amount of existing affected wind Resources under the proposed PRR830. |  |
|  | 2 | Avoidance of unnecessary cost impacts to existing wind generators assumed to be $10k/MW installed. |  |
|  | 3 | Avoids installation of additional reactive capability not justified for reliability. |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | WGRs. | Potentially $100M. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | System reliability | Potentially none |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | Avoidance of the imposition of additional reactive requirements under the presumption of reliability without technical justification is economically inefficient. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Peter Wybierala |
| E-mail Address | peter.wybierala@fpl.com |
| Company | NextEra Energy Resources |
| Phone Number | 561-304-5356 |
| Cell Number |  |
| Market Segment | Independent Generator |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Sandra Tindall |
| E-Mail Address | stindall@ercot.com |
| Phone Number | 512-248-3867 |

Proposed Protocol Language Revision

2.1	Definitions

Point of Interconnection (POI)

The location(s) where a Generation Entity’s interconnection Facilities connect to the Facilities of the Transmission and/or Distribution Service Provider (TDSP) as specified in the Standard Generation Interconnection Agreement (SGIA) between a Generation Entity and the TDSP.

Wind-powered Generation Resource (WGR)

A Generation Resource that is powered by wind, which may consist of an aggregation of wind turbines connected to the ERCOT Transmission Grid through one Point of Interconnection (POI).

Pmax

A wind power generation facility’s revised maximum output submitted in Real Time via SCADA based on the number of wind turbine generators that our out of service.

2.2	Acronyms

POI 	Point of Interconnection

SGIA	Standard Generation Interconnection Agreement

6.5.7	Voltage Support Service

All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than twenty (20) MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than twenty (20) MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

6.5.7.1	Generation Resources, Other Than Wind-powered Generation Resources, Required to Provide VSS Installed Reactive Capability

(1)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power at rated capability (MW) to maintain a Voltage Profile established by ERCOT.  This quantity of Reactive Power is the Unit Reactive Limit (URL).

(2)	Generation Resources required to provide VSS shall have and maintain a URL which has an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the POI to the TDSP.

(3)	Upon request to, and with the approval of ERCOT, multiple generating units connected to the same transmission bus may be treated as a single generating unit for the purposes of these URL requirements only.

(4)	Upon submission by a Generation Resource required to provide VSS to ERCOT of a specific proposal for requirements to substitute for these URL requirements, ERCOT shall either approve such alternative requirements or provide the submitter an explanation of its objections to the proposal.  Alternative requirements may include supplying additional static and/or dynamic Reactive Power capability as necessary to meet the area’s Reactive Power requirements.

(5)	For Generation Resources required to provide VSS, no unit equipment replacement or modification shall reduce the capability of the unit below the requirements to be met by that unit prior to the replacement/modification, unless specifically approved by ERCOT.

(6)	Generation Resources required to provide VSS shall not reduce high reactive loading on 	individual units during abnormal conditions without the consent of ERCOT (conveyed by 	way of their QSE) unless equipment damage is imminent.

6.5.7.4	Wind-powered Generation Resources Required to Provide VSS Installed Reactive Capability

(1)	WGRs are required to provide VSS and must be capable of operating at a power factor of +/- .95 or less over the full (MW) net power output range of the Resource, supplied to the ERCOT Transmission Grid, and measured at the POI to the TDSP in order to maintain a Voltage Profile established by ERCOT.  This requirement is graphically depicted in Figure 1.  The quantity of Reactive Power measured at the full rated capability of the Resource is the URL.

Figure 1.  +/- .95 Power Factor Criteria

(2)	WGRs may be required to provide VSS beyond what is required in paragraph (1) above only if the TSP or ERCOT shows, through a System Impact Study, that such capability is required to ensure grid safety or reliability.  The amount of additional reactive capability required to be provided by the Resource shall not exceed the URL specified in paragraph (1) above and be available at all MW output levels over the full output range of the Resource.  This requirement is graphically depicted in Figure 2.  This additional reactive capability may be provided through any combination of automatically switchable static reactive devices (i.e. switched shunts) and/or dynamic reactive devices (i.e. SVC, Statcom, etc.) so long as the requirement to ensure safety and reliability is met.

Figure 2.  Fixed URL Criteria (based on +/- .95 Power Factor)

(3)	Demonstration and measurement of reactive capability will be based on system Voltage Profile criteria specified by ERCOT.  This Voltage Profile criteria will consist of a low system voltage Vsys-l, where the wind Resource will be operating in a lagging power mode to produce the required amount of Reactive Power to support system voltage, and Vsys-h, where the wind Resource will be operating in a leading mode to absorb the required amount of Reactive Power to suppress system voltage.  The scheduled system voltage under normal conditions should fall somewhere in between Vsys-l and Vsys-h.

(4)	WGRs capable of remaining On-line at low output levels considered outside of their net power output range where VSS can not be provided at the POI shall be capable of operating such that they appear “VAR Neutral” at the POI.  The amount of allowable deviation from unity (1.0) power factor will be specified by the TDSP.  WGRs that cannot meet the “VAR neutrality” requirement may be required to disconnect from the ERCOT System.

(5)	Qualified renewable WGRs (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS, and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the URL as stated above, will be required to maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at its rated capability (MW) as determined using procedures and criteria as described in the Operating Guides.

(6)	WGRs connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the URL as stated above, will be required to maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at its rated capability (MW) as determined using procedures and criteria described in the Operating Guides.

(7)	WGRs connected after May 17, 2005 are required to provide VSS as described in paragraph (1) above.

(8)	Upon request to, and with the approval of ERCOT, multiple wind generating units connected to the same transmission bus may be treated as a single generating unit for the purposes of these URL requirements only.

(9)	Upon submission by a WGR required to provide VSS to ERCOT of a specific proposal for requirements to substitute for these URL requirements, ERCOT shall either approve such alternative requirements or provide the submitter an explanation of its objections to the proposal.  Alternative requirements may include supplying additional static and/or dynamic Reactive Power capability as necessary to meet the area’s Reactive Power requirements.

(10)	A wind induction generator may elect to make a contribution in aid of construction in lieu of meeting the installed capacity VSS requirements contained herein.  In order to comply with the VSS requirements under paragraph (7) above, the generator must make payment to the interconnecting TDSP under its generation Interconnection Agreement in a manner similar to that used to collect payments for the direct assignment of interconnection Facilities under applicable Public Utility Commission of Texas (PUCT) rules.  The level of payment shall reflect the cost to the TDSP of procuring, installing, operating, and maintaining any Reactive Power equipment required to replace the Reactive Power capability that otherwise would be necessary for the interconnection of the generator.  In order for paragraph (7) above to be effective for VSS compliance, the TDSP shall certify to ERCOT that the induction generator has complied with these requirements.

(11)	For WGRs required to provide VSS, no unit equipment replacement or modification shall reduce the capability of the unit below the requirements to be met by that unit prior to the replacement/modification, unless specifically approved by ERCOT.

(12)	WGRs required to provide VSS shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT (conveyed by way of their QSE) unless equipment damage is imminent.

(13)	WGRs must provide Real Time Supervisory Control And Data Acquisition (SCADA) points that communicate to ERCOT the Facility’s available Pmax and revised URL values reflecting the amount of installed turbine capacity that is out of service.

6.7.6	Deployment of Voltage Support Service

(1)	ERCOT, or Transmission Service Providers (TSPs) designated by ERCOT, will instruct Generation Resources required to provide Voltage Support Service (VSS) to make adjustments for voltage support within the Unit Reactive Limit (URL) capacity limits provided by the QSE to ERCOT.  Generation Resources providing VSS will not be requested to reduce megawatt output so as to provide additional Megavolt Ampere Reactive (MVAR), nor will they be requested to operate on a voltage schedule outside the URL specified by the QSE without a Dispatch Instruction requesting unit-specific Dispatch or an OOME instruction.

(2)	ERCOT and Transmission and/or Distribution Service Providers (TDSPs) shall develop operating procedures specifying Voltage Profiles of transmission controlled reactive Resources to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, step-up transformer tap settings will be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

(3)	The TSP, under ERCOT direction, is responsible for monitoring and ensuring that all Generation Resources required to provide VSS dynamic reactive sources in a local area are deployed in approximate proportion to their respective installed reactive capability requirements.

(4)	All Generation Resources required to provide VSS shall support the transmission voltage at the Point of Interconnection (POI) to the ERCOT Transmission Grid as directed by ERCOT within the operating Reactive Power capability of the unit(s).

(5)	The QSEs providing VSS shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Service Deployment Performance Measures.