| NOGRR Number | 030 | NOGRR Title | Deletion of Total Transfer Capability (TTC) (formerly “Synchronization – Total Transmission Capacity Correction”) |  |
| --- | --- | --- | --- | --- |
| Timeline | Urgent | Action |  | Approved |
| Date of Decision |  | October 1, 2009 |  |  |
| Effective Date |  | Upon Texas Nodal Market implementation. |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Guide Section Requiring Revision |  | 3.9.4 Responsibility for Equipment Ratings |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) deletes the use of Total Transfer Capability (TTC). |  |  |
| Reason for Revision |  | Total Transfer Capability, as defined by North American Electric Reliability Corporation (NERC), does not apply to the ERCOT Region since there is only one transmission system; therefore, ERCOT proposes deletion of the term which could otherwise give the perception that ERCOT is out of compliance with NERC Reliability Standards. |  |  |
| Overall Market Benefit |  | Diminish exposure to findings of non-compliance with the NERC Reliability Standards. |  |  |
| Overall Market Impact |  | There should be minimal to no market impact, as this is a correction to the Nodal Operating Guides. |  |  |
| Consumer Impact |  | There should be minimal to no consumer impact, as this is a correction to the Nodal Operating Guides. |  |  |
| Procedural History |  | - On 9/3/09, NOGRR030 and the associated Impact Analysis and CEO Revision Request Review were posted. - On 9/8/09, the motion to grant NOGRR030 Urgent status failed via ROS e-mail vote. - On 9/10/09, ROS considered NOGRR030. - On 9/24/09, ERCOT comments were posted. - On 10/1/09, TAC considered NOGRR030. |  |  |
| ROS Decision |  | On 9/10/09, ROS voted to grant NOGRR030 Urgent status. There were two abstentions from the Independent Retail Electric Provider (IREP) Market Segment. ROS also voted to recommend approval of NOGRR030 as submitted. There was one abstention from the Independent Retail Electric Provider (IREP) Market Segment. All Market Segments were present for the votes. |  |  |
| Summary of ROS Discussion |  | On 9/10/09, ERCOT Staff provided an explanation regarding the need to clarify the language prior to the NERC audit scheduled for October 2009. It was noted that the associated PRR829, Total Transmission Capacity Correction, was granted urgent status via a PRS email vote. |  |  |
| TAC Decision |  | On 10/1/09, TAC unanimously voted to approve NOGRR030 as amended by the 9/24/09 ERCOT comments. All Market Segments were present for the vote. |  |  |
| Summary of TAC Discussion |  | On 10/1/09, concern was expressed regarding the consistency of market rules language and NERC terminology. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | None. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Diminish risk of non-compliance with NERC Reliability Standards. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | JC Culberson |
| E-mail Address | jcculberson@ercot.com |
| Company | ERCOT |
| Phone Number | 512-248-4505 |
| Cell Number | 512-569-5520 |
| Market Segment | N/A |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| ERCOT 092409 | Proposed language changes to remove TTC from the Nodal Operating Guides. |

Proposed Guide Language Revision

- 3.9.4	Responsibility for Equipment Ratings

(1)	TSPs are responsible for determining the rating of their facilities.  Technical limits established for the operation of Transmission Elements and associated equipment shall be applied consistently in engineering and planning studies, Real-Time security analyses, and operator actions.

(2)	TSPs shall provide ERCOT with three nominal Transmission Facility Ratings:

(a)	“Continuous Rating”:  Represents the continuous MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Facility can operate at this rating indefinitely without damage, or violation of National Electrical Safety Code (NESC) clearances.

(b)	“Emergency Rating”:  Represents the two-hour MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature.  The Transmission Facility can operate at this rating for two hours without violation of NESC clearances or equipment failure.

(c)	“15-Minute Rating”:  Represents the 15 minute MVA rating of a Transmission Facility, including substation terminal equipment in series with a conductor or transformer, at the applicable ambient temperature and with a step increase from a prior loading of 90% of the Continuous Rating.  The Transmission Facility can operate at this rating for 15 minutes, assuming its pre-contingency loading was 90% of the Continuous Rating limit at the applicable ambient temperature, without violation of NESC clearances or equipment failure.  This rating takes advantage of the time delay associated with heating of a conductor or transformer following a sudden increase in current.

(3)	In operating the ERCOT Transmission Grid, ERCOT shall use these ratings as follows:

(a)	ERCOT shall limit pre-contingency flows to enforce the Continuous Rating.

(b)	If a valid Remedial Action Plan (RAP) is unavailable to unload the Transmission Facility post contingency or the pre-contingency loading is greater than 90% of the Continuous Rating, ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Facility to levels below the Emergency Rating.  The enforcement shall be implemented in a manner such that the post contingency loading will be at, or below, Continuous Rating within two hours.

(c)	If a RAP is documented at ERCOT to relieve the loading on the Transmission Facility within 15 minutes; ERCOT shall enforce pre-contingency system operating limit(s) to control the post contingency loading of the Transmission Facility to levels below the 15-Minute Rating.  The enforcement shall be implemented in a manner such that the post-contingency loading will be at, or below, Emergency Rating within 15 minutes.

(d)	ERCOT shall use best efforts to restore all Transmission Facilities to within Continuous Ratings as soon as practicable, based on Good Utility Practice.