| PRR Number | 830 | PRR Title | Reactive Power Capability Requirement |
| --- | --- | --- | --- |
| Date |  | October 8, 2009 |  |
| Submitter’s Information |  |  |  |
| Name |  | Jack Thormahlen |  |
| E-mail Address |  | jack.thormahlen@lcra.org |  |
| Company |  | LCRA |  |
| Phone Number |  | 512-473-3200 |  |
| Cell Number |  |  |  |
| Market Segment |  | Cooperative |  |

Comments

LCRA submits the following comments for clarification purposes in PRR830, Reactive Power Capability Requirement.

In paragraph (1) of Section 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability, what was paragraph (2),  LCRA notes that the language “and at the transmission system Voltage Profile established by ERCOT and both” should be deleted.  When running a lagging reactive test in the transmission corridors that are congested, the lagging reactive test often fails to reach an adequate test output due to system voltage constraints if the test is initiated at the ERCOT-established Voltage Profile.  LCRA suggests deleting that language to allow Resources to start at a lower voltage level assuming the transmission service provider can lower the voltage to facilitate a meaningful lagging reactive test.  In 6.5.7.1(3), LCRA adds the inclusion of all other Generation Resources prior to September 1, 1999 as an exemption.

LCRA also proposes additional modifications in 6.5.7.1(3) related to establishing Reactive Power requirements.  If taken literally, the language presumes that the tested value at the maximum net power to the grid can be produced across the entire megawatt (MW) range of a Generation Resource.  The reality is that different Resource types have different characteristics and therefore may not be able to completely follow a straight line curve because of electrical or mechanical limitations.  Some Resources may follow an erratic curve due to electronic derivations or have other machine specific limitations.  LCRA proposes that Resources establish a minimum of a six-point curve to provide a valid unit capability across the generator MW range.

Finally, the ERCOT requirement to disconnect a Wind-powered Generation Resource (WGR) that is operating below 10% of its nameplate capacity and is unable to support voltage at the Point of Interconnection (POI) is too unforgiving.  Because there are a number of WGRs often in a region, ERCOT should establish which particular WGR is the appropriate WGR to disconnect by performing a voltage study in Real Time.  That study should also help determine if an alternate device might do a better job of meeting the Reactive Power requirements.  Finally, if the WGR is required to disconnect as a result of the study, there shall be no repercussions from ERCOT or the Texas Regional Entity (TRE) for the inability to support the POI voltage.

In 6.7.6, Deployment of Voltage Support Service, ERCOT uses the Voltage Profile established by a Protocol-prescribed study.  If a Transmission Service Provider (TSP) changes voltage because of changes in system conditions, and they do not alert ERCOT of the change, ERCOT’s Real Time studies will not reflect the new Voltage Profiles.  LCRA proposes having the TSP provide an end-time to the voltage changes.

Revised Proposed Protocol Language

2.1	Definitions

Point of Interconnection (POI)

The location(s) where a Generation Entity’s interconnection Facilities connects to the Transmission Facilities as reflected in the Standard Generation Interconnection Agreement (SGIA) between a Generation Entity and a Transmission and/or Distribution Service Provider (TDSP).

Wind-powered Generation Resource (WGR)

A Generation Resource that is powered by wind.  Wind turbines may be aggregated together to form a WGR if each turbine is the same model and size and located behind the same Generation Step Up Transformer (GSU).

Unit Reactive Limit (URL)

The maximum reactive capability of a unit at a unit’s HSL as determined in biennial tests as required by the ERCOT Operating Guides.

2.2	Acronyms

POI		Point of Interconnection

GSU		Generation Step Up Transformer

SGIA		Standard Generation Interconnection Agreement

6.5.7	Voltage Support Service

All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than twenty (20) MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than twenty (20) MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

6.5.7.1	Installed Reactive Power Capability Requirement for Generation Resources Required to Provide VSS

(1)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established ERCOT.  	Generation Resources shall comply with the following Reactive Power requirements:

(a)	The Generation Resource shall maintain an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid, measured at the POI;

(b)	The establishment of Reactive Power requirements in a six point test curve shall be available for all MW output levels.  The Unit Reactive Limit (URL) across all levels can be determined by a six-point test curve across the MW capacity of the units;

(c)	The .95 power factor level  ay be met through a combination of the Generation Resource’s URL) which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAR capable devices. and

(d)	For Wind-powered Generation Resources (WGRs), the URL shall be determined for MW output levels utilizing the six-point test curve beginning at 10% of the WGR’s nameplate capacity through the WGR’s nameplate capacity.  When a WGR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI as determined by a Real Time voltage study, ERCOT may require a WGR to disconnect from the ERCOT System.  The Reactive Power requirements of this paragraph shall apply to all Generation Resources except as otherwise provided in paragraphs (2) through (4) below.  If the units are disconnected, they will not be found in violation of the Protocols.

(2)	WGRs that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before November 1, 2009, must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (1) above.  However, the Reactive Power requirements may be met through a combination of the WGR’s URL and/or automatically switchable static VAR capable devices and/or dynamic VAR capable devices.  WGRs shall comply with the Reactive Power requirements of this paragraph by no later than December 31, 2010, unless it is known by July 31, 2010, that related retrofits are required by the Voltage Ride-Through study conducted in accordance with Operation Guide Section 3.1.4.6.1, Protective Relaying Requirement and Voltage Ride-Through Requirement for Wind-powered Generation Resources, in which event ERCOT may in its discretion modify the deadline for an affected WGR.  ERCOT, in its sole discretion, also may grant an extension of time for other reasons.

(3)	Qualified renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (1) above, will be required to maintain a Reactive Power requirement as defined by the qualified renewable Generation Resource’s or all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999 that was submitted to ERCOT and established per the criteria in the Operating Guides.

(4)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (1) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(5)	For purposes of meeting the Reactive Power requirements in paragraphs (1) and (2) above, multiple generation units including wind turbines shall, at a Generation Entity’s option, be treated as a single Generation Resource or WGR if the units are connected to the same transmission bus.

(6)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (1) above by employing a combination of the URL and added VAR capability, provided that the added VAR capability shall be automatically switchable static and/or dynamic VAR devices. ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(7)	A Generation Resource and TDSP may enter into an agreement in which the Generation Resource compensates the TDSP to provide VSS to meet the Reactive Power requirements of paragraph (1) above in part or in whole.  The TDSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (1).

(8)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement/modification.

(9)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT (conveyed by way of their QSE) unless equipment damage is imminent.

(10)	WGRs must provide a Real Time SCADA point that communicates to ERCOT the number of wind turbines that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.  WGRs must also provide two other Real Time SCADA points that communicate to ERCOT the following:

(a)	The number of wind turbines that are not able to communicate and whose status is unknown; and

(b) 	The number of wind turbines out of service and not available for operation.  WGRs must comply with these requirements by no later than six months after the effective date of this paragraph.

(11) 	For the purpose of complying with the Reactive Power requirements under this Section, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAR capable devices.

6.7.6	Deployment of Voltage Support Service

(1)	ERCOT, or Transmission Service Providers (TSPs) designated by ERCOT, will instruct Generation Resources required to provide Voltage Support Service (VSS) to make adjustments for voltage support within the Unit Reactive Limit (URL) capacity limits and provide the QSE and/or the generator the length of time for the change provided by the QSE to ERCOT.  Generation Resources providing VSS will not be requested to reduce megawatt output so as to provide additional Megavolt Ampere Reactive (MVAR), nor will they be requested to operate on a voltage schedule outside the URL specified by the QSE without a Dispatch Instruction requesting unit-specific Dispatch or an OOME instruction.

(2)	ERCOT and Transmission and/or Distribution Service Providers (TDSPs) shall develop operating procedures specifying Voltage Profiles of transmission controlled reactive Resources to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, step-up transformer tap settings will be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

(3)	The TSP, under ERCOT direction, is responsible for monitoring and ensuring that all Generation Resources required to provide VSS dynamic reactive sources in a local area are deployed in approximate proportion to their respective installed Reactive Power capability requirements.

(4)	All Generation Resources required to provide VSS shall support the transmission voltage at the POI to the ERCOT Transmission Grid, or at the transmission bus in accordance with paragraph (5) of Section 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability, as directed by ERCOT within the operating Reactive Power capability of the unit(s).

(5)	The QSEs providing VSS shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Service Deployment Performance Measures.