September 15 : 	The last Network Data Support Working Group (NDSWG) meeting.

September 24  :	NDSWG held a 2 hour WebEx

October 01 :	NDSWG held a 2 hour WebEx

October 13 :	NDSWG meeting  via Webex Call.

The following is summary of the main topics of discussion of the September 15th meeting

- ERCOT presented a SEM update to the NDSWG.  A CIM  file was posted on September 15.  (A CIM file was posted on Oct 5 and another will be posted on the 16th corresponding with the Zonal database loads.)  ERCOT has worked through three rounds of ownership changes in NMMS and will probably need one more round to correct the last ownership problems identified by the TSP’s.    (Four rounds of station ownership iterations have been completed.  ERCOT continues to handle additional requests individually. Most of the remainder of the ownership problems are associated with lines and RARF data and are being reviewed in a separate process.)

- ERCOT staff is continuing to engage ERCOT legal on the definition and usage of operatorship/ownership designations. ERCOT legal is working on an NPRR and has responded that ERCOT cannot require TSPs to provide model data for equipment that is not owned by the TSPs, e.g. unregistered load PUNs.  If the TSP does not provide the required model data, then ERCOT will have to contact the asset owner.  There was a lot of discussion about ERCOT needing to get legal to define what the rights, responsibilities, and liabilities are for the owner or the operator.  (ERCOT Legal met with NDSWG on October 1 to better understand the concerns of MPs.)

- ERCOT presented a flow chart defining a process to work though a “Broken Outage Processes”. Because of equipment name changes are being made in NMMS to synchronize the ERCOT and TSP operations models there is a good probability of these broken outages occurring during the validation process.   (The process is in place and working.)

- The NDSWG spent a considerable amount of time working on developing a spreadsheet to capture and track issues related to NMMS that they feel need to be addressed.  This spreadsheet is also intended to capture and track template change requests, modifications by ERCOT to the modeling guidelines, and possibly new functional needs that will have to be addressed after Nodal Go Live.   Now that we have passed the SEM milestone, NDSWG requests any changes to modeling guidelines and CIM schema to be vetted through NDSWG.  (The spreadsheet currently has 28 issues of which 12 have been either closed or are waiting resolution implementation.  Spreadsheet items are discussed on a bi-weekly basis with NDSWG.)

- The Telemetry and State Estimator reports were defined to have the Nodal MIS as the system of delivery. The nodal MIS isn’t ready so ERCOT will put them on the POI site which is only accessible by TSP’S. ERCOT will send these reports to any QSE’s requesting them on CD. The new MIS site will be available the first of next year and until then ERCOT plans to send CD’s to QSE’s as an interim workaround.

- On 09/29/09, ERCOT provided TSPs a data summary of the NMMS model in Excel format in order to assist them in the validation of the data in the model.  This summary will be updated, modified, and redistributed periodically in order to assist validation efforts.

- On 10/08/09, ERCOT provided NDSWG the list of “20 most voltage critical buses “, which The State Estimator Standards require them to designate and get approved by TAC.

Major SEM / NMMS issues

ERCOT staff has been working diligently to process the influx of NOMCRs and respond to MP questions and requests.   However, some major issues or concerns remain for SEM and NMMS that could delay TSP model validation efforts.

- Owner/Operator designations continue to plague the validation efforts.  Clear definitions have not been provided and the validation rules are either unclear or restrictive.     A clear legal interpretation is required to assess liabilities with these designations.  It is essential for TSP validation efforts after SEM go-live.  Only owners are allowed to add or delete data in NMMS.  This creates problems when owners need operators to submit data on their behalf.  Dual ownership of equipment exacerbates the problem because the current validation rule does not allow either one of the owners to add or delete data.

  - NDSWG suggests ERCOT temporarily turn off or relax the validations rules associated with ownership for the TSP model validation period.

- Any change to the NMMS network model is reflected into the Zonal Model which is the current model of record.  ERCOT is manually converting NOMCRs to Zonal changes.  Although this process was understood prior to SEM, the level of dependency was not.   The approval of an NOMCR is dependent on ERCOT’s ability to manually model the change on the Zonal.  So until go-live, NMMS is essentially a new front end to the Zonal system.  This poses three main problems.

  - One is broken outages that result from equipment name changes.    Any NOMCR that changes equipment names that affect planned outages in the outage scheduler will not be approved if the outage occurs within the next two database loads.  NOMCRs that conflict with outages outside the next two database loads are allowed to proceed.  Prior to SEM the MP understanding was that not all name changes needed to be translated into Zonal.  This has caused a setback to model validation efforts by MP.  ERCOT has modified their process to reduce this impact but the problem still remains.

  - The frequency of Zonal model database loads (every 2 weeks) is affecting the NOMCR validation process in some cases.   Nodal and NMMS was designed to be a time based model that could be updated every day.  But because of the current dependency to the Zonal model, some NOMCR approvals are linked to that two weeks schedule.  Additional NOMCRS are required to keep the Zonal accurate.

  - ERCOT is limiting the TSP model changes to a number that their modeling staff can manually process in the zonal model every two weeks. In some cases, this is going to limit the TSP's model updates and could delay model validation efforts.

- The model is imbedded with equipment and objects that are not owned by the TSP.  These are used by downstream ERCOT systems.   Due to the ownership issues in the model, these present a big problem for validation efforts and for general NOMCR submittals into the future.

- The conversion of the Zonal model to Nodal carried over certain modeling constructs into the NMMS Network Model provided to the TSPs for SEM.  Unfortunately, these constructs do not pass ERCOT’s validation rules for data submittal and has caused TSPs difficulties in submitting some NOMCRs.  ERCOT is working with TSPs to identify affected data and correct these problems.