## Slide 1: Reactive Discussion Kenneth A. Donohoo, P.E. Director, System Planning Distribution and Transmission Oncor Electric Delivery Company LLC Presentation to ERCOT ROS October 15, 2009 Austin, TX

## Slide 2: ONCOR SYSTEM
Wires Only Company
Innovative Solutions
Agility in Execution
More than 14,900 circuit miles of Transmission including:
  5,044 circuit miles of 345 kV
  6,916 circuit miles of 138 kV
  2,946 circuit miles of 69 kV
More than 970 Stations
More than 1,550 Power Transformers
More than 6,000 Breakers
More than 180 Autotransformers
Significant Load Serving Distribution System

## Slide 3: RELIABILITY REQUIREMENTS
Planning Standards and Criteria
  Normal Condition
  First Contingency Condition
  Second Contingency Condition, with adjustment
Operations Constraints
  Maintenance and construction feasibility
  Complexity
  Outages and clearances
  Constantly changing

## Slide 4: TYPES OF PROBLEMS
Thermal Overload
  Loading on an element is too high to allow needed dissipation of heat, resulting in damage (substation equipment and cable) or clearance violations (lines).
Voltage Problems
  Voltage either cannot be stabilized (voltage collapse) following a contingency event, or it cannot be maintained within a band acceptable to avoid potential damage to customer or utility equipment. Low voltage rather than high voltage, is the more common problem, by far.
Stability
  Synchronism cannot be maintained between generators, either because of a contingency event (transient instability), or because a deficiency in system damping causes oscillations which continue to grow (dynamic instability).

## Slide 5: TEMPORARY SOLUTIONS CONSIDERED
Thermal
  Add temperature monitoring to allow real-time dynamic rating
  Add a Special Protection System to reduce generation or reconfigure network
  Create a Remedial Action Plan which directs specific operator actions
Voltage
  Change transformer taps
  Replace remote generation with local generation
  Maintain extra reactive reserve
Stability
  Add Special Protection System that trips some units to save others
  Adjust operations to maintain dynamic reactive reserve

## Slide 6: PERMANENT SOLUTIONS CONSIDERED
Thermal
  Increase thermal capability of the overloaded element
    Reconductor lines
    Rebuild lines
    Raise line voltage
    Increase line clearance
    Add cooling to transformers
  Redirect excess flow onto unconstrained parallel path(s)
    Increase impedance of overloaded path (switchable thermal equipment, series reactors, FACTS devices)
    Decrease impedance of parallel path(s) (series capacitors)
    Build new parallel path(s)
    Add phase-shifting transformer(s) (change phase angle)

## Slide 7: PERMANENT SOLUTIONS CONSIDERED
Voltage
  Increase reactive power support in areas of depressed voltage
    Improve load power factor
    Add distribution feeder capacitors
    Add substation (distribution or transmission) capacitors
    Add dynamic reactive device (STATCOM, FACTS device) [synchronous condensor option rare)
  Decrease reactive power losses in the network
    Add series capacitors to lines
    Add Static Synchronous Series Compensator (SSSC, FACTS device) to lines
    Add Superconducting Magnetic Energy Storage (SMES) device

## Slide 8: PERMANENT SOLUTIONS CONSIDERED
Stability
  Minimize fault duration (trip breakers quickly)
  Add independent pole fault clearing
  Decrease impedance of network by adding or upgrading lines
  Install fast generation excitation systems (usually new generating units only, difficult to retrofit)
  Use FACTS devices to boost voltage during faults, decrease line impedance, or provide damping through the modulation of reactive power flow
  Add power system stabilizer(s) to increase damping of oscillations

## Slide 9: REACTIVE COMPENSATION
Voltage control has been problematic in West Texas due to varying load, generation and transmission topology conditions.
Distance from large load centers adds additional complexity and challenges operations.
Appropriate dynamic/static and series/shunt reactive devices should be included to handle possible operating conditions. Plan should not be limited to account for unidentified operating conditions (additional reactive reserve).
Generally, we include shunt reactors to compensate for about 30% line charging.
We apply series reactors to redirect flows.
Actual reactive design to meet ERCOT reactive standard varies by location, study and actual operating conditions.

## Slide 10: REACTIVE CAPABILITY TESTING
ERCOT Protocols:
  6.10.3.5:
    generator must conduct reactive tests
    testing required on "initial qualification"Planning Standards and Criteria

## Slide 11: REACTIVE CAPABILITY TESTING
ERCOT Operating Guides:
3.1.4.3.1:
  Reactive capability curve (CURL) must be suppled by Generator to ERCOT
3.1.4.3.2:
  Non-coordinated Testing...QSE must schedule reactive verification tests with ERCOT
3.1.4.3.3:
  Coordinated testing: discusses testing
3.1.4.3.4:
  ERCOT implementation: ...ERCOT to review results of tests. Reactive tests to be reviewed by ERCOT to determine if they fall within 90% of CURL curve.
3.1.4.3.5:
  Enforcement of Unit Reactive Capability Testing....details of enforcement of reactive testing can be found on Compliance Template on ERCOT Compliance Web Page.

## Slide 12: REACTIVE CAPABILITY TESTING
ERCOT Procedure:
Go to Services, Registration & Qualification, Resource Entities...
New gen commissioning checklist...Operating Day....gen should make plans for MVAR testing
RARF Guide, section 7.3 and 7.4 says gen to provide reactive curve data points and perform reactive testing.