## Slide 1: PRR835 – Reactive Power Capability Requirement
Peter Wybierala
Regional Director of Transmission & Interconnects
Presentation to the ERCOT Reliability and Operations Subcommittee (ROS)
October 15, 2009

## Slide 2: Ancillary Services Section 6.5.7 needs to be revised
All generators are not the same
  Synchronous generators have their own inherent reactive power characteristics
  The reactive capability of wind generators is evolving
    Early machines were Type 1and 2 induction generators with no reactive capabilty
    Type 3 machines consist of a Doubly Fed Induction Generator (DFIG)
    Type 4 machines employ a full bridge converter design coupled to either an induction or synchronous machine
Other technologies such as solar and energy storage will have their own unique characteristics
The imposition of a “one size fits all” approach to reactive power capability requirements will result in economic inefficiency and create barriers to entry for the adoption of new technologies
The current ERCOT Protocol on reactive power capability requirements is obsolete
Notes: <number>
<footer>
<header>
<date/time>

## Slide 3: Ancillary Services Section 6.5.7 needs to be revised
Protocol 6.5.7.1 (2) states that...
  “Generation Resources required to provide VSS....shall have and maintain a URL which has an over-excited (lagging) power factor capabilty of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capabilty of ninety five hundredths (0.95) or less, both determined at the generating unit’s maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TDSP.”
Does “shall have and maintain” mean going forward in time or does it mean over the output range of the unit?
PRR830, if adopted, would require a wind generator interconnected after February 17, 2004 to maintain a URL over the output range of the unit.
Not only is the current ERCOT Protocol obsolete...it’s also ambiguous
Notes: <number>
<footer>
<header>
<date/time>

## Slide 4
Wind turbine generator technology continues to evolve
Type 4 machines – reactive capability comparable to synchronous generators (typical of Siemens 2.3 MW machines and comparable to conventional synchronous units)
MVar
Lagging
Leading
MW
MVar
Lagging
Leading
MW
+.95pf
-.95pf
MVar
Lagging
Leading
MW
Type 1 and 2 induction generators – no inherent reactive production capability
Type 3 doubly fed induction generators - +/- 0.95 pf (typical of GE 1.5 MW machines)
Notes: <number>
<footer>
<header>
<date/time>

## Slide 5
It carves out a separate section for the reactive power requirements of Wind Generating Resources and requires a +/- 0.95 power factor range as the minimum requirement
It provides for the imposition of additional reactive requirements consistent with PRR830 where it can be demonstrated through a system impact study that such capability is required to ensure safety and reliability
PRR835 avoids requiring generators already interconnected to make costly investment in additional reactive capability where it is not justified
PRR 835 exceeds FERC Order 661-A requirements
PRR835 does several things...
Notes: <number>
<footer>
<header>
<date/time>

## Slide 6
Comparision of PRR835 to PRR830 and FERC Order 661-A
FERC Order 661-A
  Adopts +/- 0.95PF range as the maximum requirement
  Requires wind plants to maintain the required power factor range only if the Transmission Provider shows, through the System Impact Study, that such capability is required of the plant to ensure safety and reliability
PRR830
  Adopts the URL measured at +/-0.95 PF and maximum net MW output
  Requires URL over the full operating range of the plant
PRR835
  Adopts +/-0.95PF as the minimum reactive capability
  May require URL over the full operating range of the plant only if the Transmission Provider demonstrates it is needed to ensure safety and reliability through a System Impact Study
MVar
Lagging
Leading
MW
+.95pf
-.95pf
URL
URL
Minimum
MVar
Lagging
Leading
MW
+.95pf
-.95pf
Maximum
MVar
Lagging
Leading
+.95pf
-.95pf
URL
URL
MW
Maximum
Minimum
Notes: <number>
<footer>
<header>
<date/time>

## Slide 7: Transmission Line Example
MVar
Lagging
Leading
MW
+.95pf
-.95pf
URL
URL
Minimum
Transmission Owner must provide shunt reactors to offset line charging when wind is calm and generator is not generating
PRR830 would have the Generator install an additional shunt reactor to meet its URL requirement for leading reactive capability over its range of output
Inherent Generator reactive capability
PRR830 will result in redundant and excessive reactive capability where it is not needed
Equivalent Transmission Line Representation
POI
1
2
3
PRR830 will result in the wasteful installation of redundant reactive resources.
Notes: <number>
<footer>
<header>
<date/time>

## Slide 8: Transmission Line Example
PRR835 ensures system safety and reliability without mandating investment in reactive capability for providing VSS where it is not needed
Generator shunt reactor (or capacitor) would not be required to meet its URL requirement for leading (or lagging) reactive capability over its range of output unless shown to be required by the System Impact Study
Notes: <number>
<footer>
<header>
<date/time>

## Slide 9: Study Assumptions
Reference case from ERCOT
  2010/2011 Winter off-Peak (09/17/2009 update)
  39,569 MW total generation; 3,719 MW wind generation (9.4%)
Wind farms represented per ERCOT’s modeling
  Reactive power capability expressed by Qmin and Qmax as given in the reference case (rectangular reactive power capability)
  Wind farms represented by equivalent (aggregated) models
Sensitivity cases
  Different reactive power capability (triangular capability)
  Different levels of wind generation
NextEra has engaged the services of Siemens-PTI to assess the current need for additional reactive resources in Western ERCOT
Scenarios based on ERCOT case, from no wind to high wind penetration. Limited reactive power capability in the wind farms (conservative).
Notes: <number>
<footer>
<header>
<date/time>

## Slide 10: Sensitivity Scenarios
No-Wind scenarios
  Constant load (conventional generation increased by 3,719 MW)
  Constant conventional generation (system load scaled down by 3,719 MW)
Increased wind generation scenarios
  Scenario 3 (5,849 MW of wind generation, 14.7% of total)
    Maximum wind generation in the Gulf Coast and Horse Hollow gen-tie
    West Texas wind generation increased by 1,040 MW
  Scenario 4 (6,369 MW of wind generation, 16% of total)
    Scenario 3 with an additional 520 MW of wind in West Texas
  Scenario 5 (same as scenario 4 but with additional wind in west Texas dispatched against local generation)
Wind Farm Generation Re-Dispatch was performed to model the following sensitivity scenarios
Notes: <number>
<footer>
<header>
<date/time>

## Slide 11: Results
AC contingency analysis
  ERCOT contingency file (9,000+ cat. B and cat. C contingencies)
Few post-contingency voltage violations
  Generally unrelated to the wind generation dispatch
  Also unrelated to reactive power capability at the wind farms
Thermal violations
  Existing system configuration → restrictions to dispatch of West Texas wind generation
  Significant overloads already identified before reaching full power output of wind generation in West Texas
Preliminary results indicate that voltage violations are not the issue for the current Western ERCOT system
Thermal overloads are the limiting factors. No condition has been identified that shows the need for additional reactive power capability from wind farms
Notes: <number>
<footer>
<header>
<date/time>

## Slide 12
Current ERCOT System
  West Zone load – approximately 4,000 MW
  West Zone Generation – approximately 8,000 MW
ERCOT System post CREZ
  West Zone load – approximate 4,400 MW
  West Zone Generation – 18,000 MW
WGR lagging reactive capability will need to increase with MW output to compensate for transmission line reactive losses.
WGR leading reactive capability will have little value since shunt reactors will be required to offset transmission line charging anyway when the wind is calm.
Generator reactive capability requirements are driven by system topology and the imbalance between generation and load in Western ERCOT. This trend will become further exaggerated with CREZ implementation
CREZ doesn’t make things worse but amplifies the consequences of adopting PRR830!
Notes: <number>
<footer>
<header>
<date/time>

## Slide 13
Sets minimum requirement of +/-0.95 Power Factor at the Point of Interconnection
May require additional reactive requirements when supported by a System Impact Study
Addresses the “Cone” versus “Rectangle” debate
Wind generator reactive requirements and VSS are distinguished from non-wind generators
Requires wind generators to provide real-time reactive capability through SCADA
Does not unnecessarily limit aggregation of wind turbine generators based on size and type as does PRR830
Grandfathers WGRs interconnected after May 17, 2005 and before the adoption of PRR835 in meeting the +/- 0.95 PF requirement
Highlights of PRR835
What differentiates PRR835 from PRR830 is that it provides superior economies while ensuring system safety and reliability where justified and needed!
Notes: <number>
<footer>
<header>
<date/time>