## Slide 1: PDCWG Report to ROS
October 15, 2009
Sydney Niemeyer (vice-chair)

## Slide 2: PDCWG Meeting October 14, 2009
Review August and September 2009 Frequency Events and evaluate Resource and QSE performance during these events.
Review Interconnection Primary Frequency Response average performance and Interconnection minimum frequency response.
Develop OGR to address new definitions of Primary Frequency Response and Governor.

## Slide 3
CPS1 = 141.80

## Slide 8
ERCOT CPS1 Score
CPS1 12 Month Rolling Average = 139.99

## Slide 9
*ERCOT as a single control area is exempt from CPS2. These scores are For Information Only
90.66

## Slide 19: Generation Resources Governor Settings
Generation Resources with governors presently set with an intentional deadband less than +/-0.017 Hz.
  11,107 MW Total Capacity Identified by PDCWG members.
    1690 MW Lignite
    4139 MW Coal
    3120 MW Combustion Turbine Combined Cycle
    1519 MW Combustion Turbine Simple Cycle
    399 MW Steam Turbine – natural gas fired
    240 MW Hydro
  Some PDCWG members are still gathering data.