ERCOT Operations Report

September 2009 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 9/5/2009 14:38 | 59.89400101 | 6 | Unit trip with 385 MW |
| 9/13/2009 12:20 | 60.10100174 | 4 | Generation Schedules changed after offset was entered. |
| 9/16/2009 20:12 | 59.87099838 | 10 | Unit trip with 635 MW |
| 9/25/2009 11:18 | 59.84000015 | 40 | Unit trip with 530 MW |
| 9/26/2009 18:43 | 59.84799957 | 8 | Unit trip with 565 MW |
| 9/29/2009 0:38 | 59.88999939 | 6 | East DC Tie trip, loss of 480 MW net import into ERCOT. |
| 9/30/2009 14:35 | 59.88800049 | 112 | Unit trip with 580 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 9/2 06:38:00 | 9/2 06:46:00 | 0:08:00 | 354.00 | Offset calculation error |
| 9/3 18:02:32 | 9/3 18:32:56 | 0:30:24 | 332.64 | Unit trip |
| 9/5 14:38:43 | 9/5 15:04:14 | 0:25:31 | 401.28 |  |
| 9/14 15:00:21 | 9/14 15:16:09 | 0:15:48 | 332.64 | Unit trip |
| 9/14 15:50:26 | 9/14 16:02:10 | 0:11:44 | 332.64 | Out of up regulation |
| 9/14 20:08:34 | 9/14 20:22:18 | 0:13:44 | 332.64 | Out of up regulation |
| 9/16 13:03:35 | 9/16 13:20:56 | 0:17:21 | 353.77 | SCE change -920 MW in 9m. Out of up regulation at 13:00 |
| 9/16 20:12:46 | 9/16 20:27:12 | 0:14:26 | 586.08 |  |
| 9/21 11:04:49 | 9/21 11:20:15 | 0:15:26 | 348.49 | Out of up regulation |
| 9/21 22:26:53 | 9/21 22:40:45 | 0:13:52 | 327.36 | Unit trip |
| 9/25 11:18:09 | 9/25 11:44:01 | 0:25:52 | 686.41 |  |
| 9/26 18:43:09 | 9/26 19:02:21 | 0:19:12 | 644.17 |  |
| 9/27 09:06:07 | 9/27 09:30:09 | 0:24:02 | 337.94 | Out of up regulation |
| 9/28 06:46:01 | 9/28 06:58:09 | 0:12:08 | 327.36 | Unit trip |
| 9/28 11:06:13 | 9/28 11:24:25 | 0:18:12 | 343.21 | Out of up regulation |
| 9/29 00:38:16 | 9/29 00:57:57 | 0:19:41 | 422.41 |  |
| 9/30 14:35:33 | 9/30 14:59:43 | 0:24:10 | 723.37 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| Western | 0 | 7 | 28 | 35 | 4 | 39 |
| DFW | 3 | 4 | 25 | 29 | 0 | 32 |
| North | 0 | 12 | 18 | 30 | 0 | 30 |
| Austin | 1 | 0 | 26 | 26 | 0 | 27 |
| Houston | 0 | 3 | 7 | 10 | 0 | 10 |
| San Antonio | 0 | 1 | 3 | 4 | 0 | 4 |
| Laredo | 0 | 2 | 0 | 2 | 0 | 2 |
| Northeast | 0 | 0 | 2 | 2 | 0 | 2 |
| E RIO | 0 | 1 | 0 | 1 | 0 | 1 |
| South | 0 | 1 | 0 | 1 | 0 | 1 |
| Bryan Area | 0 | 0 | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 | 0 | 0 |
| Total | 4 | 31 | 109 | 140 | 4 | 148 |

| Historical Totals | Sep-09 | Sep-08 | Aug-09 |
| --- | --- | --- | --- |
| Austin | 1 | 9 | 14 |
| Bryan Area | 0 | 0 | 0 |
| Corpus | 0 | 8 | 0 |
| DFW | 7 | 21 | 40 |
| E RIO | 1 | 2 | 7 |
| Houston | 3 | 14 | 9 |
| Laredo | 2 | 8 | 0 |
| North | 12 | 26 | 42 |
| Northeast | 0 | 0 | 0 |
| San Antonio | 1 | 0 | 5 |
| South | 1 | 1 | 0 |
| W RIO | 0 | 0 | 0 |
| Western | 11 | 2 | 19 |
| Total | 39 | 91 | 136 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Dilley Switch - San Miguel Switch 138KV | Pearsall Switch - Derby Sub 69KV | 19 |
| Austrop - Daffin & Decker 138KV | Austrop - Decker 138KV | 9 |
| Oak Creek - Ballinger 138KV | Miles - Rowena 69KV | 8 |
| Garfield - Onion Creek - Hicross AEN 138KV | Lytton Springs 345/138KV Autotransformer #2 | 4 |
| Temple Pecan Creek - Tradinghouse SES & Temple Switch - Lake Creek SES 345KV | San Angelo Power Station - Shrew Tap | 4 |
| Moss - Holt 138KV | Odessa North 138/69KV Auto | 3 |
| Oak Creek - Ballinger 138KV | Abilene South - Ballinger 69KV | 3 |
| Comanche Peak 1 and 2 345kV | Lake Whitney - Whitney TU 138KV | 2 |
| DuPont Switch - Whitepoint 138KV | DuPont Switch Ingleside - Whitepoint 138KV | 2 |
| Marion - Zorn - Clear Springs 345KV | Schertz - Parkway 138KV | 2 |
| Tradinghouse SES - Venus Switch 345KV | Rogers Hill TU - Elm Mott 138KV | 2 |
| Tradinghouse SES - Venus Switch 345KV | Bosque Switch - Rogers Hill 138KV | 2 |
| Base Case Overload | Ena Snyder - MEC Plainview TAP 69KV | 2 |
| Falfurrias - Crestonio 138KV | Freer - San Diego 69KV | 2 |
| Garfield - Onion - Hicross 138KV | Lytton Springs - Pilot Knob 138KV | 2 |
| Graham SES - Long Creek Switching Station 345KV | San Angelo Power Station - Shrew Tap 138KV | 2 |
| Morgan Creek SES - Quail Switch and Longshore Switching Station 345KV | Midland East - Stanton East 138KV | 2 |
| North Denton 138/69KV autotransformer #1 | North Denton 138/69KV autotransformer #2 | 2 |
| San Angelo Red Creek - Comanche 345KV | San Angelo Concho - Veribest 69KV | 2 |
| Tradinghouse SES - Venus 345KV | Lake Whitney - Whitney TNP 69KV | 2 |
| Trinidad - Stryker Creek and Mount Enterprise 345KV | Stryker Creek - Stryker Cherokee POI 138KV | 2 |
| Trinidad - Stryker Creek and Mount Enterprise 345KV | Lufkin Switch - Lufkin Chipper Mill 138KV | 2 |
| Victoria - Victoria DuPont Switch 138KV | Formosa - Lolita 138KV | 2 |
| Waxahachie - Ennis West 138KV | Trumbull Auto Transformer 1 138/69KV | 2 |
| Ballinger - San Angelo Red Creek 138KV | Sonora - Friend Ranch 138KV | 1 |
| Elm Creek - STP 345KV | Lockhart 138/69KV Auto | 1 |
| Miller - Weatherford West 138KV | Bunker 138/69KV transformer | 1 |
| Odessa EHV - Morgan Creek & Odessa EHV - Quail Switch 345KV | Big Spring - Big Spring West | 1 |
| Tradinghouse SES - Venus Switch 345KV | Lake Whitney - Whitney TU 138KV | 1 |
| West Levee Switch 345/138KV T1 | Industrial - Compton Street 138KV | 1 |
| Austrop - Sandow & Sandow auto transformer #2 | Austrop - Sandow 345KV | 1 |
| Austrop - Daffin and Decker 138KV | Pilot - Lytton 138KV | 1 |
| Lobo - Laredo VFT North 138KV | Wormser Road - Santo Nino 138KV | 1 |
| Lobo - Laredo VFT North 138KV | North Laredo - Wormser Road 138KV | 1 |
| Roanoke Switch - West Denton and Lewisville Switch 345KV | West Denton - Teasley 138KV | 1 |
| Abilene South - Eskota Switch 138KV | Trent - Scott REA Tap 69KV | 1 |
| Abilene South - Eskota Switch138KV | Merkel - Trent 69KV | 1 |
| Ballinger - San Angelo Red Creek 138KV | Sonora - Friend Ranch 138KV | 1 |
| Big Brown SES - Jewett 345KV | Big Brown SES - Jewett 345KV | 1 |
| Comanche Peak - Decordova & Wolf Hollow - Rock Creek 345KV | Comanche Peak - Johnson Switch 345KV | 1 |
| Comanche Peak 1 and 2 345KV | Sandow - Temple Switch 345KV | 1 |
| Elm Mott - Whitney TU 138KV | Bosque Switch - Lake Whitney 138KV | 1 |
| Everman Switch - Sherry Switch 345KV | Everman Switch - Oak Hill 2 Tap 138KV | 1 |
| Hillje - Homan 345KV | Columbus - Stafford Hill 69KV | 1 |
| Ingleside DuPont Switch - Whitepoint 138KV | Rincon - Whitepoint 138KV | 1 |
| Marion - Zorn - Clear 345KV | Seguin - Seguin West 138KV | 1 |
| Morgan Creek SES - Quail Switch & Morgan Creek SES - Longshore Switching Station 345KV | Stanton Switch - Big Spring West 138KV | 1 |
| North Denton Auto #1 | North Denton Auto #2 | 1 |
| Sandow Switch - Temple Switch 345KV | Hearne AT1 transformer 138/69KV | 1 |
| Skyline - Marion and Skyline - Elm Creek 345KV | Schertz - Parkway LCRA 138KV | 1 |
| South Lane City - Lane City 138KV | West Colombia - Pledger 138KV | 1 |
| South Texas Nuclear Project - Hillje & Whitepoint 345KV | Blessing - Lolita 138KV | 1 |
| STP - Blessing 345KV | Columbus - Stafford Hill 69KV | 1 |
| STP - Elm Creek 345KV | Blessing - Lolita 138KV | 1 |
| STP - Elm Creek 345KV | Turner - Goforth 138KV | 1 |
| STP - Elm Creek 345KV | Blessing - Palacios 69KV | 1 |
| Turner - Goforth 138KV | Turnersville - Buda | 1 |
| Twin Butte - San Angelo Red Creek 345KV | Twin Butte 345/138KV autotransformer | 1 |
| Watermill - Tricorner and Trinidad 345KV | Seagoville - Kleberg Tap 138KV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North – Houston | 8 |
| West – North | 5 |
| North – South | 2 |
| South – North | 1 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 09/03/2009 | Transmission and Security Desk V4 Rev 6 | 440 |
| 09/03/2009 | Shift Supervisor Desk V4 Rev 6 | 439 |
| 09/01/2009 | Desktop Reference Guide V1 Rev1 | 438 |
| 09/01/2009 | Shift Supervisor Desk V4 Rev 5 | 437 |
| 09/01/2009 | Frequency Control Desk V4 Rev 5 | 436 |
| 09/01/2009 | Day-Ahead Desk V4 Rev 5 | 435 |
| 09/01/2009 | Transmission and Security Desk V4 Rev 5 | 434 |

## Blackout/Load Shed Incidences

None

EEA

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

None

## ERCOT peak (Unofficial)

09/03 	   17:00 55,210 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2006 | 2007 | 2008 | 2009 |
| January | 4.79 | 4.55 | 3.30 | 4.11 |
| February | 4.81 | 3.75 | 3.59 | 3.49 |
| March | 4.95 | 2.70 | 3.29 | 3.24 |
| April | 5.59 | 3.00 | 2.45 | 2.66 |
| May | 3.59 | 3.22 | 3.01 | 2.90 |
| June | 2.65 | 4.46 | 2.81 | 2.89 |
| July | 2.62 | 4.29 | 2.55 | 2.83 |
| August | 2.09 | 3.11 | 3.66 | 3.07 |
| September | 4.03 | 3.78 | 4.99 | 3.68 |
| October | 3.63 | 3.08 | 2.79 | NA |
| November | 3.28 | 2.95 | 2.60 | NA |
| December | 3.44 | 3.74 | 4.54 | NA |
| Annual Average | 3.79 | 3.55 | 3.29 | 3.20 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 9/2/09 | 4:00 | 15:00 | ERCOT issued a Watch for a projected reserve capacity shortage for HE16, HE17 and HE18. |
| 9/2/09 | 10:30 | 15:00 | ERCOT issued a Watch for a projected reserve capacity shortage for HE16, 17 and 18. |
| 9/2/09 | 16:30 | 20:35 | Advisory issued for ARRS below 3000 MW. |
| 9/3/09 | 3:00 | 14:45 | ERCOT issued an OCN for a projected reserve capacity shortage for HE16, HE17 and HE18. |
| 9/5/09 | 13:28 | 14:40 | Advisory issued for ARRS below 3000 MW. |
| 9/5/09 | 14:40 | 18:00 | Watch issued for ARRS below 2500 MW. |
| 9/6/09 | 9:11 | 11:10 | OCN issued for potential Capacity shortage for HE 16, 17 and 18. |
| 9/6/09 | 11:10 | 17:15 | Watch issued for projected Capacity shortage for HE 16, 17 and 18. |
| 9/7/09 | 13:38 | 16:08 | Advisory issued for ARRS below 3000 MW. |
| 9/7/09 | 16:08 | 21:15 | Watch issued for ARRS below 2500 MW. |
| 9/10/09 | 10:13 | 11:25 | Advisory issued for ARRS below 3000 MW. |
| 9/15/09 | 3:00 | 15:15 | OCN issued for projected reserve capacity shortage for HE 1700. |
| 9/15/09 | 20:05 | 21:00 | Advisory issued for ARRS below 3000 MW. |
| 9/18/09 | 16:45 | 18:15 | Advisory issued for ARRS below 3000 MW. |
| 9/19/09 | 13:15 | 18:30 | Advisory issued for ARRS below 3000 MW. |
| 9/20/09 | 13:23 | 18:00 | Advisory issued for ARRS below 3000 MW. |
| 9/21/09 | 3:25 | 18:15 | OCN issued for a projected reserve capacity shortage for HE 13:00 - 21:00. |
| 9/21/09 | 9:50 | 18:15 | Advisory issued for ARRS below 3000 MW. |
| 9/30/09 | 14:47 | 18:30 | Advisory issued for ARRS below 3000 MW. |

Transmission Watch

None

Emergency Notice

09/01  13:30	Market Emergency Notice issued due to the procurement of the Ancillary Service Market for 9/2/09 did not meet the time requirement.

Texas RE Event Analysis

09/01  13:30	Market Emergency Notice issued due to the procurement of the Ancillary Service Market for 9/2/09 did not meet the time requirement.

09/14   14:38   Simultaneous loss of units, auto transformer and two 138 kV lines

Others

09/05  23:30	ERCOT held IE 00:15 Real-time Balancing deployments and resumed with IE       00:30.

09/28  23:00	ERCOT held IE 23:00 Real-time Balancing deployments and resumed with IE 23:30 due to incorrect offset calculation.