## test results
CRE test for: |  | 6410 MILES - 6411 ROWE2A | [5 empty] | FAIL
Line Rating: |  | 30
Direction |  | West | → | North |  | W-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 6410 MILES - 6411 ROWE2A
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | -0.00015276
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.00041109
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.0048761
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.00033402
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 6410 MILES - 6411 ROWE2A
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | -0.00012938
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.00041448
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.0052562
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.00033263
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 6410 MILES - 6411 ROWE2A
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.00026172
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | -0.005409
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.00017986
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.0056673
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -7.707e-05
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.0052087
PTDF tests
West | → | North | 0.81273 | 0.031872 | -0.031872 | -0.015519 | -0.81273 | 0.0050055 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.0050055 | 0.00026172
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.020068
[6 empty] | Concentration |  | 4.0093 | FAIL
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.0061321
[6 empty] | Concentration |  | 1.2251 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 2.6261
| Percent of line rating => | [6 empty] | 8.754% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 162.3688
[7 empty] | B1(N-S) | -0.082622 | -0.040127 | 0.042495 | -0.082622
[7 empty] | B2 (N-W) | 0.063482 | -0.81477 | -0.87825 | 0.063482
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.048179 | -0.018975 | 0.029204 | -0.048179
[7 empty] | B4 (S-W) | 0.14443 | -0.77577 | -0.92019 | 0.14443
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.032538 | 0.020024 | -0.012514 | 0.032538
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.052795 | 0.79294 | 0.84573 | -0.052795
[7 empty] | test | 0 | 0.81273 | 0.81273 | 0
[7 empty] | B1 | -10.17%
Deployment Error Percent | [6 empty] | B2 | 7.811%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -5.928%
[7 empty] | B4 | 17.77%
[7 empty] | B5 | 4.004%
[7 empty] | B6 | -6.496%
[7 empty] | Max Abs Error | 17.77% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | W-N
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L:6410 MILES - 6411 ROWE2A C:OAK Creek - Ballinger [6335 - 6340] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L:6410 MILES - 6411 ROWE2A C:OAK Creek - Ballinger [6335 - 6340]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.000522 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | -0.13311
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.000522 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | -0.077778
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.000605 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.009075
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | -0.000605 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | -0.009075
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | -0.000522 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | -0.079866
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.000613 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | -0.09195
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | -0.000613 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | -0.04904
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.000964 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | -0.070372
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.000964 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | -0.11472
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.000964 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | -0.19762
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.000964 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | -0.098328
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | -0.000964 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | -0.092544
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 6.5e-05 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.00078
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 6.5e-05 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.00078
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.000432 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | -0.072576
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | -0.000432 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | -0.03888
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.006588
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | -0.006588
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | -0.013908
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | -0.019008
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -0.009702
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | -0.009702
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.000113 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 0.012712
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | -7.5e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | -0.003
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | -0.005609
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | -0.007526
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | -0.010366
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | -7.1e-05 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | -0.005396
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 9.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 0.00546
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 9.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 0.005733
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | -0.00148
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | -0.00185
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | -0.003034
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | -0.000285 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | -0.13195
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 0.39376
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 0.38779
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.39972
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.39972
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 0.39972
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005966 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 0.68012
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.005966 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 3.0725
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 0.32023
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.33479
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 0.33479
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.32508
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 0.32508
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 0.31538
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 0.34587
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 0.36267
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 0.34785
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 0.71625
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 1.0505
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.004771 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 0.47233
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.004771 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 0.29103
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.004797 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 0.67638
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 0.11928
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.21803
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 0.21803
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.004797 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 0.57564
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.010243 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 0.26427
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.006489 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 0.65214
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.006888 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 0.82656
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.005827 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 0.33797
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.00569 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 1.2188
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.002105 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 0.31575
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.019939 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.1316
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.019939 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 0.68391
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.002105 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 0.2126
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.006847 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 0.82164
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.001315 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 0.48129
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.00059 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 0.14278
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.002648 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 1.0592
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.002647 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 0.62469
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.002328 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 0.38412
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 0.1324
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 0.13045
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 0.15706
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.02134
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.02134
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 0.02134
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.018139
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 6e-06 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 0.00072
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | -0.00281 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | -0.1686
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | -0.00405
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | -0.0042984
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | -0.0047736
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | -0.00848
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.008268
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | -0.010388
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | -0.008268
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | -0.008321
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | -0.010494
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -4.3e-05 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | -0.00731
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | -4.3e-05 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | -0.02236
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -5e-05 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | -0.0185
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | -0.032364
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | -0.033582
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | -0.046864
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 4.9e-05 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 0.005488
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 4.9e-05 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 0.0049
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 4.9e-05 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 0.018522
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | -0.075403
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | -0.071135
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | -0.094523
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | -0.000259 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | -0.19943
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | -0.04011
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.039537
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | -0.039537
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | -0.038964
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.000382 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | -0.44197
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | -0.000382 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | -0.44236
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | -0.045248
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | -0.045652
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.000166 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | -0.035922
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | -0.000166 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | -0.035873
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | -0.042824
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | -0.042622
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -8.3e-05 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | -0.032785
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | -8.4e-05 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | -0.03654
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | -8.3e-05 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | -0.036105
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | -2e-05 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | -0.00276
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.000112 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | -0.013216
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.000112 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | -0.01288
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | -0.000112 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | -0.062272
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -9e-05 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | -0.03492
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | -9e-05 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | -0.04635
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | -0.10676
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | -0.10812
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | -0.10608
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.000149 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | -0.027118
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | -0.000149 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | -0.072116
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | -0.000193 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | -0.043232
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | -0.000148 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | -0.0074
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | -0.000147 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | -0.006174
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.000207 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | -0.12731
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | -0.000207 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | -0.12151
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.000409 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | -0.21963
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | -0.000409 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | -0.32188
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.000439 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | -0.032925
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | -0.000439 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | -0.097458
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.000521 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -0.29645
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000353 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -0.073777
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000353 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -0.076248
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.000349 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -0.14204
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.016238
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -0.016591
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.016238
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -0.016238
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.000358 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -0.15179
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.000358 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -0.15215
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00033 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -0.01914
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00033 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -0.02937
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.01452
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -0.01452
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -0.01419
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -0.01485
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.000354 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -0.14585
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.000354 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -0.1416
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.000371 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -0.20257
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.000371 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -0.27825
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -0.022509
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -0.035055
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -0.055719
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.057815
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -0.06341
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -0.057815
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.000321 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -0.007062
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.000321 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.003531
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.000321 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.003531
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -0.015789
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -0.012346
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -0.015226
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -0.015888
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.002508
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.002299
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 7.8e-05 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.001872
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 7.8e-05 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | 0.001872
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | 7.8e-05 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | 0.001794
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.000308 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -0.12197
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000356 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -0.47455
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.000356 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -0.47277
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -0.011438
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -0.0058093
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.004515
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.000301 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -0.014147
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 0.60525
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.003517 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 0.52755
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.004087 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 0.69275
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.006398 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 0.9597
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.004901 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 0.30876
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.001905 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 1.2377
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -3.7e-05 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.00148
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | -3.7e-05 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | -0.00148
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.001256 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -0.53003
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -0.07128
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -0.07236
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -0.17442
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -0.078526
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -0.07952
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -0.086975
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -0.27857
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -0.28381
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -0.20654
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -0.098068
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -0.09855
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -0.098375
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -0.099295
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.000615 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.00492
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.000615 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.00492
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.034614
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.034614
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.028845
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.001507 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.020646
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.001117 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.020106
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.001117 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -0.020106
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.02807
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.027268
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.02807
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.001297 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -0.036316
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.001297 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -0.037613
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.005968 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 0.20888
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.005968 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 0.17904
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.0249
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.0249
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.0249
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -0.0249
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.000493 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.002958
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.0010344
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.0010344
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.0012068
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.000414 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.001656
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.00043 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.001032
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.00043 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.001032
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.058653
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -0.055062
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -0.05586
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -0.058653
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -0.072618
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -0.079002
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -0.077317
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -0.075797
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -0.11793
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -0.059356
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -0.06061
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -0.063118
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -0.12122
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.002788 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.092004
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.002788 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.0697
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.002508
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.000339 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -0.024747
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.02686
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -0.02754
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -0.009408
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.002352
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -0.02686
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -0.0272
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -0.026656
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -0.0085
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -0.01564
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.000328 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -0.20631
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.000339 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -0.048816
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.000339 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -0.063732
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.000399 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.004788
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | 0.001928 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | 0.011568
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -0.1045
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00031 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -0.10354
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00031 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -0.1054
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -0.011742
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.007725
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -0.007725
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.00031 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -0.01178
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.000307 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -0.008903
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -0.046121
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -0.046215
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -0.047583
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -0.049612
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -0.048042
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -0.0314
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -0.04553
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -0.046158
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -0.039878
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -0.041313
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -0.041708
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -0.048786
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -0.060858
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -0.06371
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -0.071148
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.042336
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -0.042336
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -0.050274
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.000601 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -0.18631
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.000601 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -0.24821
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.025116
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.026312
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.026312
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.028106
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.029008
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.027232
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.027232
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.027824
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.091168
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.087616
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.028416
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.028416
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.3794
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 0.3794
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 0.50298
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.4336
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 0.4336
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 0.6233
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 1.1299
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 0.77118
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 0.71853
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 0.73807
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 0.79777
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 1.1397
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 0.87237
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 0.52801
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 1.0393
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 0.82228
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 0.955
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 0.58207
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 0.88595
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.00532 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 0.9576
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.00532 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 0.9576
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.005383 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 1.2112
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.004373 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.54663
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.004373 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 0.54663
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | -0.007
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | -0.00705
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | -0.01545
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | -0.00715
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | -0.0072
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | -0.0155
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.000193 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | -0.037828
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | -0.000193 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | -0.021423
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | -4.1e-05 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.014812
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.015088
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | -0.015088
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | -0.038088
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | -0.014904
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | -0.014812
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | -0.014996
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | -0.037628
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -9.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | -9.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | -0.021016
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | -0.01846
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | -0.02059
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | -0.056658
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | -0.029688
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | -0.029747
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | -0.034948
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | -0.029694
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | -0.029851
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | -0.03479
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.000521 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -0.3027
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -0.22145
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | -0.22145
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | -0.000295 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | -0.00944
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.000299 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | -0.014352
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.000299 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | -0.013754
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | -0.00354
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | -0.015045
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.000295 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | -0.005015
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | -0.00649
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | -0.007375
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | -0.000299 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | -0.031395
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.004538 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 0.38119
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 0.6456
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.008089 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 1.2133
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.008089 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 1.2133
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -0.023718
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -0.022344
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -0.017755
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -0.051322
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -0.051423
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -0.051021
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -0.03216
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -0.08174
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -0.0134
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -0.0336
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -0.031121
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -0.034404
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -0.03417
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.01072
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.01005
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.038184
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -0.038184
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -0.040936
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -0.037668
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | -0.039446
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | -0.039627
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.000329 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -0.044744
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.000338 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -0.011154
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.013818
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.013818
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.012502
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.012502
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.000345 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -0.024495
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.000345 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.00345
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.055257
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -0.055257
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -0.083055
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.021515
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -0.01986
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.021515
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -0.021515
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -0.04917
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -0.021483
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -0.030212
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -0.029083
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -0.028884
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -0.018094
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.0040504
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.000327 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -0.24296
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.000328 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -0.24108
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.056244
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.056244
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -0.056244
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -0.055879
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.000329 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -0.056917
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.000329 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -0.044415
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -0.053073
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -0.052616
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -0.051801
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -0.087759
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -0.02112
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -0.020856
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -0.027258
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -0.024288
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -0.053856
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -0.051843
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -0.051975
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -0.05181
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -0.08877
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.001635
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.006867
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -0.045026
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.045552
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -0.045552
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -0.11096
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.000326 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -0.12975
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.015226
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.015226
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -0.015226
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.018205
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -0.018205
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -0.017874
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.000249 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | -0.20592
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | -0.000249 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | -0.20393
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.000339 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -0.015628
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.027132
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -0.027132
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -0.037485
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.026418
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -0.026418
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -0.036414
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -0.0594
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -0.052338
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -0.05181
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.01155
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.000333 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -0.15285
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -0.021255
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -0.021582
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -0.02289
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -0.020601
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -0.020274
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -0.034008
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -0.019293
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -0.050388
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.049742
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -0.049742
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.000323 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -0.052326
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -0.051339
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -0.02343
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -0.02376
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.01287
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.0099
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -0.025818
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -0.02648
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.005346
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -0.05445
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -0.05577
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -0.07029
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -0.07524
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00033 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.00396
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.00033 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.00594
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.000334 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -0.0167
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.034216
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -0.034216
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.017766
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -0.017437
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.017766
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -0.018753
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.017766
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -0.017766
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.019082
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -0.019082
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.000328 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.003936
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.018256
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.019234
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.018256
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.018256
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -0.019234
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -0.018256
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.000352 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -0.023232
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -0.054579
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -0.056274
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -0.084072
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000339 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -0.18509
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000339 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -0.21798
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -0.22069
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -0.1912
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -0.2034
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.000339 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.004407
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.000327 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.003924
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.011152
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.011382
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.010726
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.015055
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.0058056
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.0066912
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.0065272
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.01148
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.005904
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -0.028011
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -0.048544
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -0.021514
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -0.024776
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -0.015615
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.035047
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -0.029842
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -0.030536
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -0.01735
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.006246
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -0.032618
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -0.02429
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -0.021861
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -0.024984
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -0.022486
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -0.035047
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -0.033659
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -0.035741
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -0.026372
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.02776
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -0.02776
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -0.059337
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | 0.0013356
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.008929 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 0.68307
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 0.6456
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 0.3228
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.008018 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.64144
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.008066 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 0.64528
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.00851 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 0.6808
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.008653 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 0.72685
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.008018 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 0.64144
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -0.04731
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 0.40248
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 0.78148
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 0.57085
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -0.09213
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -0.07636
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -0.09296
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -0.047725
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -0.0415
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.002654 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 0.15924
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.001573 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.011106 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.007321 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.035141
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 0.14588
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 0.41818
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 0.52515
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 0.46291
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 0.40845
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 0.31315
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.005377 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 0.80655
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 0.6219
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 0.82644
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 1.0282
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 1.1858
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.000301 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | 0.001728 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -0.00952
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -0.014824
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -0.02516
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.028576
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -0.012464
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -0.011552
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -0.005776
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -0.028576
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -0.010944
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -0.013072
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -0.006688
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.013104
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.00504
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.002352
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.00504
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.013104
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -0.013104
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -0.044992
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.0152
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -0.01672
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -0.0152
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.000314 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.003768
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.000337 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.005055
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.000337 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -0.007751
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -0.01632
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.000335 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.00268
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -0.05598
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -0.05598
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00031 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.0558
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.00031 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -0.0558
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -6.4e-05 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0064
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -6.4e-05 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -0.0064
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.007825
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.007825
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.007825
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.005008
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.007825
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.007825
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -0.007825
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.004695
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -6.4e-05 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -6.4e-05 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.032
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -6.4e-05 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -0.032
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -6.4e-05 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.000289 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.002788 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.000139 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.00027 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L:6410 MILES - 6411 ROWE2A C:OAK Creek - Ballinger [6335 - 6340] | [7 empty] | 2.6261
Number of Bus | Name of Bus | ID | Max MW | L:6410 MILES - 6411 ROWE2A C:OAK Creek - Ballinger [6335 - 6340] | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | -0.000522 | north | Y | -0.00036924 | -0.00011091 | -0.0053981 | -0.00018798 | 0.00011091 | south | Y | 0.00036924 | 0.065875
239 | BOSQUESW | 1 | 149 | -0.000522 | north | Y | -0.00036924 | -0.00011091 | -0.0053981 | -0.00018798 | 0.00011091 | south | Y | 0.00036924 | 0.038492
244 | WHITNYDM | 1 | 15 | -0.000605 | north | N | -0.00045224 | -0.00019391 | -0.0054811 | -0.00027098 | 0.00019391 | south | Y | 0.00045224 | 0
245 | WHITNYDM | 2 | 15 | -0.000605 | north | N | -0.00045224 | -0.00019391 | -0.0054811 | -0.00027098 | 0.00019391 | south | Y | 0.00045224 | 0
247 | BOSQUESW | 2 | 153 | -0.000522 | north | Y | -0.00036924 | -0.00011091 | -0.0053981 | -0.00018798 | 0.00011091 | south | Y | 0.00036924 | 0.039525
251 | BOSQUESW | 2 | 150 | -0.000613 | north | Y | -0.00046024 | -0.00020191 | -0.0054891 | -0.00027898 | 0.00020191 | south | Y | 0.00046024 | 0.03875
253 | BOSQUESW | 2 | 80 | -0.000613 | north | Y | -0.00046024 | -0.00020191 | -0.0054891 | -0.00027898 | 0.00020191 | south | Y | 0.00046024 | 0.020667
332 | RWMILLER | 1 | 73 | -0.000964 | north | Y | -0.00081124 | -0.00055291 | -0.0058401 | -0.00062998 | 0.00055291 | south | Y | 0.00081124 | 0.018858
333 | RWMILLER | 2 | 119 | -0.000964 | north | Y | -0.00081124 | -0.00055291 | -0.0058401 | -0.00062998 | 0.00055291 | south | Y | 0.00081124 | 0.030742
334 | RWMILLER | 3 | 205 | -0.000964 | north | Y | -0.00081124 | -0.00055291 | -0.0058401 | -0.00062998 | 0.00055291 | south | Y | 0.00081124 | 0.052958
335 | RWMILLER | 4 | 102 | -0.000964 | north | Y | -0.00081124 | -0.00055291 | -0.0058401 | -0.00062998 | 0.00055291 | south | Y | 0.00081124 | 0.02635
336 | RWMILLER | 5 | 96 | -0.000964 | north | Y | -0.00081124 | -0.00055291 | -0.0058401 | -0.00062998 | 0.00055291 | south | Y | 0.00081124 | 0.0248
344 | MRSSHPRD | 1 | 12 | 6.5e-05 | north | N | 0.00021776 | 0.00047609 | -0.0048111 | 0.00039902 | 0.00021776 | North | N | 0.00021776 | 0
345 | MRSSHPRD | 2 | 12 | 6.5e-05 | north | N | 0.00021776 | 0.00047609 | -0.0048111 | 0.00039902 | 0.00021776 | North | N | 0.00021776 | 0
366 | JNSNCNTY | 1 | 168 | -0.000432 | north | Y | -0.00027924 | -2.0907e-05 | -0.0053081 | -9.7977e-05 | 2.0907e-05 | south | Y | 0.00027924 | 0.0434
367 | JNSNCNTY | 2 | 90 | -0.000432 | north | Y | -0.00027924 | -2.0907e-05 | -0.0053081 | -9.7977e-05 | 2.0907e-05 | south | Y | 0.00027924 | 0.02325
503 | NTHTEXAS | 1 | 18 | -0.000366 | north | Y | -0.00021324 | 4.5093e-05 | -0.0052421 | -3.1977e-05 | 3.1977e-05 | houston | Y | 0.00021324 | 0.0032627
504 | NTHTEXAS | 2 | 18 | -0.000366 | north | Y | -0.00021324 | 4.5093e-05 | -0.0052421 | -3.1977e-05 | 3.1977e-05 | houston | Y | 0.00021324 | 0.0032627
505 | NTHTEXAS | 3 | 38 | -0.000366 | north | Y | -0.00021324 | 4.5093e-05 | -0.0052421 | -3.1977e-05 | 3.1977e-05 | houston | Y | 0.00021324 | 0.006888
580 | JCKCNTY8 | 1 | 288 | -6.6e-05 | north | Y | 8.6761e-05 | 0.00034509 | -0.0049421 | 0.00026802 | 8.6761e-05 | North | N | 8.6761e-05 | 0
581 | JCKCNTY8 | 2 | 147 | -6.6e-05 | north | Y | 8.6761e-05 | 0.00034509 | -0.0049421 | 0.00026802 | 8.6761e-05 | North | N | 8.6761e-05 | 0
582 | JCKCNTY8 | 3 | 147 | -6.6e-05 | north | Y | 8.6761e-05 | 0.00034509 | -0.0049421 | 0.00026802 | 8.6761e-05 | North | N | 8.6761e-05 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.000113 | north | Y | 0.00026576 | 0.00052409 | -0.0047631 | 0.00044702 | 0.00026576 | North | N | 0.00026576 | 0
837 | NEWMAN_G | 1 | 40 | -7.5e-05 | north | Y | 7.7761e-05 | 0.00033609 | -0.0049511 | 0.00025902 | 7.7761e-05 | North | N | 7.7761e-05 | 0
842 | OLINGER_ | 1 | 79 | -7.1e-05 | north | Y | 8.1761e-05 | 0.00034009 | -0.0049471 | 0.00026302 | 8.1761e-05 | North | N | 8.1761e-05 | 0
843 | OLINGER_ | 1 | 106 | -7.1e-05 | north | Y | 8.1761e-05 | 0.00034009 | -0.0049471 | 0.00026302 | 8.1761e-05 | North | N | 8.1761e-05 | 0
844 | OLINGER_ | 1 | 146 | -7.1e-05 | north | Y | 8.1761e-05 | 0.00034009 | -0.0049471 | 0.00026302 | 8.1761e-05 | North | N | 8.1761e-05 | 0
845 | OLINGER_ | 1 | 76 | -7.1e-05 | north | Y | 8.1761e-05 | 0.00034009 | -0.0049471 | 0.00026302 | 8.1761e-05 | North | N | 8.1761e-05 | 0
923 | SPENCER_ | 1 | 60 | 9.1e-05 | north | Y | 0.00024376 | 0.00050209 | -0.0047851 | 0.00042502 | 0.00024376 | North | N | 0.00024376 | 0
924 | SPENCER_ | 1 | 63 | 9.1e-05 | north | Y | 0.00024376 | 0.00050209 | -0.0047851 | 0.00042502 | 0.00024376 | North | N | 0.00024376 | 0
948 | STEAM1 | 1 | 20 | -7.4e-05 | north | Y | 7.8761e-05 | 0.00033709 | -0.0049501 | 0.00026002 | 7.8761e-05 | North | N | 7.8761e-05 | 0
949 | STEAM2 | 1 | 25 | -7.4e-05 | north | Y | 7.8761e-05 | 0.00033709 | -0.0049501 | 0.00026002 | 7.8761e-05 | North | N | 7.8761e-05 | 0
950 | STEAM3 | 1 | 41 | -7.4e-05 | north | Y | 7.8761e-05 | 0.00033709 | -0.0049501 | 0.00026002 | 7.8761e-05 | North | N | 7.8761e-05 | 0
990 | GIBN_CRE | 1 | 463 | -0.000285 | north | Y | -0.00013224 | 0.00012609 | -0.0051611 | 4.9023e-05 | 4.9023e-05 | houston | Y | 0.00013224 | 0.038529
1002 | PBCTAGE_ | A | 66 | 0.005966 | west | Y | 0.0061188 | 0.0063771 | 0.0010899 | 0.0063 | 0.0010899 | west | N | 0.0010899 | 0
1003 | PBCTBGE_ | B | 65 | 0.005966 | west | Y | 0.0061188 | 0.0063771 | 0.0010899 | 0.0063 | 0.0010899 | west | N | 0.0010899 | 0
1004 | PBCTCGE_ | C | 67 | 0.005966 | west | Y | 0.0061188 | 0.0063771 | 0.0010899 | 0.0063 | 0.0010899 | west | N | 0.0010899 | 0
1005 | PBCTDGE_ | D | 67 | 0.005966 | west | Y | 0.0061188 | 0.0063771 | 0.0010899 | 0.0063 | 0.0010899 | west | N | 0.0010899 | 0
1006 | PBCTEGE_ | E | 67 | 0.005966 | west | Y | 0.0061188 | 0.0063771 | 0.0010899 | 0.0063 | 0.0010899 | west | N | 0.0010899 | 0
1007 | PB5GEN_6 | MB | 114 | 0.005966 | west | Y | 0.0061188 | 0.0063771 | 0.0010899 | 0.0063 | 0.0010899 | west | N | 0.0010899 | 0
1008 | PB6GEN_7 | MB | 515 | 0.005966 | west | Y | 0.0061188 | 0.0063771 | 0.0010899 | 0.0063 | 0.0010899 | west | N | 0.0010899 | 0
1039 | MRGNAG_1 | A | 66 | 0.004852 | west | Y | 0.0050048 | 0.0052631 | -2.4081e-05 | 0.005186 | 2.4081e-05 | west | N | 2.4081e-05 | 0
1040 | MRGNBG_2 | B | 69 | 0.004852 | west | Y | 0.0050048 | 0.0052631 | -2.4081e-05 | 0.005186 | 2.4081e-05 | west | N | 2.4081e-05 | 0
1041 | MRGNCG_3 | C | 69 | 0.004852 | west | Y | 0.0050048 | 0.0052631 | -2.4081e-05 | 0.005186 | 2.4081e-05 | west | N | 2.4081e-05 | 0
1042 | MRGNDG_4 | D | 67 | 0.004852 | west | Y | 0.0050048 | 0.0052631 | -2.4081e-05 | 0.005186 | 2.4081e-05 | west | N | 2.4081e-05 | 0
1043 | MRGNEG_5 | E | 67 | 0.004852 | west | Y | 0.0050048 | 0.0052631 | -2.4081e-05 | 0.005186 | 2.4081e-05 | west | N | 2.4081e-05 | 0
1044 | MRGNFG_6 | F | 65 | 0.004852 | west | Y | 0.0050048 | 0.0052631 | -2.4081e-05 | 0.005186 | 2.4081e-05 | west | N | 2.4081e-05 | 0
1045 | CALENG1G | 1 | 70 | 0.004941 | west | N | 0.0050938 | 0.0053521 | 6.4919e-05 | 0.005275 | 6.4919e-05 | west | N | 6.4919e-05 | 0
1046 | CALENG2G | 2 | 73.4 | 0.004941 | west | N | 0.0050938 | 0.0053521 | 6.4919e-05 | 0.005275 | 6.4919e-05 | west | N | 6.4919e-05 | 0
1047 | CALENG3G | 3 | 70.4 | 0.004941 | west | N | 0.0050938 | 0.0053521 | 6.4919e-05 | 0.005275 | 6.4919e-05 | west | N | 6.4919e-05 | 0
1058 | LONGSHOR | 1 | 150 | 0.004775 | west | Y | 0.0049278 | 0.0051861 | -0.00010108 | 0.005109 | 0.00010108 | west | N | 0.00010108 | 0
1058 | LONGSHOR | 2 | 220 | 0.004775 | west | Y | 0.0049278 | 0.0051861 | -0.00010108 | 0.005109 | 0.00010108 | west | N | 0.00010108 | 0
1061 | CIELOGEN | 1 | 99 | 0.004771 | west | Y | 0.0049238 | 0.0051821 | -0.00010508 | 0.005105 | 0.00010508 | west | N | 0.00010508 | 0
1062 | CIELOGEN | 1 | 61 | 0.004771 | west | Y | 0.0049238 | 0.0051821 | -0.00010508 | 0.005105 | 0.00010508 | west | N | 0.00010508 | 0
1068 | SCURRYCW | 1 | 141 | 0.004797 | west | Y | 0.0049498 | 0.0052081 | -7.9081e-05 | 0.005131 | 7.9081e-05 | west | N | 7.9081e-05 | 0
1069 | KINDERMG | 1 | 25 | 0.004771 | west | N | 0.0049238 | 0.0051821 | -0.00010508 | 0.005105 | 0.00010508 | west | N | 0.00010508 | 0
1070 | KINDERMG | 1 | 45.7 | 0.004771 | west | N | 0.0049238 | 0.0051821 | -0.00010508 | 0.005105 | 0.00010508 | west | N | 0.00010508 | 0
1071 | KINDERMG | 1 | 45.7 | 0.004771 | west | N | 0.0049238 | 0.0051821 | -0.00010508 | 0.005105 | 0.00010508 | west | N | 0.00010508 | 0
1073 | SCURRYCW | 2 | 120 | 0.004797 | west | Y | 0.0049498 | 0.0052081 | -7.9081e-05 | 0.005131 | 7.9081e-05 | west | N | 7.9081e-05 | 0
1320 | BSP 1 | 1 | 25.8 | 0.010243 | west | N | 0.010396 | 0.010654 | 0.0053669 | 0.010577 | 0.0053669 | west | N | 0.0053669 | 0
1326 | STANTONW | 1 | 100.5 | 0.006489 | west | Y | 0.0066418 | 0.0069001 | 0.0016129 | 0.006823 | 0.0016129 | west | N | 0.0016129 | 0
1327 | WILDHRSE | 1 | 120 | 0.006888 | west | Y | 0.0070408 | 0.0072991 | 0.0020119 | 0.007222 | 0.0020119 | west | N | 0.0020119 | 0
1328 | OCOTILLO | 1 | 58 | 0.005827 | west | Y | 0.0059798 | 0.0062381 | 0.00095092 | 0.006161 | 0.00095092 | west | N | 0.00095092 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.00569 | west | Y | 0.0058428 | 0.0061011 | 0.00081392 | 0.006024 | 0.00081392 | west | N | 0.00081392 | 0
1343 | TRENTIPP | 1 | 150 | 0.002105 | west | Y | 0.0022578 | 0.0025161 | -0.0027711 | 0.002439 | 0.0022578 | North | Y | 0.0027711 | 0.076998
1349 | WESTXWIN | 1 | 6.6 | 0.019939 | west | Y | 0.020092 | 0.02035 | 0.015063 | 0.020273 | 0.015063 | west | N | 0.015063 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.019939 | west | Y | 0.020092 | 0.02035 | 0.015063 | 0.020273 | 0.015063 | west | N | 0.015063 | 0
1354 | AEPWIND_ | 1 | 101 | 0.002105 | west | Y | 0.0022578 | 0.0025161 | -0.0027711 | 0.002439 | 0.0022578 | North | Y | 0.0027711 | 0.051845
1360 | GUNSIGHT | 1 | 120 | 0.006847 | west | Y | 0.0069998 | 0.0072581 | 0.0019709 | 0.007181 | 0.0019709 | west | N | 0.0019709 | 0
1432 | GRHAMSES | 2 | 366 | 0.001315 | north | Y | 0.0014678 | 0.0017261 | -0.0035611 | 0.001649 | 0.0014678 | North | N | 0.0014678 | 0
1433 | GRHAMSES | 1 | 242 | 0.00059 | north | Y | 0.00074276 | 0.0010011 | -0.0042861 | 0.00092402 | 0.00074276 | North | N | 0.00074276 | 0
1437 | MESQUITW | 1 | 400 | 0.002648 | west | Y | 0.0028008 | 0.0030591 | -0.0022281 | 0.002982 | 0.0022281 | west | N | 0.0022281 | 0
1438 | MESQUITW | 1 | 236 | 0.002647 | west | Y | 0.0027998 | 0.0030581 | -0.0022291 | 0.002981 | 0.0022291 | west | N | 0.0022291 | 0
1442 | COKFIELD | 1 | 165 | 0.002328 | west | Y | 0.0024808 | 0.0027391 | -0.0025481 | 0.002662 | 0.0024808 | North | Y | 0.0025481 | 0.011108
1453 | WCPWRCO_ | 1 | 204 | 0.000649 | north | Y | 0.00080176 | 0.0010601 | -0.0042271 | 0.00098302 | 0.00080176 | North | N | 0.00080176 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.000649 | north | Y | 0.00080176 | 0.0010601 | -0.0042271 | 0.00098302 | 0.00080176 | North | N | 0.00080176 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.000649 | north | Y | 0.00080176 | 0.0010601 | -0.0042271 | 0.00098302 | 0.00080176 | North | N | 0.00080176 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.001067 | west | Y | 0.0012198 | 0.0014781 | -0.0038091 | 0.001401 | 0.0012198 | North | Y | 0.0038091 | 0.051786
1479 | WFCOGEN_ | 2 | 20 | 0.001067 | west | Y | 0.0012198 | 0.0014781 | -0.0038091 | 0.001401 | 0.0012198 | North | Y | 0.0038091 | 0.051786
1482 | WFCOGEN_ | 1 | 20 | 0.001067 | west | Y | 0.0012198 | 0.0014781 | -0.0038091 | 0.001401 | 0.0012198 | North | Y | 0.0038091 | 0.051786
1482 | WFCOGEN_ | 2 | 17 | 0.001067 | west | Y | 0.0012198 | 0.0014781 | -0.0038091 | 0.001401 | 0.0012198 | North | Y | 0.0038091 | 0.044018
1600 | BARTNWND | 1 | 120 | 6e-06 | north | Y | 0.00015876 | 0.00041709 | -0.0048701 | 0.00034002 | 0.00015876 | North | N | 0.00015876 | 0
1643 | SLSTR1PP | 1 | 60 | -0.00281 | north | Y | -0.0026572 | -0.0023989 | -0.0076861 | -0.002476 | 0.0023989 | south | Y | 0.0026572 | 0.0155
1675 | PEC_1G | 1 | 75 | -5.4e-05 | north | N | 9.8761e-05 | 0.00035709 | -0.0049301 | 0.00028002 | 9.8761e-05 | North | N | 9.8761e-05 | 0
1676 | PEC_2G | 2 | 79.6 | -5.4e-05 | north | N | 9.8761e-05 | 0.00035709 | -0.0049301 | 0.00028002 | 9.8761e-05 | North | N | 9.8761e-05 | 0
1677 | PEC_3G | 3 | 88.4 | -5.4e-05 | north | N | 9.8761e-05 | 0.00035709 | -0.0049301 | 0.00028002 | 9.8761e-05 | North | N | 9.8761e-05 | 0
1678 | LAMARPWR | 1 | 160 | -5.3e-05 | north | Y | 9.9761e-05 | 0.00035809 | -0.0049291 | 0.00028102 | 9.9761e-05 | North | N | 9.9761e-05 | 0
1679 | LAMARPWR | 2 | 156 | -5.3e-05 | north | Y | 9.9761e-05 | 0.00035809 | -0.0049291 | 0.00028102 | 9.9761e-05 | North | N | 9.9761e-05 | 0
1680 | LAMARPWR | 3 | 196 | -5.3e-05 | north | Y | 9.9761e-05 | 0.00035809 | -0.0049291 | 0.00028102 | 9.9761e-05 | North | N | 9.9761e-05 | 0
1681 | LAMARPWR | 4 | 156 | -5.3e-05 | north | Y | 9.9761e-05 | 0.00035809 | -0.0049291 | 0.00028102 | 9.9761e-05 | North | N | 9.9761e-05 | 0
1682 | LAMARPWR | 5 | 157 | -5.3e-05 | north | Y | 9.9761e-05 | 0.00035809 | -0.0049291 | 0.00028102 | 9.9761e-05 | North | N | 9.9761e-05 | 0
1683 | LAMARPWR | 6 | 198 | -5.3e-05 | north | Y | 9.9761e-05 | 0.00035809 | -0.0049291 | 0.00028102 | 9.9761e-05 | North | N | 9.9761e-05 | 0
1687 | VALLEY_1 | 1 | 170 | -4.3e-05 | north | Y | 0.00010976 | 0.00036809 | -0.0049191 | 0.00029102 | 0.00010976 | North | N | 0.00010976 | 0
1688 | VALLEY_2 | 2 | 520 | -4.3e-05 | north | Y | 0.00010976 | 0.00036809 | -0.0049191 | 0.00029102 | 0.00010976 | North | N | 0.00010976 | 0
1689 | VALLEY_3 | 3 | 370 | -5e-05 | north | Y | 0.00010276 | 0.00036109 | -0.0049261 | 0.00028402 | 0.00010276 | North | N | 0.00010276 | 0
1701 | MOSES_1G | 1 | 558 | -5.8e-05 | north | Y | 9.4761e-05 | 0.00035309 | -0.0049341 | 0.00027602 | 9.4761e-05 | North | N | 9.4761e-05 | 0
1702 | MOSES_2G | 2 | 579 | -5.8e-05 | north | Y | 9.4761e-05 | 0.00035309 | -0.0049341 | 0.00027602 | 9.4761e-05 | North | N | 9.4761e-05 | 0
1703 | MOSES_3G | 3 | 808 | -5.8e-05 | north | Y | 9.4761e-05 | 0.00035309 | -0.0049341 | 0.00027602 | 9.4761e-05 | North | N | 9.4761e-05 | 0
1861 | EAGLEMNT | MB | 112 | 4.9e-05 | north | Y | 0.00020176 | 0.00046009 | -0.0048271 | 0.00038302 | 0.00020176 | North | N | 0.00020176 | 0
1862 | EAGLEMNT | MB | 100 | 4.9e-05 | north | Y | 0.00020176 | 0.00046009 | -0.0048271 | 0.00038302 | 0.00020176 | North | N | 0.00020176 | 0
1863 | EAGLEMNT | MB | 378 | 4.9e-05 | north | Y | 0.00020176 | 0.00046009 | -0.0048271 | 0.00038302 | 0.00020176 | North | N | 0.00020176 | 0
1877 | WLFHOLW_ | 1 | 217.3 | -0.000347 | north | Y | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | Y | 0.00019424 | 0.039388
1878 | WLFHOLW_ | 2 | 205 | -0.000347 | north | Y | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | Y | 0.00019424 | 0.037159
1879 | WLFHOLW_ | 3 | 272.4 | -0.000347 | north | Y | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | Y | 0.00019424 | 0.049376
1889 | DECRDOVA | MB | 770 | -0.000259 | north | Y | -0.00010624 | 0.00015209 | -0.0051351 | 7.5023e-05 | 7.5023e-05 | houston | Y | 0.00010624 | 0
1892 | DECRDOVA | A | 70 | -0.000573 | north | Y | -0.00042024 | -0.00016191 | -0.0054491 | -0.00023898 | 0.00016191 | south | Y | 0.00042024 | 0.018083
1893 | DECRDOVA | B | 69 | -0.000573 | north | Y | -0.00042024 | -0.00016191 | -0.0054491 | -0.00023898 | 0.00016191 | south | Y | 0.00042024 | 0.017825
1894 | DECRDOVA | C | 69 | -0.000573 | north | Y | -0.00042024 | -0.00016191 | -0.0054491 | -0.00023898 | 0.00016191 | south | Y | 0.00042024 | 0.017825
1895 | DECRDOVA | D | 68 | -0.000573 | north | Y | -0.00042024 | -0.00016191 | -0.0054491 | -0.00023898 | 0.00016191 | south | Y | 0.00042024 | 0.017567
1898 | COMCHEPK | 1 | 1157 | -0.000382 | north | N | -0.00022924 | 2.9093e-05 | -0.0052581 | -4.7977e-05 | 2.9093e-05 | south | Y | 0.00022924 | 0
1899 | COMCHEPK | 2 | 1158 | -0.000382 | north | N | -0.00022924 | 2.9093e-05 | -0.0052581 | -4.7977e-05 | 2.9093e-05 | south | Y | 0.00022924 | 0
1937 | MDLTHELP | 5 | 224 | -0.000202 | north | Y | -4.9239e-05 | 0.00020909 | -0.0050781 | 0.00013202 | 4.9239e-05 | North | N | 4.9239e-05 | 0
1938 | MDLTHELP | 6 | 226 | -0.000202 | north | Y | -4.9239e-05 | 0.00020909 | -0.0050781 | 0.00013202 | 4.9239e-05 | North | N | 4.9239e-05 | 0
1941 | MDLTHELP | 1 | 216.4 | -0.000166 | north | Y | -1.3239e-05 | 0.00024509 | -0.0050421 | 0.00016802 | 1.3239e-05 | North | N | 1.3239e-05 | 0
1942 | MDLTHELP | 2 | 216.1 | -0.000166 | north | Y | -1.3239e-05 | 0.00024509 | -0.0050421 | 0.00016802 | 1.3239e-05 | North | N | 1.3239e-05 | 0
1943 | MDLTHELP | 3 | 212 | -0.000202 | north | Y | -4.9239e-05 | 0.00020909 | -0.0050781 | 0.00013202 | 4.9239e-05 | North | N | 4.9239e-05 | 0
1944 | MDLTHELP | 4 | 211 | -0.000202 | north | Y | -4.9239e-05 | 0.00020909 | -0.0050781 | 0.00013202 | 4.9239e-05 | North | N | 4.9239e-05 | 0
1947 | HANDLEY_ | 3 | 395 | -8.3e-05 | north | Y | 6.9761e-05 | 0.00032809 | -0.0049591 | 0.00025102 | 6.9761e-05 | North | N | 6.9761e-05 | 0
1948 | HANDLEY_ | 4 | 435 | -8.4e-05 | north | Y | 6.8761e-05 | 0.00032709 | -0.0049601 | 0.00025002 | 6.8761e-05 | North | N | 6.8761e-05 | 0
1949 | HANDLEY_ | 5 | 435 | -8.3e-05 | north | Y | 6.9761e-05 | 0.00032809 | -0.0049591 | 0.00025102 | 6.9761e-05 | North | N | 6.9761e-05 | 0
2371 | COLLIN_1 | MB | 138 | -2e-05 | north | Y | 0.00013276 | 0.00039109 | -0.0048961 | 0.00031402 | 0.00013276 | North | N | 0.00013276 | 0
2413 | MTCK6_G | 6 | 118 | -0.000112 | north | Y | 4.0761e-05 | 0.00029909 | -0.0049881 | 0.00022202 | 4.0761e-05 | North | N | 4.0761e-05 | 0
2414 | MTCK7_G | 7 | 115 | -0.000112 | north | Y | 4.0761e-05 | 0.00029909 | -0.0049881 | 0.00022202 | 4.0761e-05 | North | N | 4.0761e-05 | 0
2417 | MTCK8_G | 8 | 556 | -0.000112 | north | Y | 4.0761e-05 | 0.00029909 | -0.0049881 | 0.00022202 | 4.0761e-05 | North | N | 4.0761e-05 | 0
2451 | LKHB1_G | 1 | 388 | -9e-05 | north | Y | 6.2761e-05 | 0.00032109 | -0.0049661 | 0.00024402 | 6.2761e-05 | North | N | 6.2761e-05 | 0
2452 | LKHB2_G | 2 | 515 | -9e-05 | north | Y | 6.2761e-05 | 0.00032109 | -0.0049661 | 0.00024402 | 6.2761e-05 | North | N | 6.2761e-05 | 0
3097 | MARTLAKE | 1 | 785 | -0.000136 | north | Y | 1.6761e-05 | 0.00027509 | -0.0050121 | 0.00019802 | 1.6761e-05 | North | N | 1.6761e-05 | 0
3098 | MARTLAKE | 2 | 795 | -0.000136 | north | Y | 1.6761e-05 | 0.00027509 | -0.0050121 | 0.00019802 | 1.6761e-05 | North | N | 1.6761e-05 | 0
3099 | MARTLAKE | 3 | 780 | -0.000136 | north | Y | 1.6761e-05 | 0.00027509 | -0.0050121 | 0.00019802 | 1.6761e-05 | North | N | 1.6761e-05 | 0
3107 | STRYKER_ | 1 | 182 | -0.000149 | north | Y | 3.7609e-06 | 0.00026209 | -0.0050251 | 0.00018502 | 3.7609e-06 | North | N | 3.7609e-06 | 0
3108 | STRYKER_ | 2 | 484 | -0.000149 | north | Y | 3.7609e-06 | 0.00026209 | -0.0050251 | 0.00018502 | 3.7609e-06 | North | N | 3.7609e-06 | 0
3126 | TRINIDAD | 1 | 224 | -0.000193 | north | Y | -4.0239e-05 | 0.00021809 | -0.0050691 | 0.00014102 | 4.0239e-05 | North | N | 4.0239e-05 | 0
3309 | ASPN_G | 1 | 50 | -0.000148 | north | Y | 4.7609e-06 | 0.00026309 | -0.0050241 | 0.00018602 | 4.7609e-06 | North | N | 4.7609e-06 | 0
3348 | CHAMPION | MB | 42 | -0.000147 | north | N | 5.7609e-06 | 0.00026409 | -0.0050231 | 0.00018702 | 5.7609e-06 | North | N | 5.7609e-06 | 0
3381 | BBRN_1G | 1 | 615 | -0.000207 | north | Y | -5.4239e-05 | 0.00020409 | -0.0050831 | 0.00012702 | 5.4239e-05 | North | N | 5.4239e-05 | 0
3382 | BBRN_2G | 2 | 587 | -0.000207 | north | Y | -5.4239e-05 | 0.00020409 | -0.0050831 | 0.00012702 | 5.4239e-05 | North | N | 5.4239e-05 | 0
3403 | THOUSE_1 | MB | 537 | -0.000409 | north | Y | -0.00025624 | 2.0932e-06 | -0.0052851 | -7.4977e-05 | 2.0932e-06 | south | Y | 0.00025624 | 0
3404 | THOUSE_2 | 2 | 787 | -0.000409 | north | Y | -0.00025624 | 2.0932e-06 | -0.0052851 | -7.4977e-05 | 2.0932e-06 | south | Y | 0.00025624 | 0.20001
3416 | LAKE_CRK | MB | 75 | -0.000439 | north | Y | -0.00028624 | -2.7907e-05 | -0.0053151 | -0.00010498 | 2.7907e-05 | south | Y | 0.00028624 | 0
3417 | LAKE_CRK | MB | 222 | -0.000439 | north | Y | -0.00028624 | -2.7907e-05 | -0.0053151 | -0.00010498 | 2.7907e-05 | south | Y | 0.00028624 | 0
3432 | SANDOW_4 | 4 | 569 | -0.000521 | south | Y | -0.00036824 | -0.00010991 | -0.0053971 | -0.00018698 | 0.00010991 | south | N | 0.00010991 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.000353 | south | Y | -0.00020024 | 5.8093e-05 | -0.0052291 | -1.8977e-05 | 1.8977e-05 | houston | Y | 5.8093e-05 | 0.0081753
5027 | BRAUNIG_ | 2 | 216 | -0.000353 | south | Y | -0.00020024 | 5.8093e-05 | -0.0052291 | -1.8977e-05 | 1.8977e-05 | houston | Y | 5.8093e-05 | 0.0084492
5028 | BRAUNIG_ | 3 | 407 | -0.000349 | south | Y | -0.00019624 | 6.2093e-05 | -0.0052251 | -1.4977e-05 | 1.4977e-05 | houston | Y | 6.2093e-05 | 0.019176
5031 | BRA_VHBC | 1 | 46 | -0.000353 | south | Y | -0.00020024 | 5.8093e-05 | -0.0052291 | -1.8977e-05 | 1.8977e-05 | houston | Y | 5.8093e-05 | 0.0017994
5032 | BRA_VHBC | 2 | 47 | -0.000353 | south | Y | -0.00020024 | 5.8093e-05 | -0.0052291 | -1.8977e-05 | 1.8977e-05 | houston | Y | 5.8093e-05 | 0.0018385
5033 | BRA_VHBC | 3 | 46 | -0.000353 | south | Y | -0.00020024 | 5.8093e-05 | -0.0052291 | -1.8977e-05 | 1.8977e-05 | houston | Y | 5.8093e-05 | 0.0017994
5034 | BRA_VHBC | 4 | 46 | -0.000353 | south | Y | -0.00020024 | 5.8093e-05 | -0.0052291 | -1.8977e-05 | 1.8977e-05 | houston | Y | 5.8093e-05 | 0.0017994
5111 | CALAVER_ | 1 | 424 | -0.000358 | south | Y | -0.00020524 | 5.3093e-05 | -0.0052341 | -2.3977e-05 | 2.3977e-05 | houston | Y | 5.3093e-05 | 0.012345
5112 | CALAVER_ | 2 | 425 | -0.000358 | south | Y | -0.00020524 | 5.3093e-05 | -0.0052341 | -2.3977e-05 | 2.3977e-05 | houston | Y | 5.3093e-05 | 0.012374
5264 | LEON_LCP | 3 | 58 | -0.00033 | south | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | Y | 8.1093e-05 | 0.0044701
5265 | LEON_LCP | 4 | 89 | -0.00033 | south | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | Y | 8.1093e-05 | 0.0068592
5266 | LEON_LCP | 1 | 44 | -0.00033 | south | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | Y | 8.1093e-05 | 0.0033911
5267 | LEON_LCP | 2 | 44 | -0.00033 | south | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | Y | 8.1093e-05 | 0.0033911
5268 | LEON_LCP | 3 | 43 | -0.00033 | south | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | Y | 8.1093e-05 | 0.003314
5269 | LEON_LCP | 4 | 45 | -0.00033 | south | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | Y | 8.1093e-05 | 0.0034682
5396 | CALAVER_ | 1 | 412 | -0.000354 | south | Y | -0.00020124 | 5.7093e-05 | -0.0052301 | -1.9977e-05 | 1.9977e-05 | houston | Y | 5.7093e-05 | 0.015292
5397 | CALAVER_ | 2 | 400 | -0.000354 | south | Y | -0.00020124 | 5.7093e-05 | -0.0052301 | -1.9977e-05 | 1.9977e-05 | houston | Y | 5.7093e-05 | 0.014847
5401 | CALAVER_ | 1 | 546 | -0.000371 | south | Y | -0.00021824 | 4.0093e-05 | -0.0052471 | -3.6977e-05 | 3.6977e-05 | houston | Y | 4.0093e-05 | 0.0017016
5402 | CALAVER_ | 2 | 750 | -0.000371 | south | Y | -0.00021824 | 4.0093e-05 | -0.0052471 | -3.6977e-05 | 3.6977e-05 | houston | Y | 4.0093e-05 | 0.0023373
5436 | TUTTL_WB | MB | 61 | -0.000369 | south | Y | -0.00021624 | 4.2093e-05 | -0.0052451 | -3.4977e-05 | 3.4977e-05 | houston | Y | 4.2093e-05 | 0
5438 | TUTTL_WB | MB | 95 | -0.000369 | south | Y | -0.00021624 | 4.2093e-05 | -0.0052451 | -3.4977e-05 | 3.4977e-05 | houston | Y | 4.2093e-05 | 0
5439 | TUTTL_WB | MB | 151 | -0.000369 | south | Y | -0.00021624 | 4.2093e-05 | -0.0052451 | -3.4977e-05 | 3.4977e-05 | houston | Y | 4.2093e-05 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.000373 | south | Y | -0.00022024 | 3.8093e-05 | -0.0052491 | -3.8977e-05 | 3.8093e-05 | south | N | 3.8093e-05 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.000373 | south | Y | -0.00022024 | 3.8093e-05 | -0.0052491 | -3.8977e-05 | 3.8093e-05 | south | N | 3.8093e-05 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.000373 | south | Y | -0.00022024 | 3.8093e-05 | -0.0052491 | -3.8977e-05 | 3.8093e-05 | south | N | 3.8093e-05 | 0
5503 | RAYBURNG | 1 | 22 | -0.000321 | south | Y | -0.00016824 | 9.0093e-05 | -0.0051971 | 1.3023e-05 | 1.3023e-05 | houston | Y | 9.0093e-05 | 0.0016955
5505 | RAYBURNG | 1 | 11 | -0.000321 | south | Y | -0.00016824 | 9.0093e-05 | -0.0051971 | 1.3023e-05 | 1.3023e-05 | houston | Y | 9.0093e-05 | 0.00084777
5506 | RAYBURNG | 1 | 11 | -0.000321 | south | Y | -0.00016824 | 9.0093e-05 | -0.0051971 | 1.3023e-05 | 1.3023e-05 | houston | Y | 9.0093e-05 | 0.00084777
5508 | RAYBURNC | 1 | 47.7 | -0.000331 | south | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | Y | 8.0093e-05 | 0.0036762
5509 | RAYBURNC | 1 | 37.3 | -0.000331 | south | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | Y | 8.0093e-05 | 0.0028747
5511 | RAYBURNC | 1 | 46 | -0.000331 | south | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | Y | 8.0093e-05 | 0.0035452
5512 | RAYBURNC | 1 | 48 | -0.000331 | south | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | Y | 8.0093e-05 | 0.0036994
5728 | FALCONHY | 2 | 12 | -0.000209 | south | N | -5.6239e-05 | 0.00020209 | -0.0050851 | 0.00012502 | 5.6239e-05 | North | Y | 0.00020209 | 0
5729 | FALCONHY | 3 | 11 | -0.000209 | south | N | -5.6239e-05 | 0.00020209 | -0.0050851 | 0.00012502 | 5.6239e-05 | North | Y | 0.00020209 | 0
5890 | PEARSALL | 1 | 24 | 7.8e-05 | south | Y | 0.00023076 | 0.00048909 | -0.0047981 | 0.00041202 | 0.00023076 | North | Y | 0.00048909 | 0.0062
5891 | PEARSALL | 1 | 24 | 7.8e-05 | south | Y | 0.00023076 | 0.00048909 | -0.0047981 | 0.00041202 | 0.00023076 | North | Y | 0.00048909 | 0.0062
5892 | PEARSALL | 1 | 23 | 7.8e-05 | south | Y | 0.00023076 | 0.00048909 | -0.0047981 | 0.00041202 | 0.00023076 | North | Y | 0.00048909 | 0.0059416
5903 | SANMIGUE | 1 | 396 | -0.000308 | south | Y | -0.00015524 | 0.00010309 | -0.0051841 | 2.6023e-05 | 2.6023e-05 | houston | Y | 0.00010309 | 0.03052
5911 | STP_GN1_ | 1 | 1333 | -0.000356 | houston | N | -0.00020324 | 5.5093e-05 | -0.0052321 | -2.1977e-05 | 2.1977e-05 | houston | N | 2.1977e-05 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.000356 | houston | N | -0.00020324 | 5.5093e-05 | -0.0052321 | -2.1977e-05 | 2.1977e-05 | houston | N | 2.1977e-05 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | N | 0.00015276 | 0
5932 | SI_RAY9 | 9 | 38 | -0.000301 | south | Y | -0.00014824 | 0.00011009 | -0.0051771 | 3.3023e-05 | 3.3023e-05 | houston | Y | 0.00011009 | 0.0029287
5933 | SI_RAY6 | 6 | 19.3 | -0.000301 | south | Y | -0.00014824 | 0.00011009 | -0.0051771 | 3.3023e-05 | 3.3023e-05 | houston | Y | 0.00011009 | 0.0014875
5934 | SI_RAY5 | 5 | 15 | -0.000301 | south | Y | -0.00014824 | 0.00011009 | -0.0051771 | 3.3023e-05 | 3.3023e-05 | houston | Y | 0.00011009 | 0.0011561
5935 | SI_RAY10 | 10 | 47 | -0.000301 | south | Y | -0.00014824 | 0.00011009 | -0.0051771 | 3.3023e-05 | 3.3023e-05 | houston | Y | 0.00011009 | 0.0036223
6016 | SWMESA | 1 | 75 | 0.00807 | west | Y | 0.0082228 | 0.0084811 | 0.0031939 | 0.008404 | 0.0031939 | west | N | 0.0031939 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.0048761 | 0
6144 | MCADOO1A | 1 | 150 | 0.003517 | west | Y | 0.0036698 | 0.0039281 | -0.0013591 | 0.003851 | 0.0013591 | west | N | 0.0013591 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.004087 | west | Y | 0.0042398 | 0.0044981 | -0.00078908 | 0.004421 | 0.00078908 | west | N | 0.00078908 | 0
6476 | LANGFORD | 1 | 150 | 0.006398 | west | Y | 0.0065508 | 0.0068091 | 0.0015219 | 0.006732 | 0.0015219 | west | N | 0.0015219 | 0
6637 | SNYDERW1 | 1 | 63 | 0.004901 | west | Y | 0.0050538 | 0.0053121 | 2.4919e-05 | 0.005235 | 2.4919e-05 | west | N | 2.4919e-05 | 0
6752 | OKLA0A | 1 | 649.7 | 0.001905 | west | Y | 0.0020578 | 0.0023161 | -0.0029711 | 0.002239 | 0.0020578 | North | Y | 0.0029711 | 0.59338
6948 | DENISNDM | 1 | 40 | -3.7e-05 | north | N | 0.00011576 | 0.00037409 | -0.0049131 | 0.00029702 | 0.00011576 | North | N | 0.00011576 | 0
6948 | DENISNDM | 2 | 40 | -3.7e-05 | north | N | 0.00011576 | 0.00037409 | -0.0049131 | 0.00029702 | 0.00011576 | North | N | 0.00011576 | 0
7000 | L_FERGUS | 1 | 422 | -0.001256 | south | Y | -0.0011032 | -0.00084491 | -0.0061321 | -0.00092198 | 0.00084491 | south | N | 0.00084491 | 0
7004 | L_SIMGID | 1 | 132 | -0.00054 | south | Y | -0.00038724 | -0.00012891 | -0.0054161 | -0.00020598 | 0.00012891 | south | N | 0.00012891 | 0
7005 | L_SIMGID | 2 | 134 | -0.00054 | south | Y | -0.00038724 | -0.00012891 | -0.0054161 | -0.00020598 | 0.00012891 | south | N | 0.00012891 | 0
7006 | L_SIMGID | 3 | 323 | -0.00054 | south | Y | -0.00038724 | -0.00012891 | -0.0054161 | -0.00020598 | 0.00012891 | south | N | 0.00012891 | 0
7007 | L_LOSTPI | 1 | 158 | -0.000497 | south | Y | -0.00034424 | -8.5907e-05 | -0.0053731 | -0.00016298 | 8.5907e-05 | south | N | 8.5907e-05 | 0
7008 | L_LOSTPI | 2 | 160 | -0.000497 | south | Y | -0.00034424 | -8.5907e-05 | -0.0053731 | -0.00016298 | 8.5907e-05 | south | N | 8.5907e-05 | 0
7009 | L_LOSTPI | 3 | 175 | -0.000497 | south | Y | -0.00034424 | -8.5907e-05 | -0.0053731 | -0.00016298 | 8.5907e-05 | south | N | 8.5907e-05 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.000477 | south | Y | -0.00032424 | -6.5907e-05 | -0.0053531 | -0.00014298 | 6.5907e-05 | south | N | 6.5907e-05 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.000477 | south | Y | -0.00032424 | -6.5907e-05 | -0.0053531 | -0.00014298 | 6.5907e-05 | south | N | 6.5907e-05 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.000477 | south | Y | -0.00032424 | -6.5907e-05 | -0.0053531 | -0.00014298 | 6.5907e-05 | south | N | 6.5907e-05 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.000438 | south | Y | -0.00028524 | -2.6907e-05 | -0.0053141 | -0.00010398 | 2.6907e-05 | south | N | 2.6907e-05 | 0
7015 | L_HAYSEN | 2 | 225 | -0.000438 | south | Y | -0.00028524 | -2.6907e-05 | -0.0053141 | -0.00010398 | 2.6907e-05 | south | N | 2.6907e-05 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.000438 | south | Y | -0.00028524 | -2.6907e-05 | -0.0053141 | -0.00010398 | 2.6907e-05 | south | N | 2.6907e-05 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.000438 | south | Y | -0.00028524 | -2.6907e-05 | -0.0053141 | -0.00010398 | 2.6907e-05 | south | N | 2.6907e-05 | 0
7020 | L_AUSTPL | 1 | 8 | -0.000615 | south | N | -0.00046224 | -0.00020391 | -0.0054911 | -0.00028098 | 0.00020391 | south | N | 0.00020391 | 0
7020 | L_AUSTPL | 2 | 8 | -0.000615 | south | N | -0.00046224 | -0.00020391 | -0.0054911 | -0.00028098 | 0.00020391 | south | N | 0.00020391 | 0
7022 | L_BUCHAN | 1 | 18 | -0.001923 | south | N | -0.0017702 | -0.0015119 | -0.0067991 | -0.001589 | 0.0015119 | south | N | 0.0015119 | 0
7023 | L_BUCHAN | 2 | 18 | -0.001923 | south | N | -0.0017702 | -0.0015119 | -0.0067991 | -0.001589 | 0.0015119 | south | N | 0.0015119 | 0
7024 | L_BUCHAN | 3 | 15 | -0.001923 | south | N | -0.0017702 | -0.0015119 | -0.0067991 | -0.001589 | 0.0015119 | south | N | 0.0015119 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.001507 | south | N | -0.0013542 | -0.0010959 | -0.0063831 | -0.001173 | 0.0010959 | south | N | 0.0010959 | 0
7028 | L_MARBFA | 1 | 18 | -0.001117 | south | N | -0.00096424 | -0.00070591 | -0.0059931 | -0.00078298 | 0.00070591 | south | N | 0.00070591 | 0
7029 | L_MARBFA | 2 | 18 | -0.001117 | south | N | -0.00096424 | -0.00070591 | -0.0059931 | -0.00078298 | 0.00070591 | south | N | 0.00070591 | 0
7031 | L_MARSFO | 1 | 35 | -0.000802 | south | N | -0.00064924 | -0.00039091 | -0.0056781 | -0.00046798 | 0.00039091 | south | N | 0.00039091 | 0
7032 | L_MARSFO | 2 | 34 | -0.000802 | south | N | -0.00064924 | -0.00039091 | -0.0056781 | -0.00046798 | 0.00039091 | south | N | 0.00039091 | 0
7033 | L_MARSFO | 3 | 35 | -0.000802 | south | N | -0.00064924 | -0.00039091 | -0.0056781 | -0.00046798 | 0.00039091 | south | N | 0.00039091 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.001297 | south | N | -0.0011442 | -0.00088591 | -0.0061731 | -0.00096298 | 0.00088591 | south | N | 0.00088591 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.001297 | south | N | -0.0011442 | -0.00088591 | -0.0061731 | -0.00096298 | 0.00088591 | south | N | 0.00088591 | 0
7038 | L_DELAWA | 1 | 35 | 0.005968 | west | Y | 0.0061208 | 0.0063791 | 0.0010919 | 0.006302 | 0.0010919 | west | N | 0.0010919 | 0
7038 | L_DELAWA | 2 | 30 | 0.005968 | west | Y | 0.0061208 | 0.0063791 | 0.0010919 | 0.006302 | 0.0010919 | west | N | 0.0010919 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.000498 | south | Y | -0.00034524 | -8.6907e-05 | -0.0053741 | -0.00016398 | 8.6907e-05 | south | N | 8.6907e-05 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.000498 | south | Y | -0.00034524 | -8.6907e-05 | -0.0053741 | -0.00016398 | 8.6907e-05 | south | N | 8.6907e-05 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.000498 | south | Y | -0.00034524 | -8.6907e-05 | -0.0053741 | -0.00016398 | 8.6907e-05 | south | N | 8.6907e-05 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.000498 | south | Y | -0.00034524 | -8.6907e-05 | -0.0053741 | -0.00016398 | 8.6907e-05 | south | N | 8.6907e-05 | 0
7487 | L_CANYHY | 1 | 6 | -0.000493 | south | N | -0.00034024 | -8.1907e-05 | -0.0053691 | -0.00015898 | 8.1907e-05 | south | N | 8.1907e-05 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.000431 | south | N | -0.00027824 | -1.9907e-05 | -0.0053071 | -9.6977e-05 | 1.9907e-05 | south | N | 1.9907e-05 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.000431 | south | N | -0.00027824 | -1.9907e-05 | -0.0053071 | -9.6977e-05 | 1.9907e-05 | south | N | 1.9907e-05 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.000431 | south | N | -0.00027824 | -1.9907e-05 | -0.0053071 | -9.6977e-05 | 1.9907e-05 | south | N | 1.9907e-05 | 0
7609 | L_SCHUMA | 1 | 4 | -0.000414 | south | N | -0.00026124 | -2.9068e-06 | -0.0052901 | -7.9977e-05 | 2.9068e-06 | south | N | 2.9068e-06 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.00043 | south | N | -0.00027724 | -1.8907e-05 | -0.0053061 | -9.5977e-05 | 1.8907e-05 | south | N | 1.8907e-05 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.00043 | south | N | -0.00027724 | -1.8907e-05 | -0.0053061 | -9.5977e-05 | 1.8907e-05 | south | N | 1.8907e-05 | 0
7800 | L_GUADGE | 1 | 147 | -0.000399 | south | Y | -0.00024624 | 1.2093e-05 | -0.0052751 | -6.4977e-05 | 1.2093e-05 | south | N | 1.2093e-05 | 0
7801 | L_GUADGE | 2 | 138 | -0.000399 | south | Y | -0.00024624 | 1.2093e-05 | -0.0052751 | -6.4977e-05 | 1.2093e-05 | south | N | 1.2093e-05 | 0
7802 | L_GUADGE | 3 | 140 | -0.000399 | south | Y | -0.00024624 | 1.2093e-05 | -0.0052751 | -6.4977e-05 | 1.2093e-05 | south | N | 1.2093e-05 | 0
7803 | L_GUADGE | 4 | 147 | -0.000399 | south | Y | -0.00024624 | 1.2093e-05 | -0.0052751 | -6.4977e-05 | 1.2093e-05 | south | N | 1.2093e-05 | 0
7804 | L_GUADGE | 5 | 182 | -0.000399 | south | Y | -0.00024624 | 1.2093e-05 | -0.0052751 | -6.4977e-05 | 1.2093e-05 | south | N | 1.2093e-05 | 0
7805 | L_GUADGE | 6 | 198 | -0.000399 | south | Y | -0.00024624 | 1.2093e-05 | -0.0052751 | -6.4977e-05 | 1.2093e-05 | south | N | 1.2093e-05 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.000507 | south | Y | -0.00035424 | -9.5907e-05 | -0.0053831 | -0.00017298 | 9.5907e-05 | south | N | 9.5907e-05 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.000507 | south | Y | -0.00035424 | -9.5907e-05 | -0.0053831 | -0.00017298 | 9.5907e-05 | south | N | 9.5907e-05 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.000507 | south | Y | -0.00035424 | -9.5907e-05 | -0.0053831 | -0.00017298 | 9.5907e-05 | south | N | 9.5907e-05 | 0
7810 | L_RIONOG | 1 | 142 | -0.000418 | south | Y | -0.00026524 | -6.9068e-06 | -0.0052941 | -8.3977e-05 | 6.9068e-06 | south | N | 6.9068e-06 | 0
7811 | L_RIONOG | 2 | 145 | -0.000418 | south | Y | -0.00026524 | -6.9068e-06 | -0.0052941 | -8.3977e-05 | 6.9068e-06 | south | N | 6.9068e-06 | 0
7812 | L_RIONOG | 3 | 151 | -0.000418 | south | Y | -0.00026524 | -6.9068e-06 | -0.0052941 | -8.3977e-05 | 6.9068e-06 | south | N | 6.9068e-06 | 0
7813 | L_RIONOG | 4 | 290 | -0.000418 | south | Y | -0.00026524 | -6.9068e-06 | -0.0052941 | -8.3977e-05 | 6.9068e-06 | south | N | 6.9068e-06 | 0
8032 | AMISTADH | 1 | 33 | 0.002788 | south | N | 0.0029408 | 0.0031991 | -0.0020881 | 0.003122 | 0.0020881 | west | Y | 0.0031991 | 0
8033 | AMISTADH | 2 | 25 | 0.002788 | south | N | 0.0029408 | 0.0031991 | -0.0020881 | 0.003122 | 0.0020881 | west | Y | 0.0031991 | 0
8048 | FALCONHY | 1 | 12 | -0.000209 | south | N | -5.6239e-05 | 0.00020209 | -0.0050851 | 0.00012502 | 5.6239e-05 | North | Y | 0.00020209 | 0
8066 | DUP1V#1 | 1 | 73 | -0.000339 | south | N | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | Y | 7.2093e-05 | 0
8134 | FOR69CG0 | 1 | 79 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
8138 | FOR69CG0 | 2 | 81 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8147 | UCAR #2 | 10 | 28 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
8148 | UCAR #1 | 2 | 7 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
8153 | FOR69CG0 | 3 | 79 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
8154 | FOR69CG0 | 4 | 80 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
8156 | FOR69CG0 | 6 | 25 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
8157 | FOR69CG0 | 7 | 46 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
8161 | COLETOU1 | 1 | 629 | -0.000328 | south | Y | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | Y | 8.3093e-05 | 0.048477
8173 | VICEC51A | 5 | 144 | -0.000339 | south | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | Y | 7.2093e-05 | 0.0096648
8174 | VICEC61A | 6 | 188 | -0.000339 | south | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | Y | 7.2093e-05 | 0.012618
8189 | CUERO 2 | 1 | 12 | -0.000399 | south | N | -0.00024624 | 1.2093e-05 | -0.0052751 | -6.4977e-05 | 1.2093e-05 | south | N | 1.2093e-05 | 0
8262 | ELPS | 1 | 6 | 0.001928 | south | N | 0.0020808 | 0.0023391 | -0.0029481 | 0.002262 | 0.0020808 | North | Y | 0.0023391 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8442 | NBEC71A | 1 | 336 | -0.000311 | south | Y | -0.00015824 | 0.00010009 | -0.0051871 | 2.3023e-05 | 2.3023e-05 | houston | Y | 0.00010009 | 0.025896
8456 | COSW#1 | 1 | 20 | 0 | south | N | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | 0.00015276 | 0.00041109 | -0.0048761 | 0.00033402 | 0.00015276 | North | Y | 0.00041109 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.00031 | south | Y | -0.00015724 | 0.00010109 | -0.0051861 | 2.4023e-05 | 2.4023e-05 | houston | Y | 0.00010109 | 0.025741
8460 | B_DAVIS2 | 2 | 340 | -0.00031 | south | Y | -0.00015724 | 0.00010109 | -0.0051861 | 2.4023e-05 | 2.4023e-05 | houston | Y | 0.00010109 | 0.026204
8461 | KOCH_UP0 | 1 | 38 | -0.000309 | south | N | -0.00015624 | 0.00010209 | -0.0051851 | 2.5023e-05 | 2.5023e-05 | houston | Y | 0.00010209 | 0
8506 | VAL #1 | 1 | 25 | -0.000309 | south | N | -0.00015624 | 0.00010209 | -0.0051851 | 2.5023e-05 | 2.5023e-05 | houston | Y | 0.00010209 | 0
8507 | VAL #2 | 2 | 25 | -0.000309 | south | N | -0.00015624 | 0.00010209 | -0.0051851 | 2.5023e-05 | 2.5023e-05 | houston | Y | 0.00010209 | 0
8511 | OXY_CC0A | 1 | 38 | -0.00031 | south | N | -0.00015724 | 0.00010109 | -0.0051861 | 2.4023e-05 | 2.4023e-05 | houston | Y | 0.00010109 | 0
8517 | CELANEBI | 1 | 29 | -0.000307 | south | N | -0.00015424 | 0.00010409 | -0.0051831 | 2.7023e-05 | 2.7023e-05 | houston | Y | 0.00010409 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.000311 | south | N | -0.00015824 | 0.00010009 | -0.0051871 | 2.3023e-05 | 2.3023e-05 | houston | Y | 0.00010009 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.000311 | south | N | -0.00015824 | 0.00010009 | -0.0051871 | 2.3023e-05 | 2.3023e-05 | houston | Y | 0.00010009 | 0
8562 | CNOPST1 | 3 | 153 | -0.000311 | south | N | -0.00015824 | 0.00010009 | -0.0051871 | 2.3023e-05 | 2.3023e-05 | houston | Y | 0.00010009 | 0
8926 | LGE_GT10 | 1 | 158 | -0.000314 | south | N | -0.00016124 | 9.7093e-05 | -0.0051901 | 2.0023e-05 | 2.0023e-05 | houston | Y | 9.7093e-05 | 0
8927 | LGE_GT20 | 2 | 153 | -0.000314 | south | N | -0.00016124 | 9.7093e-05 | -0.0051901 | 2.0023e-05 | 2.0023e-05 | houston | Y | 9.7093e-05 | 0
8928 | LGE_STG0 | 3 | 100 | -0.000314 | south | N | -0.00016124 | 9.7093e-05 | -0.0051901 | 2.0023e-05 | 2.0023e-05 | houston | Y | 9.7093e-05 | 0
8930 | ICPGN10A | 1 | 145 | -0.000314 | south | N | -0.00016124 | 9.7093e-05 | -0.0051901 | 2.0023e-05 | 2.0023e-05 | houston | Y | 9.7093e-05 | 0
8931 | ICPGN20A | 2 | 147 | -0.000314 | south | N | -0.00016124 | 9.7093e-05 | -0.0051901 | 2.0023e-05 | 2.0023e-05 | houston | Y | 9.7093e-05 | 0
8932 | ICPGN30A | 3 | 127 | -0.000314 | south | N | -0.00016124 | 9.7093e-05 | -0.0051901 | 2.0023e-05 | 2.0023e-05 | houston | Y | 9.7093e-05 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.000282 | south | Y | -0.00012924 | 0.00012909 | -0.0051581 | 5.2023e-05 | 5.2023e-05 | houston | Y | 0.00012909 | 0.011291
8934 | FGNTS101 | 2 | 147.9 | -0.000282 | south | Y | -0.00012924 | 0.00012909 | -0.0051581 | 5.2023e-05 | 5.2023e-05 | houston | Y | 0.00012909 | 0.011399
8935 | FGNTS201 | 3 | 173 | -0.000282 | south | Y | -0.00012924 | 0.00012909 | -0.0051581 | 5.2023e-05 | 5.2023e-05 | houston | Y | 0.00012909 | 0.013333
8936 | MVGN#1 | 1 | 207 | -0.000294 | south | Y | -0.00014124 | 0.00011709 | -0.0051701 | 4.0023e-05 | 4.0023e-05 | houston | Y | 0.00011709 | 0.015953
8937 | MVGN#2 | 2 | 216.7 | -0.000294 | south | Y | -0.00014124 | 0.00011709 | -0.0051701 | 4.0023e-05 | 4.0023e-05 | houston | Y | 0.00011709 | 0.016701
8938 | MVGN#3 | 3 | 242 | -0.000294 | south | Y | -0.00014124 | 0.00011709 | -0.0051701 | 4.0023e-05 | 4.0023e-05 | houston | Y | 0.00011709 | 0.018651
8981 | HECN1 | 1 | 144 | -0.000294 | south | Y | -0.00014124 | 0.00011709 | -0.0051701 | 4.0023e-05 | 4.0023e-05 | houston | Y | 0.00011709 | 0.011098
8982 | HECN2 | 2 | 144 | -0.000294 | south | Y | -0.00014124 | 0.00011709 | -0.0051701 | 4.0023e-05 | 4.0023e-05 | houston | Y | 0.00011709 | 0.011098
8983 | HECN3 | 3 | 171 | -0.000294 | south | Y | -0.00014124 | 0.00011709 | -0.0051701 | 4.0023e-05 | 4.0023e-05 | houston | Y | 0.00011709 | 0.013179
9000 | DECKR_G1 | 1 | 310 | -0.000601 | south | Y | -0.00044824 | -0.00018991 | -0.0054771 | -0.00026698 | 0.00018991 | south | N | 0.00018991 | 0
9001 | DECKR_G2 | 2 | 413 | -0.000601 | south | Y | -0.00044824 | -0.00018991 | -0.0054771 | -0.00026698 | 0.00018991 | south | N | 0.00018991 | 0
9002 | DECKR_G3 | 3 | 42 | -0.000598 | south | Y | -0.00044524 | -0.00018691 | -0.0054741 | -0.00026398 | 0.00018691 | south | N | 0.00018691 | 0
9003 | DECKR_G4 | 4 | 44 | -0.000598 | south | Y | -0.00044524 | -0.00018691 | -0.0054741 | -0.00026398 | 0.00018691 | south | N | 0.00018691 | 0
9004 | DECKR_G5 | 5 | 44 | -0.000598 | south | Y | -0.00044524 | -0.00018691 | -0.0054741 | -0.00026398 | 0.00018691 | south | N | 0.00018691 | 0
9005 | DECKR_G6 | 6 | 47 | -0.000598 | south | Y | -0.00044524 | -0.00018691 | -0.0054741 | -0.00026398 | 0.00018691 | south | N | 0.00018691 | 0
9016 | SANDH_G1 | 1 | 49 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
9017 | SANDH_G2 | 2 | 46 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
9018 | SANDH_G3 | 3 | 46 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
9019 | SANDH_G4 | 4 | 47 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
9020 | SANDHG5A | 5A | 154 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
9021 | SANDHG5C | 5C | 148 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
9022 | SANDH_G6 | 6 | 48 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
9023 | SANDH_G7 | 7 | 48 | -0.000592 | south | Y | -0.00043924 | -0.00018091 | -0.0054681 | -0.00025798 | 0.00018091 | south | N | 0.00018091 | 0
11001 | NAV1CT | 1 | 70 | 0.00542 | west | Y | 0.0055728 | 0.0058311 | 0.00054392 | 0.005754 | 0.00054392 | west | N | 0.00054392 | 0
11009 | NAV2CT | 1 | 70 | 0.00542 | west | Y | 0.0055728 | 0.0058311 | 0.00054392 | 0.005754 | 0.00054392 | west | N | 0.00054392 | 0
11011 | NAV3ST | 1 | 92.8 | 0.00542 | west | Y | 0.0055728 | 0.0058311 | 0.00054392 | 0.005754 | 0.00054392 | west | N | 0.00054392 | 0
11012 | NAV4CT | 1 | 80 | 0.00542 | west | Y | 0.0055728 | 0.0058311 | 0.00054392 | 0.005754 | 0.00054392 | west | N | 0.00054392 | 0
11013 | NAV5CT | 1 | 80 | 0.00542 | west | Y | 0.0055728 | 0.0058311 | 0.00054392 | 0.005754 | 0.00054392 | west | N | 0.00054392 | 0
11014 | NAV6ST | 1 | 115 | 0.00542 | west | Y | 0.0055728 | 0.0058311 | 0.00054392 | 0.005754 | 0.00054392 | west | N | 0.00054392 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.005427 | west | Y | 0.0055798 | 0.0058381 | 0.00055092 | 0.005761 | 0.00055092 | west | N | 0.00055092 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.005427 | west | Y | 0.0055798 | 0.0058381 | 0.00055092 | 0.005761 | 0.00055092 | west | N | 0.00055092 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.005427 | west | Y | 0.0055798 | 0.0058381 | 0.00055092 | 0.005761 | 0.00055092 | west | N | 0.00055092 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.005427 | west | Y | 0.0055798 | 0.0058381 | 0.00055092 | 0.005761 | 0.00055092 | west | N | 0.00055092 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.005427 | west | Y | 0.0055798 | 0.0058381 | 0.00055092 | 0.005761 | 0.00055092 | west | N | 0.00055092 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.005427 | west | Y | 0.0055798 | 0.0058381 | 0.00055092 | 0.005761 | 0.00055092 | west | N | 0.00055092 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.004174 | west | Y | 0.0043268 | 0.0045851 | -0.00070208 | 0.004508 | 0.00070208 | west | N | 0.00070208 | 0
11057 | CHAMPION | 1 | 126.5 | 0.004174 | west | Y | 0.0043268 | 0.0045851 | -0.00070208 | 0.004508 | 0.00070208 | west | N | 0.00070208 | 0
11058 | PYRON_1G | 1 | 249 | 0.004174 | west | Y | 0.0043268 | 0.0045851 | -0.00070208 | 0.004508 | 0.00070208 | west | N | 0.00070208 | 0
11059 | INADALE_ | 1 | 197 | 0.004174 | west | Y | 0.0043268 | 0.0045851 | -0.00070208 | 0.004508 | 0.00070208 | west | N | 0.00070208 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.004775 | west | Y | 0.0049278 | 0.0051861 | -0.00010108 | 0.005109 | 0.00010108 | west | N | 0.00010108 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.004775 | west | Y | 0.0049278 | 0.0051861 | -0.00010108 | 0.005109 | 0.00010108 | west | N | 0.00010108 | 0
11147 | NOTREES_ | 1 | 149 | 0.005946 | west | Y | 0.0060988 | 0.0063571 | 0.0010699 | 0.00628 | 0.0010699 | west | N | 0.0010699 | 0
11309 | BULLCREK | 1 | 180 | 0.00532 | west | Y | 0.0054728 | 0.0057311 | 0.00044392 | 0.005654 | 0.00044392 | west | N | 0.00044392 | 0
11310 | BULLCREK | 1 | 180 | 0.00532 | west | Y | 0.0054728 | 0.0057311 | 0.00044392 | 0.005654 | 0.00044392 | west | N | 0.00044392 | 0
11320 | COYOTE_1 | 1 | 225 | 0.005383 | west | Y | 0.0055358 | 0.0057941 | 0.00050692 | 0.005717 | 0.00050692 | west | N | 0.00050692 | 0
11415 | LORAINE_ | 1 | 125 | 0.004373 | west | Y | 0.0045258 | 0.0047841 | -0.00050308 | 0.004707 | 0.00050308 | west | N | 0.00050308 | 0
11416 | LORAINE_ | 1 | 125 | 0.004373 | west | Y | 0.0045258 | 0.0047841 | -0.00050308 | 0.004707 | 0.00050308 | west | N | 0.00050308 | 0
11691 | KMICHICT | 1 | 140 | -5e-05 | north | N | 0.00010276 | 0.00036109 | -0.0049261 | 0.00028402 | 0.00010276 | North | N | 0.00010276 | 0
11692 | KMICHICT | 2 | 141 | -5e-05 | north | N | 0.00010276 | 0.00036109 | -0.0049261 | 0.00028402 | 0.00010276 | North | N | 0.00010276 | 0
11693 | KMICHIST | 3 | 309 | -5e-05 | north | N | 0.00010276 | 0.00036109 | -0.0049261 | 0.00028402 | 0.00010276 | North | N | 0.00010276 | 0
11694 | KMICHICT | 4 | 143 | -5e-05 | north | N | 0.00010276 | 0.00036109 | -0.0049261 | 0.00028402 | 0.00010276 | North | N | 0.00010276 | 0
11695 | KMICHICT | 5 | 144 | -5e-05 | north | N | 0.00010276 | 0.00036109 | -0.0049261 | 0.00028402 | 0.00010276 | North | N | 0.00010276 | 0
11696 | KMICHIST | 6 | 310 | -5e-05 | north | N | 0.00010276 | 0.00036109 | -0.0049261 | 0.00028402 | 0.00010276 | North | N | 0.00010276 | 0
12322 | ENNSTRAC | 1 | 196 | -0.000193 | north | Y | -4.0239e-05 | 0.00021809 | -0.0050691 | 0.00014102 | 4.0239e-05 | North | N | 4.0239e-05 | 0
12323 | ENNSTRAC | 2 | 111 | -0.000193 | north | Y | -4.0239e-05 | 0.00021809 | -0.0050691 | 0.00014102 | 4.0239e-05 | North | N | 4.0239e-05 | 0
12357 | RNRTPL_1 | 1 | 0 | -4.1e-05 | north | N | 0.00011176 | 0.00037009 | -0.0049171 | 0.00029302 | 0.00011176 | North | N | 0.00011176 | 0
12411 | FPLEFR1A | 1 | 161 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12412 | FPLEFR1B | 2 | 164 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12413 | FPLEFR1C | 3 | 164 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12414 | FPLEFR1S | 4 | 414 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12421 | FPLEFR2A | 1 | 162 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12422 | FPLEFR2B | 2 | 161 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12423 | FPLEFR2C | 3 | 163 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12424 | FPLEFR2S | 4 | 409 | -9.2e-05 | north | Y | 6.0761e-05 | 0.00031909 | -0.0049681 | 0.00024202 | 6.0761e-05 | North | N | 6.0761e-05 | 0
12440 | PARKD_1S | 1 | 0 | -9.5e-05 | north | N | 5.7761e-05 | 0.00031609 | -0.0049711 | 0.00023902 | 5.7761e-05 | North | N | 5.7761e-05 | 0
12449 | PARKD_2S | 1 | 0 | -9.5e-05 | north | N | 5.7761e-05 | 0.00031609 | -0.0049711 | 0.00023902 | 5.7761e-05 | North | N | 5.7761e-05 | 0
13116 | TGATEWAY | 1 | 148 | -0.000142 | north | N | 1.0761e-05 | 0.00026909 | -0.0050181 | 0.00019202 | 1.0761e-05 | North | N | 1.0761e-05 | 0
13117 | TGATEWAY | 2 | 130 | -0.000142 | north | N | 1.0761e-05 | 0.00026909 | -0.0050181 | 0.00019202 | 1.0761e-05 | North | N | 1.0761e-05 | 0
13118 | TGATEWAY | 3 | 145 | -0.000142 | north | N | 1.0761e-05 | 0.00026909 | -0.0050181 | 0.00019202 | 1.0761e-05 | North | N | 1.0761e-05 | 0
13119 | TGATEWAY | 4 | 399 | -0.000142 | north | N | 1.0761e-05 | 0.00026909 | -0.0050181 | 0.00019202 | 1.0761e-05 | North | N | 1.0761e-05 | 0
13131 | CALFREST | 1 | 150.7 | -0.000197 | north | Y | -4.4239e-05 | 0.00021409 | -0.0050731 | 0.00013702 | 4.4239e-05 | North | N | 4.4239e-05 | 0
13132 | CALFREST | 2 | 151 | -0.000197 | north | Y | -4.4239e-05 | 0.00021409 | -0.0050731 | 0.00013702 | 4.4239e-05 | North | N | 4.4239e-05 | 0
13133 | CALFREST | 3 | 177.4 | -0.000197 | north | Y | -4.4239e-05 | 0.00021409 | -0.0050731 | 0.00013702 | 4.4239e-05 | North | N | 4.4239e-05 | 0
13134 | CALFREST | 4 | 151.5 | -0.000196 | north | Y | -4.3239e-05 | 0.00021509 | -0.0050721 | 0.00013802 | 4.3239e-05 | North | N | 4.3239e-05 | 0
13135 | CALFREST | 5 | 152.3 | -0.000196 | north | Y | -4.3239e-05 | 0.00021509 | -0.0050721 | 0.00013802 | 4.3239e-05 | North | N | 4.3239e-05 | 0
13136 | CALFREST | 6 | 177.5 | -0.000196 | north | Y | -4.3239e-05 | 0.00021509 | -0.0050721 | 0.00013802 | 4.3239e-05 | North | N | 4.3239e-05 | 0
13432 | SANDOW_5 | 5 | 581 | -0.000521 | south | Y | -0.00036824 | -0.00010991 | -0.0053971 | -0.00018698 | 0.00010991 | south | N | 0.00010991 | 0
13691 | OAKGROVE | 1 | 855 | -0.000259 | north | Y | -0.00010624 | 0.00015209 | -0.0051351 | 7.5023e-05 | 7.5023e-05 | houston | Y | 0.00010624 | 0.02669
13692 | OAKGROVE | 2 | 855 | -0.000259 | north | Y | -0.00010624 | 0.00015209 | -0.0051351 | 7.5023e-05 | 7.5023e-05 | houston | Y | 0.00010624 | 0.02669
32798 | BRYN_TAM | 1 | 32 | -0.000295 | north | N | -0.00014224 | 0.00011609 | -0.0051711 | 3.9023e-05 | 3.9023e-05 | houston | Y | 0.00014224 | 0
32883 | BRYN_DNS | 1 | 48 | -0.000299 | north | Y | -0.00014624 | 0.00011209 | -0.0051751 | 3.5023e-05 | 3.5023e-05 | houston | Y | 0.00014624 | 0.0053384
32884 | BRYN_DNS | 1 | 46 | -0.000299 | north | Y | -0.00014624 | 0.00011209 | -0.0051751 | 3.5023e-05 | 3.5023e-05 | houston | Y | 0.00014624 | 0.0051159
32886 | BRYN_ATK | MB | 12 | -0.000295 | north | Y | -0.00014224 | 0.00011609 | -0.0051711 | 3.9023e-05 | 3.9023e-05 | houston | Y | 0.00014224 | 0
32887 | BRYN_ATK | MB | 51 | -0.000295 | north | Y | -0.00014224 | 0.00011609 | -0.0051711 | 3.9023e-05 | 3.9023e-05 | houston | Y | 0.00014224 | 0
32888 | BRYN_ATK | 1 | 17 | -0.000295 | north | Y | -0.00014224 | 0.00011609 | -0.0051711 | 3.9023e-05 | 3.9023e-05 | houston | Y | 0.00014224 | 0.0017547
32890 | BRYN_ATK | MB | 22 | -0.000295 | north | Y | -0.00014224 | 0.00011609 | -0.0051711 | 3.9023e-05 | 3.9023e-05 | houston | Y | 0.00014224 | 0
32891 | BRYN_ATK | MB | 25 | -0.000295 | north | Y | -0.00014224 | 0.00011609 | -0.0051711 | 3.9023e-05 | 3.9023e-05 | houston | Y | 0.00014224 | 0
32892 | BRYN_DNS | 1 | 105 | -0.000299 | north | Y | -0.00014624 | 0.00011209 | -0.0051751 | 3.5023e-05 | 3.5023e-05 | houston | Y | 0.00014624 | 0.011678
36998 | RDCNYNG1 | 1 | 84 | 0.004538 | west | Y | 0.0046908 | 0.0049491 | -0.00033808 | 0.004872 | 0.00033808 | west | N | 0.00033808 | 0
38332 | WDWRDU2 | 1 | 80 | 0.00807 | west | Y | 0.0082228 | 0.0084811 | 0.0031939 | 0.008404 | 0.0031939 | west | N | 0.0031939 | 0
38437 | TNSRBNMS | 1 | 150 | 0.008089 | west | Y | 0.0082418 | 0.0085001 | 0.0032129 | 0.008423 | 0.0032129 | west | N | 0.0032129 | 0
38438 | TNSRBNMS | 1 | 150 | 0.008089 | west | Y | 0.0082418 | 0.0085001 | 0.0032129 | 0.008423 | 0.0032129 | west | N | 0.0032129 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38600 | TNBP_CGN | 5 | 53 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38614 | TNBPAMCG | 4 | 96 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38615 | TNBPAMCG | 1 | 244 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38690 | TNBP_CGN | 3 | 40 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
39470 | TNDOWCGN | 1 | 32 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
39480 | TNDOWCGN | 1 | 30 | -0.000335 | houston | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | N | 9.7679e-07 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.000344 | houston | N | -0.00019124 | 6.7093e-05 | -0.0052201 | -9.9768e-06 | 9.9768e-06 | houston | N | 9.9768e-06 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.000344 | houston | N | -0.00019124 | 6.7093e-05 | -0.0052201 | -9.9768e-06 | 9.9768e-06 | houston | N | 9.9768e-06 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.000344 | houston | N | -0.00019124 | 6.7093e-05 | -0.0052201 | -9.9768e-06 | 9.9768e-06 | houston | N | 9.9768e-06 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.000344 | houston | N | -0.00019124 | 6.7093e-05 | -0.0052201 | -9.9768e-06 | 9.9768e-06 | houston | N | 9.9768e-06 | 0
39960 | TNTNPONE | 1 | 152.3 | -0.000259 | north | Y | -0.00010624 | 0.00015209 | -0.0051351 | 7.5023e-05 | 7.5023e-05 | houston | Y | 0.00010624 | 0.0047542
39970 | TNTNPONE | 1 | 153 | -0.000259 | north | Y | -0.00010624 | 0.00015209 | -0.0051351 | 7.5023e-05 | 7.5023e-05 | houston | Y | 0.00010624 | 0.004776
48500 | APD_GT1_ | 1 | 136 | -0.000329 | houston | N | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48510 | AK_GT1__ | 1 | 33 | -0.000338 | houston | N | -0.00018524 | 7.3093e-05 | -0.0052141 | -3.9768e-06 | 3.9768e-06 | houston | N | 3.9768e-06 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.000345 | houston | N | -0.00019224 | 6.6093e-05 | -0.0052211 | -1.0977e-05 | 1.0977e-05 | houston | N | 1.0977e-05 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.000345 | houston | N | -0.00019224 | 6.6093e-05 | -0.0052211 | -1.0977e-05 | 1.0977e-05 | houston | N | 1.0977e-05 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.000339 | houston | N | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.000339 | houston | N | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.000339 | houston | N | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.000331 | houston | N | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.000331 | houston | N | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.000331 | houston | N | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.000331 | houston | N | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.000332 | houston | N | -0.00017924 | 7.9093e-05 | -0.0052081 | 2.0232e-06 | 2.0232e-06 | houston | N | 2.0232e-06 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.000332 | houston | N | -0.00017924 | 7.9093e-05 | -0.0052081 | 2.0232e-06 | 2.0232e-06 | houston | N | 2.0232e-06 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.000332 | houston | N | -0.00017924 | 7.9093e-05 | -0.0052081 | 2.0232e-06 | 2.0232e-06 | houston | N | 2.0232e-06 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.000332 | houston | N | -0.00017924 | 7.9093e-05 | -0.0052081 | 2.0232e-06 | 2.0232e-06 | houston | N | 2.0232e-06 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.000332 | houston | N | -0.00017924 | 7.9093e-05 | -0.0052081 | 2.0232e-06 | 2.0232e-06 | houston | N | 2.0232e-06 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.000327 | houston | Y | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.000328 | houston | Y | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.000327 | houston | Y | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.000327 | houston | Y | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.000327 | houston | Y | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.000323 | houston | N | -0.00017024 | 8.8093e-05 | -0.0051991 | 1.1023e-05 | 1.1023e-05 | houston | N | 1.1023e-05 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.000329 | houston | N | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.000329 | houston | N | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.000326 | houston | N | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.000326 | houston | N | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.000326 | houston | N | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.000326 | houston | N | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48651 | EP_1_2 | 1 | 5 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48651 | EP_1_2 | 2 | 21 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.000292 | north | N | -0.00013924 | 0.00011909 | -0.0051681 | 4.2023e-05 | 4.2023e-05 | houston | Y | 0.00013924 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.000292 | north | N | -0.00013924 | 0.00011909 | -0.0051681 | 4.2023e-05 | 4.2023e-05 | houston | Y | 0.00013924 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.000292 | north | N | -0.00013924 | 0.00011909 | -0.0051681 | 4.2023e-05 | 4.2023e-05 | houston | Y | 0.00013924 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.000292 | north | N | -0.00013924 | 0.00011909 | -0.0051681 | 4.2023e-05 | 4.2023e-05 | houston | Y | 0.00013924 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.000326 | houston | Y | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48691 | GBY_7374 | A | 46 | -0.000331 | houston | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48691 | GBY_7374 | B | 46 | -0.000331 | houston | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48692 | GBY_8182 | C | 46 | -0.000331 | houston | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48692 | GBY_8182 | D | 55 | -0.000331 | houston | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48693 | GBY_8384 | E | 55 | -0.000331 | houston | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48693 | GBY_8384 | F | 54 | -0.000331 | houston | Y | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48721 | LEG_1___ | 1 | 827 | -0.000249 | north | Y | -9.6239e-05 | 0.00016209 | -0.0051251 | 8.5023e-05 | 8.5023e-05 | houston | Y | 9.6239e-05 | 0.0092755
48722 | LEG_2___ | 2 | 819 | -0.000249 | north | Y | -9.6239e-05 | 0.00016209 | -0.0051251 | 8.5023e-05 | 8.5023e-05 | houston | Y | 9.6239e-05 | 0.0091858
48730 | MNS_GT | 1 | 46.1 | -0.000339 | houston | N | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48731 | CBE_GT1 | 1 | 76 | -0.000357 | houston | Y | -0.00020424 | 5.4093e-05 | -0.0052331 | -2.2977e-05 | 2.2977e-05 | houston | N | 2.2977e-05 | 0
48732 | CBE_GT2 | 1 | 76 | -0.000357 | houston | Y | -0.00020424 | 5.4093e-05 | -0.0052331 | -2.2977e-05 | 2.2977e-05 | houston | N | 2.2977e-05 | 0
48733 | CBE_ST12 | 1 | 105 | -0.000357 | houston | Y | -0.00020424 | 5.4093e-05 | -0.0052331 | -2.2977e-05 | 2.2977e-05 | houston | N | 2.2977e-05 | 0
48734 | CBE_GT3 | 1 | 74 | -0.000357 | houston | Y | -0.00020424 | 5.4093e-05 | -0.0052331 | -2.2977e-05 | 2.2977e-05 | houston | N | 2.2977e-05 | 0
48735 | CBE_GT4 | 1 | 74 | -0.000357 | houston | Y | -0.00020424 | 5.4093e-05 | -0.0052331 | -2.2977e-05 | 2.2977e-05 | houston | N | 2.2977e-05 | 0
48736 | CBE_ST34 | 1 | 102 | -0.000357 | houston | Y | -0.00020424 | 5.4093e-05 | -0.0052331 | -2.2977e-05 | 2.2977e-05 | houston | N | 2.2977e-05 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48761 | PR_GT1__ | 1 | 35 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48772 | PHR_GN2_ | MB | 459 | -0.000333 | houston | Y | -0.00018024 | 7.8093e-05 | -0.0052091 | 1.0232e-06 | 1.0232e-06 | houston | N | 1.0232e-06 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.000323 | houston | N | -0.00017024 | 8.8093e-05 | -0.0051991 | 1.1023e-05 | 1.1023e-05 | houston | N | 1.1023e-05 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.000323 | houston | N | -0.00017024 | 8.8093e-05 | -0.0051991 | 1.1023e-05 | 1.1023e-05 | houston | N | 1.1023e-05 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.000323 | houston | N | -0.00017024 | 8.8093e-05 | -0.0051991 | 1.1023e-05 | 1.1023e-05 | houston | N | 1.1023e-05 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.000323 | houston | N | -0.00017024 | 8.8093e-05 | -0.0051991 | 1.1023e-05 | 1.1023e-05 | houston | N | 1.1023e-05 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.000327 | houston | N | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
48820 | SHELLG1_ | 1 | 71 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48821 | SHELLG2 | 2 | 72 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48822 | SHELLG3_ | 1 | 39 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48822 | SHELLG3_ | 2 | 30 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.000331 | houston | N | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.000331 | houston | N | -0.00017824 | 8.0093e-05 | -0.0052071 | 3.0232e-06 | 3.0232e-06 | houston | N | 3.0232e-06 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.00033 | houston | N | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.00033 | houston | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.00033 | houston | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.00033 | houston | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.00033 | houston | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48855 | SRB_GT21 | B2 | 12 | -0.00033 | houston | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48855 | SRB_GT21 | MB | 18 | -0.00033 | houston | Y | -0.00017724 | 8.1093e-05 | -0.0052061 | 4.0232e-06 | 4.0232e-06 | houston | N | 4.0232e-06 | 0
48865 | TECO_GT1 | 1 | 50 | -0.000334 | houston | Y | -0.00018124 | 7.7093e-05 | -0.0052101 | 2.3211e-08 | 2.3211e-08 | houston | N | 2.3211e-08 | 0
48873 | THW_ST3_ | 3 | 104 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48874 | THW_ST4_ | 4 | 104 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48875 | THW_3132 | A | 54 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48875 | THW_3132 | B | 53 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48877 | THW_3334 | C | 54 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48877 | THW_3334 | D | 57 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48879 | THW_4142 | E | 54 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48879 | THW_4142 | F | 54 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48881 | THW_4344 | G | 58 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48881 | THW_4344 | H | 58 | -0.000329 | houston | Y | -0.00017624 | 8.2093e-05 | -0.0052051 | 5.0232e-06 | 5.0232e-06 | houston | N | 5.0232e-06 | 0
48883 | THW_GT1_ | B2 | 12 | -0.000328 | houston | Y | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
48885 | THW_5152 | A | 56 | -0.000326 | houston | Y | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48885 | THW_5152 | B | 59 | -0.000326 | houston | Y | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48886 | THW_5354 | C | 56 | -0.000326 | houston | Y | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48886 | THW_5354 | D | 56 | -0.000326 | houston | Y | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48887 | THW_5556 | E | 59 | -0.000326 | houston | Y | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48887 | THW_5556 | F | 56 | -0.000326 | houston | Y | -0.00017324 | 8.5093e-05 | -0.0052021 | 8.0232e-06 | 8.0232e-06 | houston | N | 8.0232e-06 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.000352 | houston | Y | -0.00019924 | 5.9093e-05 | -0.0052281 | -1.7977e-05 | 1.7977e-05 | houston | N | 1.7977e-05 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.000339 | houston | N | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48929 | WAPGT21_ | B1 | 13 | -0.000339 | houston | Y | -0.00018624 | 7.2093e-05 | -0.0052151 | -4.9768e-06 | 4.9768e-06 | houston | N | 4.9768e-06 | 0
48940 | WARVUE_G | G1 | 12 | -0.000327 | houston | Y | -0.00017424 | 8.4093e-05 | -0.0052031 | 7.0232e-06 | 7.0232e-06 | houston | N | 7.0232e-06 | 0
49803 | EXN_15GT | 1 | 34 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49826 | EXN938GT | 5 | 45.9 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49828 | EXN941GT | 10 | 17.7 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49829 | EXN942GT | 11 | 20.4 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49830 | EXN943GT | 12 | 19.9 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49831 | EXN944GT | 13 | 35 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49832 | EXN945GT | 9 | 18 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49837 | EXN_GT | 4 | 85.4 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49838 | EXN_14GT | 14 | 148 | -0.000328 | houston | N | -0.00017524 | 8.3093e-05 | -0.0052041 | 6.0232e-06 | 6.0232e-06 | houston | N | 6.0232e-06 | 0
49851 | DOW17000 | 37 | 62 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49858 | DOW38100 | 31 | 71.4 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49859 | DOW38200 | 33 | 45 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49860 | DOW38300 | 32 | 101 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49862 | DOW39100 | 36 | 86 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49863 | DOW39200 | 35 | 88 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49865 | DOW41000 | 41 | 50 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49866 | DOW42000 | 42 | 18 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49869 | DOW49000 | 45 | 94 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49870 | DOW61000 | 61 | 70 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49871 | DOW62000 | 62 | 63 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49872 | DOW63000 | 63 | 72 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49873 | DOW64000 | 64 | 64.8 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49876 | DOW65000 | 65 | 101 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49877 | DOW66000 | 66 | 97 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49878 | DOW67000 | 67 | 103 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49882 | DOW81000 | 81 | 76 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49884 | DOW82000 | 82 | 80 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49885 | DOW83000 | 83 | 80 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
49886 | DOW84000 | 84 | 171 | -0.000347 | houston | N | -0.00019424 | 6.4093e-05 | -0.0052231 | -1.2977e-05 | 1.2977e-05 | houston | N | 1.2977e-05 | 0
58909 | PEARSALL | 1 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58909 | PEARSALL | 2 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58909 | PEARSALL | 3 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58909 | PEARSALL | 4 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58909 | PEARSALL | 5 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58909 | PEARSALL | 6 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58919 | PEARSALL | 1 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58919 | PEARSALL | 2 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58919 | PEARSALL | 3 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58919 | PEARSALL | 4 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58919 | PEARSALL | 5 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58919 | PEARSALL | 6 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58929 | PEARSALL | 1 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58929 | PEARSALL | 2 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58929 | PEARSALL | 3 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58929 | PEARSALL | 4 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58929 | PEARSALL | 5 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58929 | PEARSALL | 6 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58949 | PEARSALL | 1 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58949 | PEARSALL | 2 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58949 | PEARSALL | 3 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58949 | PEARSALL | 4 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58949 | PEARSALL | 5 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
58949 | PEARSALL | 6 | 8.4 | 0.000159 | south | Y | 0.00031176 | 0.00057009 | -0.0047171 | 0.00049302 | 0.00031176 | North | Y | 0.00057009 | 0.00217
60000 | DSKY2 | 1 | 76.5 | 0.008929 | west | Y | 0.0090818 | 0.0093401 | 0.0040529 | 0.009263 | 0.0040529 | west | N | 0.0040529 | 0
60003 | KING_NE1 | 1 | 80 | 0.00807 | west | Y | 0.0082228 | 0.0084811 | 0.0031939 | 0.008404 | 0.0031939 | west | N | 0.0031939 | 0
60005 | KING_SE1 | 1 | 40 | 0.00807 | west | Y | 0.0082228 | 0.0084811 | 0.0031939 | 0.008404 | 0.0031939 | west | N | 0.0031939 | 0
60007 | KING_SW1 | 1 | 80 | 0.008018 | west | Y | 0.0081708 | 0.0084291 | 0.0031419 | 0.008352 | 0.0031419 | west | N | 0.0031419 | 0
60016 | WOODWRD1 | 1 | 80 | 0.008066 | west | Y | 0.0082188 | 0.0084771 | 0.0031899 | 0.0084 | 0.0031899 | west | N | 0.0031899 | 0
60017 | ORNNWP1 | 1 | 80 | 0.00851 | west | Y | 0.0086628 | 0.0089211 | 0.0036339 | 0.008844 | 0.0036339 | west | N | 0.0036339 | 0
60018 | DSKY1 | 1 | 84 | 0.008653 | west | Y | 0.0088058 | 0.0090641 | 0.0037769 | 0.008987 | 0.0037769 | west | N | 0.0037769 | 0
60019 | KING_NW1 | 1 | 80 | 0.008018 | west | Y | 0.0081708 | 0.0084291 | 0.0031419 | 0.008352 | 0.0031419 | west | N | 0.0031419 | 0
60057 | CALLAHAN | 1 | 114 | -0.000415 | south | Y | -0.00026224 | -3.9068e-06 | -0.0052911 | -8.0977e-05 | 3.9068e-06 | south | N | 3.9068e-06 | 0
60058 | BUFF_GAP | 1 | 120 | 0.003354 | west | Y | 0.0035068 | 0.0037651 | -0.0015221 | 0.003688 | 0.0015221 | west | N | 0.0015221 | 0
60060 | CIRELLO | 1 | 233 | 0.003354 | west | Y | 0.0035068 | 0.0037651 | -0.0015221 | 0.003688 | 0.0015221 | west | N | 0.0015221 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.003354 | west | Y | 0.0035068 | 0.0037651 | -0.0015221 | 0.003688 | 0.0015221 | west | N | 0.0015221 | 0
60066 | H_HOLLOW | 1 | 222 | -0.000415 | south | Y | -0.00026224 | -3.9068e-06 | -0.0052911 | -8.0977e-05 | 3.9068e-06 | south | N | 3.9068e-06 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.000415 | south | Y | -0.00026224 | -3.9068e-06 | -0.0052911 | -8.0977e-05 | 3.9068e-06 | south | N | 3.9068e-06 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.000415 | south | Y | -0.00026224 | -3.9068e-06 | -0.0052911 | -8.0977e-05 | 3.9068e-06 | south | N | 3.9068e-06 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.000415 | south | Y | -0.00026224 | -3.9068e-06 | -0.0052911 | -8.0977e-05 | 3.9068e-06 | south | N | 3.9068e-06 | 0
60074 | HORSH5 | 1 | 100 | -0.000415 | south | Y | -0.00026224 | -3.9068e-06 | -0.0052911 | -8.0977e-05 | 3.9068e-06 | south | N | 3.9068e-06 | 0
60081 | WHRLWIND | 1 | 60 | 0.002654 | west | Y | 0.0028068 | 0.0030651 | -0.0022221 | 0.002988 | 0.0022221 | west | N | 0.0022221 | 0
60201 | RIO DRCS | F | 0 | 0.001573 | south | N | 0.0017258 | 0.0019841 | -0.0033031 | 0.001907 | 0.0017258 | North | Y | 0.0019841 | 0
60202 | FRIEND_R | F | 0 | 0.011106 | west | N | 0.011259 | 0.011517 | 0.0062299 | 0.01144 | 0.0062299 | west | N | 0.0062299 | 0
60203 | PRES0A | BT | 4.8 | 0.007321 | west | N | 0.0074738 | 0.0077321 | 0.0024449 | 0.007655 | 0.0024449 | west | N | 0.0024449 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.00389 | west | Y | 0.0040428 | 0.0043011 | -0.00098608 | 0.004224 | 0.00098608 | west | N | 0.00098608 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.00389 | west | Y | 0.0040428 | 0.0043011 | -0.00098608 | 0.004224 | 0.00098608 | west | N | 0.00098608 | 0
71057 | L_SWEETW | W1 | 135 | 0.00389 | west | Y | 0.0040428 | 0.0043011 | -0.00098608 | 0.004224 | 0.00098608 | west | N | 0.00098608 | 0
71059 | L_SWEETW | W1 | 119 | 0.00389 | west | Y | 0.0040428 | 0.0043011 | -0.00098608 | 0.004224 | 0.00098608 | west | N | 0.00098608 | 0
71060 | L_SWEETW | W1 | 105 | 0.00389 | west | Y | 0.0040428 | 0.0043011 | -0.00098608 | 0.004224 | 0.00098608 | west | N | 0.00098608 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.00389 | west | Y | 0.0040428 | 0.0043011 | -0.00098608 | 0.004224 | 0.00098608 | west | N | 0.00098608 | 0
76031 | L_GASCCR | W1 | 150 | 0.005377 | west | Y | 0.0055298 | 0.0057881 | 0.00050092 | 0.005711 | 0.00050092 | west | N | 0.00050092 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.005528 | west | Y | 0.0056808 | 0.0059391 | 0.00065192 | 0.005862 | 0.00065192 | west | N | 0.00065192 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.005528 | west | Y | 0.0056808 | 0.0059391 | 0.00065192 | 0.005862 | 0.00065192 | west | N | 0.00065192 | 0
76096 | L_CAPRSI | W1 | 186 | 0.005528 | west | Y | 0.0056808 | 0.0059391 | 0.00065192 | 0.005862 | 0.00065192 | west | N | 0.00065192 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.005528 | west | Y | 0.0056808 | 0.0059391 | 0.00065192 | 0.005862 | 0.00065192 | west | N | 0.00065192 | 0
80003 | MILHWYS | F | 0 | -0.000301 | south | N | -0.00014824 | 0.00011009 | -0.0051771 | 3.3023e-05 | 3.3023e-05 | houston | Y | 0.00011009 | 0
80010 | EPLVT1 | F | 0 | 0.001728 | south | N | 0.0018808 | 0.0021391 | -0.0031481 | 0.002062 | 0.0018808 | North | Y | 0.0021391 | 0
80012 | LAR | F | 0 | -6.4e-05 | south | N | 8.8761e-05 | 0.00034709 | -0.0049401 | 0.00027002 | 8.8761e-05 | North | Y | 0.00034709 | 0
80051 | FORPVCM0 | 8 | 28 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
80053 | FOR69CG0 | 10 | 74 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
80080 | GWINDT11 | 1 | 94 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0072446
80080 | GWINDT11 | 2 | 41 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0031599
80080 | GWINDT11 | 3 | 38 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0029287
80080 | GWINDT11 | 4 | 19 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0014643
80081 | GWINDT21 | 1 | 94 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0072446
80081 | GWINDT21 | 2 | 36 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0027745
80081 | GWINDT21 | 3 | 43 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.003314
80081 | GWINDT21 | 4 | 22 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0016955
80137 | CSDR89 | 8 | 39 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
80137 | CSDR89 | 9 | 15 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
80138 | CSDR7 | 7 | 7 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
80139 | CSDR56 | 5 | 15 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
80139 | CSDR56 | 6 | 39 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
80140 | CSDR11 | 11 | 39 | -0.000336 | south | N | -0.00018324 | 7.5093e-05 | -0.0052121 | -1.9768e-06 | 1.9768e-06 | houston | Y | 7.5093e-05 | 0
80180 | PNSCALT1 | 1 | 148 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.011406
80180 | PNSCALT1 | 2 | 50 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0038535
80181 | PNSCALT2 | 1 | 55 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0042389
80181 | PNSCALT2 | 2 | 50 | -0.000304 | south | Y | -0.00015124 | 0.00010709 | -0.0051801 | 3.0023e-05 | 3.0023e-05 | houston | Y | 0.00010709 | 0.0038535
80223 | REYSHR G | 1 | 12 | -0.000314 | south | N | -0.00016124 | 9.7093e-05 | -0.0051901 | 2.0023e-05 | 2.0023e-05 | houston | Y | 9.7093e-05 | 0
80224 | VISTRONG | 1 | 15 | -0.000337 | south | N | -0.00018424 | 7.4093e-05 | -0.0052131 | -2.9768e-06 | 2.9768e-06 | houston | Y | 7.4093e-05 | 0
80225 | VISTRONG | 2 | 23 | -0.000337 | south | N | -0.00018424 | 7.4093e-05 | -0.0052131 | -2.9768e-06 | 2.9768e-06 | houston | Y | 7.4093e-05 | 0
80226 | ALCOA G | 1 | 48 | -0.00034 | south | N | -0.00018724 | 7.1093e-05 | -0.0052161 | -5.9768e-06 | 5.9768e-06 | houston | Y | 7.1093e-05 | 0
80227 | AIRCO G | 1 | 8 | -0.000335 | south | N | -0.00018224 | 7.6093e-05 | -0.0052111 | -9.7679e-07 | 9.7679e-07 | houston | Y | 7.6093e-05 | 0
80261 | NBEC81A | 1 | 180 | -0.000311 | south | Y | -0.00015824 | 0.00010009 | -0.0051871 | 2.3023e-05 | 2.3023e-05 | houston | Y | 0.00010009 | 0.013873
80262 | NBEC91A | 1 | 180 | -0.000311 | south | Y | -0.00015824 | 0.00010009 | -0.0051871 | 2.3023e-05 | 2.3023e-05 | houston | Y | 0.00010009 | 0.013873
80263 | B_DAVIS3 | 3 | 180 | -0.00031 | south | Y | -0.00015724 | 0.00010109 | -0.0051861 | 2.4023e-05 | 2.4023e-05 | houston | Y | 0.00010109 | 0.013873
80264 | B_DAVIS4 | 4 | 180 | -0.00031 | south | Y | -0.00015724 | 0.00010109 | -0.0051861 | 2.4023e-05 | 2.4023e-05 | houston | Y | 0.00010109 | 0.013873
80265 | LARECU40 | 4 | 100 | -6.4e-05 | south | Y | 8.8761e-05 | 0.00034709 | -0.0049401 | 0.00027002 | 8.8761e-05 | North | Y | 0.00034709 | 0.025833
80266 | LARECU50 | 5 | 100 | -6.4e-05 | south | Y | 8.8761e-05 | 0.00034709 | -0.0049401 | 0.00027002 | 8.8761e-05 | North | Y | 0.00034709 | 0.025833
80291 | PAPALOTE | 1 | 25 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0019268
80291 | PAPALOTE | 2 | 25 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0019268
80291 | PAPALOTE | 3 | 25 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0019268
80291 | PAPALOTE | 4 | 16 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0012331
80294 | PAPALOTE | 5 | 25 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0019268
80294 | PAPALOTE | 6 | 25 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0019268
80294 | PAPALOTE | 7 | 25 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0019268
80294 | PAPALOTE | 8 | 15 | -0.000313 | south | Y | -0.00016024 | 9.8093e-05 | -0.0051891 | 2.1023e-05 | 2.1023e-05 | houston | Y | 9.8093e-05 | 0.0011561
86104 | CID-138 | EQ | 0 | -6.4e-05 | south | N | 8.8761e-05 | 0.00034709 | -0.0049401 | 0.00027002 | 8.8761e-05 | North | Y | 0.00034709 | 0
86105 | CID-230 | EQ | 500 | -6.4e-05 | south | N | 8.8761e-05 | 0.00034709 | -0.0049401 | 0.00027002 | 8.8761e-05 | North | Y | 0.00034709 | 0
86106 | CUF-230 | EQ | 500 | -6.4e-05 | south | N | 8.8761e-05 | 0.00034709 | -0.0049401 | 0.00027002 | 8.8761e-05 | North | Y | 0.00034709 | 0
86107 | CUF-138 | EQ | 0 | -6.4e-05 | south | N | 8.8761e-05 | 0.00034709 | -0.0049401 | 0.00027002 | 8.8761e-05 | North | Y | 0.00034709 | 0
88198 | BEEVILLE | F | 0 | -0.000289 | south | N | -0.00013624 | 0.00012209 | -0.0051651 | 4.5023e-05 | 4.5023e-05 | houston | Y | 0.00012209 | 0
88253 | HAMILTON | F | 0 | 0.002788 | south | N | 0.0029408 | 0.0031991 | -0.0020881 | 0.003122 | 0.0020881 | west | Y | 0.0031991 | 0
88299 | ZAPATA | F | 0 | -0.000139 | south | N | 1.3761e-05 | 0.00027209 | -0.0050151 | 0.00019502 | 1.3761e-05 | North | Y | 0.00027209 | 0
88508 | FALFURRI | F | 0 | -0.00027 | south | N | -0.00011724 | 0.00014109 | -0.0051461 | 6.4023e-05 | 6.4023e-05 | houston | Y | 0.00014109 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:6410 MILES - 6411 ROWE2A C:OAK Creek - Ballinger [6335 - 6340] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.1316 | 6.6 | 0.020068 | 0.13245 | 6.6 | 0.13245
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68391 | 34.3 | 0.020068 | 0.68835 | 40.9 | 0.8208
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.011106 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.011235 | 0 | 40.9 | 0.8208
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.010243 | west | 8 | N | N | Nwest | Nwest | 1 | 0.26427 | 0 | 0.010372 | 0 | 40.9 | 0.8208 | Weighted Shift Factors
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.008929 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68307 | 76.5 | 0.0090584 | 0.69297 |  |  | West | 0.0048761
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.008653 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.72685 | 84 | 0.0087824 | 0.73772 |  |  | North | -0.00012938
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.00851 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6808 | 80 | 0.0086394 | 0.69115 |  |  |  | 0.0050055
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.008089 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2133 | 150 | 0.0082184 | 1.2328
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.008089 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2133 | 150 | 0.0082184 | 1.2328 |  |  | Line Rating | 30
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.60525 | 75 | 0.0081994 | 0.61495 |  |  | Conc Gen | 40.9
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6456 | 80 | 0.0081994 | 0.65595 |  |  | Weighted Imp. | 0.8208
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.3228 | 40 | 0.0081994 | 0.32798 |  |  | PTDF | 0.020068
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6456 | 80 | 0.0081994 | 0.65595
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.008066 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64528 | 80 | 0.0081954 | 0.65563 |  |  | Concentration | 4.0093
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.008018 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64144 | 80 | 0.0081474 | 0.65179
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.008018 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64144 | 80 | 0.0081474 | 0.65179
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.007321 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.035141 | 0 | 0.0074504 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.006888 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82656 | 120 | 0.0070174 | 0.84209
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.006847 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82164 | 120 | 0.0069764 | 0.83717
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.006489 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.65214 | 100.5 | 0.0066184 | 0.66515
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.006398 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9597 | 150 | 0.0065274 | 0.97911
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.005968 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20888 | 35 | 0.0060974 | 0.21341
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.005968 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.17904 | 30 | 0.0060974 | 0.18292
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39376 | 66 | 0.0060954 | 0.4023
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38779 | 65 | 0.0060954 | 0.3962
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39972 | 67 | 0.0060954 | 0.40839
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39972 | 67 | 0.0060954 | 0.40839
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39972 | 67 | 0.0060954 | 0.40839
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.005966 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060954 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.005966 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060954 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88595 | 149 | 0.0060754 | 0.90523
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.005827 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.33797 | 58 | 0.0059564 | 0.34547
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.00569 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2188 | 214.2 | 0.0058194 | 1.2465
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6219 | 112.5 | 0.0056574 | 0.63646
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82644 | 149.5 | 0.0056574 | 0.84578
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0282 | 186 | 0.0056574 | 1.0523
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1858 | 214.5 | 0.0056574 | 1.2135
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1299 | 208.2 | 0.0055564 | 1.1568
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.77118 | 142.1 | 0.0055564 | 0.78956
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.71853 | 132.4 | 0.0055564 | 0.73567
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.73807 | 136 | 0.0055564 | 0.75567
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79777 | 147 | 0.0055564 | 0.81679
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1397 | 210 | 0.0055564 | 1.1668
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3794 | 70 | 0.0055494 | 0.38846
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3794 | 70 | 0.0055494 | 0.38846
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.50298 | 92.8 | 0.0055494 | 0.51498
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4336 | 80 | 0.0055494 | 0.44395
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4336 | 80 | 0.0055494 | 0.44395
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.6233 | 115 | 0.0055494 | 0.63818
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005383 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2112 | 225 | 0.0055124 | 1.2403
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.005377 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.80655 | 150 | 0.0055064 | 0.82596
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.00532 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9576 | 180 | 0.0054494 | 0.98089
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.00532 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9576 | 180 | 0.0054494 | 0.98089
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 1 | 0.34587 | 0 | 0.0050704 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 1 | 0.36267 | 0 | 0.0050704 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 1 | 0.34785 | 0 | 0.0050704 | 0
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.004901 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.30876 | 63 | 0.0050304 | 0.31691
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.32023 | 66 | 0.0049814 | 0.32877
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.33479 | 69 | 0.0049814 | 0.34372
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.33479 | 69 | 0.0049814 | 0.34372
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.32508 | 67 | 0.0049814 | 0.33375
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.32508 | 67 | 0.0049814 | 0.33375
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.31538 | 65 | 0.0049814 | 0.32379
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.004797 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67638 | 141 | 0.0049264 | 0.69462
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.004797 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57564 | 120 | 0.0049264 | 0.59117
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71625 | 150 | 0.0049044 | 0.73566
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0505 | 220 | 0.0049044 | 1.079
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.955 | 200 | 0.0049044 | 0.98088
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.58207 | 121.9 | 0.0049044 | 0.59784
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.004771 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.47233 | 99 | 0.0049004 | 0.48514
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.004771 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.29103 | 61 | 0.0049004 | 0.29892
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 1 | 0.11928 | 0 | 0.0049004 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 1 | 0.21803 | 0 | 0.0049004 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 1 | 0.21803 | 0 | 0.0049004 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.004538 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.38119 | 84 | 0.0046674 | 0.39206
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.004373 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.54663 | 125 | 0.0045024 | 0.5628
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.004373 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.54663 | 125 | 0.0045024 | 0.5628
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.87237 | 209 | 0.0043034 | 0.89941
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52801 | 126.5 | 0.0043034 | 0.54438
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0393 | 249 | 0.0043034 | 1.0715
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82228 | 197 | 0.0043034 | 0.84777
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.004087 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69275 | 169.5 | 0.0042164 | 0.71468
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.14588 | 37.5 | 0.0040194 | 0.15073
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.41818 | 107.5 | 0.0040194 | 0.43208
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52515 | 135 | 0.0040194 | 0.54262
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46291 | 119 | 0.0040194 | 0.47831
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.40845 | 105 | 0.0040194 | 0.42204
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.31315 | 80.5 | 0.0040194 | 0.32356
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.003517 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52755 | 150 | 0.0036464 | 0.54696
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.40248 | 120 | 0.0034834 | 0.41801
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.78148 | 233 | 0.0034834 | 0.81163
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57085 | 170.2 | 0.0034834 | 0.59287
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.002654 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.15924 | 60 | 0.0027834 | 0.167
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.002648 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0592 | 400 | 0.0027774 | 1.111
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.002647 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.62469 | 236 | 0.0027764 | 0.65523
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.002328 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.38412 | 165 | 0.0024574 | 0.40547
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.002105 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.31575 | 150 | 0.0022344 | 0.33516
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.002105 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2126 | 101 | 0.0022344 | 0.22567
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.001905 | west | 4 | Y | N | Ywest | Nwest | 1 | 1.2377 | 649.7 | 0.0020344 | 1.3217
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.001573 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.0017024 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.001315 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.48129 | 366 | 0.0014444 | 0.52864
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.02134 | 20 | 0.0011964 | 0.023928
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.02134 | 20 | 0.0011964 | 0.023928
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.02134 | 20 | 0.0011964 | 0.023928
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.018139 | 17 | 0.0011964 | 0.020338
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.1324 | 204 | 0.00077838 | 0.15879
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13045 | 201 | 0.00077838 | 0.15645
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.15706 | 242 | 0.00077838 | 0.18837
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.00059 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.14278 | 242 | 0.00071938 | 0.17409
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.000113 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.012712 | 112.5 | 0.00024238 | 0.027268
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 9.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.00546 | 60 | 0.00022038 | 0.013223
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 9.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.005733 | 63 | 0.00022038 | 0.013884
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 6.5e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.00078 | 0 | 0.00019438 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 6.5e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.00078 | 0 | 0.00019438 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 4.9e-05 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00017838 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 4.9e-05 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00017838 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 4.9e-05 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00017838 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 6e-06 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.00072 | 120 | 0.00013538 | 0.016246
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00012938 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.00012938 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -2e-05 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00010938 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -3.7e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00148 | 0 | 9.2382e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -3.7e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00148 | 0 | 9.2382e-05 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -4.1e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 8.8382e-05 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -4.3e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.00731 | 170 | 8.6382e-05 | 0.014685
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -4.3e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.02236 | 520 | 8.6382e-05 | 0.044919
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -5e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.0185 | 370 | 7.9382e-05 | 0.029371
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.007 | 0 | 7.9382e-05 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00705 | 0 | 7.9382e-05 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.01545 | 0 | 7.9382e-05 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00715 | 0 | 7.9382e-05 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.0072 | 0 | 7.9382e-05 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.0155 | 0 | 7.9382e-05 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.00848 | 160 | 7.6382e-05 | 0.012221
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.008268 | 156 | 7.6382e-05 | 0.011916
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.010388 | 196 | 7.6382e-05 | 0.014971
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.008268 | 156 | 7.6382e-05 | 0.011916
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.008321 | 157 | 7.6382e-05 | 0.011992
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.010494 | 198 | 7.6382e-05 | 0.015124
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.00405 | 0 | 7.5382e-05 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.0042984 | 0 | 7.5382e-05 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.0047736 | 0 | 7.5382e-05 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.032364 | 558 | 7.1382e-05 | 0.039831
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.033582 | 579 | 7.1382e-05 | 0.04133
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.046864 | 808 | 7.1382e-05 | 0.057677
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.019008 | 288 | 6.3382e-05 | 0.018254
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.009702 | 147 | 6.3382e-05 | 0.0093172
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.009702 | 147 | 6.3382e-05 | 0.0093172
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.005609 | 79 | 5.8382e-05 | 0.0046122
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.007526 | 106 | 5.8382e-05 | 0.0061885
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.010366 | 146 | 5.8382e-05 | 0.0085238
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -7.1e-05 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.005396 | 76 | 5.8382e-05 | 0.0044371
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.00148 | 20 | 5.5382e-05 | 0.0011076
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.00185 | 25 | 5.5382e-05 | 0.0013846
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.003034 | 41 | 5.5382e-05 | 0.0022707
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -7.5e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.003 | 40 | 5.4382e-05 | 0.0021753
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -8.3e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.032785 | 395 | 4.6382e-05 | 0.018321
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -8.3e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.036105 | 435 | 4.6382e-05 | 0.020176
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -8.4e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.03654 | 435 | 4.5382e-05 | 0.019741
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -9e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.03492 | 388 | 3.9382e-05 | 0.01528
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -9e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.04635 | 515 | 3.9382e-05 | 0.020282
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014812 | 161 | 3.7382e-05 | 0.0060186
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.015088 | 164 | 3.7382e-05 | 0.0061307
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.015088 | 164 | 3.7382e-05 | 0.0061307
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.038088 | 414 | 3.7382e-05 | 0.015476
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014904 | 162 | 3.7382e-05 | 0.0060559
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014812 | 161 | 3.7382e-05 | 0.0060186
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014996 | 163 | 3.7382e-05 | 0.0060933
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.037628 | 409 | 3.7382e-05 | 0.015289
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -9.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 3.4382e-05 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -9.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 3.4382e-05 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.000112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.013216 | 118 | 1.7382e-05 | 0.0020511
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.000112 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.01288 | 115 | 1.7382e-05 | 0.001999
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.000112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.062272 | 556 | 1.7382e-05 | 0.0096646
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.10676 | 785 | -6.6177e-06 | -0.0051949
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.10812 | 795 | -6.6177e-06 | -0.0052611
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.10608 | 780 | -6.6177e-06 | -0.0051618
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.021016 | 0 | -1.2618e-05 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.01846 | 0 | -1.2618e-05 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.02059 | 0 | -1.2618e-05 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.056658 | 0 | -1.2618e-05 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.000147 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -1.7618e-05 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.000148 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.0074 | 50 | -1.8618e-05 | -0.00093088
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.000149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.027118 | 182 | -1.9618e-05 | -0.0035704
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.000149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.072116 | 484 | -1.9618e-05 | -0.009495
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.000166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.035922 | 216.4 | -3.6618e-05 | -0.0079241
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.000166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.035873 | 216.1 | -3.6618e-05 | -0.0079131
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.000193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.037828 | 196 | -6.3618e-05 | -0.012469
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.000193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.021423 | 111 | -6.3618e-05 | -0.0070616
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.000193 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.043232 | 224 | -6.3618e-05 | -0.01425
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029694 | 151.5 | -6.6618e-05 | -0.010093
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029851 | 152.3 | -6.6618e-05 | -0.010146
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.03479 | 177.5 | -6.6618e-05 | -0.011825
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029688 | 150.7 | -6.7618e-05 | -0.01019
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029747 | 151 | -6.7618e-05 | -0.01021
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.034948 | 177.4 | -6.7618e-05 | -0.011995
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.045248 | 224 | -7.2618e-05 | -0.016266
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.045652 | 226 | -7.2618e-05 | -0.016412
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.042824 | 212 | -7.2618e-05 | -0.015395
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.042622 | 211 | -7.2618e-05 | -0.015322
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.000207 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.12731 | 615 | -7.7618e-05 | -0.047735
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.000207 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.12151 | 587 | -7.7618e-05 | -0.045562
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.000249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.20592 | 827 | -0.00011962 | -0.098924
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.000249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.20393 | 819 | -0.00011962 | -0.097967
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.000259 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00012962 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.22145 | 855 | -0.00012962 | -0.11082
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.22145 | 855 | -0.00012962 | -0.11082
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.039446 | 152.3 | -0.00012962 | -0.019741
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.039627 | 153 | -0.00012962 | -0.019832
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.000285 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.13195 | 463 | -0.00015562 | -0.072051
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.045026 | 0 | -0.00016262 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.045552 | 0 | -0.00016262 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.045552 | 0 | -0.00016262 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.11096 | 0 | -0.00016262 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.000295 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.00944 | 0 | -0.00016562 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.000295 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.005015 | 17 | -0.00016562 | -0.0028155
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.000299 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.014352 | 48 | -0.00016962 | -0.0081416
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.000299 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.013754 | 46 | -0.00016962 | -0.0078024
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.000299 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.031395 | 105 | -0.00016962 | -0.01781
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.075403 | 217.3 | -0.00021762 | -0.047288
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.071135 | 205 | -0.00021762 | -0.044612
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.094523 | 272.4 | -0.00021762 | -0.059279
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.006588 | 18 | -0.00023662 | -0.0042591
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.006588 | 18 | -0.00023662 | -0.0042591
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.013908 | 38 | -0.00023662 | -0.0089915
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.000382 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.44197 | 0 | -0.00025262 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.000382 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.44236 | 0 | -0.00025262 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.000409 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00027962 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.000409 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.32188 | 787 | -0.00027962 | -0.22006
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0415 | 100 | -0.00028562 | -0.028562
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.000432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.072576 | 168 | -0.00030262 | -0.05084
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.000432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.03888 | 90 | -0.00030262 | -0.027236
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.000439 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00030962 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.000439 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00030962 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.000522 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13311 | 255 | -0.00039262 | -0.10012
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.000522 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.077778 | 149 | -0.00039262 | -0.0585
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.000522 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.079866 | 153 | -0.00039262 | -0.060071
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.04011 | 70 | -0.00044362 | -0.031053
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.039537 | 69 | -0.00044362 | -0.03061
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.039537 | 69 | -0.00044362 | -0.03061
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.038964 | 68 | -0.00044362 | -0.030166
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.000605 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.009075 | 0 | -0.00047562 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.000605 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.009075 | 0 | -0.00047562 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.000613 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.09195 | 150 | -0.00048362 | -0.072543
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.000613 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.04904 | 80 | -0.00048362 | -0.038689
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.000964 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.070372 | 73 | -0.00083462 | -0.060927
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.000964 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.11472 | 119 | -0.00083462 | -0.09932
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.000964 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.19762 | 205 | -0.00083462 | -0.1711
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.000964 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.098328 | 102 | -0.00083462 | -0.085131
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.000964 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.092544 | 96 | -0.00083462 | -0.080123
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.002788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.092004 | 0 | -0.0020881 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.002788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0697 | 0 | -0.0020881 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.002788 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0020881 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.00281 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.1686 | 60 | -0.0026806 | -0.16084
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.001928 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011568 | 0 | -0.0029481 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.001728 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0031481 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 7.8e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.001872 | 24 | -0.0047981 | -0.11515
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 7.8e-05 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.001872 | 24 | -0.0047981 | -0.11515
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 7.8e-05 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.001794 | 23 | -0.0047981 | -0.11036
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0048761 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0048761 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -6.4e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0064 | 100 | -0.0049401 | -0.49401
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -6.4e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0064 | 100 | -0.0049401 | -0.49401
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000139 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0050151 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002508 | 0 | -0.0050851 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002299 | 0 | -0.0050851 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002508 | 0 | -0.0050851 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.00027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0051461 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.041313 | 146.5 | -0.0051581 | -0.75566
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.041708 | 147.9 | -0.0051581 | -0.76288
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.048786 | 173 | -0.0051581 | -0.89235
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.000289 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0051651 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.042336 | 144 | -0.0051701 | -0.74449
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.042336 | 144 | -0.0051701 | -0.74449
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.050274 | 171 | -0.0051701 | -0.88408
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.060858 | 207 | -0.0051701 | -1.0702
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.06371 | 216.7 | -0.0051701 | -1.1204
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.071148 | 242 | -0.0051701 | -1.2512
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.000301 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0051771 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.011438 | 38 | -0.0051771 | -0.19673
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0058093 | 19.3 | -0.0051771 | -0.099918
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.004515 | 15 | -0.0051771 | -0.077656
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.000301 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.014147 | 47 | -0.0051771 | -0.24332
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.028576 | 94 | -0.0051801 | -0.48693
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.012464 | 41 | -0.0051801 | -0.21238
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.011552 | 38 | -0.0051801 | -0.19684
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.005776 | 19 | -0.0051801 | -0.098422
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.028576 | 94 | -0.0051801 | -0.48693
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.010944 | 36 | -0.0051801 | -0.18648
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.013072 | 43 | -0.0051801 | -0.22274
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.006688 | 22 | -0.0051801 | -0.11396
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.044992 | 148 | -0.0051801 | -0.76665
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0152 | 50 | -0.0051801 | -0.259
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01672 | 55 | -0.0051801 | -0.2849
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0152 | 50 | -0.0051801 | -0.259
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.000307 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.008903 | 0 | -0.0051831 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.000308 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.12197 | 396 | -0.0051841 | -2.0529
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.011742 | 0 | -0.0051851 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.007725 | 0 | -0.0051851 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.007725 | 0 | -0.0051851 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.00031 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01178 | 0 | -0.0051861 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.00031 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.10354 | 334 | -0.0051861 | -1.7322
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.00031 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1054 | 340 | -0.0051861 | -1.7633
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.00031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0558 | 180 | -0.0051861 | -0.93349
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.00031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0558 | 180 | -0.0051861 | -0.93349
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.05598 | 180 | -0.0051871 | -0.93367
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.1045 | 336 | -0.0051871 | -1.7429
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.05598 | 180 | -0.0051871 | -0.93367
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.046121 | 0 | -0.0051871 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.046215 | 0 | -0.0051871 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.047583 | 0 | -0.0051871 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 25 | -0.0051891 | -0.12973
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 25 | -0.0051891 | -0.12973
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 25 | -0.0051891 | -0.12973
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.005008 | 16 | -0.0051891 | -0.083025
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 25 | -0.0051891 | -0.12973
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 25 | -0.0051891 | -0.12973
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 25 | -0.0051891 | -0.12973
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.004695 | 15 | -0.0051891 | -0.077836
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.049612 | 0 | -0.0051901 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.048042 | 0 | -0.0051901 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.0314 | 0 | -0.0051901 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.04553 | 0 | -0.0051901 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.046158 | 0 | -0.0051901 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.039878 | 0 | -0.0051901 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.000314 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.003768 | 0 | -0.0051901 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.000321 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.007062 | 22 | -0.0051971 | -0.11434
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.000321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.003531 | 11 | -0.0051971 | -0.057168
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.000321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.003531 | 11 | -0.0051971 | -0.057168
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.055879 | 0 | -0.0051991 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.050388 | 0 | -0.0051991 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.049742 | 0 | -0.0051991 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.049742 | 0 | -0.0051991 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.000323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052326 | 0 | -0.0051991 | 0
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.053073 | 0 | -0.0052021 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052616 | 0 | -0.0052021 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051801 | 0 | -0.0052021 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.087759 | 0 | -0.0052021 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.000326 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.12975 | 398 | -0.0052021 | -2.0704
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.019234 | 59 | -0.0052021 | -0.30692
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.019234 | 59 | -0.0052021 | -0.30692
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.000327 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.24296 | 743 | -0.0052031 | -3.8659
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.000327 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.003924 | 12 | -0.0052031 | -0.062437
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021255 | 0 | -0.0052031 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021582 | 0 | -0.0052031 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02289 | 0 | -0.0052031 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020601 | 0 | -0.0052031 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020274 | 0 | -0.0052031 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034008 | 0 | -0.0052031 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.019293 | 0 | -0.0052031 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.001635 | 0 | -0.0052031 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.006867 | 0 | -0.0052031 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.056244 | 172 | -0.0052031 | -0.89493
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.056244 | 172 | -0.0052031 | -0.89493
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.056244 | 172 | -0.0052031 | -0.89493
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051339 | 0 | -0.0052031 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.000328 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.20631 | 629 | -0.0052041 | -3.2734
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.000328 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.24108 | 735 | -0.0052041 | -3.825
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011152 | 0 | -0.0052041 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011382 | 0 | -0.0052041 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.010726 | 0 | -0.0052041 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015055 | 0 | -0.0052041 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0058056 | 0 | -0.0052041 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0066912 | 0 | -0.0052041 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0065272 | 0 | -0.0052041 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01148 | 0 | -0.0052041 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.005904 | 0 | -0.0052041 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.028011 | 0 | -0.0052041 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.048544 | 0 | -0.0052041 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000328 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.003936 | 12 | -0.0052041 | -0.062449
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.013818 | 42 | -0.0052051 | -0.21861
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.013818 | 42 | -0.0052051 | -0.21861
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.012502 | 38 | -0.0052051 | -0.19779
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.012502 | 38 | -0.0052051 | -0.19779
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.000329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044744 | 0 | -0.0052051 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.000329 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056917 | 0 | -0.0052051 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.000329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044415 | 0 | -0.0052051 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034216 | 104 | -0.0052051 | -0.54133
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034216 | 104 | -0.0052051 | -0.54133
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017437 | 53 | -0.0052051 | -0.27587
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.018753 | 57 | -0.0052051 | -0.29669
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.019082 | 58 | -0.0052051 | -0.30189
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.019082 | 58 | -0.0052051 | -0.30189
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.00033 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01914 | 58 | -0.0052061 | -0.30195
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.00033 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.02937 | 89 | -0.0052061 | -0.46334
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01452 | 44 | -0.0052061 | -0.22907
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01452 | 44 | -0.0052061 | -0.22907
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01419 | 43 | -0.0052061 | -0.22386
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01485 | 45 | -0.0052061 | -0.23427
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.053856 | 0 | -0.0052061 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051843 | 0 | -0.0052061 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051975 | 0 | -0.0052061 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05181 | 0 | -0.0052061 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.08877 | 0 | -0.0052061 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01155 | 0 | -0.0052061 | 0
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04917 | 0 | -0.0052061 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021483 | 0 | -0.0052061 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.05445 | 165 | -0.0052061 | -0.859
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.05577 | 169 | -0.0052061 | -0.87983
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00033 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.00396 | 12 | -0.0052061 | -0.062473
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00033 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052061 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.0594 | 0 | -0.0052061 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.052338 | 0 | -0.0052061 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05181 | 0 | -0.0052061 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.07524 | 228 | -0.0052061 | -1.187
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02112 | 0 | -0.0052061 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020856 | 0 | -0.0052061 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027258 | 0 | -0.0052061 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024288 | 0 | -0.0052061 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.005346 | 0 | -0.0052061 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.07029 | 213 | -0.0052061 | -1.1089
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02343 | 0 | -0.0052061 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02376 | 0 | -0.0052061 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01287 | 0 | -0.0052061 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0099 | 0 | -0.0052061 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.015789 | 47.7 | -0.0052071 | -0.24838
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.012346 | 37.3 | -0.0052071 | -0.19422
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.015888 | 48 | -0.0052071 | -0.24994
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.021515 | 0 | -0.0052071 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.01986 | 0 | -0.0052071 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.021515 | 0 | -0.0052071 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.021515 | 0 | -0.0052071 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018205 | 55 | -0.0052071 | -0.28639
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018205 | 55 | -0.0052071 | -0.28639
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.017874 | 54 | -0.0052071 | -0.28118
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.025818 | 0 | -0.0052071 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.02648 | 0 | -0.0052071 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030212 | 0 | -0.0052081 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.029083 | 0 | -0.0052081 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.028884 | 0 | -0.0052081 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.018094 | 0 | -0.0052081 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0040504 | 0 | -0.0052081 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.000333 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052091 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.000334 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.0167 | 50 | -0.0052101 | -0.2605
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.000335 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00268 | 0 | -0.0052111 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.023718 | 0 | -0.0052111 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.022344 | 0 | -0.0052111 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.017755 | 0 | -0.0052111 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051322 | 0 | -0.0052111 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051423 | 0 | -0.0052111 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051021 | 0 | -0.0052111 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.03216 | 0 | -0.0052111 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.08174 | 0 | -0.0052111 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0134 | 0 | -0.0052111 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01072 | 0 | -0.0052111 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01005 | 0 | -0.0052111 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.0336 | 0 | -0.0052111 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.031121 | 0 | -0.0052111 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.034404 | 0 | -0.0052111 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.03417 | 0 | -0.0052111 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.009408 | 0 | -0.0052121 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.002352 | 0 | -0.0052121 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013104 | 0 | -0.0052121 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00504 | 0 | -0.0052121 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.002352 | 0 | -0.0052121 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00504 | 0 | -0.0052121 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013104 | 0 | -0.0052121 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013104 | 0 | -0.0052121 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.000337 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.005055 | 0 | -0.0052131 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.000337 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.007751 | 0 | -0.0052131 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.000338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011154 | 0 | -0.0052141 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.000339 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.048816 | 144 | -0.0052151 | -0.75097
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.000339 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.063732 | 188 | -0.0052151 | -0.98044
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.000339 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.024747 | 0 | -0.0052151 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.000339 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015628 | 0 | -0.0052151 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.055257 | 0 | -0.0052151 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.055257 | 0 | -0.0052151 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.083055 | 0 | -0.0052151 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.22069 | 651 | -0.0052151 | -3.395
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.1912 | 564 | -0.0052151 | -2.9413
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.2034 | 600 | -0.0052151 | -3.129
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.054579 | 161 | -0.0052151 | -0.83963
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.056274 | 166 | -0.0052151 | -0.8657
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.084072 | 248 | -0.0052151 | -1.2933
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.000339 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.18509 | 546 | -0.0052151 | -2.8474
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.000339 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -0.21798 | 0 | -0.0052151 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.000339 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.004407 | 13 | -0.0052151 | -0.067796
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01632 | 0 | -0.0052161 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02686 | 0 | -0.0052161 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02754 | 0 | -0.0052161 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02686 | 0 | -0.0052161 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0272 | 0 | -0.0052161 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.026656 | 0 | -0.0052161 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0085 | 0 | -0.0052161 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01564 | 0 | -0.0052161 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00952 | 0 | -0.0052161 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.014824 | 0 | -0.0052161 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02516 | 0 | -0.0052161 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.038184 | 0 | -0.0052201 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.038184 | 0 | -0.0052201 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.040936 | 0 | -0.0052201 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.037668 | 0 | -0.0052201 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.000345 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024495 | 0 | -0.0052211 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.000345 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00345 | 0 | -0.0052211 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021514 | 0 | -0.0052231 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024776 | 0 | -0.0052231 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015615 | 0 | -0.0052231 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.035047 | 0 | -0.0052231 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.029842 | 0 | -0.0052231 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030536 | 0 | -0.0052231 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01735 | 0 | -0.0052231 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.006246 | 0 | -0.0052231 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.032618 | 0 | -0.0052231 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02429 | 0 | -0.0052231 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021861 | 0 | -0.0052231 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024984 | 0 | -0.0052231 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.022486 | 0 | -0.0052231 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.035047 | 0 | -0.0052231 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.033659 | 0 | -0.0052231 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.035741 | 0 | -0.0052231 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026372 | 0 | -0.0052231 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02776 | 0 | -0.0052231 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02776 | 0 | -0.0052231 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059337 | 0 | -0.0052231 | 0
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000349 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.14204 | 407 | -0.0052251 | -2.1266
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.000352 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.023232 | 66 | -0.0052281 | -0.34505
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.000353 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.073777 | 209 | -0.0052291 | -1.0929
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.000353 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.076248 | 216 | -0.0052291 | -1.1295
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016238 | 46 | -0.0052291 | -0.24054
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016591 | 47 | -0.0052291 | -0.24577
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016238 | 46 | -0.0052291 | -0.24054
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016238 | 46 | -0.0052291 | -0.24054
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.000354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.14585 | 412 | -0.0052301 | -2.1548
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.000354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1416 | 400 | -0.0052301 | -2.092
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.47455 | 0 | -0.0052321 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.47277 | 0 | -0.0052321 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.027132 | 76 | -0.0052331 | -0.39771
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.027132 | 76 | -0.0052331 | -0.39771
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.037485 | 105 | -0.0052331 | -0.54947
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.026418 | 74 | -0.0052331 | -0.38725
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.026418 | 74 | -0.0052331 | -0.38725
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.036414 | 102 | -0.0052331 | -0.53377
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.000358 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.15179 | 424 | -0.0052341 | -2.2193
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.000358 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.15215 | 425 | -0.0052341 | -2.2245
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052451 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052451 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052451 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.000371 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.20257 | 546 | -0.0052471 | -2.8649
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.000371 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.27825 | 750 | -0.0052471 | -3.9353
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057815 | 155 | -0.0052491 | -0.81361
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.06341 | 170 | -0.0052491 | -0.89234
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057815 | 155 | -0.0052491 | -0.81361
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.058653 | 147 | -0.0052751 | -0.77544
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.055062 | 138 | -0.0052751 | -0.72796
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.05586 | 140 | -0.0052751 | -0.73851
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.058653 | 147 | -0.0052751 | -0.77544
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.072618 | 182 | -0.0052751 | -0.96006
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.079002 | 198 | -0.0052751 | -1.0445
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000399 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004788 | 0 | -0.0052751 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.000414 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.001656 | 0 | -0.0052901 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.04731 | 114 | -0.0052911 | -0.60318
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09213 | 222 | -0.0052911 | -1.1746
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.07636 | 184 | -0.0052911 | -0.97356
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09296 | 224 | -0.0052911 | -1.1852
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.047725 | 115 | -0.0052911 | -0.60847
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.059356 | 142 | -0.0052941 | -0.75176
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.06061 | 145 | -0.0052941 | -0.76764
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.063118 | 151 | -0.0052941 | -0.79941
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12122 | 290 | -0.0052941 | -1.5353
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.00043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.001032 | 0 | -0.0053061 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.00043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.001032 | 0 | -0.0053061 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0010344 | 0 | -0.0053071 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0010344 | 0 | -0.0053071 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0012068 | 0 | -0.0053071 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.098068 | 223.9 | -0.0053141 | -1.1898
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.09855 | 225 | -0.0053141 | -1.1957
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.098375 | 224.6 | -0.0053141 | -1.1935
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.099295 | 226.7 | -0.0053141 | -1.2047
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.20654 | 433 | -0.0053531 | -2.3179
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.27857 | 584 | -0.0053531 | -3.1262
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.28381 | 595 | -0.0053531 | -3.1851
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002958 | 0 | -0.0053691 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.078526 | 158 | -0.0053731 | -0.84895
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.07952 | 160 | -0.0053731 | -0.85969
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.086975 | 175 | -0.0053731 | -0.94029
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.077317 | 152.5 | -0.0053831 | -0.82092
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.075797 | 149.5 | -0.0053831 | -0.80477
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.11793 | 232.6 | -0.0053831 | -1.2521
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.000521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.29645 | 569 | -0.0053971 | -3.0709
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.000521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.3027 | 581 | -0.0053971 | -3.1357
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.07128 | 132 | -0.0054161 | -0.71492
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.07236 | 134 | -0.0054161 | -0.72575
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.17442 | 323 | -0.0054161 | -1.7494
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029008 | 49 | -0.0054681 | -0.26794
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027232 | 46 | -0.0054681 | -0.25153
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027232 | 46 | -0.0054681 | -0.25153
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027824 | 47 | -0.0054681 | -0.257
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.000592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.091168 | 154 | -0.0054681 | -0.84208
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.000592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.087616 | 148 | -0.0054681 | -0.80928
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.028416 | 48 | -0.0054681 | -0.26247
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.028416 | 48 | -0.0054681 | -0.26247
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.025116 | 42 | -0.0054741 | -0.22991
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.026312 | 44 | -0.0054741 | -0.24086
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.026312 | 44 | -0.0054741 | -0.24086
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.028106 | 47 | -0.0054741 | -0.25728
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.000601 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.18631 | 310 | -0.0054771 | -1.6979
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.000601 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.24821 | 413 | -0.0054771 | -2.262
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.000615 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00492 | 0 | -0.0054911 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.000615 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00492 | 0 | -0.0054911 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02807 | 0 | -0.0056781 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.027268 | 0 | -0.0056781 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02807 | 0 | -0.0056781 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.001117 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.020106 | 0 | -0.0059931 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.001117 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.020106 | 0 | -0.0059931 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.001256 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.53003 | 422 | -0.0061321 | -2.5877
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.001297 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036316 | 0 | -0.0061731 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.001297 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.037613 | 0 | -0.0061731 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.001507 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.020646 | 0 | -0.0063831 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.034614 | 0 | -0.0067991 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.034614 | 0 | -0.0067991 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.028845 | 0 | -0.0067991 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L:6410 MILES - 6411 ROWE2A C:OAK Creek - Ballinger [6335 - 6340] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.034614 | 0 | -0.0067991 | 0 | 0 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.034614 | 0 | -0.0067991 | 0 | 0 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.001923 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.028845 | 0 | -0.0067991 | 0 | 0 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.001507 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.020646 | 0 | -0.0063831 | 0 | 0 | 0 | Weighted Shift Factors
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.001297 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.036316 | 0 | -0.0061731 | 0 | 0 | 0 | West | 0.0048761
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.001297 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.037613 | 0 | -0.0061731 | 0 | 0 | 0 | North | -0.00012938
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.001256 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.53003 | 422 | -0.0061321 | -2.5877 | 422 | 2.5877 |  | 0.0050055
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.001117 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.020106 | 0 | -0.0059931 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.001117 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.020106 | 0 | -0.0059931 | 0 |  |  | Line Rating | 30
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02807 | 0 | -0.0056781 | 0 |  |  | Conc Gen | 422
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.027268 | 0 | -0.0056781 | 0 |  |  | Weighted Imp. | 2.5877
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.000802 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.02807 | 0 | -0.0056781 | 0 |  |  | PTDF | 0.0061321
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.000615 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00492 | 0 | -0.0054911 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.000615 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.00492 | 0 | -0.0054911 | 0 |  |  | Concentration | 1.2251
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.000601 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.18631 | 310 | -0.0054771 | -1.6979
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.000601 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.24821 | 413 | -0.0054771 | -2.262
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.025116 | 42 | -0.0054741 | -0.22991
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.026312 | 44 | -0.0054741 | -0.24086
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.026312 | 44 | -0.0054741 | -0.24086
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.000598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.028106 | 47 | -0.0054741 | -0.25728
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.029008 | 49 | -0.0054681 | -0.26794
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027232 | 46 | -0.0054681 | -0.25153
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027232 | 46 | -0.0054681 | -0.25153
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.027824 | 47 | -0.0054681 | -0.257
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.000592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.091168 | 154 | -0.0054681 | -0.84208
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.000592 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.087616 | 148 | -0.0054681 | -0.80928
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.028416 | 48 | -0.0054681 | -0.26247
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.000592 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.028416 | 48 | -0.0054681 | -0.26247
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.07128 | 132 | -0.0054161 | -0.71492
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.07236 | 134 | -0.0054161 | -0.72575
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.00054 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.17442 | 323 | -0.0054161 | -1.7494
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.000521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.29645 | 0 | -0.0053971 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.000521 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.3027 | 0 | -0.0053971 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.077317 | 152.5 | -0.0053831 | -0.82092
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.075797 | 149.5 | -0.0053831 | -0.80477
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.000507 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.11793 | 232.6 | -0.0053831 | -1.2521
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.000498 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0249 | 50 | -0.0053741 | -0.2687
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.078526 | 158 | -0.0053731 | -0.84895
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.07952 | 160 | -0.0053731 | -0.85969
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.000497 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.086975 | 175 | -0.0053731 | -0.94029
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.000493 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002958 | 0 | -0.0053691 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.27857 | 0 | -0.0053531 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.28381 | 0 | -0.0053531 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.000477 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.20654 | 0 | -0.0053531 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.098068 | 223.9 | -0.0053141 | -1.1898
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.09855 | 225 | -0.0053141 | -1.1957
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.098375 | 224.6 | -0.0053141 | -1.1935
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.000438 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.099295 | 226.7 | -0.0053141 | -1.2047
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0010344 | 0 | -0.0053071 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0010344 | 0 | -0.0053071 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.000431 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.0012068 | 0 | -0.0053071 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.00043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.001032 | 0 | -0.0053061 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.00043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.001032 | 0 | -0.0053061 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.059356 | 142 | -0.0052941 | -0.75176
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.06061 | 145 | -0.0052941 | -0.76764
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.063118 | 151 | -0.0052941 | -0.79941
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.000418 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.12122 | 290 | -0.0052941 | -1.5353
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.04731 | 0 | -0.0052911 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09213 | 0 | -0.0052911 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.07636 | 0 | -0.0052911 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.09296 | 0 | -0.0052911 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.047725 | 0 | -0.0052911 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.000414 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.001656 | 0 | -0.0052901 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000399 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.004788 | 0 | -0.0052751 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.058653 | 147 | -0.0052751 | -0.77544
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.055062 | 138 | -0.0052751 | -0.72796
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.05586 | 140 | -0.0052751 | -0.73851
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.058653 | 147 | -0.0052751 | -0.77544
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.072618 | 182 | -0.0052751 | -0.96006
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.000399 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.079002 | 198 | -0.0052751 | -1.0445
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057815 | 155 | -0.0052491 | -0.81361
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.06341 | 170 | -0.0052491 | -0.89234
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.000373 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.057815 | 155 | -0.0052491 | -0.81361
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.000371 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.20257 | 0 | -0.0052471 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.000371 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.27825 | 0 | -0.0052471 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052451 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052451 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.000369 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052451 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.000358 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.15179 | 0 | -0.0052341 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.000358 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.15215 | 0 | -0.0052341 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.027132 | 76 | -0.0052331 | -0.39771
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.027132 | 76 | -0.0052331 | -0.39771
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.037485 | 105 | -0.0052331 | -0.54947
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.026418 | 74 | -0.0052331 | -0.38725
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.026418 | 74 | -0.0052331 | -0.38725
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.000357 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.036414 | 102 | -0.0052331 | -0.53377
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.000356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.47455 | 0 | -0.0052321 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.000356 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -0.47277 | 0 | -0.0052321 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.000354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.14585 | 412 | -0.0052301 | -2.1548
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.000354 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1416 | 400 | -0.0052301 | -2.092
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.000353 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.073777 | 209 | -0.0052291 | -1.0929
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.000353 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.076248 | 216 | -0.0052291 | -1.1295
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016238 | 46 | -0.0052291 | -0.24054
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016591 | 47 | -0.0052291 | -0.24577
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016238 | 46 | -0.0052291 | -0.24054
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.000353 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.016238 | 46 | -0.0052291 | -0.24054
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.000352 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.023232 | 66 | -0.0052281 | -0.34505
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.000349 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.14204 | 407 | -0.0052251 | -2.1266
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021514 | 0 | -0.0052231 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024776 | 0 | -0.0052231 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015615 | 0 | -0.0052231 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.035047 | 0 | -0.0052231 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.029842 | 0 | -0.0052231 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030536 | 0 | -0.0052231 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01735 | 0 | -0.0052231 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.006246 | 0 | -0.0052231 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.032618 | 0 | -0.0052231 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02429 | 0 | -0.0052231 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021861 | 0 | -0.0052231 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024984 | 0 | -0.0052231 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.022486 | 0 | -0.0052231 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.035047 | 0 | -0.0052231 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.033659 | 0 | -0.0052231 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.035741 | 0 | -0.0052231 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.026372 | 0 | -0.0052231 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02776 | 0 | -0.0052231 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02776 | 0 | -0.0052231 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.000347 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.059337 | 0 | -0.0052231 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.000345 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024495 | 0 | -0.0052211 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.000345 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.00345 | 0 | -0.0052211 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.038184 | 0 | -0.0052201 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.038184 | 0 | -0.0052201 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.040936 | 0 | -0.0052201 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.000344 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.037668 | 0 | -0.0052201 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02686 | 0 | -0.0052161 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02754 | 0 | -0.0052161 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02686 | 0 | -0.0052161 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0272 | 0 | -0.0052161 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.026656 | 0 | -0.0052161 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.0085 | 0 | -0.0052161 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01564 | 0 | -0.0052161 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00952 | 0 | -0.0052161 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.014824 | 0 | -0.0052161 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.02516 | 0 | -0.0052161 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.00034 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01632 | 0 | -0.0052161 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.054579 | 161 | -0.0052151 | -0.83963
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.056274 | 166 | -0.0052151 | -0.8657
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.000339 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.084072 | 248 | -0.0052151 | -1.2933
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.000339 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.18509 | 546 | -0.0052151 | -2.8474
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.000339 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -0.21798 | 0 | -0.0052151 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.000339 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.004407 | 13 | -0.0052151 | -0.067796
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.22069 | 0 | -0.0052151 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.1912 | 0 | -0.0052151 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.000339 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -0.2034 | 0 | -0.0052151 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.055257 | 0 | -0.0052151 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.055257 | 0 | -0.0052151 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.000339 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.083055 | 0 | -0.0052151 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.000339 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015628 | 0 | -0.0052151 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.000339 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.024747 | 0 | -0.0052151 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.000339 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.048816 | 144 | -0.0052151 | -0.75097
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.000339 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.063732 | 188 | -0.0052151 | -0.98044
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.000338 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011154 | 0 | -0.0052141 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.000337 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.005055 | 0 | -0.0052131 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.000337 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.007751 | 0 | -0.0052131 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.009408 | 0 | -0.0052121 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.002352 | 0 | -0.0052121 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013104 | 0 | -0.0052121 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00504 | 0 | -0.0052121 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.002352 | 0 | -0.0052121 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00504 | 0 | -0.0052121 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013104 | 0 | -0.0052121 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.000336 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.013104 | 0 | -0.0052121 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.0336 | 0 | -0.0052111 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.031121 | 0 | -0.0052111 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.034404 | 0 | -0.0052111 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.03417 | 0 | -0.0052111 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01072 | 0 | -0.0052111 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01005 | 0 | -0.0052111 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.023718 | 0 | -0.0052111 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.022344 | 0 | -0.0052111 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.017755 | 0 | -0.0052111 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051322 | 0 | -0.0052111 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051423 | 0 | -0.0052111 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051021 | 0 | -0.0052111 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.03216 | 0 | -0.0052111 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.000335 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.08174 | 0 | -0.0052111 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.000335 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0134 | 0 | -0.0052111 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.000335 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.00268 | 0 | -0.0052111 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.000334 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.0167 | 50 | -0.0052101 | -0.2605
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.000333 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052091 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.030212 | 0 | -0.0052081 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.029083 | 0 | -0.0052081 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.028884 | 0 | -0.0052081 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.018094 | 0 | -0.0052081 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.000332 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0040504 | 0 | -0.0052081 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.025818 | 0 | -0.0052071 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.02648 | 0 | -0.0052071 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018205 | 55 | -0.0052071 | -0.28639
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018205 | 55 | -0.0052071 | -0.28639
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.000331 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.017874 | 54 | -0.0052071 | -0.28118
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.021515 | 0 | -0.0052071 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.01986 | 0 | -0.0052071 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.021515 | 0 | -0.0052071 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.000331 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.021515 | 0 | -0.0052071 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.015789 | 47.7 | -0.0052071 | -0.24838
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.012346 | 37.3 | -0.0052071 | -0.19422
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.015226 | 46 | -0.0052071 | -0.23953
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.000331 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.015888 | 48 | -0.0052071 | -0.24994
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02343 | 0 | -0.0052061 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02376 | 0 | -0.0052061 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01287 | 0 | -0.0052061 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0099 | 0 | -0.0052061 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.07029 | 213 | -0.0052061 | -1.1089
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.005346 | 0 | -0.0052061 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02112 | 0 | -0.0052061 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020856 | 0 | -0.0052061 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.027258 | 0 | -0.0052061 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.024288 | 0 | -0.0052061 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.07524 | 228 | -0.0052061 | -1.187
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.0594 | 0 | -0.0052061 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.052338 | 0 | -0.0052061 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05181 | 0 | -0.0052061 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.00033 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.00396 | 12 | -0.0052061 | -0.062473
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.00033 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0052061 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.05577 | 169 | -0.0052061 | -0.87983
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.00033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.05445 | 165 | -0.0052061 | -0.859
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.04917 | 0 | -0.0052061 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021483 | 0 | -0.0052061 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.00033 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01155 | 0 | -0.0052061 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.053856 | 0 | -0.0052061 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051843 | 0 | -0.0052061 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051975 | 0 | -0.0052061 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.05181 | 0 | -0.0052061 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.00033 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.08877 | 0 | -0.0052061 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.00033 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.01914 | 58 | -0.0052061 | -0.30195
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.00033 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.02937 | 89 | -0.0052061 | -0.46334
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01452 | 44 | -0.0052061 | -0.22907
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01452 | 44 | -0.0052061 | -0.22907
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01419 | 43 | -0.0052061 | -0.22386
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.00033 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.01485 | 45 | -0.0052061 | -0.23427
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034216 | 104 | -0.0052051 | -0.54133
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.034216 | 104 | -0.0052051 | -0.54133
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017437 | 53 | -0.0052051 | -0.27587
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.018753 | 57 | -0.0052051 | -0.29669
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.017766 | 54 | -0.0052051 | -0.28107
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.019082 | 58 | -0.0052051 | -0.30189
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.000329 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.019082 | 58 | -0.0052051 | -0.30189
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.000329 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.056917 | 0 | -0.0052051 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.000329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044415 | 0 | -0.0052051 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.000329 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.044744 | 0 | -0.0052051 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.013818 | 42 | -0.0052051 | -0.21861
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.013818 | 42 | -0.0052051 | -0.21861
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.012502 | 38 | -0.0052051 | -0.19779
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.000329 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.012502 | 38 | -0.0052051 | -0.19779
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.000328 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.003936 | 12 | -0.0052041 | -0.062449
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011152 | 0 | -0.0052041 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.011382 | 0 | -0.0052041 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.010726 | 0 | -0.0052041 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.015055 | 0 | -0.0052041 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0058056 | 0 | -0.0052041 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0066912 | 0 | -0.0052041 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.0065272 | 0 | -0.0052041 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.01148 | 0 | -0.0052041 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.005904 | 0 | -0.0052041 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.028011 | 0 | -0.0052041 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.000328 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.048544 | 0 | -0.0052041 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.000328 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.24108 | 735 | -0.0052041 | -3.825
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.000328 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.20631 | 0 | -0.0052041 | 0
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.000327 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.051339 | 0 | -0.0052031 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.056244 | 172 | -0.0052031 | -0.89493
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.056244 | 172 | -0.0052031 | -0.89493
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.000327 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -0.056244 | 172 | -0.0052031 | -0.89493
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.001635 | 0 | -0.0052031 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.006867 | 0 | -0.0052031 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021255 | 0 | -0.0052031 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.021582 | 0 | -0.0052031 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.02289 | 0 | -0.0052031 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020601 | 0 | -0.0052031 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.020274 | 0 | -0.0052031 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.034008 | 0 | -0.0052031 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.000327 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.019293 | 0 | -0.0052031 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.000327 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.003924 | 0 | -0.0052031 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.000327 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -0.24296 | 743 | -0.0052031 | -3.8659
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.019234 | 59 | -0.0052021 | -0.30692
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.019234 | 59 | -0.0052021 | -0.30692
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.000326 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.018256 | 56 | -0.0052021 | -0.29132
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.000326 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -0.12975 | 398 | -0.0052021 | -2.0704
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.053073 | 0 | -0.0052021 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052616 | 0 | -0.0052021 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.051801 | 0 | -0.0052021 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.000326 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.087759 | 0 | -0.0052021 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.055879 | 0 | -0.0051991 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.050388 | 0 | -0.0051991 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.049742 | 0 | -0.0051991 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.000323 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -0.049742 | 0 | -0.0051991 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.000323 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.052326 | 0 | -0.0051991 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.000321 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.007062 | 22 | -0.0051971 | -0.11434
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.000321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.003531 | 11 | -0.0051971 | -0.057168
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.000321 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.003531 | 11 | -0.0051971 | -0.057168
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.049612 | 0 | -0.0051901 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.048042 | 0 | -0.0051901 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.0314 | 0 | -0.0051901 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.04553 | 0 | -0.0051901 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.046158 | 0 | -0.0051901 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.000314 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.039878 | 0 | -0.0051901 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.000314 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.003768 | 0 | -0.0051901 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 0 | -0.0051891 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 0 | -0.0051891 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 0 | -0.0051891 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.005008 | 0 | -0.0051891 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 0 | -0.0051891 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 0 | -0.0051891 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.007825 | 0 | -0.0051891 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.000313 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.004695 | 0 | -0.0051891 | 0
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.046121 | 0 | -0.0051871 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.046215 | 0 | -0.0051871 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.000311 | south | 8 | N | N | Nsouth | Nsouth | -1 | -0.047583 | 0 | -0.0051871 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.1045 | 336 | -0.0051871 | -1.7429
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.05598 | 180 | -0.0051871 | -0.93367
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.000311 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.05598 | 180 | -0.0051871 | -0.93367
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.00031 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.10354 | 334 | -0.0051861 | -1.7322
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.00031 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.1054 | 340 | -0.0051861 | -1.7633
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.00031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0558 | 180 | -0.0051861 | -0.93349
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.00031 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.0558 | 180 | -0.0051861 | -0.93349
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.00031 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.01178 | 0 | -0.0051861 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.007725 | 0 | -0.0051851 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.007725 | 0 | -0.0051851 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.000309 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.011742 | 0 | -0.0051851 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.000308 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -0.12197 | 0 | -0.0051841 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.000307 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.008903 | 0 | -0.0051831 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.028576 | 0 | -0.0051801 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.012464 | 0 | -0.0051801 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.011552 | 0 | -0.0051801 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.005776 | 0 | -0.0051801 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.028576 | 0 | -0.0051801 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.010944 | 0 | -0.0051801 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.013072 | 0 | -0.0051801 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.006688 | 0 | -0.0051801 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.044992 | 0 | -0.0051801 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0152 | 0 | -0.0051801 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.01672 | 0 | -0.0051801 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.000304 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.0152 | 0 | -0.0051801 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.011438 | 38 | -0.0051771 | -0.19673
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.0058093 | 19.3 | -0.0051771 | -0.099918
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.000301 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.004515 | 15 | -0.0051771 | -0.077656
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.000301 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.014147 | 47 | -0.0051771 | -0.24332
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.000301 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0051771 | 0
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.060858 | 207 | -0.0051701 | -1.0702
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.06371 | 216.7 | -0.0051701 | -1.1204
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.071148 | 242 | -0.0051701 | -1.2512
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.042336 | 144 | -0.0051701 | -0.74449
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.042336 | 144 | -0.0051701 | -0.74449
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.000294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.050274 | 171 | -0.0051701 | -0.88408
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.000289 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0051651 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.041313 | 146.5 | -0.0051581 | -0.75566
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.041708 | 147.9 | -0.0051581 | -0.76288
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.000282 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.048786 | 173 | -0.0051581 | -0.89235
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.00027 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0051461 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002508 | 0 | -0.0050851 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002299 | 0 | -0.0050851 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.000209 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.002508 | 0 | -0.0050851 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.000139 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0050151 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -6.4e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0064 | 100 | -0.0049401 | -0.49401
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -6.4e-05 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.0064 | 100 | -0.0049401 | -0.49401
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -6.4e-05 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0049401 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.0048761 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0048761 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0048761 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 7.8e-05 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 0.001872 | 24 | -0.0047981 | -0.11515
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 7.8e-05 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.001872 | 24 | -0.0047981 | -0.11515
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 7.8e-05 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | 0.001794 | 23 | -0.0047981 | -0.11036
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.000159 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | 0.0013356 | 8.4 | -0.0047171 | -0.039623
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.001728 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0031481 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.001928 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.011568 | 0 | -0.0029481 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | -0.00281 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.1686 | 0 | -0.0026806 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.002788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.092004 | 0 | -0.0020881 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.002788 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.0697 | 0 | -0.0020881 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.002788 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.0020881 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | -0.000964 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.070372 | 73 | -0.00083462 | -0.060927
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | -0.000964 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.11472 | 119 | -0.00083462 | -0.09932
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | -0.000964 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.19762 | 205 | -0.00083462 | -0.1711
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | -0.000964 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.098328 | 102 | -0.00083462 | -0.085131
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | -0.000964 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.092544 | 96 | -0.00083462 | -0.080123
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.000613 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.09195 | 150 | -0.00048362 | -0.072543
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.000613 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.04904 | 80 | -0.00048362 | -0.038689
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.000605 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.009075 | 0 | -0.00047562 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.000605 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.009075 | 0 | -0.00047562 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.04011 | 70 | -0.00044362 | -0.031053
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.039537 | 69 | -0.00044362 | -0.03061
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.039537 | 69 | -0.00044362 | -0.03061
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.000573 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.038964 | 68 | -0.00044362 | -0.030166
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.000522 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.13311 | 255 | -0.00039262 | -0.10012
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.000522 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.077778 | 149 | -0.00039262 | -0.0585
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.000522 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.079866 | 153 | -0.00039262 | -0.060071
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.000439 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00030962 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.000439 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00030962 | 0
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.000432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.072576 | 168 | -0.00030262 | -0.05084
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.000432 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.03888 | 90 | -0.00030262 | -0.027236
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.000415 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -0.0415 | 0 | -0.00028562 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.000409 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00027962 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.000409 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.32188 | 787 | -0.00027962 | -0.22006
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.000382 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.44197 | 0 | -0.00025262 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.000382 | north | 3 | N | N | Nnorth | Nnorth | 1 | -0.44236 | 0 | -0.00025262 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.006588 | 18 | -0.00023662 | -0.0042591
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.006588 | 18 | -0.00023662 | -0.0042591
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | -0.000366 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.013908 | 38 | -0.00023662 | -0.0089915
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.075403 | 217.3 | -0.00021762 | -0.047288
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.071135 | 205 | -0.00021762 | -0.044612
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.000347 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.094523 | 272.4 | -0.00021762 | -0.059279
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.000299 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.014352 | 48 | -0.00016962 | -0.0081416
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.000299 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.013754 | 46 | -0.00016962 | -0.0078024
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.000299 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.031395 | 105 | -0.00016962 | -0.01781
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.000295 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.005015 | 17 | -0.00016562 | -0.0028155
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.000295 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00016562 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.000295 | north | 7 | N | N | Nnorth | Nnorth | 1 | -0.00944 | 0 | -0.00016562 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.045026 | 0 | -0.00016262 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.045552 | 0 | -0.00016262 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.045552 | 0 | -0.00016262 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.000292 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.11096 | 0 | -0.00016262 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.000285 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.13195 | 0 | -0.00015562 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.22145 | 0 | -0.00012962 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.22145 | 0 | -0.00012962 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.039446 | 0 | -0.00012962 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.000259 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.039627 | 0 | -0.00012962 | 0
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.000259 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00012962 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.000249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.20592 | 0 | -0.00011962 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.000249 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.20393 | 0 | -0.00011962 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.000207 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.12731 | 0 | -7.7618e-05 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.000207 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.12151 | 0 | -7.7618e-05 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.045248 | 224 | -7.2618e-05 | -0.016266
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.045652 | 226 | -7.2618e-05 | -0.016412
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.042824 | 212 | -7.2618e-05 | -0.015395
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.000202 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.042622 | 211 | -7.2618e-05 | -0.015322
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029688 | 150.7 | -6.7618e-05 | -0.01019
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029747 | 151 | -6.7618e-05 | -0.01021
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.000197 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.034948 | 177.4 | -6.7618e-05 | -0.011995
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029694 | 151.5 | -6.6618e-05 | -0.010093
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.029851 | 152.3 | -6.6618e-05 | -0.010146
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.000196 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.03479 | 177.5 | -6.6618e-05 | -0.011825
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.000193 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.043232 | 224 | -6.3618e-05 | -0.01425
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.000193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.037828 | 196 | -6.3618e-05 | -0.012469
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.000193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.021423 | 111 | -6.3618e-05 | -0.0070616
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.000166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.035922 | 216.4 | -3.6618e-05 | -0.0079241
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.000166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.035873 | 216.1 | -3.6618e-05 | -0.0079131
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.000149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.027118 | 182 | -1.9618e-05 | -0.0035704
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.000149 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.072116 | 484 | -1.9618e-05 | -0.009495
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.000148 | north | 6 | Y | N | Ynorth | Nnorth | 1 | -0.0074 | 0 | -1.8618e-05 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.000147 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -1.7618e-05 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.021016 | 0 | -1.2618e-05 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.01846 | 0 | -1.2618e-05 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.02059 | 0 | -1.2618e-05 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.000142 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.056658 | 0 | -1.2618e-05 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.10676 | 0 | -6.6177e-06 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.10812 | 0 | -6.6177e-06 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.000136 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.10608 | 0 | -6.6177e-06 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.000112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.013216 | 118 | 1.7382e-05 | 0.0020511
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.000112 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.01288 | 115 | 1.7382e-05 | 0.001999
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.000112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.062272 | 556 | 1.7382e-05 | 0.0096646
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -9.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 3.4382e-05 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -9.5e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 3.4382e-05 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014812 | 161 | 3.7382e-05 | 0.0060186
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.015088 | 164 | 3.7382e-05 | 0.0061307
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.015088 | 164 | 3.7382e-05 | 0.0061307
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.038088 | 414 | 3.7382e-05 | 0.015476
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014904 | 162 | 3.7382e-05 | 0.0060559
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014812 | 161 | 3.7382e-05 | 0.0060186
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.014996 | 163 | 3.7382e-05 | 0.0060933
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -9.2e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.037628 | 409 | 3.7382e-05 | 0.015289
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -9e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.03492 | 388 | 3.9382e-05 | 0.01528
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -9e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.04635 | 515 | 3.9382e-05 | 0.020282
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -8.4e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.03654 | 435 | 4.5382e-05 | 0.019741
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -8.3e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.032785 | 395 | 4.6382e-05 | 0.018321
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -8.3e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.036105 | 435 | 4.6382e-05 | 0.020176
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -7.5e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.003 | 40 | 5.4382e-05 | 0.0021753
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.00148 | 20 | 5.5382e-05 | 0.0011076
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.00185 | 25 | 5.5382e-05 | 0.0013846
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -7.4e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.003034 | 41 | 5.5382e-05 | 0.0022707
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.005609 | 79 | 5.8382e-05 | 0.0046122
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.007526 | 106 | 5.8382e-05 | 0.0061885
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -7.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.010366 | 146 | 5.8382e-05 | 0.0085238
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -7.1e-05 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | -0.005396 | 76 | 5.8382e-05 | 0.0044371
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.019008 | 288 | 6.3382e-05 | 0.018254
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.009702 | 147 | 6.3382e-05 | 0.0093172
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | -6.6e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.009702 | 147 | 6.3382e-05 | 0.0093172
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.032364 | 0 | 7.1382e-05 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.033582 | 0 | 7.1382e-05 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -5.8e-05 | north | 4 | Y | N | Ynorth | Nnorth | 1 | -0.046864 | 0 | 7.1382e-05 | 0
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.00405 | 0 | 7.5382e-05 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.0042984 | 0 | 7.5382e-05 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -5.4e-05 | north | 8 | N | N | Nnorth | Nnorth | 1 | -0.0047736 | 0 | 7.5382e-05 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.00848 | 160 | 7.6382e-05 | 0.012221
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.008268 | 156 | 7.6382e-05 | 0.011916
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.010388 | 196 | 7.6382e-05 | 0.014971
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.008268 | 156 | 7.6382e-05 | 0.011916
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.008321 | 157 | 7.6382e-05 | 0.011992
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -5.3e-05 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | -0.010494 | 198 | 7.6382e-05 | 0.015124
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -5e-05 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | -0.0185 | 370 | 7.9382e-05 | 0.029371
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.007 | 0 | 7.9382e-05 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00705 | 0 | 7.9382e-05 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.01545 | 0 | 7.9382e-05 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.00715 | 0 | 7.9382e-05 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.0072 | 0 | 7.9382e-05 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -5e-05 | north | 1 | N | N | Nnorth | Nnorth | 1 | -0.0155 | 0 | 7.9382e-05 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -4.3e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | -0.00731 | 170 | 8.6382e-05 | 0.014685
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -4.3e-05 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | -0.02236 | 520 | 8.6382e-05 | 0.044919
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -4.1e-05 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 8.8382e-05 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -3.7e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00148 | 0 | 9.2382e-05 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -3.7e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | -0.00148 | 0 | 9.2382e-05 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -2e-05 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00010938 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.00012938 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.00012938 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 6e-06 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.00072 | 0 | 0.00013538 | 0
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 4.9e-05 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00017838 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 4.9e-05 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00017838 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 4.9e-05 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.00017838 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 6.5e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.00078 | 0 | 0.00019438 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 6.5e-05 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.00078 | 0 | 0.00019438 | 0
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 9.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.00546 | 60 | 0.00022038 | 0.013223
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 9.1e-05 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 0.005733 | 63 | 0.00022038 | 0.013884
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.000113 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 0.012712 | 0 | 0.00024238 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.00059 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.14278 | 242 | 0.00071938 | 0.17409
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.1324 | 204 | 0.00077838 | 0.15879
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.13045 | 201 | 0.00077838 | 0.15645
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.000649 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 0.15706 | 242 | 0.00077838 | 0.18837
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.02134 | 20 | 0.0011964 | 0.023928
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.02134 | 20 | 0.0011964 | 0.023928
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.02134 | 20 | 0.0011964 | 0.023928
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.001067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.018139 | 17 | 0.0011964 | 0.020338
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.001315 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 0.48129 | 366 | 0.0014444 | 0.52864
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.001573 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.0017024 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.001905 | west | 4 | Y | N | Ywest | Nwest | 1 | 1.2377 | 0 | 0.0020344 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.002105 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.31575 | 0 | 0.0022344 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.002105 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.2126 | 0 | 0.0022344 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.002328 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.38412 | 0 | 0.0024574 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.002647 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.62469 | 0 | 0.0027764 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.002648 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0592 | 0 | 0.0027774 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.002654 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.15924 | 0 | 0.0027834 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.40248 | 0 | 0.0034834 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.78148 | 0 | 0.0034834 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.003354 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57085 | 0 | 0.0034834 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.003517 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52755 | 0 | 0.0036464 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.14588 | 0 | 0.0040194 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.41818 | 0 | 0.0040194 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52515 | 0 | 0.0040194 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.46291 | 0 | 0.0040194 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.40845 | 0 | 0.0040194 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.00389 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.31315 | 0 | 0.0040194 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.004087 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69275 | 0 | 0.0042164 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.87237 | 0 | 0.0043034 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.52801 | 0 | 0.0043034 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0393 | 0 | 0.0043034 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.004174 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82228 | 0 | 0.0043034 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.004373 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.54663 | 0 | 0.0045024 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.004373 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.54663 | 0 | 0.0045024 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.004538 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.38119 | 0 | 0.0046674 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.004771 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.47233 | 0 | 0.0049004 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.004771 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.29103 | 0 | 0.0049004 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 1 | 0.11928 | 0 | 0.0049004 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 1 | 0.21803 | 0 | 0.0049004 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.004771 | west | 7 | N | N | Nwest | Nwest | 1 | 0.21803 | 0 | 0.0049004 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.71625 | 0 | 0.0049044 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0505 | 0 | 0.0049044 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.955 | 0 | 0.0049044 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.004775 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.58207 | 0 | 0.0049044 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.004797 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.67638 | 0 | 0.0049264 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.004797 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.57564 | 0 | 0.0049264 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.32023 | 66 | 0.0049814 | 0.32877
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.33479 | 69 | 0.0049814 | 0.34372
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.33479 | 69 | 0.0049814 | 0.34372
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.32508 | 67 | 0.0049814 | 0.33375
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.32508 | 67 | 0.0049814 | 0.33375
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.004852 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.31538 | 65 | 0.0049814 | 0.32379
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.004901 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.30876 | 0 | 0.0050304 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 1 | 0.34587 | 0 | 0.0050704 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 1 | 0.36267 | 0 | 0.0050704 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.004941 | west | 8 | N | N | Nwest | Nwest | 1 | 0.34785 | 0 | 0.0050704 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.00532 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9576 | 0 | 0.0054494 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.00532 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9576 | 0 | 0.0054494 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.005377 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.80655 | 0 | 0.0055064 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.005383 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2112 | 0 | 0.0055124 | 0
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3794 | 70 | 0.0055494 | 0.38846
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.3794 | 70 | 0.0055494 | 0.38846
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.50298 | 92.8 | 0.0055494 | 0.51498
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4336 | 80 | 0.0055494 | 0.44395
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.4336 | 80 | 0.0055494 | 0.44395
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.00542 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.6233 | 115 | 0.0055494 | 0.63818
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1299 | 208.2 | 0.0055564 | 1.1568
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.77118 | 142.1 | 0.0055564 | 0.78956
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.71853 | 132.4 | 0.0055564 | 0.73567
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.73807 | 136 | 0.0055564 | 0.75567
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.79777 | 147 | 0.0055564 | 0.81679
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.005427 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1397 | 210 | 0.0055564 | 1.1668
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6219 | 0 | 0.0056574 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82644 | 0 | 0.0056574 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.0282 | 0 | 0.0056574 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.005528 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.1858 | 0 | 0.0056574 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.00569 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2188 | 0 | 0.0058194 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.005827 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.33797 | 0 | 0.0059564 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.005946 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.88595 | 0 | 0.0060754 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39376 | 66 | 0.0060954 | 0.4023
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.38779 | 65 | 0.0060954 | 0.3962
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39972 | 67 | 0.0060954 | 0.40839
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39972 | 67 | 0.0060954 | 0.40839
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.005966 | west | 13 | Y | Y | Ywest | Ywest | 1 | 0.39972 | 67 | 0.0060954 | 0.40839
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.005966 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060954 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.005966 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.0060954 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.005968 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.20888 | 0 | 0.0060974 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.005968 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.17904 | 0 | 0.0060974 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.006398 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.9597 | 0 | 0.0065274 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.006489 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.65214 | 0 | 0.0066184 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.006847 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82164 | 0 | 0.0069764 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.006888 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.82656 | 0 | 0.0070174 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.007321 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.035141 | 0 | 0.0074504 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.008018 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64144 | 0 | 0.0081474 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.008018 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64144 | 0 | 0.0081474 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.008066 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.64528 | 0 | 0.0081954 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6456 | 0 | 0.0081994 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.60525 | 0 | 0.0081994 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6456 | 0 | 0.0081994 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.00807 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.3228 | 0 | 0.0081994 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.008089 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2133 | 0 | 0.0082184 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.008089 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.2133 | 0 | 0.0082184 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.00851 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.6808 | 0 | 0.0086394 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.008653 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.72685 | 0 | 0.0087824 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.008929 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68307 | 0 | 0.0090584 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.010243 | west | 8 | N | N | Nwest | Nwest | 1 | 0.26427 | 0 | 0.010372 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.011106 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.011235 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.1316 | 0 | 0.020068 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.019939 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.68391 | 0 | 0.020068 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown