## test results
CRE test for: |  | TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429] | [5 empty] | FAIL
Line Rating: |  | 1072
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.055404
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.089063
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.05261
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.026817
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.061299
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.084791
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.052847
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.02554
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.14019
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.0025567
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.080944
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.14191
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.062246
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.078151
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.14019 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.14019 | 0.14019
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.17082
[6 empty] | Concentration |  | 1.2185 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.16293
[6 empty] | Concentration |  | 1.1621 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 30.7427
| Percent of line rating => | [6 empty] | 2.868% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 2.8669
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.009284 | 0.016614 | 0.0073299 | 0.009284
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.012908 | 0.21915 | 0.23206 | -0.012908
[7 empty] | B4 (S-W) | 0.017262 | -0.38958 | -0.40685 | 0.017262
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0085913 | -0.18705 | -0.17845 | -0.0085913
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.022257 | 0.20179 | 0.22405 | -0.022257
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 2.31%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -3.212%
[7 empty] | B4 | 4.295%
[7 empty] | B5 | -2.138%
[7 empty] | B6 | -5.538%
[7 empty] | Max Abs Error | 5.538% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.091074 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 23.2239
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.091074 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 13.57
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.083008 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.2451
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.083008 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.2451
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.091074 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 13.9343
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.087779 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 13.1669
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.087779 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 7.0223
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.061862 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 4.5159
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.061862 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 7.3616
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.061862 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 12.6817
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.061862 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 6.3099
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.061862 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 5.9388
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.059677 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.71612
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.059677 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.71612
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.064488 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 10.834
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.064488 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 5.8039
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.0963
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.0963
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 2.3145
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 17.3097
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 8.8351
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 8.8351
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.059265 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 6.6673
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.057883 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 2.3153
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 4.571
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 6.1333
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 8.4477
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.057861 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 4.3974
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.059107 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 3.5464
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.059107 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 3.7237
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 1.1553
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 1.4441
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 2.3683
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.014502 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 6.7144
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 3.4109
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 3.3592
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.4626
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.4626
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.4626
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.05168 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 5.8915
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.05168 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 26.6152
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 3.5383
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.6991
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.6991
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.5919
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.5919
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 3.4846
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 3.7318
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 3.9131
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 3.7532
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 8.0196
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 11.7621
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.053724 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 5.3187
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.053724 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 3.2772
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.053709 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 7.573
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.3431
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.4552
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.4552
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.053709 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 6.4451
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.052915 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.3652
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.052701 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 5.2965
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.053188 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 6.3826
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.052683 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 3.0556
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.052812 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 11.3123
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.054125 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 8.1188
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.052308 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.34523
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.052308 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.7942
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.054125 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 5.4666
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.053211 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 6.3853
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.057944 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 21.2075
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.058218 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 14.0888
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.055832 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 22.3328
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.055834 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 13.1768
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.056341 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 9.2963
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 12.048
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 11.8709
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 14.2923
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.1613
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.1613
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.1613
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.98714
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.059685 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 7.1622
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.061783 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 3.707
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 4.3424
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 4.6088
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 5.1183
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 9.2717
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 9.0399
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 11.3578
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 9.0399
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 9.0978
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 11.4737
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.0581 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 9.877
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.0581 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 30.212
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058003 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 21.4611
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 32.2842
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 33.4992
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 46.7485
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.060138 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 6.7355
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.060138 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 6.0138
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.060138 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 22.7322
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 13.2668
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 12.5159
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 16.6308
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.061187 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 47.114
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 4.373
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 4.3106
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 4.3106
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 4.2481
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.060962 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 70.533
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.060962 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 70.594
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 14.239
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 14.3661
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.063159 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 13.6676
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.063159 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 13.6487
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 13.4762
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 13.4126
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.061066 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 24.1211
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.060929 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 26.5041
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.061066 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 26.5637
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.058527 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 8.0767
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.058987 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 6.9605
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.058987 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 6.7835
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.058987 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 32.7968
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.05778 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 22.4186
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.05778 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 29.7567
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 42.9246
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 43.4714
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 42.6512
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.053703 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 9.7739
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.053703 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 25.9923
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.057595 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 12.9013
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.053927 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 2.6963
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.053958 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 2.2662
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.049507 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 30.4468
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.049507 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 29.0606
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.095404 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 51.2319
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.095404 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 75.0829
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.091624 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 6.8718
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.091624 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 20.3405
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.14621 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -83.1952
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.086399 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -18.0574
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.086399 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -18.6622
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.086374 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -35.1542
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -3.9744
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -4.0608
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -3.9744
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -3.9744
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.086629 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -36.7307
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.086629 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -36.8173
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.085832 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -4.9783
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.085832 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -7.639
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -3.7766
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -3.7766
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -3.6908
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -3.8624
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.086499 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -35.6376
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.086499 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -34.5996
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.086202 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -47.0663
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.086202 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -64.6515
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -5.3066
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -8.2643
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -13.1359
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -13.3925
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -14.6885
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -13.3925
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.071384 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.5704
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.071384 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.78522
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.071384 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.78522
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.4304
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.6825
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.3082
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.452
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.89842
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.82355
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077254 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.8541
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077254 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.8541
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077254 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -1.7768
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.082282 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -32.5837
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.049882 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -66.4927
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.049882 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -66.2433
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.8093
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.4268
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -1.1089
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.073928 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -3.4746
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 3.4758
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.054466 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 8.1699
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.052053 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 8.823
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.024951 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 3.7426
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.05367 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 3.3812
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.056763 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 36.8789
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.058183 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 2.3273
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.058183 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 2.3273
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.051203 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -21.6077
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -11.9562
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -12.1373
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -29.2564
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -19.1197
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -19.3618
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -21.1769
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.10361 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -60.5059
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.10361 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -61.6456
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.10347 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -44.8034
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -21.6811
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -21.7876
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -21.7489
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -21.9523
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.0771 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.6168
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.0771 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.6168
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.64928
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.64928
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.54107
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.039538 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.54167
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.055927 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.0067
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.055927 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.0067
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -2.3324
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -2.2658
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -2.3324
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.050969 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -1.4271
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.050969 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -1.4781
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.051729 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.8105
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.051729 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.5519
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.5969
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.5969
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.5969
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.5969
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.090176 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.54106
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.21682
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.21682
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.25296
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.090158 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.36063
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.087938 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.21105
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.087938 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.21105
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -13.1897
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -12.3822
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -12.5616
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -13.1897
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -16.3301
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -17.7657
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -17.8295
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -17.4788
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -27.1944
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -13.2203
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -13.4996
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -14.0583
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -26.9993
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.042838 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -1.4137
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.042838 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.071
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.89842
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.071952 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -5.2525
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.3684
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -5.5044
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -1.9632
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.4908
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.3684
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -5.4364
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -5.3277
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.6989
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.1259
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.075826 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -47.6946
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.072629 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -10.4586
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.072629 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -13.6543
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.08356 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -1.0027
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.053575 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.32145
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.073228 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -24.6046
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073377 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -24.5079
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073377 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -24.9482
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.073455 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.7913
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.073391 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8348
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.073391 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8348
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.073461 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.7915
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.073781 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -2.1396
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -10.8609
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -10.8829
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -11.2051
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -11.4653
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -11.1024
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -7.2565
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -10.5219
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -10.6671
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -9.2158
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -10.8644
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -10.9683
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -12.8297
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -15.3277
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -16.046
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -17.9194
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.6625
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.6625
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -12.6617
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.081553 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -25.2814
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.081553 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -33.6814
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -3.4941
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -3.6605
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -3.6605
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -3.9101
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -4.1626
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -3.9078
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -3.9078
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -3.9927
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -13.0826
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -12.5729
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -4.0777
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -4.0777
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.6845
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.6845
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 4.8846
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 4.2109
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 4.2109
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 6.0531
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 10.9569
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 7.4783
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 6.9678
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 7.1573
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 7.7362
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 11.0517
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 11.3364
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 6.8615
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 13.506
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 10.6855
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 10.6928
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 6.5173
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.051895 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 7.7324
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.053347 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 9.6025
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.053347 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 9.6025
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.053297 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 11.9918
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.053938 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.7423
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.053938 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.7423
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 8.1204
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 8.1784
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 17.9229
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 8.2944
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 8.3524
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 17.9809
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.060186 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 11.7965
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.060186 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 6.6806
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.058492 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 9.2073
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 9.3788
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 9.3788
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 23.6758
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 9.2645
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 9.2073
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 9.3216
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 23.3899
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.058015 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.058015 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 8.0431
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 7.0648
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 7.88
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 21.6837
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 7.5885
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 7.6036
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 8.933
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 7.6526
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 7.693
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 8.9659
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.14621 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -84.9498
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 26.9864
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 26.9864
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.01139 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.36448
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.009873 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.4739
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.009873 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.45416
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.13728
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.58344
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01144 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.19448
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.25168
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.286
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.009873 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 1.0367
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.053861 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 4.5243
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.046247 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 3.6998
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.046198 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 6.9297
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.046198 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 6.9297
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -1.9675
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -1.8535
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -1.4728
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -4.2573
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -4.2656
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -4.2323
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -2.6677
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -6.7805
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.1116
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -2.7886
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -2.5829
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -2.8554
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -2.8359
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.027802 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.88966
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.027802 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.83406
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -4.0593
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -4.0593
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -4.3518
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -4.0044
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 4.807
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 4.8291
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.022383 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -3.0441
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.030716 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.0136
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.9387
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.9387
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.8493
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.8493
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.038022 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -2.6996
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.038022 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.38022
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -5.1048
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -5.1048
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -7.6729
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.586
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -1.464
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.586
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.586
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.023083 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -3.4394
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.023083 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -1.5027
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -2.2565
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -2.1722
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -2.1573
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.3514
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.30252
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.020697 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -15.3779
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.021368 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -15.7055
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -3.5251
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -3.5251
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -3.5251
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -2.9016
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.02225 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -3.8493
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.02225 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -3.0038
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -3.2594
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -3.2314
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -3.1813
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -5.3897
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -1.4745
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -1.4561
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -1.903
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -1.6957
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -3.8287
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -3.6856
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -3.6949
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -3.6832
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -6.3107
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.020733 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.10366
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.020733 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.43539
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 1.4637
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.4808
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.4808
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 3.607
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.019857 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -7.9031
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.0955
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.0955
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.0955
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.3099
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.3099
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -1.2861
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.038747 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 32.0438
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.038747 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 31.7338
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.031481 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -1.4513
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -3.7492
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -3.7492
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -5.1799
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -3.6506
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -3.6506
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -5.0319
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -4.1449
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -3.6521
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -3.6152
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.023295 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.81532
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.025809 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -11.8463
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -1.3473
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -1.368
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -1.451
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -1.3059
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -1.2851
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -2.1557
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -1.223
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -2.6164
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5829
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5829
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016772 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -2.7171
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.020575 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -3.2303
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -1.6172
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -1.6399
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.8883
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.68331
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.023663 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -1.8457
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.023663 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -1.893
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.023042 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.37328
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.023094 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -3.8105
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.023108 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -3.9053
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.023047 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -4.909
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.023033 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -5.2515
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.023118 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.27742
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.023118 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.41612
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.02668 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -1.334
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.2483
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.2483
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1674
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.1458
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1674
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.2322
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1674
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1674
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.2538
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.2538
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.021001 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.25201
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.096
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.1547
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.096
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.096
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.1547
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.096
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.046966 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -3.0998
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -4.9099
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -5.0623
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -7.563
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030496 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -16.6508
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030496 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -19.6089
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -20.4167
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -17.6882
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -18.8172
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030496 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.39645
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.020716 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.24859
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.72097
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.73581
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.6934
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.97331
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.37533
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.43258
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.42198
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.74218
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.38169
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -1.8109
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -3.1383
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -2.4709
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -2.8456
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -1.7934
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -4.0253
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -3.4274
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -3.5072
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -1.9927
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.71737
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -3.7463
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -2.7898
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -2.5108
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -2.8695
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -2.5825
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -4.0253
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -3.8658
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -4.105
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -3.0289
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -3.1883
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -3.1883
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -6.815
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.64151
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.043921 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 3.36
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 3.7075
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.8538
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.046737 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.739
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.046259 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 3.7007
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.044241 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 3.5393
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.04358 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 3.6607
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.046737 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.739
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -9.9594
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 6.414
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 12.4538
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 9.0972
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -19.3946
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -16.0748
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -19.5693
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -10.0467
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -8.7363
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.05515 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 3.309
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.028706 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.033046 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.048181 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.23127
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 2.0335
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 5.8295
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 7.3208
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 6.4531
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 5.6939
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 4.3654
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.052824 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 7.9236
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 5.9237
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 7.8719
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 9.7938
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 11.2945
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.073928 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.056072 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.077199 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -1.9027
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -2.9628
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -5.0287
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.9454
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -3.0294
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.8077
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.4039
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.9454
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.6599
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -3.1771
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.6255
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7345
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0517
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.4908
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0517
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7345
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7345
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -10.9353
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.6944
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -4.0638
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.6944
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.072565 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.87078
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.070787 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.0618
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.070787 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.6281
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.068459 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.286
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.070368 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.56294
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.073248 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -13.1846
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.073228 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -13.181
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073377 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.2079
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073377 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.2079
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077205 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -7.7205
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077205 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -7.7205
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8208
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8208
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8208
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.1653
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8208
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8208
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8208
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.0924
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077205 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077205 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -38.6025
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077205 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -38.6025
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077205 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.076548 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.042838 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.075546 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.074962 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | [7 empty] | 30.7427
Number of Bus | Name of Bus | ID | Max MW | L: TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.091074 | north | Y | 0.03567 | 0.18014 | 0.038464 | 0.11789 | 0.03567 | North | N | 0.03567 | 0
239 | BOSQUESW | 1 | 149 | 0.091074 | north | Y | 0.03567 | 0.18014 | 0.038464 | 0.11789 | 0.03567 | North | N | 0.03567 | 0
244 | WHITNYDM | 1 | 15 | 0.083008 | north | N | 0.027604 | 0.17207 | 0.030398 | 0.10983 | 0.027604 | North | N | 0.027604 | 0
245 | WHITNYDM | 2 | 15 | 0.083008 | north | N | 0.027604 | 0.17207 | 0.030398 | 0.10983 | 0.027604 | North | N | 0.027604 | 0
247 | BOSQUESW | 2 | 153 | 0.091074 | north | Y | 0.03567 | 0.18014 | 0.038464 | 0.11789 | 0.03567 | North | N | 0.03567 | 0
251 | BOSQUESW | 2 | 150 | 0.087779 | north | Y | 0.032375 | 0.17684 | 0.035169 | 0.1146 | 0.032375 | North | N | 0.032375 | 0
253 | BOSQUESW | 2 | 80 | 0.087779 | north | Y | 0.032375 | 0.17684 | 0.035169 | 0.1146 | 0.032375 | North | N | 0.032375 | 0
332 | RWMILLER | 1 | 73 | 0.061862 | north | Y | 0.0064582 | 0.15093 | 0.0092517 | 0.088679 | 0.0064582 | North | N | 0.0064582 | 0
333 | RWMILLER | 2 | 119 | 0.061862 | north | Y | 0.0064582 | 0.15093 | 0.0092517 | 0.088679 | 0.0064582 | North | N | 0.0064582 | 0
334 | RWMILLER | 3 | 205 | 0.061862 | north | Y | 0.0064582 | 0.15093 | 0.0092517 | 0.088679 | 0.0064582 | North | N | 0.0064582 | 0
335 | RWMILLER | 4 | 102 | 0.061862 | north | Y | 0.0064582 | 0.15093 | 0.0092517 | 0.088679 | 0.0064582 | North | N | 0.0064582 | 0
336 | RWMILLER | 5 | 96 | 0.061862 | north | Y | 0.0064582 | 0.15093 | 0.0092517 | 0.088679 | 0.0064582 | North | N | 0.0064582 | 0
344 | MRSSHPRD | 1 | 12 | 0.059677 | north | N | 0.0042732 | 0.14874 | 0.0070667 | 0.086494 | 0.0042732 | North | N | 0.0042732 | 0
345 | MRSSHPRD | 2 | 12 | 0.059677 | north | N | 0.0042732 | 0.14874 | 0.0070667 | 0.086494 | 0.0042732 | North | N | 0.0042732 | 0
366 | JNSNCNTY | 1 | 168 | 0.064488 | north | Y | 0.0090842 | 0.15355 | 0.011878 | 0.091305 | 0.0090842 | North | N | 0.0090842 | 0
367 | JNSNCNTY | 2 | 90 | 0.064488 | north | Y | 0.0090842 | 0.15355 | 0.011878 | 0.091305 | 0.0090842 | North | N | 0.0090842 | 0
503 | NTHTEXAS | 1 | 18 | 0.060907 | north | Y | 0.0055032 | 0.14997 | 0.0082967 | 0.087724 | 0.0055032 | North | N | 0.0055032 | 0
504 | NTHTEXAS | 2 | 18 | 0.060907 | north | Y | 0.0055032 | 0.14997 | 0.0082967 | 0.087724 | 0.0055032 | North | N | 0.0055032 | 0
505 | NTHTEXAS | 3 | 38 | 0.060907 | north | Y | 0.0055032 | 0.14997 | 0.0082967 | 0.087724 | 0.0055032 | North | N | 0.0055032 | 0
580 | JCKCNTY8 | 1 | 288 | 0.060103 | north | Y | 0.0046992 | 0.14917 | 0.0074927 | 0.08692 | 0.0046992 | North | N | 0.0046992 | 0
581 | JCKCNTY8 | 2 | 147 | 0.060103 | north | Y | 0.0046992 | 0.14917 | 0.0074927 | 0.08692 | 0.0046992 | North | N | 0.0046992 | 0
582 | JCKCNTY8 | 3 | 147 | 0.060103 | north | Y | 0.0046992 | 0.14917 | 0.0074927 | 0.08692 | 0.0046992 | North | N | 0.0046992 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.059265 | north | Y | 0.0038612 | 0.14833 | 0.0066547 | 0.086082 | 0.0038612 | North | N | 0.0038612 | 0
837 | NEWMAN_G | 1 | 40 | 0.057883 | north | Y | 0.0024792 | 0.14695 | 0.0052727 | 0.0847 | 0.0024792 | North | N | 0.0024792 | 0
842 | OLINGER_ | 1 | 79 | 0.057861 | north | Y | 0.0024572 | 0.14692 | 0.0052507 | 0.084678 | 0.0024572 | North | N | 0.0024572 | 0
843 | OLINGER_ | 1 | 106 | 0.057861 | north | Y | 0.0024572 | 0.14692 | 0.0052507 | 0.084678 | 0.0024572 | North | N | 0.0024572 | 0
844 | OLINGER_ | 1 | 146 | 0.057861 | north | Y | 0.0024572 | 0.14692 | 0.0052507 | 0.084678 | 0.0024572 | North | N | 0.0024572 | 0
845 | OLINGER_ | 1 | 76 | 0.057861 | north | Y | 0.0024572 | 0.14692 | 0.0052507 | 0.084678 | 0.0024572 | North | N | 0.0024572 | 0
923 | SPENCER_ | 1 | 60 | 0.059107 | north | Y | 0.0037032 | 0.14817 | 0.0064967 | 0.085924 | 0.0037032 | North | N | 0.0037032 | 0
924 | SPENCER_ | 1 | 63 | 0.059107 | north | Y | 0.0037032 | 0.14817 | 0.0064967 | 0.085924 | 0.0037032 | North | N | 0.0037032 | 0
948 | STEAM1 | 1 | 20 | 0.057763 | north | Y | 0.0023592 | 0.14683 | 0.0051527 | 0.08458 | 0.0023592 | North | N | 0.0023592 | 0
949 | STEAM2 | 1 | 25 | 0.057763 | north | Y | 0.0023592 | 0.14683 | 0.0051527 | 0.08458 | 0.0023592 | North | N | 0.0023592 | 0
950 | STEAM3 | 1 | 41 | 0.057763 | north | Y | 0.0023592 | 0.14683 | 0.0051527 | 0.08458 | 0.0023592 | North | N | 0.0023592 | 0
990 | GIBN_CRE | 1 | 463 | 0.014502 | north | Y | -0.040902 | 0.10357 | -0.038108 | 0.041319 | 0.038108 | west | Y | 0.040902 | 1.2934
1002 | PBCTAGE_ | A | 66 | 0.05168 | west | Y | -0.0037238 | 0.14074 | -0.00093035 | 0.078497 | 0.00093035 | west | N | 0.00093035 | 0
1003 | PBCTBGE_ | B | 65 | 0.05168 | west | Y | -0.0037238 | 0.14074 | -0.00093035 | 0.078497 | 0.00093035 | west | N | 0.00093035 | 0
1004 | PBCTCGE_ | C | 67 | 0.05168 | west | Y | -0.0037238 | 0.14074 | -0.00093035 | 0.078497 | 0.00093035 | west | N | 0.00093035 | 0
1005 | PBCTDGE_ | D | 67 | 0.05168 | west | Y | -0.0037238 | 0.14074 | -0.00093035 | 0.078497 | 0.00093035 | west | N | 0.00093035 | 0
1006 | PBCTEGE_ | E | 67 | 0.05168 | west | Y | -0.0037238 | 0.14074 | -0.00093035 | 0.078497 | 0.00093035 | west | N | 0.00093035 | 0
1007 | PB5GEN_6 | MB | 114 | 0.05168 | west | Y | -0.0037238 | 0.14074 | -0.00093035 | 0.078497 | 0.00093035 | west | N | 0.00093035 | 0
1008 | PB6GEN_7 | MB | 515 | 0.05168 | west | Y | -0.0037238 | 0.14074 | -0.00093035 | 0.078497 | 0.00093035 | west | N | 0.00093035 | 0
1039 | MRGNAG_1 | A | 66 | 0.05361 | west | Y | -0.0017938 | 0.14267 | 0.00099965 | 0.080427 | 0.00099965 | west | N | 0.00099965 | 0
1040 | MRGNBG_2 | B | 69 | 0.05361 | west | Y | -0.0017938 | 0.14267 | 0.00099965 | 0.080427 | 0.00099965 | west | N | 0.00099965 | 0
1041 | MRGNCG_3 | C | 69 | 0.05361 | west | Y | -0.0017938 | 0.14267 | 0.00099965 | 0.080427 | 0.00099965 | west | N | 0.00099965 | 0
1042 | MRGNDG_4 | D | 67 | 0.05361 | west | Y | -0.0017938 | 0.14267 | 0.00099965 | 0.080427 | 0.00099965 | west | N | 0.00099965 | 0
1043 | MRGNEG_5 | E | 67 | 0.05361 | west | Y | -0.0017938 | 0.14267 | 0.00099965 | 0.080427 | 0.00099965 | west | N | 0.00099965 | 0
1044 | MRGNFG_6 | F | 65 | 0.05361 | west | Y | -0.0017938 | 0.14267 | 0.00099965 | 0.080427 | 0.00099965 | west | N | 0.00099965 | 0
1045 | CALENG1G | 1 | 70 | 0.053312 | west | N | -0.0020918 | 0.14238 | 0.00070165 | 0.080129 | 0.00070165 | west | N | 0.00070165 | 0
1046 | CALENG2G | 2 | 73.4 | 0.053312 | west | N | -0.0020918 | 0.14238 | 0.00070165 | 0.080129 | 0.00070165 | west | N | 0.00070165 | 0
1047 | CALENG3G | 3 | 70.4 | 0.053312 | west | N | -0.0020918 | 0.14238 | 0.00070165 | 0.080129 | 0.00070165 | west | N | 0.00070165 | 0
1058 | LONGSHOR | 1 | 150 | 0.053464 | west | Y | -0.0019398 | 0.14253 | 0.00085365 | 0.080281 | 0.00085365 | west | N | 0.00085365 | 0
1058 | LONGSHOR | 2 | 220 | 0.053464 | west | Y | -0.0019398 | 0.14253 | 0.00085365 | 0.080281 | 0.00085365 | west | N | 0.00085365 | 0
1061 | CIELOGEN | 1 | 99 | 0.053724 | west | Y | -0.0016798 | 0.14279 | 0.0011137 | 0.080541 | 0.0011137 | west | N | 0.0011137 | 0
1062 | CIELOGEN | 1 | 61 | 0.053724 | west | Y | -0.0016798 | 0.14279 | 0.0011137 | 0.080541 | 0.0011137 | west | N | 0.0011137 | 0
1068 | SCURRYCW | 1 | 141 | 0.053709 | west | Y | -0.0016948 | 0.14277 | 0.0010987 | 0.080526 | 0.0010987 | west | N | 0.0010987 | 0
1069 | KINDERMG | 1 | 25 | 0.053724 | west | N | -0.0016798 | 0.14279 | 0.0011137 | 0.080541 | 0.0011137 | west | N | 0.0011137 | 0
1070 | KINDERMG | 1 | 45.7 | 0.053724 | west | N | -0.0016798 | 0.14279 | 0.0011137 | 0.080541 | 0.0011137 | west | N | 0.0011137 | 0
1071 | KINDERMG | 1 | 45.7 | 0.053724 | west | N | -0.0016798 | 0.14279 | 0.0011137 | 0.080541 | 0.0011137 | west | N | 0.0011137 | 0
1073 | SCURRYCW | 2 | 120 | 0.053709 | west | Y | -0.0016948 | 0.14277 | 0.0010987 | 0.080526 | 0.0010987 | west | N | 0.0010987 | 0
1320 | BSP 1 | 1 | 25.8 | 0.052915 | west | N | -0.0024888 | 0.14198 | 0.00030465 | 0.079732 | 0.00030465 | west | N | 0.00030465 | 0
1326 | STANTONW | 1 | 100.5 | 0.052701 | west | Y | -0.0027028 | 0.14176 | 9.065e-05 | 0.079518 | 9.065e-05 | west | N | 9.065e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.053188 | west | Y | -0.0022158 | 0.14225 | 0.00057765 | 0.080005 | 0.00057765 | west | N | 0.00057765 | 0
1328 | OCOTILLO | 1 | 58 | 0.052683 | west | Y | -0.0027208 | 0.14175 | 7.265e-05 | 0.0795 | 7.265e-05 | west | N | 7.265e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.052812 | west | Y | -0.0025918 | 0.14188 | 0.00020165 | 0.079629 | 0.00020165 | west | N | 0.00020165 | 0
1343 | TRENTIPP | 1 | 150 | 0.054125 | west | Y | -0.0012788 | 0.14319 | 0.0015147 | 0.080942 | 0.0012788 | North | Y | 0.0015147 | 0.035378
1349 | WESTXWIN | 1 | 6.6 | 0.052308 | west | Y | -0.0030958 | 0.14137 | -0.00030235 | 0.079125 | 0.00030235 | west | N | 0.00030235 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.052308 | west | Y | -0.0030958 | 0.14137 | -0.00030235 | 0.079125 | 0.00030235 | west | N | 0.00030235 | 0
1354 | AEPWIND_ | 1 | 101 | 0.054125 | west | Y | -0.0012788 | 0.14319 | 0.0015147 | 0.080942 | 0.0012788 | North | Y | 0.0015147 | 0.023821
1360 | GUNSIGHT | 1 | 120 | 0.053211 | west | Y | -0.0021928 | 0.14227 | 0.00060065 | 0.080028 | 0.00060065 | west | N | 0.00060065 | 0
1432 | GRHAMSES | 2 | 366 | 0.057944 | north | Y | 0.0025402 | 0.14701 | 0.0053337 | 0.084761 | 0.0025402 | North | N | 0.0025402 | 0
1433 | GRHAMSES | 1 | 242 | 0.058218 | north | Y | 0.0028142 | 0.14728 | 0.0056077 | 0.085035 | 0.0028142 | North | N | 0.0028142 | 0
1437 | MESQUITW | 1 | 400 | 0.055832 | west | Y | 0.0004282 | 0.1449 | 0.0032217 | 0.082649 | 0.0004282 | North | Y | 0.0032217 | 1.1174
1438 | MESQUITW | 1 | 236 | 0.055834 | west | Y | 0.0004302 | 0.1449 | 0.0032237 | 0.082651 | 0.0004302 | North | Y | 0.0032237 | 0.65925
1442 | COKFIELD | 1 | 165 | 0.056341 | west | Y | 0.0009372 | 0.1454 | 0.0037307 | 0.083158 | 0.0009372 | North | Y | 0.0037307 | 0.46092
1453 | WCPWRCO_ | 1 | 204 | 0.059059 | north | Y | 0.0036552 | 0.14812 | 0.0064487 | 0.085876 | 0.0036552 | North | N | 0.0036552 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.059059 | north | Y | 0.0036552 | 0.14812 | 0.0064487 | 0.085876 | 0.0036552 | North | N | 0.0036552 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.059059 | north | Y | 0.0036552 | 0.14812 | 0.0064487 | 0.085876 | 0.0036552 | North | N | 0.0036552 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.058067 | west | Y | 0.0026632 | 0.14713 | 0.0054567 | 0.084884 | 0.0026632 | North | Y | 0.0054567 | 0.055869
1479 | WFCOGEN_ | 2 | 20 | 0.058067 | west | Y | 0.0026632 | 0.14713 | 0.0054567 | 0.084884 | 0.0026632 | North | Y | 0.0054567 | 0.055869
1482 | WFCOGEN_ | 1 | 20 | 0.058067 | west | Y | 0.0026632 | 0.14713 | 0.0054567 | 0.084884 | 0.0026632 | North | Y | 0.0054567 | 0.055869
1482 | WFCOGEN_ | 2 | 17 | 0.058067 | west | Y | 0.0026632 | 0.14713 | 0.0054567 | 0.084884 | 0.0026632 | North | Y | 0.0054567 | 0.047489
1600 | BARTNWND | 1 | 120 | 0.059685 | north | Y | 0.0042812 | 0.14875 | 0.0070747 | 0.086502 | 0.0042812 | North | N | 0.0042812 | 0
1643 | SLSTR1PP | 1 | 60 | 0.061783 | north | Y | 0.0063792 | 0.15085 | 0.0091727 | 0.0886 | 0.0063792 | North | N | 0.0063792 | 0
1675 | PEC_1G | 1 | 75 | 0.057899 | north | N | 0.0024952 | 0.14696 | 0.0052887 | 0.084716 | 0.0024952 | North | N | 0.0024952 | 0
1676 | PEC_2G | 2 | 79.6 | 0.057899 | north | N | 0.0024952 | 0.14696 | 0.0052887 | 0.084716 | 0.0024952 | North | N | 0.0024952 | 0
1677 | PEC_3G | 3 | 88.4 | 0.057899 | north | N | 0.0024952 | 0.14696 | 0.0052887 | 0.084716 | 0.0024952 | North | N | 0.0024952 | 0
1678 | LAMARPWR | 1 | 160 | 0.057948 | north | Y | 0.0025442 | 0.14701 | 0.0053377 | 0.084765 | 0.0025442 | North | N | 0.0025442 | 0
1679 | LAMARPWR | 2 | 156 | 0.057948 | north | Y | 0.0025442 | 0.14701 | 0.0053377 | 0.084765 | 0.0025442 | North | N | 0.0025442 | 0
1680 | LAMARPWR | 3 | 196 | 0.057948 | north | Y | 0.0025442 | 0.14701 | 0.0053377 | 0.084765 | 0.0025442 | North | N | 0.0025442 | 0
1681 | LAMARPWR | 4 | 156 | 0.057948 | north | Y | 0.0025442 | 0.14701 | 0.0053377 | 0.084765 | 0.0025442 | North | N | 0.0025442 | 0
1682 | LAMARPWR | 5 | 157 | 0.057948 | north | Y | 0.0025442 | 0.14701 | 0.0053377 | 0.084765 | 0.0025442 | North | N | 0.0025442 | 0
1683 | LAMARPWR | 6 | 198 | 0.057948 | north | Y | 0.0025442 | 0.14701 | 0.0053377 | 0.084765 | 0.0025442 | North | N | 0.0025442 | 0
1687 | VALLEY_1 | 1 | 170 | 0.0581 | north | Y | 0.0026962 | 0.14716 | 0.0054897 | 0.084917 | 0.0026962 | North | N | 0.0026962 | 0
1688 | VALLEY_2 | 2 | 520 | 0.0581 | north | Y | 0.0026962 | 0.14716 | 0.0054897 | 0.084917 | 0.0026962 | North | N | 0.0026962 | 0
1689 | VALLEY_3 | 3 | 370 | 0.058003 | north | Y | 0.0025992 | 0.14707 | 0.0053927 | 0.08482 | 0.0025992 | North | N | 0.0025992 | 0
1701 | MOSES_1G | 1 | 558 | 0.057857 | north | Y | 0.0024532 | 0.14692 | 0.0052467 | 0.084674 | 0.0024532 | North | N | 0.0024532 | 0
1702 | MOSES_2G | 2 | 579 | 0.057857 | north | Y | 0.0024532 | 0.14692 | 0.0052467 | 0.084674 | 0.0024532 | North | N | 0.0024532 | 0
1703 | MOSES_3G | 3 | 808 | 0.057857 | north | Y | 0.0024532 | 0.14692 | 0.0052467 | 0.084674 | 0.0024532 | North | N | 0.0024532 | 0
1861 | EAGLEMNT | MB | 112 | 0.060138 | north | Y | 0.0047342 | 0.1492 | 0.0075277 | 0.086955 | 0.0047342 | North | N | 0.0047342 | 0
1862 | EAGLEMNT | MB | 100 | 0.060138 | north | Y | 0.0047342 | 0.1492 | 0.0075277 | 0.086955 | 0.0047342 | North | N | 0.0047342 | 0
1863 | EAGLEMNT | MB | 378 | 0.060138 | north | Y | 0.0047342 | 0.1492 | 0.0075277 | 0.086955 | 0.0047342 | North | N | 0.0047342 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.061053 | north | Y | 0.0056492 | 0.15012 | 0.0084427 | 0.08787 | 0.0056492 | North | N | 0.0056492 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.061053 | north | Y | 0.0056492 | 0.15012 | 0.0084427 | 0.08787 | 0.0056492 | North | N | 0.0056492 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.061053 | north | Y | 0.0056492 | 0.15012 | 0.0084427 | 0.08787 | 0.0056492 | North | N | 0.0056492 | 0
1889 | DECRDOVA | MB | 770 | 0.061187 | north | Y | 0.0057832 | 0.15025 | 0.0085767 | 0.088004 | 0.0057832 | North | N | 0.0057832 | 0
1892 | DECRDOVA | A | 70 | 0.062472 | north | Y | 0.0070682 | 0.15154 | 0.0098617 | 0.089289 | 0.0070682 | North | N | 0.0070682 | 0
1893 | DECRDOVA | B | 69 | 0.062472 | north | Y | 0.0070682 | 0.15154 | 0.0098617 | 0.089289 | 0.0070682 | North | N | 0.0070682 | 0
1894 | DECRDOVA | C | 69 | 0.062472 | north | Y | 0.0070682 | 0.15154 | 0.0098617 | 0.089289 | 0.0070682 | North | N | 0.0070682 | 0
1895 | DECRDOVA | D | 68 | 0.062472 | north | Y | 0.0070682 | 0.15154 | 0.0098617 | 0.089289 | 0.0070682 | North | N | 0.0070682 | 0
1898 | COMCHEPK | 1 | 1157 | 0.060962 | north | N | 0.0055582 | 0.15003 | 0.0083517 | 0.087779 | 0.0055582 | North | N | 0.0055582 | 0
1899 | COMCHEPK | 2 | 1158 | 0.060962 | north | N | 0.0055582 | 0.15003 | 0.0083517 | 0.087779 | 0.0055582 | North | N | 0.0055582 | 0
1937 | MDLTHELP | 5 | 224 | 0.063567 | north | Y | 0.0081632 | 0.15263 | 0.010957 | 0.090384 | 0.0081632 | North | N | 0.0081632 | 0
1938 | MDLTHELP | 6 | 226 | 0.063567 | north | Y | 0.0081632 | 0.15263 | 0.010957 | 0.090384 | 0.0081632 | North | N | 0.0081632 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.063159 | north | Y | 0.0077552 | 0.15222 | 0.010549 | 0.089976 | 0.0077552 | North | N | 0.0077552 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.063159 | north | Y | 0.0077552 | 0.15222 | 0.010549 | 0.089976 | 0.0077552 | North | N | 0.0077552 | 0
1943 | MDLTHELP | 3 | 212 | 0.063567 | north | Y | 0.0081632 | 0.15263 | 0.010957 | 0.090384 | 0.0081632 | North | N | 0.0081632 | 0
1944 | MDLTHELP | 4 | 211 | 0.063567 | north | Y | 0.0081632 | 0.15263 | 0.010957 | 0.090384 | 0.0081632 | North | N | 0.0081632 | 0
1947 | HANDLEY_ | 3 | 395 | 0.061066 | north | Y | 0.0056622 | 0.15013 | 0.0084557 | 0.087883 | 0.0056622 | North | N | 0.0056622 | 0
1948 | HANDLEY_ | 4 | 435 | 0.060929 | north | Y | 0.0055252 | 0.14999 | 0.0083187 | 0.087746 | 0.0055252 | North | N | 0.0055252 | 0
1949 | HANDLEY_ | 5 | 435 | 0.061066 | north | Y | 0.0056622 | 0.15013 | 0.0084557 | 0.087883 | 0.0056622 | North | N | 0.0056622 | 0
2371 | COLLIN_1 | MB | 138 | 0.058527 | north | Y | 0.0031232 | 0.14759 | 0.0059167 | 0.085344 | 0.0031232 | North | N | 0.0031232 | 0
2413 | MTCK6_G | 6 | 118 | 0.058987 | north | Y | 0.0035832 | 0.14805 | 0.0063767 | 0.085804 | 0.0035832 | North | N | 0.0035832 | 0
2414 | MTCK7_G | 7 | 115 | 0.058987 | north | Y | 0.0035832 | 0.14805 | 0.0063767 | 0.085804 | 0.0035832 | North | N | 0.0035832 | 0
2417 | MTCK8_G | 8 | 556 | 0.058987 | north | Y | 0.0035832 | 0.14805 | 0.0063767 | 0.085804 | 0.0035832 | North | N | 0.0035832 | 0
2451 | LKHB1_G | 1 | 388 | 0.05778 | north | Y | 0.0023762 | 0.14684 | 0.0051697 | 0.084597 | 0.0023762 | North | N | 0.0023762 | 0
2452 | LKHB2_G | 2 | 515 | 0.05778 | north | Y | 0.0023762 | 0.14684 | 0.0051697 | 0.084597 | 0.0023762 | North | N | 0.0023762 | 0
3097 | MARTLAKE | 1 | 785 | 0.054681 | north | Y | -0.0007228 | 0.14374 | 0.0020707 | 0.081498 | 0.0007228 | North | N | 0.0007228 | 0
3098 | MARTLAKE | 2 | 795 | 0.054681 | north | Y | -0.0007228 | 0.14374 | 0.0020707 | 0.081498 | 0.0007228 | North | N | 0.0007228 | 0
3099 | MARTLAKE | 3 | 780 | 0.054681 | north | Y | -0.0007228 | 0.14374 | 0.0020707 | 0.081498 | 0.0007228 | North | N | 0.0007228 | 0
3107 | STRYKER_ | 1 | 182 | 0.053703 | north | Y | -0.0017008 | 0.14277 | 0.0010927 | 0.08052 | 0.0010927 | west | Y | 0.0017008 | 0.11068
3108 | STRYKER_ | 2 | 484 | 0.053703 | north | Y | -0.0017008 | 0.14277 | 0.0010927 | 0.08052 | 0.0010927 | west | Y | 0.0017008 | 0.29434
3126 | TRINIDAD | 1 | 224 | 0.057595 | north | Y | 0.0021912 | 0.14666 | 0.0049847 | 0.084412 | 0.0021912 | North | N | 0.0021912 | 0
3309 | ASPN_G | 1 | 50 | 0.053927 | north | Y | -0.0014768 | 0.14299 | 0.0013167 | 0.080744 | 0.0013167 | west | Y | 0.0014768 | 0.0080073
3348 | CHAMPION | MB | 42 | 0.053958 | north | N | -0.0014458 | 0.14302 | 0.0013477 | 0.080775 | 0.0013477 | west | Y | 0.0014458 | 0
3381 | BBRN_1G | 1 | 615 | 0.049507 | north | Y | -0.0058968 | 0.13857 | -0.0031033 | 0.076324 | 0.0031033 | west | Y | 0.0058968 | 1.718
3382 | BBRN_2G | 2 | 587 | 0.049507 | north | Y | -0.0058968 | 0.13857 | -0.0031033 | 0.076324 | 0.0031033 | west | Y | 0.0058968 | 1.6398
3403 | THOUSE_1 | MB | 537 | 0.095404 | north | Y | 0.04 | 0.18447 | 0.042794 | 0.12222 | 0.04 | North | N | 0.04 | 0
3404 | THOUSE_2 | 2 | 787 | 0.095404 | north | Y | 0.04 | 0.18447 | 0.042794 | 0.12222 | 0.04 | North | N | 0.04 | 0
3416 | LAKE_CRK | MB | 75 | 0.091624 | north | Y | 0.03622 | 0.18069 | 0.039014 | 0.11844 | 0.03622 | North | N | 0.03622 | 0
3417 | LAKE_CRK | MB | 222 | 0.091624 | north | Y | 0.03622 | 0.18069 | 0.039014 | 0.11844 | 0.03622 | North | N | 0.03622 | 0
3432 | SANDOW_4 | 4 | 569 | -0.14621 | south | Y | -0.20162 | -0.05715 | -0.19882 | -0.1194 | 0.05715 | south | N | 0.05715 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.086399 | south | Y | -0.1418 | 0.0026644 | -0.13901 | -0.059582 | 0.0026644 | south | N | 0.0026644 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.086399 | south | Y | -0.1418 | 0.0026644 | -0.13901 | -0.059582 | 0.0026644 | south | N | 0.0026644 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.086374 | south | Y | -0.14178 | 0.0026894 | -0.13898 | -0.059557 | 0.0026894 | south | N | 0.0026894 | 0
5031 | BRA_VHBC | 1 | 46 | -0.086399 | south | Y | -0.1418 | 0.0026644 | -0.13901 | -0.059582 | 0.0026644 | south | N | 0.0026644 | 0
5032 | BRA_VHBC | 2 | 47 | -0.086399 | south | Y | -0.1418 | 0.0026644 | -0.13901 | -0.059582 | 0.0026644 | south | N | 0.0026644 | 0
5033 | BRA_VHBC | 3 | 46 | -0.086399 | south | Y | -0.1418 | 0.0026644 | -0.13901 | -0.059582 | 0.0026644 | south | N | 0.0026644 | 0
5034 | BRA_VHBC | 4 | 46 | -0.086399 | south | Y | -0.1418 | 0.0026644 | -0.13901 | -0.059582 | 0.0026644 | south | N | 0.0026644 | 0
5111 | CALAVER_ | 1 | 424 | -0.086629 | south | Y | -0.14203 | 0.0024344 | -0.13924 | -0.059812 | 0.0024344 | south | N | 0.0024344 | 0
5112 | CALAVER_ | 2 | 425 | -0.086629 | south | Y | -0.14203 | 0.0024344 | -0.13924 | -0.059812 | 0.0024344 | south | N | 0.0024344 | 0
5264 | LEON_LCP | 3 | 58 | -0.085832 | south | Y | -0.14124 | 0.0032314 | -0.13844 | -0.059015 | 0.0032314 | south | N | 0.0032314 | 0
5265 | LEON_LCP | 4 | 89 | -0.085832 | south | Y | -0.14124 | 0.0032314 | -0.13844 | -0.059015 | 0.0032314 | south | N | 0.0032314 | 0
5266 | LEON_LCP | 1 | 44 | -0.085832 | south | Y | -0.14124 | 0.0032314 | -0.13844 | -0.059015 | 0.0032314 | south | N | 0.0032314 | 0
5267 | LEON_LCP | 2 | 44 | -0.085832 | south | Y | -0.14124 | 0.0032314 | -0.13844 | -0.059015 | 0.0032314 | south | N | 0.0032314 | 0
5268 | LEON_LCP | 3 | 43 | -0.085832 | south | Y | -0.14124 | 0.0032314 | -0.13844 | -0.059015 | 0.0032314 | south | N | 0.0032314 | 0
5269 | LEON_LCP | 4 | 45 | -0.085832 | south | Y | -0.14124 | 0.0032314 | -0.13844 | -0.059015 | 0.0032314 | south | N | 0.0032314 | 0
5396 | CALAVER_ | 1 | 412 | -0.086499 | south | Y | -0.1419 | 0.0025644 | -0.13911 | -0.059682 | 0.0025644 | south | N | 0.0025644 | 0
5397 | CALAVER_ | 2 | 400 | -0.086499 | south | Y | -0.1419 | 0.0025644 | -0.13911 | -0.059682 | 0.0025644 | south | N | 0.0025644 | 0
5401 | CALAVER_ | 1 | 546 | -0.086202 | south | Y | -0.14161 | 0.0028614 | -0.13881 | -0.059385 | 0.0028614 | south | N | 0.0028614 | 0
5402 | CALAVER_ | 2 | 750 | -0.086202 | south | Y | -0.14161 | 0.0028614 | -0.13881 | -0.059385 | 0.0028614 | south | N | 0.0028614 | 0
5436 | TUTTL_WB | MB | 61 | -0.086993 | south | Y | -0.1424 | 0.0020704 | -0.1396 | -0.060176 | 0.0020704 | south | N | 0.0020704 | 0
5438 | TUTTL_WB | MB | 95 | -0.086993 | south | Y | -0.1424 | 0.0020704 | -0.1396 | -0.060176 | 0.0020704 | south | N | 0.0020704 | 0
5439 | TUTTL_WB | MB | 151 | -0.086993 | south | Y | -0.1424 | 0.0020704 | -0.1396 | -0.060176 | 0.0020704 | south | N | 0.0020704 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.086403 | south | Y | -0.14181 | 0.0026604 | -0.13901 | -0.059586 | 0.0026604 | south | N | 0.0026604 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.086403 | south | Y | -0.14181 | 0.0026604 | -0.13901 | -0.059586 | 0.0026604 | south | N | 0.0026604 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.086403 | south | Y | -0.14181 | 0.0026604 | -0.13901 | -0.059586 | 0.0026604 | south | N | 0.0026604 | 0
5503 | RAYBURNG | 1 | 22 | -0.071384 | south | Y | -0.12679 | 0.017679 | -0.12399 | -0.044567 | 0.017679 | south | N | 0.017679 | 0
5505 | RAYBURNG | 1 | 11 | -0.071384 | south | Y | -0.12679 | 0.017679 | -0.12399 | -0.044567 | 0.017679 | south | N | 0.017679 | 0
5506 | RAYBURNG | 1 | 11 | -0.071384 | south | Y | -0.12679 | 0.017679 | -0.12399 | -0.044567 | 0.017679 | south | N | 0.017679 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.071917 | south | Y | -0.12732 | 0.017146 | -0.12453 | -0.0451 | 0.017146 | south | N | 0.017146 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.071917 | south | Y | -0.12732 | 0.017146 | -0.12453 | -0.0451 | 0.017146 | south | N | 0.017146 | 0
5511 | RAYBURNC | 1 | 46 | -0.071917 | south | Y | -0.12732 | 0.017146 | -0.12453 | -0.0451 | 0.017146 | south | N | 0.017146 | 0
5512 | RAYBURNC | 1 | 48 | -0.071917 | south | Y | -0.12732 | 0.017146 | -0.12453 | -0.0451 | 0.017146 | south | N | 0.017146 | 0
5728 | FALCONHY | 2 | 12 | -0.074868 | south | N | -0.13027 | 0.014195 | -0.12748 | -0.048051 | 0.014195 | south | N | 0.014195 | 0
5729 | FALCONHY | 3 | 11 | -0.074868 | south | N | -0.13027 | 0.014195 | -0.12748 | -0.048051 | 0.014195 | south | N | 0.014195 | 0
5890 | PEARSALL | 1 | 24 | -0.077254 | south | Y | -0.13266 | 0.011809 | -0.12986 | -0.050437 | 0.011809 | south | N | 0.011809 | 0
5891 | PEARSALL | 1 | 24 | -0.077254 | south | Y | -0.13266 | 0.011809 | -0.12986 | -0.050437 | 0.011809 | south | N | 0.011809 | 0
5892 | PEARSALL | 1 | 23 | -0.077254 | south | Y | -0.13266 | 0.011809 | -0.12986 | -0.050437 | 0.011809 | south | N | 0.011809 | 0
5903 | SANMIGUE | 1 | 396 | -0.082282 | south | Y | -0.13769 | 0.0067814 | -0.13489 | -0.055465 | 0.0067814 | south | N | 0.0067814 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.049882 | houston | N | -0.10529 | 0.039181 | -0.10249 | -0.023065 | 0.023065 | houston | N | 0.023065 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.049882 | houston | N | -0.10529 | 0.039181 | -0.10249 | -0.023065 | 0.023065 | houston | N | 0.023065 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.055404 | 0
5932 | SI_RAY9 | 9 | 38 | -0.073928 | south | Y | -0.12933 | 0.015135 | -0.12654 | -0.047111 | 0.015135 | south | N | 0.015135 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.073928 | south | Y | -0.12933 | 0.015135 | -0.12654 | -0.047111 | 0.015135 | south | N | 0.015135 | 0
5934 | SI_RAY5 | 5 | 15 | -0.073928 | south | Y | -0.12933 | 0.015135 | -0.12654 | -0.047111 | 0.015135 | south | N | 0.015135 | 0
5935 | SI_RAY10 | 10 | 47 | -0.073928 | south | Y | -0.12933 | 0.015135 | -0.12654 | -0.047111 | 0.015135 | south | N | 0.015135 | 0
6016 | SWMESA | 1 | 75 | 0.046344 | west | Y | -0.0090598 | 0.13541 | -0.0062663 | 0.073161 | 0.0062663 | west | N | 0.0062663 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.05261 | 0
6144 | MCADOO1A | 1 | 150 | 0.054466 | west | Y | -0.0009378 | 0.14353 | 0.0018557 | 0.081283 | 0.0009378 | North | Y | 0.0018557 | 0.13768
6407 | TURKTRAK | 1 | 169.5 | 0.052053 | west | Y | -0.0033508 | 0.14112 | -0.00055735 | 0.07887 | 0.00055735 | west | N | 0.00055735 | 0
6476 | LANGFORD | 1 | 150 | 0.024951 | west | Y | -0.030453 | 0.11401 | -0.027659 | 0.051768 | 0.027659 | west | N | 0.027659 | 0
6637 | SNYDERW1 | 1 | 63 | 0.05367 | west | Y | -0.0017338 | 0.14273 | 0.0010597 | 0.080487 | 0.0010597 | west | N | 0.0010597 | 0
6752 | OKLA0A | 1 | 649.7 | 0.056763 | west | Y | 0.0013592 | 0.14583 | 0.0041527 | 0.08358 | 0.0013592 | North | Y | 0.0041527 | 1.8149
6948 | DENISNDM | 1 | 40 | 0.058183 | north | N | 0.0027792 | 0.14725 | 0.0055727 | 0.085 | 0.0027792 | North | N | 0.0027792 | 0
6948 | DENISNDM | 2 | 40 | 0.058183 | north | N | 0.0027792 | 0.14725 | 0.0055727 | 0.085 | 0.0027792 | North | N | 0.0027792 | 0
7000 | L_FERGUS | 1 | 422 | -0.051203 | south | Y | -0.10661 | 0.03786 | -0.10381 | -0.024386 | 0.024386 | houston | Y | 0.03786 | 5.6863
7004 | L_SIMGID | 1 | 132 | -0.090577 | south | Y | -0.14598 | -0.0015136 | -0.14319 | -0.06376 | 0.0015136 | south | N | 0.0015136 | 0
7005 | L_SIMGID | 2 | 134 | -0.090577 | south | Y | -0.14598 | -0.0015136 | -0.14319 | -0.06376 | 0.0015136 | south | N | 0.0015136 | 0
7006 | L_SIMGID | 3 | 323 | -0.090577 | south | Y | -0.14598 | -0.0015136 | -0.14319 | -0.06376 | 0.0015136 | south | N | 0.0015136 | 0
7007 | L_LOSTPI | 1 | 158 | -0.12101 | south | Y | -0.17641 | -0.031948 | -0.17362 | -0.094194 | 0.031948 | south | N | 0.031948 | 0
7008 | L_LOSTPI | 2 | 160 | -0.12101 | south | Y | -0.17641 | -0.031948 | -0.17362 | -0.094194 | 0.031948 | south | N | 0.031948 | 0
7009 | L_LOSTPI | 3 | 175 | -0.12101 | south | Y | -0.17641 | -0.031948 | -0.17362 | -0.094194 | 0.031948 | south | N | 0.031948 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.10361 | south | Y | -0.15901 | -0.014543 | -0.15622 | -0.076789 | 0.014543 | south | N | 0.014543 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.10361 | south | Y | -0.15901 | -0.014543 | -0.15622 | -0.076789 | 0.014543 | south | N | 0.014543 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.10347 | south | Y | -0.15888 | -0.014409 | -0.15608 | -0.076655 | 0.014409 | south | N | 0.014409 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.096834 | south | Y | -0.15224 | -0.0077706 | -0.14944 | -0.070017 | 0.0077706 | south | N | 0.0077706 | 0
7015 | L_HAYSEN | 2 | 225 | -0.096834 | south | Y | -0.15224 | -0.0077706 | -0.14944 | -0.070017 | 0.0077706 | south | N | 0.0077706 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.096834 | south | Y | -0.15224 | -0.0077706 | -0.14944 | -0.070017 | 0.0077706 | south | N | 0.0077706 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.096834 | south | Y | -0.15224 | -0.0077706 | -0.14944 | -0.070017 | 0.0077706 | south | N | 0.0077706 | 0
7020 | L_AUSTPL | 1 | 8 | -0.0771 | south | N | -0.1325 | 0.011963 | -0.12971 | -0.050283 | 0.011963 | south | N | 0.011963 | 0
7020 | L_AUSTPL | 2 | 8 | -0.0771 | south | N | -0.1325 | 0.011963 | -0.12971 | -0.050283 | 0.011963 | south | N | 0.011963 | 0
7022 | L_BUCHAN | 1 | 18 | -0.036071 | south | N | -0.091475 | 0.052992 | -0.088681 | -0.0092537 | 0.0092537 | houston | Y | 0.052992 | 0
7023 | L_BUCHAN | 2 | 18 | -0.036071 | south | N | -0.091475 | 0.052992 | -0.088681 | -0.0092537 | 0.0092537 | houston | Y | 0.052992 | 0
7024 | L_BUCHAN | 3 | 15 | -0.036071 | south | N | -0.091475 | 0.052992 | -0.088681 | -0.0092537 | 0.0092537 | houston | Y | 0.052992 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.039538 | south | N | -0.094942 | 0.049525 | -0.092148 | -0.012721 | 0.012721 | houston | Y | 0.049525 | 0
7028 | L_MARBFA | 1 | 18 | -0.055927 | south | N | -0.11133 | 0.033136 | -0.10854 | -0.02911 | 0.02911 | houston | Y | 0.033136 | 0
7029 | L_MARBFA | 2 | 18 | -0.055927 | south | N | -0.11133 | 0.033136 | -0.10854 | -0.02911 | 0.02911 | houston | Y | 0.033136 | 0
7031 | L_MARSFO | 1 | 35 | -0.066641 | south | N | -0.12204 | 0.022422 | -0.11925 | -0.039824 | 0.022422 | south | N | 0.022422 | 0
7032 | L_MARSFO | 2 | 34 | -0.066641 | south | N | -0.12204 | 0.022422 | -0.11925 | -0.039824 | 0.022422 | south | N | 0.022422 | 0
7033 | L_MARSFO | 3 | 35 | -0.066641 | south | N | -0.12204 | 0.022422 | -0.11925 | -0.039824 | 0.022422 | south | N | 0.022422 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.050969 | south | N | -0.10637 | 0.038094 | -0.10358 | -0.024152 | 0.024152 | houston | Y | 0.038094 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.050969 | south | N | -0.10637 | 0.038094 | -0.10358 | -0.024152 | 0.024152 | houston | Y | 0.038094 | 0
7038 | L_DELAWA | 1 | 35 | 0.051729 | west | Y | -0.0036748 | 0.14079 | -0.00088135 | 0.078546 | 0.00088135 | west | N | 0.00088135 | 0
7038 | L_DELAWA | 2 | 30 | 0.051729 | west | Y | -0.0036748 | 0.14079 | -0.00088135 | 0.078546 | 0.00088135 | west | N | 0.00088135 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.091938 | south | Y | -0.14734 | -0.0028746 | -0.14455 | -0.065121 | 0.0028746 | south | N | 0.0028746 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.091938 | south | Y | -0.14734 | -0.0028746 | -0.14455 | -0.065121 | 0.0028746 | south | N | 0.0028746 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.091938 | south | Y | -0.14734 | -0.0028746 | -0.14455 | -0.065121 | 0.0028746 | south | N | 0.0028746 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.091938 | south | Y | -0.14734 | -0.0028746 | -0.14455 | -0.065121 | 0.0028746 | south | N | 0.0028746 | 0
7487 | L_CANYHY | 1 | 6 | -0.090176 | south | N | -0.14558 | -0.0011126 | -0.14279 | -0.063359 | 0.0011126 | south | N | 0.0011126 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.090343 | south | N | -0.14575 | -0.0012796 | -0.14295 | -0.063526 | 0.0012796 | south | N | 0.0012796 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.090343 | south | N | -0.14575 | -0.0012796 | -0.14295 | -0.063526 | 0.0012796 | south | N | 0.0012796 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.090343 | south | N | -0.14575 | -0.0012796 | -0.14295 | -0.063526 | 0.0012796 | south | N | 0.0012796 | 0
7609 | L_SCHUMA | 1 | 4 | -0.090158 | south | N | -0.14556 | -0.0010946 | -0.14277 | -0.063341 | 0.0010946 | south | N | 0.0010946 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.087938 | south | N | -0.14334 | 0.0011254 | -0.14055 | -0.061121 | 0.0011254 | south | N | 0.0011254 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.087938 | south | N | -0.14334 | 0.0011254 | -0.14055 | -0.061121 | 0.0011254 | south | N | 0.0011254 | 0
7800 | L_GUADGE | 1 | 147 | -0.089726 | south | Y | -0.14513 | -0.00066257 | -0.14234 | -0.062909 | 0.00066257 | south | N | 0.00066257 | 0
7801 | L_GUADGE | 2 | 138 | -0.089726 | south | Y | -0.14513 | -0.00066257 | -0.14234 | -0.062909 | 0.00066257 | south | N | 0.00066257 | 0
7802 | L_GUADGE | 3 | 140 | -0.089726 | south | Y | -0.14513 | -0.00066257 | -0.14234 | -0.062909 | 0.00066257 | south | N | 0.00066257 | 0
7803 | L_GUADGE | 4 | 147 | -0.089726 | south | Y | -0.14513 | -0.00066257 | -0.14234 | -0.062909 | 0.00066257 | south | N | 0.00066257 | 0
7804 | L_GUADGE | 5 | 182 | -0.089726 | south | Y | -0.14513 | -0.00066257 | -0.14234 | -0.062909 | 0.00066257 | south | N | 0.00066257 | 0
7805 | L_GUADGE | 6 | 198 | -0.089726 | south | Y | -0.14513 | -0.00066257 | -0.14234 | -0.062909 | 0.00066257 | south | N | 0.00066257 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.11692 | south | Y | -0.17232 | -0.027852 | -0.16953 | -0.090098 | 0.027852 | south | N | 0.027852 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.11692 | south | Y | -0.17232 | -0.027852 | -0.16953 | -0.090098 | 0.027852 | south | N | 0.027852 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.11692 | south | Y | -0.17232 | -0.027852 | -0.16953 | -0.090098 | 0.027852 | south | N | 0.027852 | 0
7810 | L_RIONOG | 1 | 142 | -0.093101 | south | Y | -0.1485 | -0.0040376 | -0.14571 | -0.066284 | 0.0040376 | south | N | 0.0040376 | 0
7811 | L_RIONOG | 2 | 145 | -0.093101 | south | Y | -0.1485 | -0.0040376 | -0.14571 | -0.066284 | 0.0040376 | south | N | 0.0040376 | 0
7812 | L_RIONOG | 3 | 151 | -0.093101 | south | Y | -0.1485 | -0.0040376 | -0.14571 | -0.066284 | 0.0040376 | south | N | 0.0040376 | 0
7813 | L_RIONOG | 4 | 290 | -0.093101 | south | Y | -0.1485 | -0.0040376 | -0.14571 | -0.066284 | 0.0040376 | south | N | 0.0040376 | 0
8032 | AMISTADH | 1 | 33 | -0.042838 | south | N | -0.098242 | 0.046225 | -0.095448 | -0.016021 | 0.016021 | houston | Y | 0.046225 | 0
8033 | AMISTADH | 2 | 25 | -0.042838 | south | N | -0.098242 | 0.046225 | -0.095448 | -0.016021 | 0.016021 | houston | Y | 0.046225 | 0
8048 | FALCONHY | 1 | 12 | -0.074868 | south | N | -0.13027 | 0.014195 | -0.12748 | -0.048051 | 0.014195 | south | N | 0.014195 | 0
8066 | DUP1V#1 | 1 | 73 | -0.071952 | south | N | -0.12736 | 0.017111 | -0.12456 | -0.045135 | 0.017111 | south | N | 0.017111 | 0
8134 | FOR69CG0 | 1 | 79 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
8138 | FOR69CG0 | 2 | 81 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8147 | UCAR #2 | 10 | 28 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
8148 | UCAR #1 | 2 | 7 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
8153 | FOR69CG0 | 3 | 79 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
8154 | FOR69CG0 | 4 | 80 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
8156 | FOR69CG0 | 6 | 25 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
8157 | FOR69CG0 | 7 | 46 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
8161 | COLETOU1 | 1 | 629 | -0.075826 | south | Y | -0.13123 | 0.013237 | -0.12844 | -0.049009 | 0.013237 | south | N | 0.013237 | 0
8173 | VICEC51A | 5 | 144 | -0.072629 | south | Y | -0.12803 | 0.016434 | -0.12524 | -0.045812 | 0.016434 | south | N | 0.016434 | 0
8174 | VICEC61A | 6 | 188 | -0.072629 | south | Y | -0.12803 | 0.016434 | -0.12524 | -0.045812 | 0.016434 | south | N | 0.016434 | 0
8189 | CUERO 2 | 1 | 12 | -0.08356 | south | N | -0.13896 | 0.0055034 | -0.13617 | -0.056743 | 0.0055034 | south | N | 0.0055034 | 0
8262 | ELPS | 1 | 6 | -0.053575 | south | N | -0.10898 | 0.035488 | -0.10619 | -0.026758 | 0.026758 | houston | Y | 0.035488 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8442 | NBEC71A | 1 | 336 | -0.073228 | south | Y | -0.12863 | 0.015835 | -0.12584 | -0.046411 | 0.015835 | south | N | 0.015835 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.055404 | 0.089063 | -0.05261 | 0.026817 | 0.026817 | houston | Y | 0.089063 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.073377 | south | Y | -0.12878 | 0.015686 | -0.12599 | -0.04656 | 0.015686 | south | N | 0.015686 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.073377 | south | Y | -0.12878 | 0.015686 | -0.12599 | -0.04656 | 0.015686 | south | N | 0.015686 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.073455 | south | N | -0.12886 | 0.015608 | -0.12607 | -0.046638 | 0.015608 | south | N | 0.015608 | 0
8506 | VAL #1 | 1 | 25 | -0.073391 | south | N | -0.12879 | 0.015672 | -0.126 | -0.046574 | 0.015672 | south | N | 0.015672 | 0
8507 | VAL #2 | 2 | 25 | -0.073391 | south | N | -0.12879 | 0.015672 | -0.126 | -0.046574 | 0.015672 | south | N | 0.015672 | 0
8511 | OXY_CC0A | 1 | 38 | -0.073461 | south | N | -0.12886 | 0.015602 | -0.12607 | -0.046644 | 0.015602 | south | N | 0.015602 | 0
8517 | CELANEBI | 1 | 29 | -0.073781 | south | N | -0.12918 | 0.015282 | -0.12639 | -0.046964 | 0.015282 | south | N | 0.015282 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.073236 | south | N | -0.12864 | 0.015827 | -0.12585 | -0.046419 | 0.015827 | south | N | 0.015827 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.073236 | south | N | -0.12864 | 0.015827 | -0.12585 | -0.046419 | 0.015827 | south | N | 0.015827 | 0
8562 | CNOPST1 | 3 | 153 | -0.073236 | south | N | -0.12864 | 0.015827 | -0.12585 | -0.046419 | 0.015827 | south | N | 0.015827 | 0
8926 | LGE_GT10 | 1 | 158 | -0.072565 | south | N | -0.12797 | 0.016498 | -0.12518 | -0.045748 | 0.016498 | south | N | 0.016498 | 0
8927 | LGE_GT20 | 2 | 153 | -0.072565 | south | N | -0.12797 | 0.016498 | -0.12518 | -0.045748 | 0.016498 | south | N | 0.016498 | 0
8928 | LGE_STG0 | 3 | 100 | -0.072565 | south | N | -0.12797 | 0.016498 | -0.12518 | -0.045748 | 0.016498 | south | N | 0.016498 | 0
8930 | ICPGN10A | 1 | 145 | -0.072565 | south | N | -0.12797 | 0.016498 | -0.12518 | -0.045748 | 0.016498 | south | N | 0.016498 | 0
8931 | ICPGN20A | 2 | 147 | -0.072565 | south | N | -0.12797 | 0.016498 | -0.12518 | -0.045748 | 0.016498 | south | N | 0.016498 | 0
8932 | ICPGN30A | 3 | 127 | -0.072565 | south | N | -0.12797 | 0.016498 | -0.12518 | -0.045748 | 0.016498 | south | N | 0.016498 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.07416 | south | Y | -0.12956 | 0.014903 | -0.12677 | -0.047343 | 0.014903 | south | N | 0.014903 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.07416 | south | Y | -0.12956 | 0.014903 | -0.12677 | -0.047343 | 0.014903 | south | N | 0.014903 | 0
8935 | FGNTS201 | 3 | 173 | -0.07416 | south | Y | -0.12956 | 0.014903 | -0.12677 | -0.047343 | 0.014903 | south | N | 0.014903 | 0
8936 | MVGN#1 | 1 | 207 | -0.074047 | south | Y | -0.12945 | 0.015016 | -0.12666 | -0.04723 | 0.015016 | south | N | 0.015016 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.074047 | south | Y | -0.12945 | 0.015016 | -0.12666 | -0.04723 | 0.015016 | south | N | 0.015016 | 0
8938 | MVGN#3 | 3 | 242 | -0.074047 | south | Y | -0.12945 | 0.015016 | -0.12666 | -0.04723 | 0.015016 | south | N | 0.015016 | 0
8981 | HECN1 | 1 | 144 | -0.074045 | south | Y | -0.12945 | 0.015018 | -0.12666 | -0.047228 | 0.015018 | south | N | 0.015018 | 0
8982 | HECN2 | 2 | 144 | -0.074045 | south | Y | -0.12945 | 0.015018 | -0.12666 | -0.047228 | 0.015018 | south | N | 0.015018 | 0
8983 | HECN3 | 3 | 171 | -0.074045 | south | Y | -0.12945 | 0.015018 | -0.12666 | -0.047228 | 0.015018 | south | N | 0.015018 | 0
9000 | DECKR_G1 | 1 | 310 | -0.081553 | south | Y | -0.13696 | 0.0075104 | -0.13416 | -0.054736 | 0.0075104 | south | N | 0.0075104 | 0
9001 | DECKR_G2 | 2 | 413 | -0.081553 | south | Y | -0.13696 | 0.0075104 | -0.13416 | -0.054736 | 0.0075104 | south | N | 0.0075104 | 0
9002 | DECKR_G3 | 3 | 42 | -0.083193 | south | Y | -0.1386 | 0.0058704 | -0.1358 | -0.056376 | 0.0058704 | south | N | 0.0058704 | 0
9003 | DECKR_G4 | 4 | 44 | -0.083193 | south | Y | -0.1386 | 0.0058704 | -0.1358 | -0.056376 | 0.0058704 | south | N | 0.0058704 | 0
9004 | DECKR_G5 | 5 | 44 | -0.083193 | south | Y | -0.1386 | 0.0058704 | -0.1358 | -0.056376 | 0.0058704 | south | N | 0.0058704 | 0
9005 | DECKR_G6 | 6 | 47 | -0.083193 | south | Y | -0.1386 | 0.0058704 | -0.1358 | -0.056376 | 0.0058704 | south | N | 0.0058704 | 0
9016 | SANDH_G1 | 1 | 49 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
9017 | SANDH_G2 | 2 | 46 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
9018 | SANDH_G3 | 3 | 46 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
9019 | SANDH_G4 | 4 | 47 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
9020 | SANDHG5A | 5A | 154 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
9021 | SANDHG5C | 5C | 148 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
9022 | SANDH_G6 | 6 | 48 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
9023 | SANDH_G7 | 7 | 48 | -0.084952 | south | Y | -0.14036 | 0.0041114 | -0.13756 | -0.058135 | 0.0041114 | south | N | 0.0041114 | 0
11001 | NAV1CT | 1 | 70 | 0.052636 | west | Y | -0.0027678 | 0.1417 | 2.565e-05 | 0.079453 | 2.565e-05 | west | N | 2.565e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.052636 | west | Y | -0.0027678 | 0.1417 | 2.565e-05 | 0.079453 | 2.565e-05 | west | N | 2.565e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.052636 | west | Y | -0.0027678 | 0.1417 | 2.565e-05 | 0.079453 | 2.565e-05 | west | N | 2.565e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.052636 | west | Y | -0.0027678 | 0.1417 | 2.565e-05 | 0.079453 | 2.565e-05 | west | N | 2.565e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.052636 | west | Y | -0.0027678 | 0.1417 | 2.565e-05 | 0.079453 | 2.565e-05 | west | N | 2.565e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.052636 | west | Y | -0.0027678 | 0.1417 | 2.565e-05 | 0.079453 | 2.565e-05 | west | N | 2.565e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.052627 | west | Y | -0.0027768 | 0.14169 | 1.665e-05 | 0.079444 | 1.665e-05 | west | N | 1.665e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.052627 | west | Y | -0.0027768 | 0.14169 | 1.665e-05 | 0.079444 | 1.665e-05 | west | N | 1.665e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.052627 | west | Y | -0.0027768 | 0.14169 | 1.665e-05 | 0.079444 | 1.665e-05 | west | N | 1.665e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.052627 | west | Y | -0.0027768 | 0.14169 | 1.665e-05 | 0.079444 | 1.665e-05 | west | N | 1.665e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.052627 | west | Y | -0.0027768 | 0.14169 | 1.665e-05 | 0.079444 | 1.665e-05 | west | N | 1.665e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.052627 | west | Y | -0.0027768 | 0.14169 | 1.665e-05 | 0.079444 | 1.665e-05 | west | N | 1.665e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.054241 | west | Y | -0.0011628 | 0.1433 | 0.0016307 | 0.081058 | 0.0011628 | North | Y | 0.0016307 | 0.097781
11057 | CHAMPION | 1 | 126.5 | 0.054241 | west | Y | -0.0011628 | 0.1433 | 0.0016307 | 0.081058 | 0.0011628 | North | Y | 0.0016307 | 0.059184
11058 | PYRON_1G | 1 | 249 | 0.054241 | west | Y | -0.0011628 | 0.1433 | 0.0016307 | 0.081058 | 0.0011628 | North | Y | 0.0016307 | 0.1165
11059 | INADALE_ | 1 | 197 | 0.054241 | west | Y | -0.0011628 | 0.1433 | 0.0016307 | 0.081058 | 0.0011628 | North | Y | 0.0016307 | 0.092167
11061 | PNTHRCK1 | 1 | 200 | 0.053464 | west | Y | -0.0019398 | 0.14253 | 0.00085365 | 0.080281 | 0.00085365 | west | N | 0.00085365 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.053464 | west | Y | -0.0019398 | 0.14253 | 0.00085365 | 0.080281 | 0.00085365 | west | N | 0.00085365 | 0
11147 | NOTREES_ | 1 | 149 | 0.051895 | west | Y | -0.0035088 | 0.14096 | -0.00071535 | 0.078712 | 0.00071535 | west | N | 0.00071535 | 0
11309 | BULLCREK | 1 | 180 | 0.053347 | west | Y | -0.0020568 | 0.14241 | 0.00073665 | 0.080164 | 0.00073665 | west | N | 0.00073665 | 0
11310 | BULLCREK | 1 | 180 | 0.053347 | west | Y | -0.0020568 | 0.14241 | 0.00073665 | 0.080164 | 0.00073665 | west | N | 0.00073665 | 0
11320 | COYOTE_1 | 1 | 225 | 0.053297 | west | Y | -0.0021068 | 0.14236 | 0.00068665 | 0.080114 | 0.00068665 | west | N | 0.00068665 | 0
11415 | LORAINE_ | 1 | 125 | 0.053938 | west | Y | -0.0014658 | 0.143 | 0.0013277 | 0.080755 | 0.0013277 | west | N | 0.0013277 | 0
11416 | LORAINE_ | 1 | 125 | 0.053938 | west | Y | -0.0014658 | 0.143 | 0.0013277 | 0.080755 | 0.0013277 | west | N | 0.0013277 | 0
11691 | KMICHICT | 1 | 140 | 0.058003 | north | N | 0.0025992 | 0.14707 | 0.0053927 | 0.08482 | 0.0025992 | North | N | 0.0025992 | 0
11692 | KMICHICT | 2 | 141 | 0.058003 | north | N | 0.0025992 | 0.14707 | 0.0053927 | 0.08482 | 0.0025992 | North | N | 0.0025992 | 0
11693 | KMICHIST | 3 | 309 | 0.058003 | north | N | 0.0025992 | 0.14707 | 0.0053927 | 0.08482 | 0.0025992 | North | N | 0.0025992 | 0
11694 | KMICHICT | 4 | 143 | 0.058003 | north | N | 0.0025992 | 0.14707 | 0.0053927 | 0.08482 | 0.0025992 | North | N | 0.0025992 | 0
11695 | KMICHICT | 5 | 144 | 0.058003 | north | N | 0.0025992 | 0.14707 | 0.0053927 | 0.08482 | 0.0025992 | North | N | 0.0025992 | 0
11696 | KMICHIST | 6 | 310 | 0.058003 | north | N | 0.0025992 | 0.14707 | 0.0053927 | 0.08482 | 0.0025992 | North | N | 0.0025992 | 0
12322 | ENNSTRAC | 1 | 196 | 0.060186 | north | Y | 0.0047822 | 0.14925 | 0.0075757 | 0.087003 | 0.0047822 | North | N | 0.0047822 | 0
12323 | ENNSTRAC | 2 | 111 | 0.060186 | north | Y | 0.0047822 | 0.14925 | 0.0075757 | 0.087003 | 0.0047822 | North | N | 0.0047822 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.058492 | north | N | 0.0030882 | 0.14756 | 0.0058817 | 0.085309 | 0.0030882 | North | N | 0.0030882 | 0
12411 | FPLEFR1A | 1 | 161 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12412 | FPLEFR1B | 2 | 164 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12413 | FPLEFR1C | 3 | 164 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12414 | FPLEFR1S | 4 | 414 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12421 | FPLEFR2A | 1 | 162 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12422 | FPLEFR2B | 2 | 161 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12423 | FPLEFR2C | 3 | 163 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12424 | FPLEFR2S | 4 | 409 | 0.057188 | north | Y | 0.0017842 | 0.14625 | 0.0045777 | 0.084005 | 0.0017842 | North | N | 0.0017842 | 0
12440 | PARKD_1S | 1 | 0 | 0.058015 | north | N | 0.0026112 | 0.14708 | 0.0054047 | 0.084832 | 0.0026112 | North | N | 0.0026112 | 0
12449 | PARKD_2S | 1 | 0 | 0.058015 | north | N | 0.0026112 | 0.14708 | 0.0054047 | 0.084832 | 0.0026112 | North | N | 0.0026112 | 0
13116 | TGATEWAY | 1 | 148 | 0.054345 | north | N | -0.0010588 | 0.14341 | 0.0017347 | 0.081162 | 0.0010588 | North | N | 0.0010588 | 0
13117 | TGATEWAY | 2 | 130 | 0.054345 | north | N | -0.0010588 | 0.14341 | 0.0017347 | 0.081162 | 0.0010588 | North | N | 0.0010588 | 0
13118 | TGATEWAY | 3 | 145 | 0.054345 | north | N | -0.0010588 | 0.14341 | 0.0017347 | 0.081162 | 0.0010588 | North | N | 0.0010588 | 0
13119 | TGATEWAY | 4 | 399 | 0.054345 | north | N | -0.0010588 | 0.14341 | 0.0017347 | 0.081162 | 0.0010588 | North | N | 0.0010588 | 0
13131 | CALFREST | 1 | 150.7 | 0.050355 | north | Y | -0.0050488 | 0.13942 | -0.0022553 | 0.077172 | 0.0022553 | west | Y | 0.0050488 | 0.42097
13132 | CALFREST | 2 | 151 | 0.050355 | north | Y | -0.0050488 | 0.13942 | -0.0022553 | 0.077172 | 0.0022553 | west | Y | 0.0050488 | 0.42181
13133 | CALFREST | 3 | 177.4 | 0.050355 | north | Y | -0.0050488 | 0.13942 | -0.0022553 | 0.077172 | 0.0022553 | west | Y | 0.0050488 | 0.49556
13134 | CALFREST | 4 | 151.5 | 0.050512 | north | Y | -0.0048918 | 0.13958 | -0.0020983 | 0.077329 | 0.0020983 | west | Y | 0.0048918 | 0.42321
13135 | CALFREST | 5 | 152.3 | 0.050512 | north | Y | -0.0048918 | 0.13958 | -0.0020983 | 0.077329 | 0.0020983 | west | Y | 0.0048918 | 0.42544
13136 | CALFREST | 6 | 177.5 | 0.050512 | north | Y | -0.0048918 | 0.13958 | -0.0020983 | 0.077329 | 0.0020983 | west | Y | 0.0048918 | 0.49584
13432 | SANDOW_5 | 5 | 581 | -0.14621 | south | Y | -0.20162 | -0.05715 | -0.19882 | -0.1194 | 0.05715 | south | N | 0.05715 | 0
13691 | OAKGROVE | 1 | 855 | 0.031563 | north | Y | -0.023841 | 0.12063 | -0.021047 | 0.05838 | 0.021047 | west | Y | 0.023841 | 2.3884
13692 | OAKGROVE | 2 | 855 | 0.031563 | north | Y | -0.023841 | 0.12063 | -0.021047 | 0.05838 | 0.021047 | west | Y | 0.023841 | 2.3884
32798 | BRYN_TAM | 1 | 32 | 0.01139 | north | N | -0.044014 | 0.10045 | -0.04122 | 0.038207 | 0.038207 | houston | Y | 0.044014 | 0
32883 | BRYN_DNS | 1 | 48 | 0.009873 | north | Y | -0.045531 | 0.098936 | -0.042737 | 0.03669 | 0.03669 | houston | Y | 0.045531 | 0.42434
32884 | BRYN_DNS | 1 | 46 | 0.009873 | north | Y | -0.045531 | 0.098936 | -0.042737 | 0.03669 | 0.03669 | houston | Y | 0.045531 | 0.40666
32886 | BRYN_ATK | MB | 12 | 0.01144 | north | Y | -0.043964 | 0.1005 | -0.04117 | 0.038257 | 0.038257 | houston | Y | 0.043964 | 0
32887 | BRYN_ATK | MB | 51 | 0.01144 | north | Y | -0.043964 | 0.1005 | -0.04117 | 0.038257 | 0.038257 | houston | Y | 0.043964 | 0
32888 | BRYN_ATK | 1 | 17 | 0.01144 | north | Y | -0.043964 | 0.1005 | -0.04117 | 0.038257 | 0.038257 | houston | Y | 0.043964 | 0.097011
32890 | BRYN_ATK | MB | 22 | 0.01144 | north | Y | -0.043964 | 0.1005 | -0.04117 | 0.038257 | 0.038257 | houston | Y | 0.043964 | 0
32891 | BRYN_ATK | MB | 25 | 0.01144 | north | Y | -0.043964 | 0.1005 | -0.04117 | 0.038257 | 0.038257 | houston | Y | 0.043964 | 0
32892 | BRYN_DNS | 1 | 105 | 0.009873 | north | Y | -0.045531 | 0.098936 | -0.042737 | 0.03669 | 0.03669 | houston | Y | 0.045531 | 0.92825
36998 | RDCNYNG1 | 1 | 84 | 0.053861 | west | Y | -0.0015428 | 0.14292 | 0.0012507 | 0.080678 | 0.0012507 | west | N | 0.0012507 | 0
38332 | WDWRDU2 | 1 | 80 | 0.046247 | west | Y | -0.0091568 | 0.13531 | -0.0063633 | 0.073064 | 0.0063633 | west | N | 0.0063633 | 0
38437 | TNSRBNMS | 1 | 150 | 0.046198 | west | Y | -0.0092058 | 0.13526 | -0.0064123 | 0.073015 | 0.0064123 | west | N | 0.0064123 | 0
38438 | TNSRBNMS | 1 | 150 | 0.046198 | west | Y | -0.0092058 | 0.13526 | -0.0064123 | 0.073015 | 0.0064123 | west | N | 0.0064123 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38600 | TNBP_CGN | 5 | 53 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38614 | TNBPAMCG | 4 | 96 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38615 | TNBPAMCG | 1 | 244 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38690 | TNBP_CGN | 3 | 40 | -0.027789 | houston | N | -0.083193 | 0.061274 | -0.080399 | -0.00097171 | 0.00097171 | houston | N | 0.00097171 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.027803 | houston | N | -0.083207 | 0.06126 | -0.080413 | -0.00098571 | 0.00098571 | houston | N | 0.00098571 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.027803 | houston | N | -0.083207 | 0.06126 | -0.080413 | -0.00098571 | 0.00098571 | houston | N | 0.00098571 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.027803 | houston | N | -0.083207 | 0.06126 | -0.080413 | -0.00098571 | 0.00098571 | houston | N | 0.00098571 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.027803 | houston | N | -0.083207 | 0.06126 | -0.080413 | -0.00098571 | 0.00098571 | houston | N | 0.00098571 | 0
39470 | TNDOWCGN | 1 | 32 | -0.027802 | houston | N | -0.083206 | 0.061261 | -0.080412 | -0.00098471 | 0.00098471 | houston | N | 0.00098471 | 0
39480 | TNDOWCGN | 1 | 30 | -0.027802 | houston | N | -0.083206 | 0.061261 | -0.080412 | -0.00098471 | 0.00098471 | houston | N | 0.00098471 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.03657 | houston | N | -0.091974 | 0.052493 | -0.08918 | -0.0097527 | 0.0097527 | houston | N | 0.0097527 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.03657 | houston | N | -0.091974 | 0.052493 | -0.08918 | -0.0097527 | 0.0097527 | houston | N | 0.0097527 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.03657 | houston | N | -0.091974 | 0.052493 | -0.08918 | -0.0097527 | 0.0097527 | houston | N | 0.0097527 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.03657 | houston | N | -0.091974 | 0.052493 | -0.08918 | -0.0097527 | 0.0097527 | houston | N | 0.0097527 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.031563 | north | Y | -0.023841 | 0.12063 | -0.021047 | 0.05838 | 0.021047 | west | Y | 0.023841 | 0.42544
39970 | TNTNPONE | 1 | 153 | 0.031563 | north | Y | -0.023841 | 0.12063 | -0.021047 | 0.05838 | 0.021047 | west | Y | 0.023841 | 0.4274
48500 | APD_GT1_ | 1 | 136 | -0.022383 | houston | N | -0.077787 | 0.06668 | -0.074993 | 0.0044343 | 0.0044343 | houston | N | 0.0044343 | 0
48510 | AK_GT1__ | 1 | 33 | -0.030716 | houston | N | -0.08612 | 0.058347 | -0.083326 | -0.0038987 | 0.0038987 | houston | N | 0.0038987 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.02235 | houston | Y | -0.077754 | 0.066713 | -0.07496 | 0.0044673 | 0.0044673 | houston | N | 0.0044673 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.02235 | houston | Y | -0.077754 | 0.066713 | -0.07496 | 0.0044673 | 0.0044673 | houston | N | 0.0044673 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.02235 | houston | Y | -0.077754 | 0.066713 | -0.07496 | 0.0044673 | 0.0044673 | houston | N | 0.0044673 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.02235 | houston | Y | -0.077754 | 0.066713 | -0.07496 | 0.0044673 | 0.0044673 | houston | N | 0.0044673 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.038022 | houston | N | -0.093426 | 0.051041 | -0.090632 | -0.011205 | 0.011205 | houston | N | 0.011205 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.038022 | houston | N | -0.093426 | 0.051041 | -0.090632 | -0.011205 | 0.011205 | houston | N | 0.011205 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.031318 | houston | N | -0.086722 | 0.057745 | -0.083928 | -0.0045007 | 0.0045007 | houston | N | 0.0045007 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.031318 | houston | N | -0.086722 | 0.057745 | -0.083928 | -0.0045007 | 0.0045007 | houston | N | 0.0045007 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.031318 | houston | N | -0.086722 | 0.057745 | -0.083928 | -0.0045007 | 0.0045007 | houston | N | 0.0045007 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.0244 | houston | N | -0.079804 | 0.064663 | -0.07701 | 0.0024173 | 0.0024173 | houston | N | 0.0024173 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.0244 | houston | N | -0.079804 | 0.064663 | -0.07701 | 0.0024173 | 0.0024173 | houston | N | 0.0024173 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.0244 | houston | N | -0.079804 | 0.064663 | -0.07701 | 0.0024173 | 0.0024173 | houston | N | 0.0024173 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.0244 | houston | N | -0.079804 | 0.064663 | -0.07701 | 0.0024173 | 0.0024173 | houston | N | 0.0024173 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.023083 | houston | N | -0.078487 | 0.06598 | -0.075693 | 0.0037343 | 0.0037343 | houston | N | 0.0037343 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.023083 | houston | N | -0.078487 | 0.06598 | -0.075693 | 0.0037343 | 0.0037343 | houston | N | 0.0037343 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.024797 | houston | N | -0.080201 | 0.064266 | -0.077407 | 0.0020203 | 0.0020203 | houston | N | 0.0020203 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.024797 | houston | N | -0.080201 | 0.064266 | -0.077407 | 0.0020203 | 0.0020203 | houston | N | 0.0020203 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.024797 | houston | N | -0.080201 | 0.064266 | -0.077407 | 0.0020203 | 0.0020203 | houston | N | 0.0020203 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.024797 | houston | N | -0.080201 | 0.064266 | -0.077407 | 0.0020203 | 0.0020203 | houston | N | 0.0020203 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.024797 | houston | N | -0.080201 | 0.064266 | -0.077407 | 0.0020203 | 0.0020203 | houston | N | 0.0020203 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.020697 | houston | Y | -0.076101 | 0.068366 | -0.073307 | 0.0061203 | 0.0061203 | houston | N | 0.0061203 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.021368 | houston | Y | -0.076772 | 0.067695 | -0.073978 | 0.0054493 | 0.0054493 | houston | N | 0.0054493 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.020495 | houston | Y | -0.075899 | 0.068568 | -0.073105 | 0.0063223 | 0.0063223 | houston | N | 0.0063223 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.020495 | houston | Y | -0.075899 | 0.068568 | -0.073105 | 0.0063223 | 0.0063223 | houston | N | 0.0063223 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.020495 | houston | Y | -0.075899 | 0.068568 | -0.073105 | 0.0063223 | 0.0063223 | houston | N | 0.0063223 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.016772 | houston | N | -0.072176 | 0.072291 | -0.069382 | 0.010045 | 0.010045 | houston | N | 0.010045 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.02225 | houston | N | -0.077654 | 0.066813 | -0.07486 | 0.0045673 | 0.0045673 | houston | N | 0.0045673 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.02225 | houston | N | -0.077654 | 0.066813 | -0.07486 | 0.0045673 | 0.0045673 | houston | N | 0.0045673 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.020021 | houston | N | -0.075425 | 0.069042 | -0.072631 | 0.0067963 | 0.0067963 | houston | N | 0.0067963 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.020021 | houston | N | -0.075425 | 0.069042 | -0.072631 | 0.0067963 | 0.0067963 | houston | N | 0.0067963 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.020021 | houston | N | -0.075425 | 0.069042 | -0.072631 | 0.0067963 | 0.0067963 | houston | N | 0.0067963 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.020021 | houston | N | -0.075425 | 0.069042 | -0.072631 | 0.0067963 | 0.0067963 | houston | N | 0.0067963 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.023039 | houston | N | -0.078443 | 0.066024 | -0.075649 | 0.0037783 | 0.0037783 | houston | N | 0.0037783 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.023039 | houston | N | -0.078443 | 0.066024 | -0.075649 | 0.0037783 | 0.0037783 | houston | N | 0.0037783 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.023039 | houston | N | -0.078443 | 0.066024 | -0.075649 | 0.0037783 | 0.0037783 | houston | N | 0.0037783 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.023039 | houston | N | -0.078443 | 0.066024 | -0.075649 | 0.0037783 | 0.0037783 | houston | N | 0.0037783 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.02346 | houston | N | -0.078864 | 0.065603 | -0.07607 | 0.0033573 | 0.0033573 | houston | N | 0.0033573 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.02346 | houston | N | -0.078864 | 0.065603 | -0.07607 | 0.0033573 | 0.0033573 | houston | N | 0.0033573 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.02346 | houston | N | -0.078864 | 0.065603 | -0.07607 | 0.0033573 | 0.0033573 | houston | N | 0.0033573 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.02346 | houston | N | -0.078864 | 0.065603 | -0.07607 | 0.0033573 | 0.0033573 | houston | N | 0.0033573 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.02346 | houston | N | -0.078864 | 0.065603 | -0.07607 | 0.0033573 | 0.0033573 | houston | N | 0.0033573 | 0
48651 | EP_1_2 | 1 | 5 | -0.020733 | houston | N | -0.076137 | 0.06833 | -0.073343 | 0.0060843 | 0.0060843 | houston | N | 0.0060843 | 0
48651 | EP_1_2 | 2 | 21 | -0.020733 | houston | N | -0.076137 | 0.06833 | -0.073343 | 0.0060843 | 0.0060843 | houston | N | 0.0060843 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.009492 | north | N | -0.045912 | 0.098555 | -0.043118 | 0.036309 | 0.036309 | houston | Y | 0.045912 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.009492 | north | N | -0.045912 | 0.098555 | -0.043118 | 0.036309 | 0.036309 | houston | Y | 0.045912 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.009492 | north | N | -0.045912 | 0.098555 | -0.043118 | 0.036309 | 0.036309 | houston | Y | 0.045912 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.009492 | north | N | -0.045912 | 0.098555 | -0.043118 | 0.036309 | 0.036309 | houston | Y | 0.045912 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.019857 | houston | Y | -0.075261 | 0.069206 | -0.072467 | 0.0069603 | 0.0069603 | houston | N | 0.0069603 | 0
48691 | GBY_7374 | A | 46 | -0.023816 | houston | Y | -0.07922 | 0.065247 | -0.076426 | 0.0030013 | 0.0030013 | houston | N | 0.0030013 | 0
48691 | GBY_7374 | B | 46 | -0.023816 | houston | Y | -0.07922 | 0.065247 | -0.076426 | 0.0030013 | 0.0030013 | houston | N | 0.0030013 | 0
48692 | GBY_8182 | C | 46 | -0.023816 | houston | Y | -0.07922 | 0.065247 | -0.076426 | 0.0030013 | 0.0030013 | houston | N | 0.0030013 | 0
48692 | GBY_8182 | D | 55 | -0.023816 | houston | Y | -0.07922 | 0.065247 | -0.076426 | 0.0030013 | 0.0030013 | houston | N | 0.0030013 | 0
48693 | GBY_8384 | E | 55 | -0.023816 | houston | Y | -0.07922 | 0.065247 | -0.076426 | 0.0030013 | 0.0030013 | houston | N | 0.0030013 | 0
48693 | GBY_8384 | F | 54 | -0.023816 | houston | Y | -0.07922 | 0.065247 | -0.076426 | 0.0030013 | 0.0030013 | houston | N | 0.0030013 | 0
48721 | LEG_1___ | 1 | 827 | 0.038747 | north | Y | -0.016657 | 0.12781 | -0.013863 | 0.065564 | 0.013863 | west | Y | 0.016657 | 2.3102
48722 | LEG_2___ | 2 | 819 | 0.038747 | north | Y | -0.016657 | 0.12781 | -0.013863 | 0.065564 | 0.013863 | west | Y | 0.016657 | 2.2878
48730 | MNS_GT | 1 | 46.1 | -0.031481 | houston | N | -0.086885 | 0.057582 | -0.084091 | -0.0046637 | 0.0046637 | houston | N | 0.0046637 | 0
48731 | CBE_GT1 | 1 | 76 | -0.049332 | houston | Y | -0.10474 | 0.039731 | -0.10194 | -0.022515 | 0.022515 | houston | N | 0.022515 | 0
48732 | CBE_GT2 | 1 | 76 | -0.049332 | houston | Y | -0.10474 | 0.039731 | -0.10194 | -0.022515 | 0.022515 | houston | N | 0.022515 | 0
48733 | CBE_ST12 | 1 | 105 | -0.049332 | houston | Y | -0.10474 | 0.039731 | -0.10194 | -0.022515 | 0.022515 | houston | N | 0.022515 | 0
48734 | CBE_GT3 | 1 | 74 | -0.049332 | houston | Y | -0.10474 | 0.039731 | -0.10194 | -0.022515 | 0.022515 | houston | N | 0.022515 | 0
48735 | CBE_GT4 | 1 | 74 | -0.049332 | houston | Y | -0.10474 | 0.039731 | -0.10194 | -0.022515 | 0.022515 | houston | N | 0.022515 | 0
48736 | CBE_ST34 | 1 | 102 | -0.049332 | houston | Y | -0.10474 | 0.039731 | -0.10194 | -0.022515 | 0.022515 | houston | N | 0.022515 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.023027 | houston | N | -0.078431 | 0.066036 | -0.075637 | 0.0037903 | 0.0037903 | houston | N | 0.0037903 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.023027 | houston | N | -0.078431 | 0.066036 | -0.075637 | 0.0037903 | 0.0037903 | houston | N | 0.0037903 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.023027 | houston | N | -0.078431 | 0.066036 | -0.075637 | 0.0037903 | 0.0037903 | houston | N | 0.0037903 | 0
48761 | PR_GT1__ | 1 | 35 | -0.023295 | houston | N | -0.078699 | 0.065768 | -0.075905 | 0.0035223 | 0.0035223 | houston | N | 0.0035223 | 0
48772 | PHR_GN2_ | MB | 459 | -0.025809 | houston | Y | -0.081213 | 0.063254 | -0.078419 | 0.0010083 | 0.0010083 | houston | N | 0.0010083 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.020728 | houston | N | -0.076132 | 0.068335 | -0.073338 | 0.0060893 | 0.0060893 | houston | N | 0.0060893 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.020728 | houston | N | -0.076132 | 0.068335 | -0.073338 | 0.0060893 | 0.0060893 | houston | N | 0.0060893 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.020728 | houston | N | -0.076132 | 0.068335 | -0.073338 | 0.0060893 | 0.0060893 | houston | N | 0.0060893 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.020728 | houston | N | -0.076132 | 0.068335 | -0.073338 | 0.0060893 | 0.0060893 | houston | N | 0.0060893 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.020728 | houston | N | -0.076132 | 0.068335 | -0.073338 | 0.0060893 | 0.0060893 | houston | N | 0.0060893 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.020728 | houston | N | -0.076132 | 0.068335 | -0.073338 | 0.0060893 | 0.0060893 | houston | N | 0.0060893 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.020728 | houston | N | -0.076132 | 0.068335 | -0.073338 | 0.0060893 | 0.0060893 | houston | N | 0.0060893 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.016772 | houston | N | -0.072176 | 0.072291 | -0.069382 | 0.010045 | 0.010045 | houston | N | 0.010045 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.016772 | houston | N | -0.072176 | 0.072291 | -0.069382 | 0.010045 | 0.010045 | houston | N | 0.010045 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.016772 | houston | N | -0.072176 | 0.072291 | -0.069382 | 0.010045 | 0.010045 | houston | N | 0.010045 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.016772 | houston | N | -0.072176 | 0.072291 | -0.069382 | 0.010045 | 0.010045 | houston | N | 0.010045 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.020575 | houston | N | -0.075979 | 0.068488 | -0.073185 | 0.0062423 | 0.0062423 | houston | N | 0.0062423 | 0
48820 | SHELLG1_ | 1 | 71 | -0.022777 | houston | N | -0.078181 | 0.066286 | -0.075387 | 0.0040403 | 0.0040403 | houston | N | 0.0040403 | 0
48821 | SHELLG2 | 2 | 72 | -0.022777 | houston | N | -0.078181 | 0.066286 | -0.075387 | 0.0040403 | 0.0040403 | houston | N | 0.0040403 | 0
48822 | SHELLG3_ | 1 | 39 | -0.022777 | houston | N | -0.078181 | 0.066286 | -0.075387 | 0.0040403 | 0.0040403 | houston | N | 0.0040403 | 0
48822 | SHELLG3_ | 2 | 30 | -0.022777 | houston | N | -0.078181 | 0.066286 | -0.075387 | 0.0040403 | 0.0040403 | houston | N | 0.0040403 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.023663 | houston | N | -0.079067 | 0.0654 | -0.076273 | 0.0031543 | 0.0031543 | houston | N | 0.0031543 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.023663 | houston | N | -0.079067 | 0.0654 | -0.076273 | 0.0031543 | 0.0031543 | houston | N | 0.0031543 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.023042 | houston | N | -0.078446 | 0.066021 | -0.075652 | 0.0037753 | 0.0037753 | houston | N | 0.0037753 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.023094 | houston | Y | -0.078498 | 0.065969 | -0.075704 | 0.0037233 | 0.0037233 | houston | N | 0.0037233 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.023108 | houston | Y | -0.078512 | 0.065955 | -0.075718 | 0.0037093 | 0.0037093 | houston | N | 0.0037093 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.023047 | houston | Y | -0.078451 | 0.066016 | -0.075657 | 0.0037703 | 0.0037703 | houston | N | 0.0037703 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.023033 | houston | Y | -0.078437 | 0.06603 | -0.075643 | 0.0037843 | 0.0037843 | houston | N | 0.0037843 | 0
48855 | SRB_GT21 | B2 | 12 | -0.023118 | houston | Y | -0.078522 | 0.065945 | -0.075728 | 0.0036993 | 0.0036993 | houston | N | 0.0036993 | 0
48855 | SRB_GT21 | MB | 18 | -0.023118 | houston | Y | -0.078522 | 0.065945 | -0.075728 | 0.0036993 | 0.0036993 | houston | N | 0.0036993 | 0
48865 | TECO_GT1 | 1 | 50 | -0.02668 | houston | Y | -0.082084 | 0.062383 | -0.07929 | 0.00013729 | 0.00013729 | houston | N | 0.00013729 | 0
48873 | THW_ST3_ | 3 | 104 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48874 | THW_ST4_ | 4 | 104 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48875 | THW_3132 | A | 54 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48875 | THW_3132 | B | 53 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48877 | THW_3334 | C | 54 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48877 | THW_3334 | D | 57 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48879 | THW_4142 | E | 54 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48879 | THW_4142 | F | 54 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48881 | THW_4344 | G | 58 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48881 | THW_4344 | H | 58 | -0.021618 | houston | Y | -0.077022 | 0.067445 | -0.074228 | 0.0051993 | 0.0051993 | houston | N | 0.0051993 | 0
48883 | THW_GT1_ | B2 | 12 | -0.021001 | houston | Y | -0.076405 | 0.068062 | -0.073611 | 0.0058163 | 0.0058163 | houston | N | 0.0058163 | 0
48885 | THW_5152 | A | 56 | -0.019572 | houston | Y | -0.074976 | 0.069491 | -0.072182 | 0.0072453 | 0.0072453 | houston | N | 0.0072453 | 0
48885 | THW_5152 | B | 59 | -0.019572 | houston | Y | -0.074976 | 0.069491 | -0.072182 | 0.0072453 | 0.0072453 | houston | N | 0.0072453 | 0
48886 | THW_5354 | C | 56 | -0.019572 | houston | Y | -0.074976 | 0.069491 | -0.072182 | 0.0072453 | 0.0072453 | houston | N | 0.0072453 | 0
48886 | THW_5354 | D | 56 | -0.019572 | houston | Y | -0.074976 | 0.069491 | -0.072182 | 0.0072453 | 0.0072453 | houston | N | 0.0072453 | 0
48887 | THW_5556 | E | 59 | -0.019572 | houston | Y | -0.074976 | 0.069491 | -0.072182 | 0.0072453 | 0.0072453 | houston | N | 0.0072453 | 0
48887 | THW_5556 | F | 56 | -0.019572 | houston | Y | -0.074976 | 0.069491 | -0.072182 | 0.0072453 | 0.0072453 | houston | N | 0.0072453 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.046966 | houston | Y | -0.10237 | 0.042097 | -0.099576 | -0.020149 | 0.020149 | houston | N | 0.020149 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.030496 | houston | Y | -0.0859 | 0.058567 | -0.083106 | -0.0036787 | 0.0036787 | houston | N | 0.0036787 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.030496 | houston | Y | -0.0859 | 0.058567 | -0.083106 | -0.0036787 | 0.0036787 | houston | N | 0.0036787 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.030496 | houston | Y | -0.0859 | 0.058567 | -0.083106 | -0.0036787 | 0.0036787 | houston | N | 0.0036787 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.030496 | houston | Y | -0.0859 | 0.058567 | -0.083106 | -0.0036787 | 0.0036787 | houston | N | 0.0036787 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.030496 | houston | N | -0.0859 | 0.058567 | -0.083106 | -0.0036787 | 0.0036787 | houston | N | 0.0036787 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.031362 | houston | Y | -0.086766 | 0.057701 | -0.083972 | -0.0045447 | 0.0045447 | houston | N | 0.0045447 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.031362 | houston | Y | -0.086766 | 0.057701 | -0.083972 | -0.0045447 | 0.0045447 | houston | N | 0.0045447 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.031362 | houston | Y | -0.086766 | 0.057701 | -0.083972 | -0.0045447 | 0.0045447 | houston | N | 0.0045447 | 0
48929 | WAPGT21_ | B1 | 13 | -0.030496 | houston | Y | -0.0859 | 0.058567 | -0.083106 | -0.0036787 | 0.0036787 | houston | N | 0.0036787 | 0
48940 | WARVUE_G | G1 | 12 | -0.020716 | houston | Y | -0.07612 | 0.068347 | -0.073326 | 0.0061013 | 0.0061013 | houston | N | 0.0061013 | 0
49803 | EXN_15GT | 1 | 34 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49826 | EXN938GT | 5 | 45.9 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49828 | EXN941GT | 10 | 17.7 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49829 | EXN942GT | 11 | 20.4 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49830 | EXN943GT | 12 | 19.9 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49831 | EXN944GT | 13 | 35 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49832 | EXN945GT | 9 | 18 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49837 | EXN_GT | 4 | 85.4 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49838 | EXN_14GT | 14 | 148 | -0.021205 | houston | N | -0.076609 | 0.067858 | -0.073815 | 0.0056123 | 0.0056123 | houston | N | 0.0056123 | 0
49851 | DOW17000 | 37 | 62 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49858 | DOW38100 | 31 | 71.4 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49859 | DOW38200 | 33 | 45 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49860 | DOW38300 | 32 | 101 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49862 | DOW39100 | 36 | 86 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49863 | DOW39200 | 35 | 88 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49865 | DOW41000 | 41 | 50 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49866 | DOW42000 | 42 | 18 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49869 | DOW49000 | 45 | 94 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49870 | DOW61000 | 61 | 70 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49871 | DOW62000 | 62 | 63 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49872 | DOW63000 | 63 | 72 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49873 | DOW64000 | 64 | 64.8 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49876 | DOW65000 | 65 | 101 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49877 | DOW66000 | 66 | 97 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49878 | DOW67000 | 67 | 103 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49882 | DOW81000 | 81 | 76 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49884 | DOW82000 | 82 | 80 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49885 | DOW83000 | 83 | 80 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
49886 | DOW84000 | 84 | 171 | -0.039854 | houston | N | -0.095258 | 0.049209 | -0.092464 | -0.013037 | 0.013037 | houston | N | 0.013037 | 0
58909 | PEARSALL | 1 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58909 | PEARSALL | 2 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58909 | PEARSALL | 3 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58909 | PEARSALL | 4 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58909 | PEARSALL | 5 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58909 | PEARSALL | 6 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58919 | PEARSALL | 1 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58919 | PEARSALL | 2 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58919 | PEARSALL | 3 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58919 | PEARSALL | 4 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58919 | PEARSALL | 5 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58919 | PEARSALL | 6 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58929 | PEARSALL | 1 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58929 | PEARSALL | 2 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58929 | PEARSALL | 3 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58929 | PEARSALL | 4 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58929 | PEARSALL | 5 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58929 | PEARSALL | 6 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58949 | PEARSALL | 1 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58949 | PEARSALL | 2 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58949 | PEARSALL | 3 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58949 | PEARSALL | 4 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58949 | PEARSALL | 5 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
58949 | PEARSALL | 6 | 8.4 | -0.07637 | south | Y | -0.13177 | 0.012693 | -0.12898 | -0.049553 | 0.012693 | south | N | 0.012693 | 0
60000 | DSKY2 | 1 | 76.5 | 0.043921 | west | Y | -0.011483 | 0.13298 | -0.0086893 | 0.070738 | 0.0086893 | west | N | 0.0086893 | 0
60003 | KING_NE1 | 1 | 80 | 0.046344 | west | Y | -0.0090598 | 0.13541 | -0.0062663 | 0.073161 | 0.0062663 | west | N | 0.0062663 | 0
60005 | KING_SE1 | 1 | 40 | 0.046344 | west | Y | -0.0090598 | 0.13541 | -0.0062663 | 0.073161 | 0.0062663 | west | N | 0.0062663 | 0
60007 | KING_SW1 | 1 | 80 | 0.046737 | west | Y | -0.0086668 | 0.1358 | -0.0058733 | 0.073554 | 0.0058733 | west | N | 0.0058733 | 0
60016 | WOODWRD1 | 1 | 80 | 0.046259 | west | Y | -0.0091448 | 0.13532 | -0.0063513 | 0.073076 | 0.0063513 | west | N | 0.0063513 | 0
60017 | ORNNWP1 | 1 | 80 | 0.044241 | west | Y | -0.011163 | 0.1333 | -0.0083693 | 0.071058 | 0.0083693 | west | N | 0.0083693 | 0
60018 | DSKY1 | 1 | 84 | 0.04358 | west | Y | -0.011824 | 0.13264 | -0.0090303 | 0.070397 | 0.0090303 | west | N | 0.0090303 | 0
60019 | KING_NW1 | 1 | 80 | 0.046737 | west | Y | -0.0086668 | 0.1358 | -0.0058733 | 0.073554 | 0.0058733 | west | N | 0.0058733 | 0
60057 | CALLAHAN | 1 | 114 | -0.087363 | south | Y | -0.14277 | 0.0017004 | -0.13997 | -0.060546 | 0.0017004 | south | N | 0.0017004 | 0
60058 | BUFF_GAP | 1 | 120 | 0.05345 | west | Y | -0.0019538 | 0.14251 | 0.00083965 | 0.080267 | 0.00083965 | west | N | 0.00083965 | 0
60060 | CIRELLO | 1 | 233 | 0.05345 | west | Y | -0.0019538 | 0.14251 | 0.00083965 | 0.080267 | 0.00083965 | west | N | 0.00083965 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.05345 | west | Y | -0.0019538 | 0.14251 | 0.00083965 | 0.080267 | 0.00083965 | west | N | 0.00083965 | 0
60066 | H_HOLLOW | 1 | 222 | -0.087363 | south | Y | -0.14277 | 0.0017004 | -0.13997 | -0.060546 | 0.0017004 | south | N | 0.0017004 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.087363 | south | Y | -0.14277 | 0.0017004 | -0.13997 | -0.060546 | 0.0017004 | south | N | 0.0017004 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.087363 | south | Y | -0.14277 | 0.0017004 | -0.13997 | -0.060546 | 0.0017004 | south | N | 0.0017004 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.087363 | south | Y | -0.14277 | 0.0017004 | -0.13997 | -0.060546 | 0.0017004 | south | N | 0.0017004 | 0
60074 | HORSH5 | 1 | 100 | -0.087363 | south | Y | -0.14277 | 0.0017004 | -0.13997 | -0.060546 | 0.0017004 | south | N | 0.0017004 | 0
60081 | WHRLWIND | 1 | 60 | 0.05515 | west | Y | -0.0002538 | 0.14421 | 0.0025397 | 0.081967 | 0.0002538 | North | Y | 0.0025397 | 0.13715
60201 | RIO DRCS | F | 0 | -0.028706 | south | N | -0.08411 | 0.060357 | -0.081316 | -0.0018887 | 0.0018887 | houston | Y | 0.060357 | 0
60202 | FRIEND_R | F | 0 | 0.033046 | west | N | -0.022358 | 0.12211 | -0.019564 | 0.059863 | 0.019564 | west | N | 0.019564 | 0
60203 | PRES0A | BT | 4.8 | 0.048181 | west | N | -0.0072228 | 0.13724 | -0.0044293 | 0.074998 | 0.0044293 | west | N | 0.0044293 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.054228 | west | Y | -0.0011758 | 0.14329 | 0.0016177 | 0.081045 | 0.0011758 | North | Y | 0.0016177 | 0.01657
71054 | L_SWEETW | W1 | 107.5 | 0.054228 | west | Y | -0.0011758 | 0.14329 | 0.0016177 | 0.081045 | 0.0011758 | North | Y | 0.0016177 | 0.047499
71057 | L_SWEETW | W1 | 135 | 0.054228 | west | Y | -0.0011758 | 0.14329 | 0.0016177 | 0.081045 | 0.0011758 | North | Y | 0.0016177 | 0.05965
71059 | L_SWEETW | W1 | 119 | 0.054228 | west | Y | -0.0011758 | 0.14329 | 0.0016177 | 0.081045 | 0.0011758 | North | Y | 0.0016177 | 0.052581
71060 | L_SWEETW | W1 | 105 | 0.054228 | west | Y | -0.0011758 | 0.14329 | 0.0016177 | 0.081045 | 0.0011758 | North | Y | 0.0016177 | 0.046395
71061 | L_SWEETW | W1 | 80.5 | 0.054228 | west | Y | -0.0011758 | 0.14329 | 0.0016177 | 0.081045 | 0.0011758 | North | Y | 0.0016177 | 0.035569
76031 | L_GASCCR | W1 | 150 | 0.052824 | west | Y | -0.0025798 | 0.14189 | 0.00021365 | 0.079641 | 0.00021365 | west | N | 0.00021365 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.052655 | west | Y | -0.0027488 | 0.14172 | 4.465e-05 | 0.079472 | 4.465e-05 | west | N | 4.465e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.052655 | west | Y | -0.0027488 | 0.14172 | 4.465e-05 | 0.079472 | 4.465e-05 | west | N | 4.465e-05 | 0
76096 | L_CAPRSI | W1 | 186 | 0.052655 | west | Y | -0.0027488 | 0.14172 | 4.465e-05 | 0.079472 | 4.465e-05 | west | N | 4.465e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.052655 | west | Y | -0.0027488 | 0.14172 | 4.465e-05 | 0.079472 | 4.465e-05 | west | N | 4.465e-05 | 0
80003 | MILHWYS | F | 0 | -0.073928 | south | N | -0.12933 | 0.015135 | -0.12654 | -0.047111 | 0.015135 | south | N | 0.015135 | 0
80010 | EPLVT1 | F | 0 | -0.056072 | south | N | -0.11148 | 0.032991 | -0.10868 | -0.029255 | 0.029255 | houston | Y | 0.032991 | 0
80012 | LAR | F | 0 | -0.077199 | south | N | -0.1326 | 0.011864 | -0.12981 | -0.050382 | 0.011864 | south | N | 0.011864 | 0
80051 | FORPVCM0 | 8 | 28 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
80053 | FOR69CG0 | 10 | 74 | -0.067955 | south | N | -0.12336 | 0.021108 | -0.12057 | -0.041138 | 0.021108 | south | N | 0.021108 | 0
80080 | GWINDT11 | 1 | 94 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80080 | GWINDT11 | 2 | 41 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80080 | GWINDT11 | 3 | 38 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80080 | GWINDT11 | 4 | 19 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80081 | GWINDT21 | 1 | 94 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80081 | GWINDT21 | 2 | 36 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80081 | GWINDT21 | 3 | 43 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80081 | GWINDT21 | 4 | 22 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80137 | CSDR89 | 8 | 39 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
80137 | CSDR89 | 9 | 15 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
80138 | CSDR7 | 7 | 7 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
80139 | CSDR56 | 5 | 15 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
80139 | CSDR56 | 6 | 39 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
80140 | CSDR11 | 11 | 39 | -0.070115 | south | N | -0.12552 | 0.018948 | -0.12273 | -0.043298 | 0.018948 | south | N | 0.018948 | 0
80180 | PNSCALT1 | 1 | 148 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80180 | PNSCALT1 | 2 | 50 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80181 | PNSCALT2 | 1 | 55 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80181 | PNSCALT2 | 2 | 50 | -0.073887 | south | Y | -0.12929 | 0.015176 | -0.1265 | -0.04707 | 0.015176 | south | N | 0.015176 | 0
80223 | REYSHR G | 1 | 12 | -0.072565 | south | N | -0.12797 | 0.016498 | -0.12518 | -0.045748 | 0.016498 | south | N | 0.016498 | 0
80224 | VISTRONG | 1 | 15 | -0.070787 | south | N | -0.12619 | 0.018276 | -0.1234 | -0.04397 | 0.018276 | south | N | 0.018276 | 0
80225 | VISTRONG | 2 | 23 | -0.070787 | south | N | -0.12619 | 0.018276 | -0.1234 | -0.04397 | 0.018276 | south | N | 0.018276 | 0
80226 | ALCOA G | 1 | 48 | -0.068459 | south | N | -0.12386 | 0.020604 | -0.12107 | -0.041642 | 0.020604 | south | N | 0.020604 | 0
80227 | AIRCO G | 1 | 8 | -0.070368 | south | N | -0.12577 | 0.018695 | -0.12298 | -0.043551 | 0.018695 | south | N | 0.018695 | 0
80261 | NBEC81A | 1 | 180 | -0.073248 | south | Y | -0.12865 | 0.015815 | -0.12586 | -0.046431 | 0.015815 | south | N | 0.015815 | 0
80262 | NBEC91A | 1 | 180 | -0.073228 | south | Y | -0.12863 | 0.015835 | -0.12584 | -0.046411 | 0.015835 | south | N | 0.015835 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.073377 | south | Y | -0.12878 | 0.015686 | -0.12599 | -0.04656 | 0.015686 | south | N | 0.015686 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.073377 | south | Y | -0.12878 | 0.015686 | -0.12599 | -0.04656 | 0.015686 | south | N | 0.015686 | 0
80265 | LARECU40 | 4 | 100 | -0.077205 | south | Y | -0.13261 | 0.011858 | -0.12982 | -0.050388 | 0.011858 | south | N | 0.011858 | 0
80266 | LARECU50 | 5 | 100 | -0.077205 | south | Y | -0.13261 | 0.011858 | -0.12982 | -0.050388 | 0.011858 | south | N | 0.011858 | 0
80291 | PAPALOTE | 1 | 25 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
80291 | PAPALOTE | 2 | 25 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
80291 | PAPALOTE | 3 | 25 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
80291 | PAPALOTE | 4 | 16 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
80294 | PAPALOTE | 5 | 25 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
80294 | PAPALOTE | 6 | 25 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
80294 | PAPALOTE | 7 | 25 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
80294 | PAPALOTE | 8 | 15 | -0.07283 | south | Y | -0.12823 | 0.016233 | -0.12544 | -0.046013 | 0.016233 | south | N | 0.016233 | 0
86104 | CID-138 | EQ | 0 | -0.077205 | south | N | -0.13261 | 0.011858 | -0.12982 | -0.050388 | 0.011858 | south | N | 0.011858 | 0
86105 | CID-230 | EQ | 500 | -0.077205 | south | N | -0.13261 | 0.011858 | -0.12982 | -0.050388 | 0.011858 | south | N | 0.011858 | 0
86106 | CUF-230 | EQ | 500 | -0.077205 | south | N | -0.13261 | 0.011858 | -0.12982 | -0.050388 | 0.011858 | south | N | 0.011858 | 0
86107 | CUF-138 | EQ | 0 | -0.077205 | south | N | -0.13261 | 0.011858 | -0.12982 | -0.050388 | 0.011858 | south | N | 0.011858 | 0
88198 | BEEVILLE | F | 0 | -0.076548 | south | N | -0.13195 | 0.012515 | -0.12916 | -0.049731 | 0.012515 | south | N | 0.012515 | 0
88253 | HAMILTON | F | 0 | -0.042838 | south | N | -0.098242 | 0.046225 | -0.095448 | -0.016021 | 0.016021 | houston | Y | 0.046225 | 0
88299 | ZAPATA | F | 0 | -0.075546 | south | N | -0.13095 | 0.013517 | -0.12816 | -0.048729 | 0.013517 | south | N | 0.013517 | 0
88508 | FALFURRI | F | 0 | -0.074962 | south | N | -0.13037 | 0.014101 | -0.12757 | -0.048145 | 0.014101 | south | N | 0.014101 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.095404 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18019 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.095404 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.0829 | 787 | 0.18019 | 141.8133 | 787 | 141.8133
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.091624 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17641 | 0 | 787 | 141.8133
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.091624 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17641 | 0 | 787 | 141.8133 | Weighted Shift Factors
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.091074 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2239 | 255 | 0.17586 | 44.8455 | 1042 | 186.6588 | North | 0.055404
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.091074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.57 | 149 | 0.17586 | 26.2038 | 1191 | 212.8626 | South | -0.084791
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.091074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9343 | 153 | 0.17586 | 26.9073 | 1344 | 239.7699 |  | 0.14019
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.087779 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.1669 | 150 | 0.17257 | 25.8855 | 1494 | 265.6554
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.087779 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0223 | 80 | 0.17257 | 13.8056 | 1574 | 279.461 | Line Rating | 1072
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.083008 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2451 | 0 | 0.1678 | 0 | 1574 | 279.461 | Conc Gen | 2056
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.083008 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2451 | 0 | 0.1678 | 0 | 1574 | 279.461 | Weighted Imp. | 351.207
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.064488 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.834 | 168 | 0.14928 | 25.0788 | 1742 | 304.5398 | PTDF | 0.17082
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.064488 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.8039 | 90 | 0.14928 | 13.4351 | 1832 | 317.9749
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.239 | 224 | 0.14836 | 33.2321 | 2056 | 351.207 | Concentration | 1.2185
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3661 | 226 | 0.14836 | 33.5288
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4762 | 212 | 0.14836 | 31.4518
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4126 | 211 | 0.14836 | 31.3035
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.063159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6676 | 216.4 | 0.14795 | 32.0163
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.063159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6487 | 216.1 | 0.14795 | 31.9719
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.373 | 70 | 0.14726 | 10.3084
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3106 | 69 | 0.14726 | 10.1611
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3106 | 69 | 0.14726 | 10.1611
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2481 | 68 | 0.14726 | 10.0139
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.061862 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.5159 | 73 | 0.14665 | 10.7057
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.061862 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.3616 | 119 | 0.14665 | 17.4517
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.061862 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.6817 | 205 | 0.14665 | 30.0638
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.061862 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.3099 | 102 | 0.14665 | 14.9586
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.061862 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.9388 | 96 | 0.14665 | 14.0787
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.061783 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.707 | 60 | 0.14657 | 8.7944
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.061187 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14598 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.061066 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.1211 | 395 | 0.14586 | 57.6134
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.061066 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.5637 | 435 | 0.14586 | 63.4477
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.2668 | 217.3 | 0.14584 | 31.6918
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.5159 | 205 | 0.14584 | 29.898
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6308 | 272.4 | 0.14584 | 39.7278
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.060962 | north | 3 | N | N | Nnorth | Nnorth | 1 | 70.533 | 0 | 0.14575 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.060962 | north | 3 | N | N | Nnorth | Nnorth | 1 | 70.594 | 0 | 0.14575 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.060929 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.5041 | 435 | 0.14572 | 63.3881
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.0963 | 18 | 0.1457 | 2.6226
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.0963 | 18 | 0.1457 | 2.6226
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3145 | 38 | 0.1457 | 5.5365
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.060186 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7965 | 196 | 0.14498 | 28.4154
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.060186 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6806 | 111 | 0.14498 | 16.0924
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.060138 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14493 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.060138 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14493 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.060138 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14493 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.3097 | 288 | 0.14489 | 41.7294
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.8351 | 147 | 0.14489 | 21.2994
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.8351 | 147 | 0.14489 | 21.2994
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.059685 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.1622 | 120 | 0.14448 | 17.3371
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.059677 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71612 | 0 | 0.14447 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.059677 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71612 | 0 | 0.14447 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.059265 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.6673 | 112.5 | 0.14406 | 16.2063
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.059107 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5464 | 60 | 0.1439 | 8.6339
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.059107 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.7237 | 63 | 0.1439 | 9.0656
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.048 | 204 | 0.14385 | 29.3453
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8709 | 201 | 0.14385 | 28.9138
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.2923 | 242 | 0.14385 | 34.8116
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.058987 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.9605 | 118 | 0.14378 | 16.9658
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.058987 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.7835 | 115 | 0.14378 | 16.5344
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.058987 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.7968 | 556 | 0.14378 | 79.9404
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.058527 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14332 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.058492 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14328 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.058218 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.0888 | 242 | 0.14301 | 34.6081
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.058183 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3273 | 0 | 0.14297 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.058183 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3273 | 0 | 0.14297 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.0581 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.877 | 170 | 0.14289 | 24.2914
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.0581 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.212 | 520 | 0.14289 | 74.3032
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1613 | 20 | 0.14286 | 2.8572
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1613 | 20 | 0.14286 | 2.8572
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1613 | 20 | 0.14286 | 2.8572
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.98714 | 17 | 0.14286 | 2.4286
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058015 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14281 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058015 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14281 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.058003 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 21.4611 | 370 | 0.14279 | 52.8337
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1204 | 0 | 0.14279 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1784 | 0 | 0.14279 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.9229 | 0 | 0.14279 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.2944 | 0 | 0.14279 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.3524 | 0 | 0.14279 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.9809 | 0 | 0.14279 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2717 | 160 | 0.14274 | 22.8382
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0399 | 156 | 0.14274 | 22.2672
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.3578 | 196 | 0.14274 | 27.9768
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0399 | 156 | 0.14274 | 22.2672
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0978 | 157 | 0.14274 | 22.41
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.4737 | 198 | 0.14274 | 28.2623
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.057944 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.2075 | 366 | 0.14273 | 52.2409
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.3424 | 0 | 0.14269 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.6088 | 0 | 0.14269 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.1183 | 0 | 0.14269 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.057883 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3153 | 40 | 0.14267 | 5.7069
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.571 | 79 | 0.14265 | 11.2695
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.1333 | 106 | 0.14265 | 15.1211
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4477 | 146 | 0.14265 | 20.8272
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.057861 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3974 | 76 | 0.14265 | 10.8415
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.2842 | 558 | 0.14265 | 79.5974
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 33.4992 | 579 | 0.14265 | 82.593
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 46.7485 | 808 | 0.14265 | 115.2594
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.05778 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 22.4186 | 388 | 0.14257 | 55.3174
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.05778 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.7567 | 515 | 0.14257 | 73.4239
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1553 | 20 | 0.14255 | 2.8511
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4441 | 25 | 0.14255 | 3.5638
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3683 | 41 | 0.14255 | 5.8447
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.057595 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.9013 | 224 | 0.14239 | 31.8944
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2073 | 161 | 0.14198 | 22.8586
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3788 | 164 | 0.14198 | 23.2845
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3788 | 164 | 0.14198 | 23.2845
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6758 | 414 | 0.14198 | 58.7792
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2645 | 162 | 0.14198 | 23.0006
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2073 | 161 | 0.14198 | 22.8586
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3216 | 163 | 0.14198 | 23.1425
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3899 | 409 | 0.14198 | 58.0693
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.056763 | west | 4 | Y | N | Ywest | Nwest | 1 | 36.8789 | 649.7 | 0.14155 | 91.9675
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.056341 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2963 | 165 | 0.14113 | 23.2867
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.055834 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.1768 | 236 | 0.14062 | 33.1874
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.055832 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3328 | 400 | 0.14062 | 56.2491
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.05515 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.309 | 60 | 0.13994 | 8.3964
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 42.9246 | 785 | 0.13947 | 109.4853
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.4714 | 795 | 0.13947 | 110.88
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 42.6512 | 780 | 0.13947 | 108.788
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.054466 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1699 | 150 | 0.13926 | 20.8885
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.0431 | 0 | 0.13914 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0648 | 0 | 0.13914 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.88 | 0 | 0.13914 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.6837 | 0 | 0.13914 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3364 | 209 | 0.13903 | 29.0576
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8615 | 126.5 | 0.13903 | 17.5875
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.506 | 249 | 0.13903 | 34.6189
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6855 | 197 | 0.13903 | 27.3893
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0335 | 37.5 | 0.13902 | 5.2132
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8295 | 107.5 | 0.13902 | 14.9445
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3208 | 135 | 0.13902 | 18.7675
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4531 | 119 | 0.13902 | 16.5432
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6939 | 105 | 0.13902 | 14.597
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3654 | 80.5 | 0.13902 | 11.191
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.054125 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1188 | 150 | 0.13892 | 20.8374
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.054125 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4666 | 101 | 0.13892 | 14.0305
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.053958 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.13875 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.053938 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7423 | 125 | 0.13873 | 17.3411
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.053938 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7423 | 125 | 0.13873 | 17.3411
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.053927 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.6963 | 50 | 0.13872 | 6.9359
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.053861 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5243 | 84 | 0.13865 | 11.6467
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.053724 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3187 | 99 | 0.13851 | 13.713
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.053724 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2772 | 61 | 0.13851 | 8.4494
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3431 | 0 | 0.13851 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4552 | 0 | 0.13851 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4552 | 0 | 0.13851 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.053709 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.573 | 141 | 0.1385 | 19.5285
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.053709 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4451 | 120 | 0.1385 | 16.62
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.053703 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.7739 | 182 | 0.13849 | 25.2059
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.053703 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.9923 | 484 | 0.13849 | 67.031
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.05367 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3812 | 63 | 0.13846 | 8.723
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5383 | 66 | 0.1384 | 9.1344
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6991 | 69 | 0.1384 | 9.5497
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6991 | 69 | 0.1384 | 9.5497
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5919 | 67 | 0.1384 | 9.2728
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5919 | 67 | 0.1384 | 9.2728
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4846 | 65 | 0.1384 | 8.996
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0196 | 150 | 0.13825 | 20.7382
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7621 | 220 | 0.13825 | 30.416
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6928 | 200 | 0.13825 | 27.6509
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5173 | 121.9 | 0.13825 | 16.8533
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.414 | 120 | 0.13824 | 16.5889
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4538 | 233 | 0.13824 | 32.2101
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0972 | 170.2 | 0.13824 | 23.5286
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053347 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6025 | 180 | 0.13814 | 24.8648
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053347 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6025 | 180 | 0.13814 | 24.8648
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7318 | 0 | 0.1381 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 1 | 3.9131 | 0 | 0.1381 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7532 | 0 | 0.1381 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.053297 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9918 | 225 | 0.13809 | 31.0697
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.053211 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3853 | 120 | 0.138 | 16.5602
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.053188 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3826 | 120 | 0.13798 | 16.5574
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.052915 | west | 8 | N | N | Nwest | Nwest | 1 | 1.3652 | 0 | 0.13771 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.052824 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9236 | 150 | 0.13761 | 20.6422
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.052812 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3123 | 214.2 | 0.1376 | 29.4745
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.052701 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2965 | 100.5 | 0.13749 | 13.8179
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.052683 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0556 | 58 | 0.13747 | 7.9735
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9237 | 112.5 | 0.13745 | 15.4626
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8719 | 149.5 | 0.13745 | 20.5481
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.7938 | 186 | 0.13745 | 25.5649
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.2945 | 214.5 | 0.13745 | 29.4821
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6845 | 70 | 0.13743 | 9.6199
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6845 | 70 | 0.13743 | 9.6199
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.8846 | 92.8 | 0.13743 | 12.7532
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2109 | 80 | 0.13743 | 10.9941
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2109 | 80 | 0.13743 | 10.9941
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.0531 | 115 | 0.13743 | 15.8041
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.9569 | 208.2 | 0.13742 | 28.6104
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.4783 | 142.1 | 0.13742 | 19.5271
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.9678 | 132.4 | 0.13742 | 18.1941
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.1573 | 136 | 0.13742 | 18.6888
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.7362 | 147 | 0.13742 | 20.2004
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0517 | 210 | 0.13742 | 28.8577
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.052308 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34523 | 6.6 | 0.1371 | 0.90485
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.052308 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7942 | 34.3 | 0.1371 | 4.7025
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.052053 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.823 | 169.5 | 0.13684 | 23.195
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.051895 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7324 | 149 | 0.13669 | 20.3662
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.051729 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8105 | 35 | 0.13652 | 4.7782
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.051729 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5519 | 30 | 0.13652 | 4.0956
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4109 | 66 | 0.13647 | 9.0071
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.3592 | 65 | 0.13647 | 8.8706
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4626 | 67 | 0.13647 | 9.1435
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4626 | 67 | 0.13647 | 9.1435
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4626 | 67 | 0.13647 | 9.1435
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.05168 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13647 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.05168 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13647 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6526 | 151.5 | 0.1353 | 20.4984
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.693 | 152.3 | 0.1353 | 20.6066
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.9659 | 177.5 | 0.1353 | 24.0162
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5885 | 150.7 | 0.13515 | 20.3665
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6036 | 151 | 0.13515 | 20.407
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.933 | 177.4 | 0.13515 | 23.9749
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.049507 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.4468 | 615 | 0.1343 | 82.5931
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.049507 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.0606 | 587 | 0.1343 | 78.8328
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.048181 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.23127 | 0 | 0.13297 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046737 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.739 | 80 | 0.13153 | 10.5222
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046737 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.739 | 80 | 0.13153 | 10.5222
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4758 | 75 | 0.13113 | 9.8351
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7075 | 80 | 0.13113 | 10.4908
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8538 | 40 | 0.13113 | 5.2454
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046259 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7007 | 80 | 0.13105 | 10.484
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.046247 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6998 | 80 | 0.13104 | 10.483
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.046198 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9297 | 150 | 0.13099 | 19.6483
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.046198 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9297 | 150 | 0.13099 | 19.6483
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.044241 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5393 | 80 | 0.12903 | 10.3225
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.043921 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.36 | 76.5 | 0.12871 | 9.8464
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.04358 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6607 | 84 | 0.12837 | 10.7831
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.038747 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.0438 | 827 | 0.12354 | 102.1657
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.038747 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.7338 | 819 | 0.12354 | 101.1774
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033046 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11784 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 26.9864 | 855 | 0.11635 | 99.4824
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 26.9864 | 855 | 0.11635 | 99.4824
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.807 | 152.3 | 0.11635 | 17.7207
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.8291 | 153 | 0.11635 | 17.8021
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.024951 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7426 | 150 | 0.10974 | 16.4613
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.014502 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.7144 | 463 | 0.099293 | 45.9725
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.01144 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19448 | 17 | 0.096231 | 1.6359
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.01139 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.36448 | 0 | 0.096181 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.009873 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.4739 | 48 | 0.094664 | 4.5439
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.009873 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.45416 | 46 | 0.094664 | 4.3545
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.009873 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0367 | 105 | 0.094664 | 9.9397
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4637 | 0 | 0.094283 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4808 | 0 | 0.094283 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4808 | 0 | 0.094283 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.607 | 0 | 0.094283 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.084791 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.084791 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.028706 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.056085 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -8.7363 | 100 | -0.0025723 | -0.25723
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055404 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055404 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.9016 | 0 | -0.072176 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6164 | 0 | -0.072176 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5829 | 0 | -0.072176 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5829 | 0 | -0.072176 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7171 | 0 | -0.072176 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1547 | 59 | -0.074976 | -4.4236
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1547 | 59 | -0.074976 | -4.4236
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.019857 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.9031 | 398 | -0.075261 | -29.9538
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2594 | 0 | -0.075425 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2314 | 0 | -0.075425 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1813 | 0 | -0.075425 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3897 | 0 | -0.075425 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5251 | 172 | -0.075899 | -13.0546
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5251 | 172 | -0.075899 | -13.0546
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5251 | 172 | -0.075899 | -13.0546
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.020575 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2303 | 0 | -0.075979 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.020697 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.3779 | 743 | -0.076101 | -56.5429
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.020716 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.24859 | 12 | -0.07612 | -0.91344
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3473 | 0 | -0.076132 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.368 | 0 | -0.076132 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.451 | 0 | -0.076132 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3059 | 0 | -0.076132 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2851 | 0 | -0.076132 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1557 | 0 | -0.076132 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.223 | 0 | -0.076132 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.020733 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10366 | 0 | -0.076137 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.020733 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43539 | 0 | -0.076137 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.021001 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.25201 | 12 | -0.076405 | -0.91686
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72097 | 0 | -0.076609 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73581 | 0 | -0.076609 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6934 | 0 | -0.076609 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97331 | 0 | -0.076609 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37533 | 0 | -0.076609 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43258 | 0 | -0.076609 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42198 | 0 | -0.076609 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74218 | 0 | -0.076609 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38169 | 0 | -0.076609 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8109 | 0 | -0.076609 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1383 | 0 | -0.076609 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.021368 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.7055 | 735 | -0.076772 | -56.4273
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2483 | 104 | -0.077022 | -8.0103
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2483 | 104 | -0.077022 | -8.0103
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1458 | 53 | -0.077022 | -4.0822
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2322 | 57 | -0.077022 | -4.3902
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2538 | 58 | -0.077022 | -4.4673
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2538 | 58 | -0.077022 | -4.4673
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.02225 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8493 | 0 | -0.077654 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.02225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0038 | 0 | -0.077654 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.9387 | 42 | -0.077754 | -3.2657
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.9387 | 42 | -0.077754 | -3.2657
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.8493 | 38 | -0.077754 | -2.9546
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.8493 | 38 | -0.077754 | -2.9546
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.022383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0441 | 0 | -0.077787 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6172 | 0 | -0.078181 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6399 | 0 | -0.078181 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8883 | 0 | -0.078181 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68331 | 0 | -0.078181 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1449 | 0 | -0.078431 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6521 | 0 | -0.078431 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6152 | 0 | -0.078431 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.023033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2515 | 228 | -0.078437 | -17.8836
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4745 | 0 | -0.078443 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4561 | 0 | -0.078443 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.903 | 0 | -0.078443 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6957 | 0 | -0.078443 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.023042 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37328 | 0 | -0.078446 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.023047 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.909 | 213 | -0.078451 | -16.71
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.023083 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4394 | 0 | -0.078487 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.023083 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5027 | 0 | -0.078487 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.023094 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.8105 | 165 | -0.078498 | -12.9521
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.023108 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.9053 | 169 | -0.078512 | -13.2685
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.023118 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.27742 | 12 | -0.078522 | -0.94226
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.023118 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.078522 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.023295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.81532 | 0 | -0.078699 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8287 | 0 | -0.078864 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6856 | 0 | -0.078864 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6949 | 0 | -0.078864 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6832 | 0 | -0.078864 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3107 | 0 | -0.078864 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.023663 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8457 | 0 | -0.079067 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.023663 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.893 | 0 | -0.079067 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0955 | 46 | -0.07922 | -3.6441
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0955 | 46 | -0.07922 | -3.6441
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0955 | 46 | -0.07922 | -3.6441
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3099 | 55 | -0.07922 | -4.3571
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3099 | 55 | -0.07922 | -4.3571
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2861 | 54 | -0.07922 | -4.2779
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.586 | 0 | -0.079804 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.464 | 0 | -0.079804 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.586 | 0 | -0.079804 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.586 | 0 | -0.079804 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2565 | 0 | -0.080201 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1722 | 0 | -0.080201 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1573 | 0 | -0.080201 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3514 | 0 | -0.080201 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30252 | 0 | -0.080201 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.025809 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.081213 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.02668 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.334 | 50 | -0.082084 | -4.1042
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9675 | 0 | -0.083193 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8535 | 0 | -0.083193 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4728 | 0 | -0.083193 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2573 | 0 | -0.083193 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2656 | 0 | -0.083193 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2323 | 0 | -0.083193 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6677 | 0 | -0.083193 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7805 | 0 | -0.083193 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1116 | 0 | -0.083193 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.027802 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88966 | 0 | -0.083206 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.027802 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.83406 | 0 | -0.083206 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7886 | 0 | -0.083207 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5829 | 0 | -0.083207 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8554 | 0 | -0.083207 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8359 | 0 | -0.083207 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9099 | 161 | -0.0859 | -13.8299
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.0623 | 166 | -0.0859 | -14.2594
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.563 | 248 | -0.0859 | -21.3031
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.030496 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -16.6508 | 546 | -0.0859 | -46.9013
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.030496 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -19.6089 | 0 | -0.0859 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.030496 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39645 | 13 | -0.0859 | -1.1167
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.030716 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0136 | 0 | -0.08612 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1048 | 0 | -0.086722 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1048 | 0 | -0.086722 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.6729 | 0 | -0.086722 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -20.4167 | 651 | -0.086766 | -56.4845
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -17.6882 | 564 | -0.086766 | -48.9359
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -18.8172 | 600 | -0.086766 | -52.0595
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.031481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4513 | 0 | -0.086885 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64928 | 0 | -0.091475 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64928 | 0 | -0.091475 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54107 | 0 | -0.091475 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0593 | 0 | -0.091974 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0593 | 0 | -0.091974 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3518 | 0 | -0.091974 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0044 | 0 | -0.091974 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.038022 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6996 | 0 | -0.093426 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.038022 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38022 | 0 | -0.093426 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.039538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54167 | 0 | -0.094942 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4709 | 0 | -0.095258 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8456 | 0 | -0.095258 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7934 | 0 | -0.095258 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0253 | 0 | -0.095258 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4274 | 0 | -0.095258 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5072 | 0 | -0.095258 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9927 | 0 | -0.095258 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71737 | 0 | -0.095258 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7463 | 0 | -0.095258 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7898 | 0 | -0.095258 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5108 | 0 | -0.095258 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8695 | 0 | -0.095258 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5825 | 0 | -0.095258 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0253 | 0 | -0.095258 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8658 | 0 | -0.095258 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.105 | 0 | -0.095258 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0289 | 0 | -0.095258 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1883 | 0 | -0.095258 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1883 | 0 | -0.095258 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.815 | 0 | -0.095258 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.042838 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4137 | 0 | -0.098242 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.042838 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.071 | 0 | -0.098242 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.042838 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.098242 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.046966 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.0998 | 66 | -0.10237 | -6.7564
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7492 | 76 | -0.10474 | -7.9599
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7492 | 76 | -0.10474 | -7.9599
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.1799 | 105 | -0.10474 | -10.9973
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6506 | 74 | -0.10474 | -7.7504
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6506 | 74 | -0.10474 | -7.7504
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.0319 | 102 | -0.10474 | -10.6831
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.049882 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.4927 | 0 | -0.10529 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.049882 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.2433 | 0 | -0.10529 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.050969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4271 | 0 | -0.10637 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.050969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4781 | 0 | -0.10637 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.051203 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.6077 | 422 | -0.10661 | -44.9881
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.053575 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32145 | 0 | -0.10898 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.055927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0067 | 0 | -0.11133 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.055927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0067 | 0 | -0.11133 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.056072 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11148 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3324 | 0 | -0.12204 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.2658 | 0 | -0.12204 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3324 | 0 | -0.12204 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3684 | 0 | -0.12336 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5044 | 0 | -0.12336 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3684 | 0 | -0.12336 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4364 | 0 | -0.12336 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3277 | 0 | -0.12336 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6989 | 0 | -0.12336 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1259 | 0 | -0.12336 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9027 | 0 | -0.12336 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9628 | 0 | -0.12336 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0287 | 0 | -0.12336 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.068459 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.286 | 0 | -0.12386 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9632 | 0 | -0.12552 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4908 | 0 | -0.12552 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7345 | 0 | -0.12552 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0517 | 0 | -0.12552 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4908 | 0 | -0.12552 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0517 | 0 | -0.12552 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7345 | 0 | -0.12552 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7345 | 0 | -0.12552 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.070368 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56294 | 0 | -0.12577 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.070787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0618 | 0 | -0.12619 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.070787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6281 | 0 | -0.12619 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.071384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5704 | 22 | -0.12679 | -2.7893
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071384 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.78522 | 11 | -0.12679 | -1.3947
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071384 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.78522 | 11 | -0.12679 | -1.3947
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4304 | 47.7 | -0.12732 | -6.0732
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6825 | 37.3 | -0.12732 | -4.7491
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3082 | 46 | -0.12732 | -5.8568
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.452 | 48 | -0.12732 | -6.1114
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.071952 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2525 | 0 | -0.12736 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.4653 | 0 | -0.12797 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.1024 | 0 | -0.12797 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.2565 | 0 | -0.12797 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5219 | 0 | -0.12797 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.6671 | 0 | -0.12797 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.2158 | 0 | -0.12797 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.072565 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.87078 | 0 | -0.12797 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.072629 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.4586 | 144 | -0.12803 | -18.4367
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.072629 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6543 | 188 | -0.12803 | -24.0702
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 25 | -0.12823 | -3.2058
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 25 | -0.12823 | -3.2058
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 25 | -0.12823 | -3.2058
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1653 | 16 | -0.12823 | -2.0517
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 25 | -0.12823 | -3.2058
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 25 | -0.12823 | -3.2058
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 25 | -0.12823 | -3.2058
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0924 | 15 | -0.12823 | -1.9235
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.073228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6046 | 336 | -0.12863 | -43.2203
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.181 | 180 | -0.12863 | -23.1537
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.8609 | 0 | -0.12864 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.8829 | 0 | -0.12864 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2051 | 0 | -0.12864 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073248 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.1846 | 180 | -0.12865 | -23.1573
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.073377 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.5079 | 334 | -0.12878 | -43.0128
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.073377 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.9482 | 340 | -0.12878 | -43.7855
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.073377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2079 | 180 | -0.12878 | -23.1805
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.073377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2079 | 180 | -0.12878 | -23.1805
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.073391 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8348 | 0 | -0.12879 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.073391 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8348 | 0 | -0.12879 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.073455 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7913 | 0 | -0.12886 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.073461 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7915 | 0 | -0.12886 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.073781 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1396 | 0 | -0.12918 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9454 | 94 | -0.12929 | -12.1533
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.0294 | 41 | -0.12929 | -5.3009
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8077 | 38 | -0.12929 | -4.9131
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4039 | 19 | -0.12929 | -2.4565
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9454 | 94 | -0.12929 | -12.1533
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6599 | 36 | -0.12929 | -4.6545
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1771 | 43 | -0.12929 | -5.5595
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6255 | 22 | -0.12929 | -2.8444
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.9353 | 148 | -0.12929 | -19.135
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6944 | 50 | -0.12929 | -6.4645
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0638 | 55 | -0.12929 | -7.111
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6944 | 50 | -0.12929 | -6.4645
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.073928 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12933 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8093 | 38 | -0.12933 | -4.9146
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4268 | 19.3 | -0.12933 | -2.4961
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1089 | 15 | -0.12933 | -1.94
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.073928 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4746 | 47 | -0.12933 | -6.0786
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6625 | 144 | -0.12945 | -18.6406
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6625 | 144 | -0.12945 | -18.6406
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6617 | 171 | -0.12945 | -22.1357
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.3277 | 207 | -0.12945 | -26.7963
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.046 | 216.7 | -0.12945 | -28.052
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.9194 | 242 | -0.12945 | -31.3271
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8644 | 146.5 | -0.12956 | -18.9811
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9683 | 147.9 | -0.12956 | -19.1625
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.8297 | 173 | -0.12956 | -22.4145
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89842 | 0 | -0.13027 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.82355 | 0 | -0.13027 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89842 | 0 | -0.13027 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.074962 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13037 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.075546 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13095 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.075826 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.6946 | 629 | -0.13123 | -82.5435
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.076548 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13195 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.0771 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6168 | 0 | -0.1325 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.0771 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6168 | 0 | -0.1325 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.077199 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1326 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.077205 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7205 | 100 | -0.13261 | -13.2609
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.077205 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7205 | 100 | -0.13261 | -13.2609
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077254 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.8541 | 24 | -0.13266 | -3.1838
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077254 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.8541 | 24 | -0.13266 | -3.1838
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.077254 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.7768 | 23 | -0.13266 | -3.0511
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.081553 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.2814 | 310 | -0.13696 | -42.4566
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.081553 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -33.6814 | 413 | -0.13696 | -56.5632
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.082282 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.5837 | 396 | -0.13769 | -54.5236
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4941 | 42 | -0.1386 | -5.8211
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.6605 | 44 | -0.1386 | -6.0983
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.6605 | 44 | -0.1386 | -6.0983
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9101 | 47 | -0.1386 | -6.514
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.08356 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0027 | 0 | -0.13896 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1626 | 49 | -0.14036 | -6.8774
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9078 | 46 | -0.14036 | -6.4564
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9078 | 46 | -0.14036 | -6.4564
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9927 | 47 | -0.14036 | -6.5967
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.084952 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0826 | 154 | -0.14036 | -21.6148
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.084952 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5729 | 148 | -0.14036 | -20.7727
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0777 | 48 | -0.14036 | -6.7371
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0777 | 48 | -0.14036 | -6.7371
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.085832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9783 | 58 | -0.14124 | -8.1917
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.085832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.639 | 89 | -0.14124 | -12.57
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7766 | 44 | -0.14124 | -6.2144
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7766 | 44 | -0.14124 | -6.2144
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.6908 | 43 | -0.14124 | -6.0731
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8624 | 45 | -0.14124 | -6.3556
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.086202 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.0663 | 546 | -0.14161 | -77.3168
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.086202 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -64.6515 | 750 | -0.14161 | -106.2043
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.086374 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.1542 | 407 | -0.14178 | -57.7036
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.086399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.0574 | 209 | -0.1418 | -29.6368
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.086399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.6622 | 216 | -0.1418 | -30.6294
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9744 | 46 | -0.1418 | -6.5229
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0608 | 47 | -0.1418 | -6.6647
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9744 | 46 | -0.1418 | -6.5229
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9744 | 46 | -0.1418 | -6.5229
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3925 | 155 | -0.14181 | -21.9801
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.6885 | 170 | -0.14181 | -24.1072
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3925 | 155 | -0.14181 | -21.9801
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.086499 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.6376 | 412 | -0.1419 | -58.464
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.086499 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -34.5996 | 400 | -0.1419 | -56.7611
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.086629 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.7307 | 424 | -0.14203 | -60.2219
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.086629 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.8173 | 425 | -0.14203 | -60.3639
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1424 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1424 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1424 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.9594 | 114 | -0.14277 | -16.2754
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.3946 | 222 | -0.14277 | -31.6942
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -16.0748 | 184 | -0.14277 | -26.2691
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.5693 | 224 | -0.14277 | -31.9798
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.0467 | 115 | -0.14277 | -16.4182
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.087938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21105 | 0 | -0.14334 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.087938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21105 | 0 | -0.14334 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.1897 | 147 | -0.14513 | -21.3341
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.3822 | 138 | -0.14513 | -20.0279
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5616 | 140 | -0.14513 | -20.3182
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.1897 | 147 | -0.14513 | -21.3341
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.3301 | 182 | -0.14513 | -26.4136
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.7657 | 198 | -0.14513 | -28.7357
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.090158 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.36063 | 0 | -0.14556 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.090176 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54106 | 0 | -0.14558 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21682 | 0 | -0.14575 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21682 | 0 | -0.14575 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25296 | 0 | -0.14575 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -11.9562 | 132 | -0.14598 | -19.2695
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1373 | 134 | -0.14598 | -19.5614
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -29.2564 | 323 | -0.14598 | -47.1518
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2203 | 142 | -0.1485 | -21.0877
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.4996 | 145 | -0.1485 | -21.5332
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.0583 | 151 | -0.1485 | -22.4242
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.9993 | 290 | -0.1485 | -43.0664
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.6811 | 223.9 | -0.15224 | -34.086
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.7876 | 225 | -0.15224 | -34.2535
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.7489 | 224.6 | -0.15224 | -34.1926
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9523 | 226.7 | -0.15224 | -34.5123
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.10347 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -44.8034 | 433 | -0.15888 | -68.7932
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.10361 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -60.5059 | 584 | -0.15901 | -92.8617
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.10361 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -61.6456 | 595 | -0.15901 | -94.6108
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8295 | 152.5 | -0.17232 | -26.2786
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.4788 | 149.5 | -0.17232 | -25.7617
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.1944 | 232.6 | -0.17232 | -40.0814
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.1197 | 158 | -0.17641 | -27.8735
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.3618 | 160 | -0.17641 | -28.2264
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.1769 | 175 | -0.17641 | -30.8726
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.14621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -83.1952 | 569 | -0.20162 | -114.72
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.14621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -84.9498 | 581 | -0.20162 | -117.1394

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TEMPPSSLT_ to SANDOW_ 345kV [3413 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.14621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -83.1952 | 0 | -0.20162 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.14621 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -84.9498 | 0 | -0.20162 | 0 | 0 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.1197 | 158 | -0.17641 | -27.8735 | 158 | 27.8735
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.3618 | 160 | -0.17641 | -28.2264 | 318 | 56.0999 | Weighted Shift Factors
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.12101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.1769 | 175 | -0.17641 | -30.8726 | 493 | 86.9725 | North | 0.055404
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8295 | 152.5 | -0.17232 | -26.2786 | 645.5 | 113.2511 | South | -0.084791
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.4788 | 149.5 | -0.17232 | -25.7617 | 795 | 139.0128 |  | 0.14019
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.11692 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.1944 | 232.6 | -0.17232 | -40.0814 | 1027.6 | 179.0941
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.10361 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -60.5059 | 0 | -0.15901 | 0 | 1027.6 | 179.0941 | Line Rating | 1072
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.10361 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -61.6456 | 0 | -0.15901 | 0 | 1027.6 | 179.0941 | Conc Gen | 2069.8
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.10347 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -44.8034 | 0 | -0.15888 | 0 | 1027.6 | 179.0941 | Weighted Imp. | 337.2263
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.6811 | 223.9 | -0.15224 | -34.086 | 1251.5 | 213.1802 | PTDF | 0.16293
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.7876 | 225 | -0.15224 | -34.2535 | 1476.5 | 247.4337
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.7489 | 224.6 | -0.15224 | -34.1926 | 1701.1 | 281.6263 | Concentration | 1.1621
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.096834 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.9523 | 226.7 | -0.15224 | -34.5123 | 1927.8 | 316.1386
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2203 | 142 | -0.1485 | -21.0877 | 2069.8 | 337.2263
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.4996 | 145 | -0.1485 | -21.5332
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.0583 | 151 | -0.1485 | -22.4242
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.093101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.9993 | 290 | -0.1485 | -43.0664
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.091938 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.5969 | 50 | -0.14734 | -7.3671
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -11.9562 | 132 | -0.14598 | -19.2695
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.1373 | 134 | -0.14598 | -19.5614
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.090577 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -29.2564 | 323 | -0.14598 | -47.1518
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21682 | 0 | -0.14575 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21682 | 0 | -0.14575 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.090343 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25296 | 0 | -0.14575 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.090176 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54106 | 0 | -0.14558 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.090158 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.36063 | 0 | -0.14556 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.1897 | 147 | -0.14513 | -21.3341
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.3822 | 138 | -0.14513 | -20.0279
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5616 | 140 | -0.14513 | -20.3182
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.1897 | 147 | -0.14513 | -21.3341
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.3301 | 182 | -0.14513 | -26.4136
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.089726 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.7657 | 198 | -0.14513 | -28.7357
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.087938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21105 | 0 | -0.14334 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.087938 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21105 | 0 | -0.14334 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -9.9594 | 0 | -0.14277 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.3946 | 0 | -0.14277 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -16.0748 | 0 | -0.14277 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.5693 | 0 | -0.14277 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.0467 | 0 | -0.14277 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1424 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1424 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.086993 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.1424 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.086629 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.7307 | 0 | -0.14203 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.086629 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.8173 | 0 | -0.14203 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.086499 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.6376 | 412 | -0.1419 | -58.464
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.086499 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -34.5996 | 400 | -0.1419 | -56.7611
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3925 | 155 | -0.14181 | -21.9801
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.6885 | 170 | -0.14181 | -24.1072
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.086403 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3925 | 155 | -0.14181 | -21.9801
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.086399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.0574 | 209 | -0.1418 | -29.6368
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.086399 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.6622 | 216 | -0.1418 | -30.6294
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9744 | 46 | -0.1418 | -6.5229
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0608 | 47 | -0.1418 | -6.6647
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9744 | 46 | -0.1418 | -6.5229
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.086399 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9744 | 46 | -0.1418 | -6.5229
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.086374 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.1542 | 407 | -0.14178 | -57.7036
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.086202 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.0663 | 0 | -0.14161 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.086202 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -64.6515 | 0 | -0.14161 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.085832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -4.9783 | 58 | -0.14124 | -8.1917
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.085832 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.639 | 89 | -0.14124 | -12.57
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7766 | 44 | -0.14124 | -6.2144
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7766 | 44 | -0.14124 | -6.2144
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.6908 | 43 | -0.14124 | -6.0731
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.085832 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8624 | 45 | -0.14124 | -6.3556
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1626 | 49 | -0.14036 | -6.8774
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9078 | 46 | -0.14036 | -6.4564
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9078 | 46 | -0.14036 | -6.4564
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9927 | 47 | -0.14036 | -6.5967
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.084952 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.0826 | 154 | -0.14036 | -21.6148
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.084952 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5729 | 148 | -0.14036 | -20.7727
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0777 | 48 | -0.14036 | -6.7371
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.084952 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0777 | 48 | -0.14036 | -6.7371
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.08356 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0027 | 0 | -0.13896 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4941 | 42 | -0.1386 | -5.8211
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.6605 | 44 | -0.1386 | -6.0983
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.6605 | 44 | -0.1386 | -6.0983
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.083193 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9101 | 47 | -0.1386 | -6.514
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.082282 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.5837 | 0 | -0.13769 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.081553 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.2814 | 310 | -0.13696 | -42.4566
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.081553 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -33.6814 | 413 | -0.13696 | -56.5632
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077254 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.8541 | 24 | -0.13266 | -3.1838
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077254 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.8541 | 24 | -0.13266 | -3.1838
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.077254 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.7768 | 23 | -0.13266 | -3.0511
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.077205 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7205 | 100 | -0.13261 | -13.2609
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.077205 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7205 | 100 | -0.13261 | -13.2609
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077205 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13261 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.077199 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1326 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.0771 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6168 | 0 | -0.1325 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.0771 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6168 | 0 | -0.1325 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.076548 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13195 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.07637 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.64151 | 8.4 | -0.13177 | -1.1069
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.075826 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.6946 | 0 | -0.13123 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.075546 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13095 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.074962 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13037 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89842 | 0 | -0.13027 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.82355 | 0 | -0.13027 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.074868 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.89842 | 0 | -0.13027 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.8644 | 146.5 | -0.12956 | -18.9811
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9683 | 147.9 | -0.12956 | -19.1625
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.07416 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.8297 | 173 | -0.12956 | -22.4145
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.3277 | 207 | -0.12945 | -26.7963
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.046 | 216.7 | -0.12945 | -28.052
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.074047 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.9194 | 242 | -0.12945 | -31.3271
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6625 | 144 | -0.12945 | -18.6406
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.6625 | 144 | -0.12945 | -18.6406
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.074045 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6617 | 171 | -0.12945 | -22.1357
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8093 | 38 | -0.12933 | -4.9146
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4268 | 19.3 | -0.12933 | -2.4961
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.073928 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1089 | 15 | -0.12933 | -1.94
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.073928 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4746 | 47 | -0.12933 | -6.0786
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.073928 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12933 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9454 | 0 | -0.12929 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.0294 | 0 | -0.12929 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8077 | 0 | -0.12929 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4039 | 0 | -0.12929 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9454 | 0 | -0.12929 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6599 | 0 | -0.12929 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1771 | 0 | -0.12929 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6255 | 0 | -0.12929 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.9353 | 0 | -0.12929 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6944 | 0 | -0.12929 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0638 | 0 | -0.12929 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.073887 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.6944 | 0 | -0.12929 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.073781 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1396 | 0 | -0.12918 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.073461 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7915 | 0 | -0.12886 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.073455 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7913 | 0 | -0.12886 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.073391 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8348 | 0 | -0.12879 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.073391 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8348 | 0 | -0.12879 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.073377 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.5079 | 334 | -0.12878 | -43.0128
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.073377 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.9482 | 340 | -0.12878 | -43.7855
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.073377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2079 | 180 | -0.12878 | -23.1805
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.073377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2079 | 180 | -0.12878 | -23.1805
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073248 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.1846 | 180 | -0.12865 | -23.1573
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.8609 | 0 | -0.12864 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.8829 | 0 | -0.12864 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.073236 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2051 | 0 | -0.12864 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.073228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6046 | 336 | -0.12863 | -43.2203
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073228 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.181 | 180 | -0.12863 | -23.1537
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 0 | -0.12823 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 0 | -0.12823 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 0 | -0.12823 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1653 | 0 | -0.12823 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 0 | -0.12823 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 0 | -0.12823 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8208 | 0 | -0.12823 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.07283 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.0924 | 0 | -0.12823 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.072629 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.4586 | 144 | -0.12803 | -18.4367
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.072629 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.6543 | 188 | -0.12803 | -24.0702
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.4653 | 0 | -0.12797 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.1024 | 0 | -0.12797 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.2565 | 0 | -0.12797 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5219 | 0 | -0.12797 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.6671 | 0 | -0.12797 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.072565 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.2158 | 0 | -0.12797 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.072565 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.87078 | 0 | -0.12797 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.071952 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2525 | 0 | -0.12736 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4304 | 47.7 | -0.12732 | -6.0732
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.6825 | 37.3 | -0.12732 | -4.7491
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3082 | 46 | -0.12732 | -5.8568
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.071917 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.452 | 48 | -0.12732 | -6.1114
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.071384 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5704 | 22 | -0.12679 | -2.7893
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071384 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.78522 | 11 | -0.12679 | -1.3947
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071384 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.78522 | 11 | -0.12679 | -1.3947
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.070787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0618 | 0 | -0.12619 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.070787 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6281 | 0 | -0.12619 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.070368 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.56294 | 0 | -0.12577 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9632 | 0 | -0.12552 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4908 | 0 | -0.12552 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7345 | 0 | -0.12552 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0517 | 0 | -0.12552 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.4908 | 0 | -0.12552 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0517 | 0 | -0.12552 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7345 | 0 | -0.12552 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.070115 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7345 | 0 | -0.12552 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.068459 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.286 | 0 | -0.12386 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3684 | 0 | -0.12336 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5044 | 0 | -0.12336 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3684 | 0 | -0.12336 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4364 | 0 | -0.12336 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3277 | 0 | -0.12336 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6989 | 0 | -0.12336 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1259 | 0 | -0.12336 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9027 | 0 | -0.12336 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9628 | 0 | -0.12336 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.067955 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0287 | 0 | -0.12336 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3324 | 0 | -0.12204 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.2658 | 0 | -0.12204 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.066641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3324 | 0 | -0.12204 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.056072 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11148 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.055927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0067 | 0 | -0.11133 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.055927 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0067 | 0 | -0.11133 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.053575 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32145 | 0 | -0.10898 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.051203 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.6077 | 422 | -0.10661 | -44.9881
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.050969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4271 | 0 | -0.10637 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.050969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4781 | 0 | -0.10637 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.049882 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.4927 | 0 | -0.10529 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.049882 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.2433 | 0 | -0.10529 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7492 | 76 | -0.10474 | -7.9599
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7492 | 76 | -0.10474 | -7.9599
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.1799 | 105 | -0.10474 | -10.9973
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6506 | 74 | -0.10474 | -7.7504
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6506 | 74 | -0.10474 | -7.7504
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.049332 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.0319 | 102 | -0.10474 | -10.6831
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.046966 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.0998 | 66 | -0.10237 | -6.7564
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.042838 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4137 | 0 | -0.098242 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.042838 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.071 | 0 | -0.098242 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.042838 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.098242 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4709 | 0 | -0.095258 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8456 | 0 | -0.095258 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7934 | 0 | -0.095258 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0253 | 0 | -0.095258 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4274 | 0 | -0.095258 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5072 | 0 | -0.095258 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9927 | 0 | -0.095258 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71737 | 0 | -0.095258 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7463 | 0 | -0.095258 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7898 | 0 | -0.095258 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5108 | 0 | -0.095258 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8695 | 0 | -0.095258 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5825 | 0 | -0.095258 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0253 | 0 | -0.095258 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8658 | 0 | -0.095258 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.105 | 0 | -0.095258 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0289 | 0 | -0.095258 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1883 | 0 | -0.095258 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1883 | 0 | -0.095258 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.039854 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.815 | 0 | -0.095258 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.039538 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54167 | 0 | -0.094942 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.038022 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6996 | 0 | -0.093426 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.038022 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38022 | 0 | -0.093426 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0593 | 0 | -0.091974 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0593 | 0 | -0.091974 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3518 | 0 | -0.091974 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.03657 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0044 | 0 | -0.091974 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64928 | 0 | -0.091475 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64928 | 0 | -0.091475 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.036071 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54107 | 0 | -0.091475 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.031481 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4513 | 0 | -0.086885 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -20.4167 | 0 | -0.086766 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -17.6882 | 0 | -0.086766 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.031362 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -18.8172 | 0 | -0.086766 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1048 | 0 | -0.086722 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1048 | 0 | -0.086722 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.031318 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.6729 | 0 | -0.086722 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.030716 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0136 | 0 | -0.08612 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9099 | 161 | -0.0859 | -13.8299
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.0623 | 166 | -0.0859 | -14.2594
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.030496 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.563 | 248 | -0.0859 | -21.3031
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.030496 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -16.6508 | 546 | -0.0859 | -46.9013
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.030496 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -19.6089 | 0 | -0.0859 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.030496 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39645 | 13 | -0.0859 | -1.1167
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7886 | 0 | -0.083207 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5829 | 0 | -0.083207 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8554 | 0 | -0.083207 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.027803 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8359 | 0 | -0.083207 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.027802 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.88966 | 0 | -0.083206 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.027802 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.83406 | 0 | -0.083206 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9675 | 0 | -0.083193 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8535 | 0 | -0.083193 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4728 | 0 | -0.083193 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2573 | 0 | -0.083193 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2656 | 0 | -0.083193 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2323 | 0 | -0.083193 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6677 | 0 | -0.083193 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.027789 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.7805 | 0 | -0.083193 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.027789 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1116 | 0 | -0.083193 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.02668 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.334 | 50 | -0.082084 | -4.1042
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.025809 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.081213 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2565 | 0 | -0.080201 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1722 | 0 | -0.080201 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1573 | 0 | -0.080201 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3514 | 0 | -0.080201 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.024797 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30252 | 0 | -0.080201 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.586 | 0 | -0.079804 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.464 | 0 | -0.079804 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.586 | 0 | -0.079804 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.0244 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.586 | 0 | -0.079804 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0955 | 46 | -0.07922 | -3.6441
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0955 | 46 | -0.07922 | -3.6441
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.0955 | 46 | -0.07922 | -3.6441
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3099 | 55 | -0.07922 | -4.3571
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3099 | 55 | -0.07922 | -4.3571
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.023816 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2861 | 54 | -0.07922 | -4.2779
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.023663 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8457 | 0 | -0.079067 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.023663 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.893 | 0 | -0.079067 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8287 | 0 | -0.078864 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6856 | 0 | -0.078864 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6949 | 0 | -0.078864 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6832 | 0 | -0.078864 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.02346 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3107 | 0 | -0.078864 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.023295 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.81532 | 0 | -0.078699 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.023118 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.27742 | 12 | -0.078522 | -0.94226
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.023118 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.078522 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.023108 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.9053 | 169 | -0.078512 | -13.2685
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.023094 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.8105 | 165 | -0.078498 | -12.9521
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.023083 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4394 | 0 | -0.078487 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.023083 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5027 | 0 | -0.078487 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.023047 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.909 | 213 | -0.078451 | -16.71
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.023042 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37328 | 0 | -0.078446 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4745 | 0 | -0.078443 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4561 | 0 | -0.078443 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.903 | 0 | -0.078443 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.023039 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6957 | 0 | -0.078443 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.023033 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2515 | 228 | -0.078437 | -17.8836
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1449 | 0 | -0.078431 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6521 | 0 | -0.078431 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.023027 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6152 | 0 | -0.078431 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6172 | 0 | -0.078181 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6399 | 0 | -0.078181 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8883 | 0 | -0.078181 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.022777 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68331 | 0 | -0.078181 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.022383 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0441 | 0 | -0.077787 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.9387 | 42 | -0.077754 | -3.2657
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.9387 | 42 | -0.077754 | -3.2657
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.8493 | 38 | -0.077754 | -2.9546
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.02235 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.8493 | 38 | -0.077754 | -2.9546
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.02225 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8493 | 0 | -0.077654 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.02225 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0038 | 0 | -0.077654 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2483 | 104 | -0.077022 | -8.0103
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2483 | 104 | -0.077022 | -8.0103
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1458 | 53 | -0.077022 | -4.0822
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2322 | 57 | -0.077022 | -4.3902
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1674 | 54 | -0.077022 | -4.1592
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2538 | 58 | -0.077022 | -4.4673
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.021618 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2538 | 58 | -0.077022 | -4.4673
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.021368 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.7055 | 735 | -0.076772 | -56.4273
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72097 | 0 | -0.076609 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73581 | 0 | -0.076609 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6934 | 0 | -0.076609 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97331 | 0 | -0.076609 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37533 | 0 | -0.076609 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43258 | 0 | -0.076609 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42198 | 0 | -0.076609 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74218 | 0 | -0.076609 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38169 | 0 | -0.076609 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8109 | 0 | -0.076609 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.021205 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1383 | 0 | -0.076609 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.021001 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.25201 | 12 | -0.076405 | -0.91686
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.020733 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10366 | 0 | -0.076137 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.020733 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43539 | 0 | -0.076137 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3473 | 0 | -0.076132 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.368 | 0 | -0.076132 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.451 | 0 | -0.076132 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3059 | 0 | -0.076132 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2851 | 0 | -0.076132 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1557 | 0 | -0.076132 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.020728 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.223 | 0 | -0.076132 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.020716 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.24859 | 0 | -0.07612 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.020697 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.3779 | 743 | -0.076101 | -56.5429
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.020575 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2303 | 0 | -0.075979 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5251 | 172 | -0.075899 | -13.0546
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5251 | 172 | -0.075899 | -13.0546
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.020495 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5251 | 172 | -0.075899 | -13.0546
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2594 | 0 | -0.075425 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2314 | 0 | -0.075425 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1813 | 0 | -0.075425 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.020021 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3897 | 0 | -0.075425 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.019857 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.9031 | 398 | -0.075261 | -29.9538
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1547 | 59 | -0.074976 | -4.4236
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1547 | 59 | -0.074976 | -4.4236
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.019572 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.096 | 56 | -0.074976 | -4.1986
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.9016 | 0 | -0.072176 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6164 | 0 | -0.072176 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5829 | 0 | -0.072176 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016772 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5829 | 0 | -0.072176 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016772 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7171 | 0 | -0.072176 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055404 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055404 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055404 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.087363 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -8.7363 | 0 | -0.0025723 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.028706 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.056085 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.084791 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.084791 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4637 | 0 | 0.094283 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4808 | 0 | 0.094283 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4808 | 0 | 0.094283 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.009492 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.607 | 0 | 0.094283 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.009873 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.4739 | 48 | 0.094664 | 4.5439
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.009873 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.45416 | 46 | 0.094664 | 4.3545
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.009873 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0367 | 105 | 0.094664 | 9.9397
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.01139 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.36448 | 0 | 0.096181 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.01144 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19448 | 17 | 0.096231 | 1.6359
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.01144 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.096231 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.014502 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.7144 | 0 | 0.099293 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.024951 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7426 | 0 | 0.10974 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 26.9864 | 0 | 0.11635 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 26.9864 | 0 | 0.11635 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.807 | 0 | 0.11635 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.031563 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.8291 | 0 | 0.11635 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033046 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11784 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.038747 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.0438 | 0 | 0.12354 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.038747 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 31.7338 | 0 | 0.12354 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.04358 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6607 | 0 | 0.12837 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.043921 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.36 | 0 | 0.12871 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.044241 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5393 | 0 | 0.12903 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.046198 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9297 | 0 | 0.13099 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.046198 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9297 | 0 | 0.13099 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.046247 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6998 | 0 | 0.13104 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046259 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7007 | 0 | 0.13105 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4758 | 0 | 0.13113 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7075 | 0 | 0.13113 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.046344 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8538 | 0 | 0.13113 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046737 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.739 | 0 | 0.13153 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046737 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.739 | 0 | 0.13153 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.048181 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.23127 | 0 | 0.13297 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.049507 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.4468 | 0 | 0.1343 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.049507 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.0606 | 0 | 0.1343 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.5885 | 150.7 | 0.13515 | 20.3665
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6036 | 151 | 0.13515 | 20.407
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.050355 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.933 | 177.4 | 0.13515 | 23.9749
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6526 | 151.5 | 0.1353 | 20.4984
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.693 | 152.3 | 0.1353 | 20.6066
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.050512 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.9659 | 177.5 | 0.1353 | 24.0162
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4109 | 66 | 0.13647 | 9.0071
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.3592 | 65 | 0.13647 | 8.8706
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4626 | 67 | 0.13647 | 9.1435
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4626 | 67 | 0.13647 | 9.1435
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.05168 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4626 | 67 | 0.13647 | 9.1435
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.05168 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13647 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.05168 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13647 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.051729 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8105 | 0 | 0.13652 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.051729 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5519 | 0 | 0.13652 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.051895 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7324 | 0 | 0.13669 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.052053 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.823 | 0 | 0.13684 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.052308 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34523 | 0 | 0.1371 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.052308 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.7942 | 0 | 0.1371 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 10.9569 | 208.2 | 0.13742 | 28.6104
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.4783 | 142.1 | 0.13742 | 19.5271
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.9678 | 132.4 | 0.13742 | 18.1941
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.1573 | 136 | 0.13742 | 18.6888
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.7362 | 147 | 0.13742 | 20.2004
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.052627 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0517 | 210 | 0.13742 | 28.8577
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6845 | 70 | 0.13743 | 9.6199
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.6845 | 70 | 0.13743 | 9.6199
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.8846 | 92.8 | 0.13743 | 12.7532
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2109 | 80 | 0.13743 | 10.9941
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2109 | 80 | 0.13743 | 10.9941
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.052636 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.0531 | 115 | 0.13743 | 15.8041
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9237 | 0 | 0.13745 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8719 | 0 | 0.13745 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.7938 | 0 | 0.13745 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.052655 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.2945 | 0 | 0.13745 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.052683 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0556 | 0 | 0.13747 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.052701 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.2965 | 0 | 0.13749 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.052812 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3123 | 0 | 0.1376 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.052824 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9236 | 0 | 0.13761 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.052915 | west | 8 | N | N | Nwest | Nwest | 1 | 1.3652 | 0 | 0.13771 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.053188 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3826 | 0 | 0.13798 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.053211 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3853 | 0 | 0.138 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.053297 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.9918 | 0 | 0.13809 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7318 | 0 | 0.1381 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 1 | 3.9131 | 0 | 0.1381 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.053312 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7532 | 0 | 0.1381 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053347 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6025 | 0 | 0.13814 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053347 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6025 | 0 | 0.13814 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.414 | 0 | 0.13824 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.4538 | 0 | 0.13824 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.05345 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.0972 | 0 | 0.13824 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0196 | 0 | 0.13825 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7621 | 0 | 0.13825 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6928 | 0 | 0.13825 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.053464 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5173 | 0 | 0.13825 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5383 | 66 | 0.1384 | 9.1344
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6991 | 69 | 0.1384 | 9.5497
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6991 | 69 | 0.1384 | 9.5497
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5919 | 67 | 0.1384 | 9.2728
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5919 | 67 | 0.1384 | 9.2728
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.05361 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4846 | 65 | 0.1384 | 8.996
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.05367 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3812 | 0 | 0.13846 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.053703 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.7739 | 182 | 0.13849 | 25.2059
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.053703 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.9923 | 484 | 0.13849 | 67.031
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.053709 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.573 | 0 | 0.1385 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.053709 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4451 | 0 | 0.1385 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.053724 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3187 | 0 | 0.13851 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.053724 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2772 | 0 | 0.13851 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3431 | 0 | 0.13851 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4552 | 0 | 0.13851 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.053724 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4552 | 0 | 0.13851 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.053861 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5243 | 0 | 0.13865 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.053927 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.6963 | 0 | 0.13872 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.053938 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7423 | 0 | 0.13873 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.053938 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7423 | 0 | 0.13873 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.053958 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.13875 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.054125 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1188 | 0 | 0.13892 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.054125 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.4666 | 0 | 0.13892 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0335 | 0 | 0.13902 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8295 | 0 | 0.13902 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3208 | 0 | 0.13902 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4531 | 0 | 0.13902 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.6939 | 0 | 0.13902 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.054228 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.3654 | 0 | 0.13902 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3364 | 0 | 0.13903 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8615 | 0 | 0.13903 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.506 | 0 | 0.13903 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.054241 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6855 | 0 | 0.13903 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.0431 | 0 | 0.13914 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.0648 | 0 | 0.13914 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.88 | 0 | 0.13914 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.054345 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.6837 | 0 | 0.13914 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.054466 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1699 | 0 | 0.13926 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 42.9246 | 0 | 0.13947 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.4714 | 0 | 0.13947 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.054681 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 42.6512 | 0 | 0.13947 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.05515 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.309 | 0 | 0.13994 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.055832 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.3328 | 0 | 0.14062 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.055834 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.1768 | 0 | 0.14062 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.056341 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.2963 | 0 | 0.14113 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.056763 | west | 4 | Y | N | Ywest | Nwest | 1 | 36.8789 | 0 | 0.14155 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2073 | 161 | 0.14198 | 22.8586
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3788 | 164 | 0.14198 | 23.2845
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3788 | 164 | 0.14198 | 23.2845
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.6758 | 414 | 0.14198 | 58.7792
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2645 | 162 | 0.14198 | 23.0006
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2073 | 161 | 0.14198 | 22.8586
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3216 | 163 | 0.14198 | 23.1425
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.057188 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3899 | 409 | 0.14198 | 58.0693
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.057595 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.9013 | 224 | 0.14239 | 31.8944
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1553 | 20 | 0.14255 | 2.8511
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4441 | 25 | 0.14255 | 3.5638
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.057763 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3683 | 41 | 0.14255 | 5.8447
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.05778 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 22.4186 | 388 | 0.14257 | 55.3174
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.05778 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 29.7567 | 515 | 0.14257 | 73.4239
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.2842 | 0 | 0.14265 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 33.4992 | 0 | 0.14265 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.057857 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 46.7485 | 0 | 0.14265 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.571 | 79 | 0.14265 | 11.2695
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.1333 | 106 | 0.14265 | 15.1211
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.057861 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4477 | 146 | 0.14265 | 20.8272
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.057861 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3974 | 76 | 0.14265 | 10.8415
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.057883 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3153 | 40 | 0.14267 | 5.7069
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.3424 | 0 | 0.14269 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.6088 | 0 | 0.14269 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.057899 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.1183 | 0 | 0.14269 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.057944 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.2075 | 366 | 0.14273 | 52.2409
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2717 | 160 | 0.14274 | 22.8382
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0399 | 156 | 0.14274 | 22.2672
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.3578 | 196 | 0.14274 | 27.9768
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0399 | 156 | 0.14274 | 22.2672
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0978 | 157 | 0.14274 | 22.41
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.057948 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.4737 | 198 | 0.14274 | 28.2623
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.058003 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 21.4611 | 370 | 0.14279 | 52.8337
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1204 | 0 | 0.14279 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1784 | 0 | 0.14279 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.9229 | 0 | 0.14279 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.2944 | 0 | 0.14279 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.3524 | 0 | 0.14279 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.058003 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.9809 | 0 | 0.14279 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058015 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14281 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058015 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14281 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1613 | 20 | 0.14286 | 2.8572
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1613 | 20 | 0.14286 | 2.8572
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1613 | 20 | 0.14286 | 2.8572
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.058067 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.98714 | 17 | 0.14286 | 2.4286
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.0581 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.877 | 170 | 0.14289 | 24.2914
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.0581 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.212 | 520 | 0.14289 | 74.3032
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.058183 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3273 | 0 | 0.14297 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.058183 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3273 | 0 | 0.14297 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.058218 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.0888 | 242 | 0.14301 | 34.6081
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.058492 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14328 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.058527 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14332 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.058987 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 6.9605 | 118 | 0.14378 | 16.9658
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.058987 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.7835 | 115 | 0.14378 | 16.5344
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.058987 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 32.7968 | 556 | 0.14378 | 79.9404
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.048 | 204 | 0.14385 | 29.3453
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8709 | 201 | 0.14385 | 28.9138
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.059059 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.2923 | 242 | 0.14385 | 34.8116
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.059107 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5464 | 60 | 0.1439 | 8.6339
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.059107 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.7237 | 63 | 0.1439 | 9.0656
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.059265 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.6673 | 0 | 0.14406 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.059677 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71612 | 0 | 0.14447 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.059677 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.71612 | 0 | 0.14447 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.059685 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.1622 | 0 | 0.14448 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.3097 | 288 | 0.14489 | 41.7294
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.8351 | 147 | 0.14489 | 21.2994
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.060103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.8351 | 147 | 0.14489 | 21.2994
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.060138 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14493 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.060138 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14493 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.060138 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14493 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.060186 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.7965 | 196 | 0.14498 | 28.4154
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.060186 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.6806 | 111 | 0.14498 | 16.0924
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.0963 | 18 | 0.1457 | 2.6226
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.0963 | 18 | 0.1457 | 2.6226
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.060907 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3145 | 38 | 0.1457 | 5.5365
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.060929 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.5041 | 435 | 0.14572 | 63.3881
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.060962 | north | 3 | N | N | Nnorth | Nnorth | 1 | 70.533 | 0 | 0.14575 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.060962 | north | 3 | N | N | Nnorth | Nnorth | 1 | 70.594 | 0 | 0.14575 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.2668 | 217.3 | 0.14584 | 31.6918
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.5159 | 205 | 0.14584 | 29.898
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.061053 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6308 | 272.4 | 0.14584 | 39.7278
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.061066 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.1211 | 395 | 0.14586 | 57.6134
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.061066 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.5637 | 435 | 0.14586 | 63.4477
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.061187 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14598 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.061783 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.707 | 0 | 0.14657 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.061862 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.5159 | 73 | 0.14665 | 10.7057
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.061862 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.3616 | 119 | 0.14665 | 17.4517
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.061862 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.6817 | 205 | 0.14665 | 30.0638
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.061862 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.3099 | 102 | 0.14665 | 14.9586
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.061862 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.9388 | 96 | 0.14665 | 14.0787
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.373 | 70 | 0.14726 | 10.3084
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3106 | 69 | 0.14726 | 10.1611
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3106 | 69 | 0.14726 | 10.1611
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.062472 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2481 | 68 | 0.14726 | 10.0139
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.063159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6676 | 216.4 | 0.14795 | 32.0163
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.063159 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.6487 | 216.1 | 0.14795 | 31.9719
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.239 | 224 | 0.14836 | 33.2321
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3661 | 226 | 0.14836 | 33.5288
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4762 | 212 | 0.14836 | 31.4518
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.063567 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.4126 | 211 | 0.14836 | 31.3035
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.064488 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.834 | 168 | 0.14928 | 25.0788
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.064488 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.8039 | 90 | 0.14928 | 13.4351
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.083008 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2451 | 0 | 0.1678 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.083008 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2451 | 0 | 0.1678 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.087779 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.1669 | 150 | 0.17257 | 25.8855
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.087779 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0223 | 80 | 0.17257 | 13.8056
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.091074 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2239 | 255 | 0.17586 | 44.8455
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.091074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.57 | 149 | 0.17586 | 26.2038
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.091074 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9343 | 153 | 0.17586 | 26.9073
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.091624 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17641 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.091624 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17641 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.095404 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18019 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.095404 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.0829 | 787 | 0.18019 | 141.8133

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown