## test results
CRE test for: |  | 3413 TEMP_SS_ to 3429 SANDOW_ | [5 empty] | PASS
Line Rating: |  | 1072
Direction |  | South | → | North |  | S-N
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3413 TEMP_SS_ to 3429 SANDOW_
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.10219
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.16129
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.09592
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.046254
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3413 TEMP_SS_ to 3429 SANDOW_
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.11234
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.15411
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.096358
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.043915
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3413 TEMP_SS_ to 3429 SANDOW_
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.2563
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.0058328
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.14611
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.25765
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.11504
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.13984
PTDF tests
South | → | North | 0.039819 | 0.42071 | -0.42071 | -0.21445 | -0.039819 | -0.27364 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | -0.27364 | 0.2563
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.12701
[6 empty] | Concentration |  | -0.46417 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.042804
[6 empty] | Concentration |  | -0.15643 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 53.3828
| Percent of line rating => | [6 empty] | 4.98% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | -1.5375
[7 empty] | B1(N-S) | -0.0078721 | -0.40193 | -0.39405 | -0.0078721
[7 empty] | B2 (N-W) | -0.007646 | -0.016614 | -0.0089679 | -0.007646
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0.0054839 | -0.21915 | -0.22464 | 0.0054839
[7 empty] | B4 (S-W) | -0.006551 | 0.38958 | 0.39613 | -0.006551
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | 0.010175 | 0.18705 | 0.17687 | 0.010175
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | 0.013202 | -0.20179 | -0.215 | 0.013202
[7 empty] | test | 0 | 0.42071 | 0.42071 | 0
[7 empty] | B1 | -1.871%
Deployment Error Percent | [6 empty] | B2 | -1.817%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 1.303%
[7 empty] | B4 | -1.557%
[7 empty] | B5 | 2.418%
[7 empty] | B6 | 3.138%
[7 empty] | Max Abs Error | 3.138% | PASS

## Generation_sensitivity
Generator Sensitivities
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: 3413 TEMP_SS_ to 3429 SANDOW_ C: 3414 TEMP_SS_ to 3429 SANDOW_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: 3413 TEMP_SS_ to 3429 SANDOW_ C: 3414 TEMP_SS_ to 3429 SANDOW_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.16306 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 41.579
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.16306 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 24.2952
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.14766 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.215
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.14766 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.215
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.16306 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 24.9474
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.15555 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 23.3319
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.15555 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 12.4437
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11249 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 8.2118
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11249 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 13.3864
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11249 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 23.0607
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11249 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 11.4741
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11249 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 10.7991
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.10892 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.307
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.10892 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.307
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11743 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 19.7287
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11743 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 10.569
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0012
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0012
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 4.2247
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 31.6662
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.1629
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.1629
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.10866 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 12.2238
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.10658 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 4.2633
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 8.4171
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 11.2939
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 15.5557
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10655 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 8.0975
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.10852 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 6.5111
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.10852 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 6.8367
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.1276
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 2.6595
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 4.3616
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.029493 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 13.6553
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 6.218
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 6.1238
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.3122
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.3122
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.3122
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094212 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 10.7402
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094212 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 48.5192
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 6.4509
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 6.7441
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 6.7441
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 6.5486
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 6.5486
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 6.3532
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 6.8041
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 7.1346
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 6.843
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 14.6221
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 21.4458
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.097947 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 9.6968
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.097947 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 5.9748
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.097919 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 13.8066
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 2.4487
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.4762
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.4762
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.097919 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 11.7503
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.096445 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 2.4883
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.096074 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 9.6554
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.09696 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 11.6352
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.096043 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 5.5705
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.096281 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 20.6234
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.098626 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 14.7939
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.095289 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.62891
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.095289 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 3.2684
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.098626 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 9.9612
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.097002 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 11.6402
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.10596 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 38.7825
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.10632 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 25.7282
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.10193 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 40.7724
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.10194 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 24.0569
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.1029 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 16.979
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 22.0577
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 21.7333
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 26.1665
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.1235
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.1235
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.1235
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 1.8049
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.10891 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 13.0694
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.11172 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 6.703
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 7.9947
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 8.485
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 9.4231
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 17.0688
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 16.6421
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 20.9093
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 16.6421
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 16.7488
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 21.1226
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.10693 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 18.1774
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.10693 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 55.6015
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10677 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 39.5056
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 59.4432
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 61.6803
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 86.0754
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11023 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 12.3459
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11023 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 11.0231
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11023 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 41.6673
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 24.2642
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 22.8907
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 30.4167
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.11193 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 86.1861
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 7.9743
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.8603
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.8603
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 7.7464
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11145 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 128.95
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11145 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 129.0614
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 26.0891
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 26.322
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.11588 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 25.0773
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.11588 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 25.0425
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 24.6914
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 24.575
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11197 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 44.2297
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.11174 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 48.6082
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11197 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 48.7087
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.10764 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 14.8542
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.10851 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 12.8039
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.10851 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 12.4784
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.10851 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 60.3304
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.10643 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 41.2945
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.10643 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 54.8109
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 79.4302
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 80.4421
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 78.9243
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.099488 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 18.1068
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.099488 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 48.1522
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.10601 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 23.7467
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.099907 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 4.9954
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.099958 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 4.1982
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.092557 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 56.9226
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.092557 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 54.331
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.17291 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 92.8521
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.17291 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 136.0794
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.16815 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 12.6115
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.16815 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 37.3302
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.26215 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -149.1656
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15615 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -32.6347
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15615 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -33.7278
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.1561 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -63.5323
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.1828
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -7.3389
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.1828
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.1828
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.15655 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -66.3768
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.15655 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -66.5333
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15513 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -8.9977
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15513 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -13.8067
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -6.8258
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -6.8258
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -6.6707
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -6.9809
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.15633 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -64.4071
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.15633 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -62.5312
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.15569 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -85.0051
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.15569 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -116.7652
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -9.5882
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -14.9324
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -23.7346
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -24.1961
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -26.5377
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -24.1961
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.1284 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -2.8249
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.1284 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.4125
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.1284 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.4125
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -6.1721
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -4.8264
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -5.9522
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -6.211
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.618
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -1.4832
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.13943 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.3463
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.13943 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.3463
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.13943 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -3.2069
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.14841 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -58.7704
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.088576 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -118.0718
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.088576 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -117.6289
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -5.0562
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -2.568
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -1.9959
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13306 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -6.2537
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 6.3336
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.099307 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 14.8961
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.094741 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 16.0586
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.04495 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 6.7425
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.097848 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 6.1644
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.1037 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 67.3726
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.10706 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.2824
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.10706 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.2824
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.10207 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -43.0748
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -22.1204
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -22.4556
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -54.128
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -34.2195
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -34.6526
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -37.9013
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.1861 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -108.6818
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.1861 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -110.7289
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.18586 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -80.4791
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -39.1366
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -39.3289
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -39.259
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -39.626
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.14694 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.1755
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.14694 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.1755
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.3978
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.3978
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -1.1648
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.082934 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -1.1362
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.11043 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.9877
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.11043 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.9877
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -4.5279
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -4.3985
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -4.5279
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.10185 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -2.8518
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.10185 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -2.9537
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.094301 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 3.3005
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.094301 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 2.829
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.382
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.382
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.382
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.382
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.16465 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.98787
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.39297
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.39297
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.45847
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.16316 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.65262
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.15961 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.38307
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.15961 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.38307
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -23.8097
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -22.352
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -22.6759
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -23.8097
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -29.4787
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -32.0703
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -32.054
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -31.4234
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -48.8902
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -23.8669
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -24.3712
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -25.3796
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -48.7423
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.077259 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.5495
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.077259 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.9315
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.618
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.12948 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -9.4523
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -9.6438
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -9.8879
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -3.5299
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.88247
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -9.6438
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -9.7658
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -9.5705
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -3.0518
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -5.6154
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.1366 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -85.9201
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.13074 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -18.8263
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.13074 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -24.5787
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.1514 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -1.8168
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.096644 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.57986
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.13177 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -44.274
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13204 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -44.1024
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13204 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -44.8946
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.13219 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -5.0232
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.13207 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.3018
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.13207 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.3018
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.1322 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -5.0235
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.13279 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -3.8508
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -19.5433
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -19.5828
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -20.1626
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -20.626
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -19.9732
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -13.0544
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -18.9289
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -19.19
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -16.5791
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -19.5569
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -19.7438
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -23.0945
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -27.589
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -28.8818
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -32.2538
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -19.1917
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -19.1917
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -22.7902
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.15418 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -47.7949
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.15418 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -63.6751
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -6.5967
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -6.9109
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -6.9109
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -7.3821
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -7.8081
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -7.3301
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -7.3301
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -7.4894
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -24.5397
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -23.5837
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -7.6488
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -7.6488
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 6.7174
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 6.7174
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 8.9054
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 7.677
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 7.677
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 11.0357
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 19.9762
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 13.6341
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 12.7034
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 13.0488
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 14.1042
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 20.1489
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 20.6785
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 12.5159
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 24.6361
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 19.4912
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 19.4962
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 11.8829
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.094604 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 14.096
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.097258 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 17.5064
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.097258 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 17.5064
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.097166 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 21.8623
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.098364 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 12.2955
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.098364 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 12.2955
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 14.9481
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 15.0549
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 32.9925
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 15.2684
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 15.3752
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 33.0993
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 21.648
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 12.2598
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.1076 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 16.9728
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 17.289
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 17.289
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 43.6443
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 17.0782
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 16.9728
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 17.1836
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 43.1172
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.10684 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.10684 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 14.8924
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 13.0811
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 14.5905
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 40.149
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 14.1623
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 14.1905
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 16.6715
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 14.2771
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 14.3524
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 16.7272
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.26215 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -152.3115
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 51.9036
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 51.9036
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.02359 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.75488
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.020745 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.99576
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.020745 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.95427
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.28414
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 1.2076
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023678 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.40253
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.52092
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.59195
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.020745 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 2.1782
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.0982 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 8.2488
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.08427 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 6.7416
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.08418 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 12.627
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.08418 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 12.627
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -3.4006
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -3.2037
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.5456
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -7.3583
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -7.3728
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -7.3151
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -4.611
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -11.7196
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.9212
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.8201
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -4.4645
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.9355
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.9018
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.048056 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.5378
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.048056 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.4417
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -7.122
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -7.122
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -7.6353
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -7.0257
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 9.2455
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 9.288
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.038116 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -5.1838
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.053408 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.7625
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.5983
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.5983
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.4461
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.4461
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.066819 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -4.7441
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.066819 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.66819
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -8.8832
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -8.8832
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -13.352
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.718
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -2.509
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.718
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.718
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.0394 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -5.8706
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.0394 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -2.5649
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -3.8714
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -3.7268
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -3.7012
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -2.3186
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.51902
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.035024 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -26.0228
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.036254 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -26.6467
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.9603
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.9603
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.9603
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -4.8139
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.037872 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -6.5519
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.037872 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -5.1127
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -5.4999
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -5.4526
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -5.3681
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -9.0944
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -2.5164
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -2.485
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -3.2477
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -2.8939
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -6.5429
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -6.2983
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -6.3143
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -6.2943
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -10.7845
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.035089 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.17544
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.035089 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.73687
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 3.1366
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 3.1732
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 3.1732
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 7.7296
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.033483 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -13.3262
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.8742
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.8742
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.8742
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -2.2409
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -2.2409
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -2.2001
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.073917 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 61.1294
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.073917 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 60.538
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.054812 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -2.5268
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.66
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.66
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -9.2014
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.4848
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.4848
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -8.9385
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -7.0735
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -6.2325
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -6.1696
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.039788 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -1.3926
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.0444 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -20.3796
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -2.2803
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -2.3153
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -2.4557
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -2.2101
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -2.175
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -3.6484
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -2.0698
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -4.3409
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -4.2852
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -4.2852
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027826 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -4.5078
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.0348 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -5.4636
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -2.7576
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -2.7964
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -1.5147
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -1.1652
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.040464 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -3.1562
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.040464 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -3.2371
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.039325 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.63706
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.03942 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -6.5043
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.039445 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -6.6662
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.039333 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -8.3779
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.039308 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -8.9622
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.039464 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.47357
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.039464 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.71035
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.045996 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -2.2998
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -3.818
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -3.818
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9824
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.9457
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9824
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -2.0926
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9824
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9824
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -2.1293
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -2.1293
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.03558 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.42696
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8458
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.9446
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8458
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8458
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.9446
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8458
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.083293 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -5.4973
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -8.5332
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -8.7982
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -13.1442
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053001 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -28.9385
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053001 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -34.0796
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -35.5303
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -30.782
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -32.7468
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053001 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.68901
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.035058 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.4207
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -1.2225
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -1.2476
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -1.1757
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.6503
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.6364
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.73348
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.7155
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -1.2584
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.64719
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -3.0706
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -5.3213
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -4.3507
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -5.0104
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.1578
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.0875
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -6.0349
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -6.1752
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -3.5086
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.2631
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -6.5963
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -4.9121
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -4.4209
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -5.0525
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -4.5472
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.0875
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -6.8068
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -7.2278
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -5.3331
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.6138
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.6138
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -11.9996
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1579
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.080012 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 6.1209
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 6.7558
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 3.3779
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.085165 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 6.8132
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.084291 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 6.7433
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.080601 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 6.4481
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.079394 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 6.6691
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.085165 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 6.8132
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -18.0787
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 11.6836
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 22.6856
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 16.5712
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -35.2059
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -29.1796
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -35.523
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -18.2373
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -15.8585
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.10058 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 6.0349
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.056041 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.060136 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.087809 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.42148
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 3.7084
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 10.6307
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 13.3501
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 11.7679
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 10.3834
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 7.9606
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.096223 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 14.4335
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 10.7886
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 14.3369
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 17.8372
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 20.5703
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.13306 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.10115 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.1392 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -3.418
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -5.3224
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -9.0334
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -12.5002
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -5.4522
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -5.0533
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -2.5266
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -12.5002
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -4.7873
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -5.7182
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -2.9256
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -4.9166
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.891
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.88247
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.891
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -4.9166
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -4.9166
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -19.6812
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -6.649
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -7.314
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -6.649
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13054 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -1.5665
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.12732 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.9097
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.12732 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -2.9282
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.12301 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -5.9043
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.12653 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -1.0123
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.13181 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -23.7249
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.13177 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -23.7182
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -23.7677
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -23.7677
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.13921 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -13.9207
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.13921 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -13.9207
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2758
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2758
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2758
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -2.0965
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2758
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2758
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2758
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.9655
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.13921 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.13921 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -69.6035
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.13921 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -69.6035
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.13921 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.13798 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.077259 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.13612 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.13498 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: 3413 TEMP_SS_ to 3429 SANDOW_ C: 3414 TEMP_SS_ to 3429 SANDOW_ | [7 empty] | 53.3828
Number of Bus | Name of Bus | ID | Max MW | L: 3413 TEMP_SS_ to 3429 SANDOW_ C: 3414 TEMP_SS_ to 3429 SANDOW_ | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.16306 | north | Y | 0.060865 | 0.32435 | 0.067135 | 0.20931 | 0.060865 | North | N | 0.060865 | 0
239 | BOSQUESW | 1 | 149 | 0.16306 | north | Y | 0.060865 | 0.32435 | 0.067135 | 0.20931 | 0.060865 | North | N | 0.060865 | 0
244 | WHITNYDM | 1 | 15 | 0.14766 | north | N | 0.045474 | 0.30896 | 0.051744 | 0.19392 | 0.045474 | North | N | 0.045474 | 0
245 | WHITNYDM | 2 | 15 | 0.14766 | north | N | 0.045474 | 0.30896 | 0.051744 | 0.19392 | 0.045474 | North | N | 0.045474 | 0
247 | BOSQUESW | 2 | 153 | 0.16306 | north | Y | 0.060865 | 0.32435 | 0.067135 | 0.20931 | 0.060865 | North | N | 0.060865 | 0
251 | BOSQUESW | 2 | 150 | 0.15555 | north | Y | 0.053356 | 0.31684 | 0.059626 | 0.2018 | 0.053356 | North | N | 0.053356 | 0
253 | BOSQUESW | 2 | 80 | 0.15555 | north | Y | 0.053356 | 0.31684 | 0.059626 | 0.2018 | 0.053356 | North | N | 0.053356 | 0
332 | RWMILLER | 1 | 73 | 0.11249 | north | Y | 0.010301 | 0.27378 | 0.016571 | 0.15875 | 0.010301 | North | N | 0.010301 | 0
333 | RWMILLER | 2 | 119 | 0.11249 | north | Y | 0.010301 | 0.27378 | 0.016571 | 0.15875 | 0.010301 | North | N | 0.010301 | 0
334 | RWMILLER | 3 | 205 | 0.11249 | north | Y | 0.010301 | 0.27378 | 0.016571 | 0.15875 | 0.010301 | North | N | 0.010301 | 0
335 | RWMILLER | 4 | 102 | 0.11249 | north | Y | 0.010301 | 0.27378 | 0.016571 | 0.15875 | 0.010301 | North | N | 0.010301 | 0
336 | RWMILLER | 5 | 96 | 0.11249 | north | Y | 0.010301 | 0.27378 | 0.016571 | 0.15875 | 0.010301 | North | N | 0.010301 | 0
344 | MRSSHPRD | 1 | 12 | 0.10892 | north | N | 0.0067266 | 0.27021 | 0.012997 | 0.15517 | 0.0067266 | North | N | 0.0067266 | 0
345 | MRSSHPRD | 2 | 12 | 0.10892 | north | N | 0.0067266 | 0.27021 | 0.012997 | 0.15517 | 0.0067266 | North | N | 0.0067266 | 0
366 | JNSNCNTY | 1 | 168 | 0.11743 | north | Y | 0.015243 | 0.27873 | 0.021513 | 0.16369 | 0.015243 | North | N | 0.015243 | 0
367 | JNSNCNTY | 2 | 90 | 0.11743 | north | Y | 0.015243 | 0.27873 | 0.021513 | 0.16369 | 0.015243 | North | N | 0.015243 | 0
503 | NTHTEXAS | 1 | 18 | 0.11118 | north | Y | 0.0089856 | 0.27247 | 0.015256 | 0.15743 | 0.0089856 | North | N | 0.0089856 | 0
504 | NTHTEXAS | 2 | 18 | 0.11118 | north | Y | 0.0089856 | 0.27247 | 0.015256 | 0.15743 | 0.0089856 | North | N | 0.0089856 | 0
505 | NTHTEXAS | 3 | 38 | 0.11118 | north | Y | 0.0089856 | 0.27247 | 0.015256 | 0.15743 | 0.0089856 | North | N | 0.0089856 | 0
580 | JCKCNTY8 | 1 | 288 | 0.10995 | north | Y | 0.0077616 | 0.27125 | 0.014032 | 0.15621 | 0.0077616 | North | N | 0.0077616 | 0
581 | JCKCNTY8 | 2 | 147 | 0.10995 | north | Y | 0.0077616 | 0.27125 | 0.014032 | 0.15621 | 0.0077616 | North | N | 0.0077616 | 0
582 | JCKCNTY8 | 3 | 147 | 0.10995 | north | Y | 0.0077616 | 0.27125 | 0.014032 | 0.15621 | 0.0077616 | North | N | 0.0077616 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.10866 | north | Y | 0.0064656 | 0.26995 | 0.012736 | 0.15491 | 0.0064656 | North | N | 0.0064656 | 0
837 | NEWMAN_G | 1 | 40 | 0.10658 | north | Y | 0.0043926 | 0.26788 | 0.010663 | 0.15284 | 0.0043926 | North | N | 0.0043926 | 0
842 | OLINGER_ | 1 | 79 | 0.10655 | north | Y | 0.0043556 | 0.26784 | 0.010626 | 0.1528 | 0.0043556 | North | N | 0.0043556 | 0
843 | OLINGER_ | 1 | 106 | 0.10655 | north | Y | 0.0043556 | 0.26784 | 0.010626 | 0.1528 | 0.0043556 | North | N | 0.0043556 | 0
844 | OLINGER_ | 1 | 146 | 0.10655 | north | Y | 0.0043556 | 0.26784 | 0.010626 | 0.1528 | 0.0043556 | North | N | 0.0043556 | 0
845 | OLINGER_ | 1 | 76 | 0.10655 | north | Y | 0.0043556 | 0.26784 | 0.010626 | 0.1528 | 0.0043556 | North | N | 0.0043556 | 0
923 | SPENCER_ | 1 | 60 | 0.10852 | north | Y | 0.0063286 | 0.26981 | 0.012599 | 0.15477 | 0.0063286 | North | N | 0.0063286 | 0
924 | SPENCER_ | 1 | 63 | 0.10852 | north | Y | 0.0063286 | 0.26981 | 0.012599 | 0.15477 | 0.0063286 | North | N | 0.0063286 | 0
948 | STEAM1 | 1 | 20 | 0.10638 | north | Y | 0.0041906 | 0.26767 | 0.010461 | 0.15264 | 0.0041906 | North | N | 0.0041906 | 0
949 | STEAM2 | 1 | 25 | 0.10638 | north | Y | 0.0041906 | 0.26767 | 0.010461 | 0.15264 | 0.0041906 | North | N | 0.0041906 | 0
950 | STEAM3 | 1 | 41 | 0.10638 | north | Y | 0.0041906 | 0.26767 | 0.010461 | 0.15264 | 0.0041906 | North | N | 0.0041906 | 0
990 | GIBN_CRE | 1 | 463 | 0.029493 | north | Y | -0.072697 | 0.19079 | -0.066427 | 0.075747 | 0.066427 | west | Y | 0.072697 | 2.903
1002 | PBCTAGE_ | A | 66 | 0.094212 | west | Y | -0.0079784 | 0.25551 | -0.0017085 | 0.14047 | 0.0017085 | west | N | 0.0017085 | 0
1003 | PBCTBGE_ | B | 65 | 0.094212 | west | Y | -0.0079784 | 0.25551 | -0.0017085 | 0.14047 | 0.0017085 | west | N | 0.0017085 | 0
1004 | PBCTCGE_ | C | 67 | 0.094212 | west | Y | -0.0079784 | 0.25551 | -0.0017085 | 0.14047 | 0.0017085 | west | N | 0.0017085 | 0
1005 | PBCTDGE_ | D | 67 | 0.094212 | west | Y | -0.0079784 | 0.25551 | -0.0017085 | 0.14047 | 0.0017085 | west | N | 0.0017085 | 0
1006 | PBCTEGE_ | E | 67 | 0.094212 | west | Y | -0.0079784 | 0.25551 | -0.0017085 | 0.14047 | 0.0017085 | west | N | 0.0017085 | 0
1007 | PB5GEN_6 | MB | 114 | 0.094212 | west | Y | -0.0079784 | 0.25551 | -0.0017085 | 0.14047 | 0.0017085 | west | N | 0.0017085 | 0
1008 | PB6GEN_7 | MB | 515 | 0.094212 | west | Y | -0.0079784 | 0.25551 | -0.0017085 | 0.14047 | 0.0017085 | west | N | 0.0017085 | 0
1039 | MRGNAG_1 | A | 66 | 0.097741 | west | Y | -0.0044494 | 0.25903 | 0.0018205 | 0.144 | 0.0018205 | west | N | 0.0018205 | 0
1040 | MRGNBG_2 | B | 69 | 0.097741 | west | Y | -0.0044494 | 0.25903 | 0.0018205 | 0.144 | 0.0018205 | west | N | 0.0018205 | 0
1041 | MRGNCG_3 | C | 69 | 0.097741 | west | Y | -0.0044494 | 0.25903 | 0.0018205 | 0.144 | 0.0018205 | west | N | 0.0018205 | 0
1042 | MRGNDG_4 | D | 67 | 0.097741 | west | Y | -0.0044494 | 0.25903 | 0.0018205 | 0.144 | 0.0018205 | west | N | 0.0018205 | 0
1043 | MRGNEG_5 | E | 67 | 0.097741 | west | Y | -0.0044494 | 0.25903 | 0.0018205 | 0.144 | 0.0018205 | west | N | 0.0018205 | 0
1044 | MRGNFG_6 | F | 65 | 0.097741 | west | Y | -0.0044494 | 0.25903 | 0.0018205 | 0.144 | 0.0018205 | west | N | 0.0018205 | 0
1045 | CALENG1G | 1 | 70 | 0.097202 | west | N | -0.0049884 | 0.2585 | 0.0012815 | 0.14346 | 0.0012815 | west | N | 0.0012815 | 0
1046 | CALENG2G | 2 | 73.4 | 0.097202 | west | N | -0.0049884 | 0.2585 | 0.0012815 | 0.14346 | 0.0012815 | west | N | 0.0012815 | 0
1047 | CALENG3G | 3 | 70.4 | 0.097202 | west | N | -0.0049884 | 0.2585 | 0.0012815 | 0.14346 | 0.0012815 | west | N | 0.0012815 | 0
1058 | LONGSHOR | 1 | 150 | 0.097481 | west | Y | -0.0047094 | 0.25877 | 0.0015605 | 0.14374 | 0.0015605 | west | N | 0.0015605 | 0
1058 | LONGSHOR | 2 | 220 | 0.097481 | west | Y | -0.0047094 | 0.25877 | 0.0015605 | 0.14374 | 0.0015605 | west | N | 0.0015605 | 0
1061 | CIELOGEN | 1 | 99 | 0.097947 | west | Y | -0.0042434 | 0.25924 | 0.0020265 | 0.1442 | 0.0020265 | west | N | 0.0020265 | 0
1062 | CIELOGEN | 1 | 61 | 0.097947 | west | Y | -0.0042434 | 0.25924 | 0.0020265 | 0.1442 | 0.0020265 | west | N | 0.0020265 | 0
1068 | SCURRYCW | 1 | 141 | 0.097919 | west | Y | -0.0042714 | 0.25921 | 0.0019985 | 0.14417 | 0.0019985 | west | N | 0.0019985 | 0
1069 | KINDERMG | 1 | 25 | 0.097947 | west | N | -0.0042434 | 0.25924 | 0.0020265 | 0.1442 | 0.0020265 | west | N | 0.0020265 | 0
1070 | KINDERMG | 1 | 45.7 | 0.097947 | west | N | -0.0042434 | 0.25924 | 0.0020265 | 0.1442 | 0.0020265 | west | N | 0.0020265 | 0
1071 | KINDERMG | 1 | 45.7 | 0.097947 | west | N | -0.0042434 | 0.25924 | 0.0020265 | 0.1442 | 0.0020265 | west | N | 0.0020265 | 0
1073 | SCURRYCW | 2 | 120 | 0.097919 | west | Y | -0.0042714 | 0.25921 | 0.0019985 | 0.14417 | 0.0019985 | west | N | 0.0019985 | 0
1320 | BSP 1 | 1 | 25.8 | 0.096445 | west | N | -0.0057454 | 0.25774 | 0.00052454 | 0.1427 | 0.00052454 | west | N | 0.00052454 | 0
1326 | STANTONW | 1 | 100.5 | 0.096074 | west | Y | -0.0061164 | 0.25737 | 0.00015354 | 0.14233 | 0.00015354 | west | N | 0.00015354 | 0
1327 | WILDHRSE | 1 | 120 | 0.09696 | west | Y | -0.0052304 | 0.25825 | 0.0010395 | 0.14321 | 0.0010395 | west | N | 0.0010395 | 0
1328 | OCOTILLO | 1 | 58 | 0.096043 | west | Y | -0.0061474 | 0.25734 | 0.00012254 | 0.1423 | 0.00012254 | west | N | 0.00012254 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.096281 | west | Y | -0.0059094 | 0.25757 | 0.00036054 | 0.14254 | 0.00036054 | west | N | 0.00036054 | 0
1343 | TRENTIPP | 1 | 150 | 0.098626 | west | Y | -0.0035644 | 0.25992 | 0.0027055 | 0.14488 | 0.0027055 | west | N | 0.0027055 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.095289 | west | Y | -0.0069014 | 0.25658 | -0.00063146 | 0.14154 | 0.00063146 | west | N | 0.00063146 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.095289 | west | Y | -0.0069014 | 0.25658 | -0.00063146 | 0.14154 | 0.00063146 | west | N | 0.00063146 | 0
1354 | AEPWIND_ | 1 | 101 | 0.098626 | west | Y | -0.0035644 | 0.25992 | 0.0027055 | 0.14488 | 0.0027055 | west | N | 0.0027055 | 0
1360 | GUNSIGHT | 1 | 120 | 0.097002 | west | Y | -0.0051884 | 0.2583 | 0.0010815 | 0.14326 | 0.0010815 | west | N | 0.0010815 | 0
1432 | GRHAMSES | 2 | 366 | 0.10596 | north | Y | 0.0037726 | 0.26726 | 0.010043 | 0.15222 | 0.0037726 | North | N | 0.0037726 | 0
1433 | GRHAMSES | 1 | 242 | 0.10632 | north | Y | 0.0041246 | 0.26761 | 0.010395 | 0.15257 | 0.0041246 | North | N | 0.0041246 | 0
1437 | MESQUITW | 1 | 400 | 0.10193 | west | Y | -0.00025939 | 0.26322 | 0.0060105 | 0.14819 | 0.00025939 | North | Y | 0.0060105 | 2.3005
1438 | MESQUITW | 1 | 236 | 0.10194 | west | Y | -0.00025439 | 0.26323 | 0.0060155 | 0.14819 | 0.00025439 | North | Y | 0.0060155 | 1.3596
1442 | COKFIELD | 1 | 165 | 0.1029 | west | Y | 0.00071261 | 0.2642 | 0.0069825 | 0.14916 | 0.00071261 | North | Y | 0.0069825 | 1.0345
1453 | WCPWRCO_ | 1 | 204 | 0.10813 | north | Y | 0.0059356 | 0.26942 | 0.012206 | 0.15438 | 0.0059356 | North | N | 0.0059356 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.10813 | north | Y | 0.0059356 | 0.26942 | 0.012206 | 0.15438 | 0.0059356 | North | N | 0.0059356 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.10813 | north | Y | 0.0059356 | 0.26942 | 0.012206 | 0.15438 | 0.0059356 | North | N | 0.0059356 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.10617 | west | Y | 0.0039826 | 0.26747 | 0.010253 | 0.15243 | 0.0039826 | North | Y | 0.010253 | 0.1254
1479 | WFCOGEN_ | 2 | 20 | 0.10617 | west | Y | 0.0039826 | 0.26747 | 0.010253 | 0.15243 | 0.0039826 | North | Y | 0.010253 | 0.1254
1482 | WFCOGEN_ | 1 | 20 | 0.10617 | west | Y | 0.0039826 | 0.26747 | 0.010253 | 0.15243 | 0.0039826 | North | Y | 0.010253 | 0.1254
1482 | WFCOGEN_ | 2 | 17 | 0.10617 | west | Y | 0.0039826 | 0.26747 | 0.010253 | 0.15243 | 0.0039826 | North | Y | 0.010253 | 0.10659
1600 | BARTNWND | 1 | 120 | 0.10891 | north | Y | 0.0067216 | 0.27021 | 0.012992 | 0.15517 | 0.0067216 | North | N | 0.0067216 | 0
1643 | SLSTR1PP | 1 | 60 | 0.11172 | north | Y | 0.0095256 | 0.27301 | 0.015796 | 0.15797 | 0.0095256 | North | N | 0.0095256 | 0
1675 | PEC_1G | 1 | 75 | 0.1066 | north | N | 0.0044056 | 0.26789 | 0.010676 | 0.15285 | 0.0044056 | North | N | 0.0044056 | 0
1676 | PEC_2G | 2 | 79.6 | 0.1066 | north | N | 0.0044056 | 0.26789 | 0.010676 | 0.15285 | 0.0044056 | North | N | 0.0044056 | 0
1677 | PEC_3G | 3 | 88.4 | 0.1066 | north | N | 0.0044056 | 0.26789 | 0.010676 | 0.15285 | 0.0044056 | North | N | 0.0044056 | 0
1678 | LAMARPWR | 1 | 160 | 0.10668 | north | Y | 0.0044896 | 0.26797 | 0.01076 | 0.15293 | 0.0044896 | North | N | 0.0044896 | 0
1679 | LAMARPWR | 2 | 156 | 0.10668 | north | Y | 0.0044896 | 0.26797 | 0.01076 | 0.15293 | 0.0044896 | North | N | 0.0044896 | 0
1680 | LAMARPWR | 3 | 196 | 0.10668 | north | Y | 0.0044896 | 0.26797 | 0.01076 | 0.15293 | 0.0044896 | North | N | 0.0044896 | 0
1681 | LAMARPWR | 4 | 156 | 0.10668 | north | Y | 0.0044896 | 0.26797 | 0.01076 | 0.15293 | 0.0044896 | North | N | 0.0044896 | 0
1682 | LAMARPWR | 5 | 157 | 0.10668 | north | Y | 0.0044896 | 0.26797 | 0.01076 | 0.15293 | 0.0044896 | North | N | 0.0044896 | 0
1683 | LAMARPWR | 6 | 198 | 0.10668 | north | Y | 0.0044896 | 0.26797 | 0.01076 | 0.15293 | 0.0044896 | North | N | 0.0044896 | 0
1687 | VALLEY_1 | 1 | 170 | 0.10693 | north | Y | 0.0047356 | 0.26822 | 0.011006 | 0.15318 | 0.0047356 | North | N | 0.0047356 | 0
1688 | VALLEY_2 | 2 | 520 | 0.10693 | north | Y | 0.0047356 | 0.26822 | 0.011006 | 0.15318 | 0.0047356 | North | N | 0.0047356 | 0
1689 | VALLEY_3 | 3 | 370 | 0.10677 | north | Y | 0.0045816 | 0.26807 | 0.010852 | 0.15303 | 0.0045816 | North | N | 0.0045816 | 0
1701 | MOSES_1G | 1 | 558 | 0.10653 | north | Y | 0.0043386 | 0.26782 | 0.010609 | 0.15278 | 0.0043386 | North | N | 0.0043386 | 0
1702 | MOSES_2G | 2 | 579 | 0.10653 | north | Y | 0.0043386 | 0.26782 | 0.010609 | 0.15278 | 0.0043386 | North | N | 0.0043386 | 0
1703 | MOSES_3G | 3 | 808 | 0.10653 | north | Y | 0.0043386 | 0.26782 | 0.010609 | 0.15278 | 0.0043386 | North | N | 0.0043386 | 0
1861 | EAGLEMNT | MB | 112 | 0.11023 | north | Y | 0.0080406 | 0.27152 | 0.014311 | 0.15649 | 0.0080406 | North | N | 0.0080406 | 0
1862 | EAGLEMNT | MB | 100 | 0.11023 | north | Y | 0.0080406 | 0.27152 | 0.014311 | 0.15649 | 0.0080406 | North | N | 0.0080406 | 0
1863 | EAGLEMNT | MB | 378 | 0.11023 | north | Y | 0.0080406 | 0.27152 | 0.014311 | 0.15649 | 0.0080406 | North | N | 0.0080406 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.11166 | north | Y | 0.0094716 | 0.27296 | 0.015742 | 0.15792 | 0.0094716 | North | N | 0.0094716 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.11166 | north | Y | 0.0094716 | 0.27296 | 0.015742 | 0.15792 | 0.0094716 | North | N | 0.0094716 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.11166 | north | Y | 0.0094716 | 0.27296 | 0.015742 | 0.15792 | 0.0094716 | North | N | 0.0094716 | 0
1889 | DECRDOVA | MB | 770 | 0.11193 | north | Y | 0.0097396 | 0.27322 | 0.01601 | 0.15818 | 0.0097396 | North | N | 0.0097396 | 0
1892 | DECRDOVA | A | 70 | 0.11392 | north | Y | 0.011728 | 0.27521 | 0.017998 | 0.16017 | 0.011728 | North | N | 0.011728 | 0
1893 | DECRDOVA | B | 69 | 0.11392 | north | Y | 0.011728 | 0.27521 | 0.017998 | 0.16017 | 0.011728 | North | N | 0.011728 | 0
1894 | DECRDOVA | C | 69 | 0.11392 | north | Y | 0.011728 | 0.27521 | 0.017998 | 0.16017 | 0.011728 | North | N | 0.011728 | 0
1895 | DECRDOVA | D | 68 | 0.11392 | north | Y | 0.011728 | 0.27521 | 0.017998 | 0.16017 | 0.011728 | North | N | 0.011728 | 0
1898 | COMCHEPK | 1 | 1157 | 0.11145 | north | N | 0.0092616 | 0.27275 | 0.015532 | 0.15771 | 0.0092616 | North | N | 0.0092616 | 0
1899 | COMCHEPK | 2 | 1158 | 0.11145 | north | N | 0.0092616 | 0.27275 | 0.015532 | 0.15771 | 0.0092616 | North | N | 0.0092616 | 0
1937 | MDLTHELP | 5 | 224 | 0.11647 | north | Y | 0.014279 | 0.27776 | 0.020549 | 0.16272 | 0.014279 | North | N | 0.014279 | 0
1938 | MDLTHELP | 6 | 226 | 0.11647 | north | Y | 0.014279 | 0.27776 | 0.020549 | 0.16272 | 0.014279 | North | N | 0.014279 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.11588 | north | Y | 0.013694 | 0.27718 | 0.019964 | 0.16214 | 0.013694 | North | N | 0.013694 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.11588 | north | Y | 0.013694 | 0.27718 | 0.019964 | 0.16214 | 0.013694 | North | N | 0.013694 | 0
1943 | MDLTHELP | 3 | 212 | 0.11647 | north | Y | 0.014279 | 0.27776 | 0.020549 | 0.16272 | 0.014279 | North | N | 0.014279 | 0
1944 | MDLTHELP | 4 | 211 | 0.11647 | north | Y | 0.014279 | 0.27776 | 0.020549 | 0.16272 | 0.014279 | North | N | 0.014279 | 0
1947 | HANDLEY_ | 3 | 395 | 0.11197 | north | Y | 0.0097836 | 0.27327 | 0.016054 | 0.15823 | 0.0097836 | North | N | 0.0097836 | 0
1948 | HANDLEY_ | 4 | 435 | 0.11174 | north | Y | 0.0095526 | 0.27304 | 0.015823 | 0.158 | 0.0095526 | North | N | 0.0095526 | 0
1949 | HANDLEY_ | 5 | 435 | 0.11197 | north | Y | 0.0097836 | 0.27327 | 0.016054 | 0.15823 | 0.0097836 | North | N | 0.0097836 | 0
2371 | COLLIN_1 | MB | 138 | 0.10764 | north | Y | 0.0054486 | 0.26893 | 0.011719 | 0.15389 | 0.0054486 | North | N | 0.0054486 | 0
2413 | MTCK6_G | 6 | 118 | 0.10851 | north | Y | 0.0063176 | 0.2698 | 0.012588 | 0.15476 | 0.0063176 | North | N | 0.0063176 | 0
2414 | MTCK7_G | 7 | 115 | 0.10851 | north | Y | 0.0063176 | 0.2698 | 0.012588 | 0.15476 | 0.0063176 | North | N | 0.0063176 | 0
2417 | MTCK8_G | 8 | 556 | 0.10851 | north | Y | 0.0063176 | 0.2698 | 0.012588 | 0.15476 | 0.0063176 | North | N | 0.0063176 | 0
2451 | LKHB1_G | 1 | 388 | 0.10643 | north | Y | 0.0042386 | 0.26772 | 0.010509 | 0.15268 | 0.0042386 | North | N | 0.0042386 | 0
2452 | LKHB2_G | 2 | 515 | 0.10643 | north | Y | 0.0042386 | 0.26772 | 0.010509 | 0.15268 | 0.0042386 | North | N | 0.0042386 | 0
3097 | MARTLAKE | 1 | 785 | 0.10118 | north | Y | -0.0010054 | 0.26248 | 0.0052645 | 0.14744 | 0.0010054 | North | N | 0.0010054 | 0
3098 | MARTLAKE | 2 | 795 | 0.10118 | north | Y | -0.0010054 | 0.26248 | 0.0052645 | 0.14744 | 0.0010054 | North | N | 0.0010054 | 0
3099 | MARTLAKE | 3 | 780 | 0.10118 | north | Y | -0.0010054 | 0.26248 | 0.0052645 | 0.14744 | 0.0010054 | North | N | 0.0010054 | 0
3107 | STRYKER_ | 1 | 182 | 0.099488 | north | Y | -0.0027024 | 0.26078 | 0.0035675 | 0.14574 | 0.0027024 | North | N | 0.0027024 | 0
3108 | STRYKER_ | 2 | 484 | 0.099488 | north | Y | -0.0027024 | 0.26078 | 0.0035675 | 0.14574 | 0.0027024 | North | N | 0.0027024 | 0
3126 | TRINIDAD | 1 | 224 | 0.10601 | north | Y | 0.0038216 | 0.26731 | 0.010092 | 0.15227 | 0.0038216 | North | N | 0.0038216 | 0
3309 | ASPN_G | 1 | 50 | 0.099907 | north | Y | -0.0022834 | 0.2612 | 0.0039865 | 0.14616 | 0.0022834 | North | N | 0.0022834 | 0
3348 | CHAMPION | MB | 42 | 0.099958 | north | N | -0.0022324 | 0.26125 | 0.0040375 | 0.14621 | 0.0022324 | North | N | 0.0022324 | 0
3381 | BBRN_1G | 1 | 615 | 0.092557 | north | Y | -0.0096334 | 0.25385 | -0.0033635 | 0.13881 | 0.0033635 | west | Y | 0.0096334 | 3.856
3382 | BBRN_2G | 2 | 587 | 0.092557 | north | Y | -0.0096334 | 0.25385 | -0.0033635 | 0.13881 | 0.0033635 | west | Y | 0.0096334 | 3.6804
3403 | THOUSE_1 | MB | 537 | 0.17291 | north | Y | 0.070719 | 0.3342 | 0.076989 | 0.21916 | 0.070719 | North | N | 0.070719 | 0
3404 | THOUSE_2 | 2 | 787 | 0.17291 | north | Y | 0.070719 | 0.3342 | 0.076989 | 0.21916 | 0.070719 | North | N | 0.070719 | 0
3416 | LAKE_CRK | MB | 75 | 0.16815 | north | Y | 0.065964 | 0.32945 | 0.072234 | 0.21441 | 0.065964 | North | N | 0.065964 | 0
3417 | LAKE_CRK | MB | 222 | 0.16815 | north | Y | 0.065964 | 0.32945 | 0.072234 | 0.21441 | 0.065964 | North | N | 0.065964 | 0
3432 | SANDOW_4 | 4 | 569 | -0.26215 | south | Y | -0.36434 | -0.10086 | -0.35807 | -0.2159 | 0.10086 | south | N | 0.10086 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.15615 | south | Y | -0.25834 | 0.0051461 | -0.25207 | -0.10989 | 0.0051461 | south | N | 0.0051461 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.15615 | south | Y | -0.25834 | 0.0051461 | -0.25207 | -0.10989 | 0.0051461 | south | N | 0.0051461 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.1561 | south | Y | -0.25829 | 0.0051941 | -0.25202 | -0.10984 | 0.0051941 | south | N | 0.0051941 | 0
5031 | BRA_VHBC | 1 | 46 | -0.15615 | south | Y | -0.25834 | 0.0051461 | -0.25207 | -0.10989 | 0.0051461 | south | N | 0.0051461 | 0
5032 | BRA_VHBC | 2 | 47 | -0.15615 | south | Y | -0.25834 | 0.0051461 | -0.25207 | -0.10989 | 0.0051461 | south | N | 0.0051461 | 0
5033 | BRA_VHBC | 3 | 46 | -0.15615 | south | Y | -0.25834 | 0.0051461 | -0.25207 | -0.10989 | 0.0051461 | south | N | 0.0051461 | 0
5034 | BRA_VHBC | 4 | 46 | -0.15615 | south | Y | -0.25834 | 0.0051461 | -0.25207 | -0.10989 | 0.0051461 | south | N | 0.0051461 | 0
5111 | CALAVER_ | 1 | 424 | -0.15655 | south | Y | -0.25874 | 0.0047441 | -0.25247 | -0.11029 | 0.0047441 | south | N | 0.0047441 | 0
5112 | CALAVER_ | 2 | 425 | -0.15655 | south | Y | -0.25874 | 0.0047441 | -0.25247 | -0.11029 | 0.0047441 | south | N | 0.0047441 | 0
5264 | LEON_LCP | 3 | 58 | -0.15513 | south | Y | -0.25732 | 0.0061611 | -0.25105 | -0.10888 | 0.0061611 | south | N | 0.0061611 | 0
5265 | LEON_LCP | 4 | 89 | -0.15513 | south | Y | -0.25732 | 0.0061611 | -0.25105 | -0.10888 | 0.0061611 | south | N | 0.0061611 | 0
5266 | LEON_LCP | 1 | 44 | -0.15513 | south | Y | -0.25732 | 0.0061611 | -0.25105 | -0.10888 | 0.0061611 | south | N | 0.0061611 | 0
5267 | LEON_LCP | 2 | 44 | -0.15513 | south | Y | -0.25732 | 0.0061611 | -0.25105 | -0.10888 | 0.0061611 | south | N | 0.0061611 | 0
5268 | LEON_LCP | 3 | 43 | -0.15513 | south | Y | -0.25732 | 0.0061611 | -0.25105 | -0.10888 | 0.0061611 | south | N | 0.0061611 | 0
5269 | LEON_LCP | 4 | 45 | -0.15513 | south | Y | -0.25732 | 0.0061611 | -0.25105 | -0.10888 | 0.0061611 | south | N | 0.0061611 | 0
5396 | CALAVER_ | 1 | 412 | -0.15633 | south | Y | -0.25852 | 0.0049651 | -0.25225 | -0.11007 | 0.0049651 | south | N | 0.0049651 | 0
5397 | CALAVER_ | 2 | 400 | -0.15633 | south | Y | -0.25852 | 0.0049651 | -0.25225 | -0.11007 | 0.0049651 | south | N | 0.0049651 | 0
5401 | CALAVER_ | 1 | 546 | -0.15569 | south | Y | -0.25788 | 0.0056061 | -0.25161 | -0.10943 | 0.0056061 | south | N | 0.0056061 | 0
5402 | CALAVER_ | 2 | 750 | -0.15569 | south | Y | -0.25788 | 0.0056061 | -0.25161 | -0.10943 | 0.0056061 | south | N | 0.0056061 | 0
5436 | TUTTL_WB | MB | 61 | -0.15718 | south | Y | -0.25937 | 0.0041101 | -0.2531 | -0.11093 | 0.0041101 | south | N | 0.0041101 | 0
5438 | TUTTL_WB | MB | 95 | -0.15718 | south | Y | -0.25937 | 0.0041101 | -0.2531 | -0.11093 | 0.0041101 | south | N | 0.0041101 | 0
5439 | TUTTL_WB | MB | 151 | -0.15718 | south | Y | -0.25937 | 0.0041101 | -0.2531 | -0.11093 | 0.0041101 | south | N | 0.0041101 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.1561 | south | Y | -0.25829 | 0.0051891 | -0.25202 | -0.10985 | 0.0051891 | south | N | 0.0051891 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.1561 | south | Y | -0.25829 | 0.0051891 | -0.25202 | -0.10985 | 0.0051891 | south | N | 0.0051891 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.1561 | south | Y | -0.25829 | 0.0051891 | -0.25202 | -0.10985 | 0.0051891 | south | N | 0.0051891 | 0
5503 | RAYBURNG | 1 | 22 | -0.1284 | south | Y | -0.2306 | 0.032888 | -0.22433 | -0.082151 | 0.032888 | south | N | 0.032888 | 0
5505 | RAYBURNG | 1 | 11 | -0.1284 | south | Y | -0.2306 | 0.032888 | -0.22433 | -0.082151 | 0.032888 | south | N | 0.032888 | 0
5506 | RAYBURNG | 1 | 11 | -0.1284 | south | Y | -0.2306 | 0.032888 | -0.22433 | -0.082151 | 0.032888 | south | N | 0.032888 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.1294 | south | Y | -0.23159 | 0.031898 | -0.22532 | -0.083141 | 0.031898 | south | N | 0.031898 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.1294 | south | Y | -0.23159 | 0.031898 | -0.22532 | -0.083141 | 0.031898 | south | N | 0.031898 | 0
5511 | RAYBURNC | 1 | 46 | -0.1294 | south | Y | -0.23159 | 0.031898 | -0.22532 | -0.083141 | 0.031898 | south | N | 0.031898 | 0
5512 | RAYBURNC | 1 | 48 | -0.1294 | south | Y | -0.23159 | 0.031898 | -0.22532 | -0.083141 | 0.031898 | south | N | 0.031898 | 0
5728 | FALCONHY | 2 | 12 | -0.13484 | south | N | -0.23703 | 0.026458 | -0.23076 | -0.088581 | 0.026458 | south | N | 0.026458 | 0
5729 | FALCONHY | 3 | 11 | -0.13484 | south | N | -0.23703 | 0.026458 | -0.23076 | -0.088581 | 0.026458 | south | N | 0.026458 | 0
5890 | PEARSALL | 1 | 24 | -0.13943 | south | Y | -0.24162 | 0.021863 | -0.23535 | -0.093176 | 0.021863 | south | N | 0.021863 | 0
5891 | PEARSALL | 1 | 24 | -0.13943 | south | Y | -0.24162 | 0.021863 | -0.23535 | -0.093176 | 0.021863 | south | N | 0.021863 | 0
5892 | PEARSALL | 1 | 23 | -0.13943 | south | Y | -0.24162 | 0.021863 | -0.23535 | -0.093176 | 0.021863 | south | N | 0.021863 | 0
5903 | SANMIGUE | 1 | 396 | -0.14841 | south | Y | -0.2506 | 0.012883 | -0.24433 | -0.10216 | 0.012883 | south | N | 0.012883 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.088576 | houston | N | -0.19077 | 0.072717 | -0.1845 | -0.042322 | 0.042322 | houston | N | 0.042322 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.088576 | houston | N | -0.19077 | 0.072717 | -0.1845 | -0.042322 | 0.042322 | houston | N | 0.042322 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.10219 | 0
5932 | SI_RAY9 | 9 | 38 | -0.13306 | south | Y | -0.23525 | 0.028235 | -0.22898 | -0.086804 | 0.028235 | south | N | 0.028235 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.13306 | south | Y | -0.23525 | 0.028235 | -0.22898 | -0.086804 | 0.028235 | south | N | 0.028235 | 0
5934 | SI_RAY5 | 5 | 15 | -0.13306 | south | Y | -0.23525 | 0.028235 | -0.22898 | -0.086804 | 0.028235 | south | N | 0.028235 | 0
5935 | SI_RAY10 | 10 | 47 | -0.13306 | south | Y | -0.23525 | 0.028235 | -0.22898 | -0.086804 | 0.028235 | south | N | 0.028235 | 0
6016 | SWMESA | 1 | 75 | 0.084448 | west | Y | -0.017742 | 0.24574 | -0.011472 | 0.1307 | 0.011472 | west | N | 0.011472 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.09592 | 0
6144 | MCADOO1A | 1 | 150 | 0.099307 | west | Y | -0.0028834 | 0.2606 | 0.0033865 | 0.14556 | 0.0028834 | North | Y | 0.0033865 | 0.075472
6407 | TURKTRAK | 1 | 169.5 | 0.094741 | west | Y | -0.0074494 | 0.25603 | -0.0011795 | 0.141 | 0.0011795 | west | N | 0.0011795 | 0
6476 | LANGFORD | 1 | 150 | 0.04495 | west | Y | -0.05724 | 0.20624 | -0.05097 | 0.091204 | 0.05097 | west | N | 0.05097 | 0
6637 | SNYDERW1 | 1 | 63 | 0.097848 | west | Y | -0.0043424 | 0.25914 | 0.0019275 | 0.1441 | 0.0019275 | west | N | 0.0019275 | 0
6752 | OKLA0A | 1 | 649.7 | 0.1037 | west | Y | 0.0015076 | 0.26499 | 0.0077775 | 0.14995 | 0.0015076 | North | Y | 0.0077775 | 4.0736
6948 | DENISNDM | 1 | 40 | 0.10706 | north | N | 0.0048696 | 0.26835 | 0.01114 | 0.15331 | 0.0048696 | North | N | 0.0048696 | 0
6948 | DENISNDM | 2 | 40 | 0.10706 | north | N | 0.0048696 | 0.26835 | 0.01114 | 0.15331 | 0.0048696 | North | N | 0.0048696 | 0
7000 | L_FERGUS | 1 | 422 | -0.10207 | south | Y | -0.20426 | 0.05922 | -0.19799 | -0.055819 | 0.055819 | houston | Y | 0.05922 | 1.4353
7004 | L_SIMGID | 1 | 132 | -0.16758 | south | Y | -0.26977 | -0.0062859 | -0.2635 | -0.12132 | 0.0062859 | south | N | 0.0062859 | 0
7005 | L_SIMGID | 2 | 134 | -0.16758 | south | Y | -0.26977 | -0.0062859 | -0.2635 | -0.12132 | 0.0062859 | south | N | 0.0062859 | 0
7006 | L_SIMGID | 3 | 323 | -0.16758 | south | Y | -0.26977 | -0.0062859 | -0.2635 | -0.12132 | 0.0062859 | south | N | 0.0062859 | 0
7007 | L_LOSTPI | 1 | 158 | -0.21658 | south | Y | -0.31877 | -0.055286 | -0.3125 | -0.17032 | 0.055286 | south | N | 0.055286 | 0
7008 | L_LOSTPI | 2 | 160 | -0.21658 | south | Y | -0.31877 | -0.055286 | -0.3125 | -0.17032 | 0.055286 | south | N | 0.055286 | 0
7009 | L_LOSTPI | 3 | 175 | -0.21658 | south | Y | -0.31877 | -0.055286 | -0.3125 | -0.17032 | 0.055286 | south | N | 0.055286 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.1861 | south | Y | -0.28829 | -0.024806 | -0.28202 | -0.13984 | 0.024806 | south | N | 0.024806 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.1861 | south | Y | -0.28829 | -0.024806 | -0.28202 | -0.13984 | 0.024806 | south | N | 0.024806 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.18586 | south | Y | -0.28805 | -0.024571 | -0.28178 | -0.13961 | 0.024571 | south | N | 0.024571 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.1748 | south | Y | -0.27699 | -0.013502 | -0.27072 | -0.12854 | 0.013502 | south | N | 0.013502 | 0
7015 | L_HAYSEN | 2 | 225 | -0.1748 | south | Y | -0.27699 | -0.013502 | -0.27072 | -0.12854 | 0.013502 | south | N | 0.013502 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.1748 | south | Y | -0.27699 | -0.013502 | -0.27072 | -0.12854 | 0.013502 | south | N | 0.013502 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.1748 | south | Y | -0.27699 | -0.013502 | -0.27072 | -0.12854 | 0.013502 | south | N | 0.013502 | 0
7020 | L_AUSTPL | 1 | 8 | -0.14694 | south | N | -0.24913 | 0.01435 | -0.24286 | -0.10069 | 0.01435 | south | N | 0.01435 | 0
7020 | L_AUSTPL | 2 | 8 | -0.14694 | south | N | -0.24913 | 0.01435 | -0.24286 | -0.10069 | 0.01435 | south | N | 0.01435 | 0
7022 | L_BUCHAN | 1 | 18 | -0.077655 | south | N | -0.17985 | 0.083638 | -0.17358 | -0.031401 | 0.031401 | houston | Y | 0.083638 | 0
7023 | L_BUCHAN | 2 | 18 | -0.077655 | south | N | -0.17985 | 0.083638 | -0.17358 | -0.031401 | 0.031401 | houston | Y | 0.083638 | 0
7024 | L_BUCHAN | 3 | 15 | -0.077655 | south | N | -0.17985 | 0.083638 | -0.17358 | -0.031401 | 0.031401 | houston | Y | 0.083638 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.082934 | south | N | -0.18512 | 0.078359 | -0.17885 | -0.03668 | 0.03668 | houston | Y | 0.078359 | 0
7028 | L_MARBFA | 1 | 18 | -0.11043 | south | N | -0.21262 | 0.050867 | -0.20635 | -0.064172 | 0.050867 | south | N | 0.050867 | 0
7029 | L_MARBFA | 2 | 18 | -0.11043 | south | N | -0.21262 | 0.050867 | -0.20635 | -0.064172 | 0.050867 | south | N | 0.050867 | 0
7031 | L_MARSFO | 1 | 35 | -0.12937 | south | N | -0.23156 | 0.031925 | -0.22529 | -0.083114 | 0.031925 | south | N | 0.031925 | 0
7032 | L_MARSFO | 2 | 34 | -0.12937 | south | N | -0.23156 | 0.031925 | -0.22529 | -0.083114 | 0.031925 | south | N | 0.031925 | 0
7033 | L_MARSFO | 3 | 35 | -0.12937 | south | N | -0.23156 | 0.031925 | -0.22529 | -0.083114 | 0.031925 | south | N | 0.031925 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.10185 | south | N | -0.20404 | 0.059443 | -0.19777 | -0.055596 | 0.055596 | houston | Y | 0.059443 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.10185 | south | N | -0.20404 | 0.059443 | -0.19777 | -0.055596 | 0.055596 | houston | Y | 0.059443 | 0
7038 | L_DELAWA | 1 | 35 | 0.094301 | west | Y | -0.0078894 | 0.25559 | -0.0016195 | 0.14056 | 0.0016195 | west | N | 0.0016195 | 0
7038 | L_DELAWA | 2 | 30 | 0.094301 | west | Y | -0.0078894 | 0.25559 | -0.0016195 | 0.14056 | 0.0016195 | west | N | 0.0016195 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.16764 | south | Y | -0.26983 | -0.0063469 | -0.26356 | -0.12139 | 0.0063469 | south | N | 0.0063469 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.16764 | south | Y | -0.26983 | -0.0063469 | -0.26356 | -0.12139 | 0.0063469 | south | N | 0.0063469 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.16764 | south | Y | -0.26983 | -0.0063469 | -0.26356 | -0.12139 | 0.0063469 | south | N | 0.0063469 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.16764 | south | Y | -0.26983 | -0.0063469 | -0.26356 | -0.12139 | 0.0063469 | south | N | 0.0063469 | 0
7487 | L_CANYHY | 1 | 6 | -0.16465 | south | N | -0.26684 | -0.0033519 | -0.26057 | -0.11839 | 0.0033519 | south | N | 0.0033519 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.16374 | south | N | -0.26593 | -0.0024459 | -0.25966 | -0.11748 | 0.0024459 | south | N | 0.0024459 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.16374 | south | N | -0.26593 | -0.0024459 | -0.25966 | -0.11748 | 0.0024459 | south | N | 0.0024459 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.16374 | south | N | -0.26593 | -0.0024459 | -0.25966 | -0.11748 | 0.0024459 | south | N | 0.0024459 | 0
7609 | L_SCHUMA | 1 | 4 | -0.16316 | south | N | -0.26535 | -0.0018629 | -0.25908 | -0.1169 | 0.0018629 | south | N | 0.0018629 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.15961 | south | N | -0.2618 | 0.0016811 | -0.25553 | -0.11336 | 0.0016811 | south | N | 0.0016811 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.15961 | south | N | -0.2618 | 0.0016811 | -0.25553 | -0.11336 | 0.0016811 | south | N | 0.0016811 | 0
7800 | L_GUADGE | 1 | 147 | -0.16197 | south | Y | -0.26416 | -0.00067793 | -0.25789 | -0.11572 | 0.00067793 | south | N | 0.00067793 | 0
7801 | L_GUADGE | 2 | 138 | -0.16197 | south | Y | -0.26416 | -0.00067793 | -0.25789 | -0.11572 | 0.00067793 | south | N | 0.00067793 | 0
7802 | L_GUADGE | 3 | 140 | -0.16197 | south | Y | -0.26416 | -0.00067793 | -0.25789 | -0.11572 | 0.00067793 | south | N | 0.00067793 | 0
7803 | L_GUADGE | 4 | 147 | -0.16197 | south | Y | -0.26416 | -0.00067793 | -0.25789 | -0.11572 | 0.00067793 | south | N | 0.00067793 | 0
7804 | L_GUADGE | 5 | 182 | -0.16197 | south | Y | -0.26416 | -0.00067793 | -0.25789 | -0.11572 | 0.00067793 | south | N | 0.00067793 | 0
7805 | L_GUADGE | 6 | 198 | -0.16197 | south | Y | -0.26416 | -0.00067793 | -0.25789 | -0.11572 | 0.00067793 | south | N | 0.00067793 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.21019 | south | Y | -0.31238 | -0.048897 | -0.30611 | -0.16394 | 0.048897 | south | N | 0.048897 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.21019 | south | Y | -0.31238 | -0.048897 | -0.30611 | -0.16394 | 0.048897 | south | N | 0.048897 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.21019 | south | Y | -0.31238 | -0.048897 | -0.30611 | -0.16394 | 0.048897 | south | N | 0.048897 | 0
7810 | L_RIONOG | 1 | 142 | -0.16808 | south | Y | -0.27027 | -0.0067839 | -0.264 | -0.12182 | 0.0067839 | south | N | 0.0067839 | 0
7811 | L_RIONOG | 2 | 145 | -0.16808 | south | Y | -0.27027 | -0.0067839 | -0.264 | -0.12182 | 0.0067839 | south | N | 0.0067839 | 0
7812 | L_RIONOG | 3 | 151 | -0.16808 | south | Y | -0.27027 | -0.0067839 | -0.264 | -0.12182 | 0.0067839 | south | N | 0.0067839 | 0
7813 | L_RIONOG | 4 | 290 | -0.16808 | south | Y | -0.27027 | -0.0067839 | -0.264 | -0.12182 | 0.0067839 | south | N | 0.0067839 | 0
8032 | AMISTADH | 1 | 33 | -0.077259 | south | N | -0.17945 | 0.084034 | -0.17318 | -0.031005 | 0.031005 | houston | Y | 0.084034 | 0
8033 | AMISTADH | 2 | 25 | -0.077259 | south | N | -0.17945 | 0.084034 | -0.17318 | -0.031005 | 0.031005 | houston | Y | 0.084034 | 0
8048 | FALCONHY | 1 | 12 | -0.13484 | south | N | -0.23703 | 0.026458 | -0.23076 | -0.088581 | 0.026458 | south | N | 0.026458 | 0
8066 | DUP1V#1 | 1 | 73 | -0.12948 | south | N | -0.23167 | 0.03181 | -0.2254 | -0.083229 | 0.03181 | south | N | 0.03181 | 0
8134 | FOR69CG0 | 1 | 79 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
8138 | FOR69CG0 | 2 | 81 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8147 | UCAR #2 | 10 | 28 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
8148 | UCAR #1 | 2 | 7 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
8153 | FOR69CG0 | 3 | 79 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
8154 | FOR69CG0 | 4 | 80 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
8156 | FOR69CG0 | 6 | 25 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
8157 | FOR69CG0 | 7 | 46 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
8161 | COLETOU1 | 1 | 629 | -0.1366 | south | Y | -0.23879 | 0.024695 | -0.23252 | -0.090344 | 0.024695 | south | N | 0.024695 | 0
8173 | VICEC51A | 5 | 144 | -0.13074 | south | Y | -0.23293 | 0.030555 | -0.22666 | -0.084484 | 0.030555 | south | N | 0.030555 | 0
8174 | VICEC61A | 6 | 188 | -0.13074 | south | Y | -0.23293 | 0.030555 | -0.22666 | -0.084484 | 0.030555 | south | N | 0.030555 | 0
8189 | CUERO 2 | 1 | 12 | -0.1514 | south | N | -0.25359 | 0.0098921 | -0.24732 | -0.10515 | 0.0098921 | south | N | 0.0098921 | 0
8262 | ELPS | 1 | 6 | -0.096644 | south | N | -0.19883 | 0.064649 | -0.19256 | -0.05039 | 0.05039 | houston | Y | 0.064649 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8442 | NBEC71A | 1 | 336 | -0.13177 | south | Y | -0.23396 | 0.029525 | -0.22769 | -0.085514 | 0.029525 | south | N | 0.029525 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.10219 | 0.16129 | -0.09592 | 0.046254 | 0.046254 | houston | Y | 0.16129 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.13204 | south | Y | -0.23423 | 0.02925 | -0.22796 | -0.085789 | 0.02925 | south | N | 0.02925 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.13204 | south | Y | -0.23423 | 0.02925 | -0.22796 | -0.085789 | 0.02925 | south | N | 0.02925 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.13219 | south | N | -0.23438 | 0.029103 | -0.22811 | -0.085936 | 0.029103 | south | N | 0.029103 | 0
8506 | VAL #1 | 1 | 25 | -0.13207 | south | N | -0.23426 | 0.029223 | -0.22799 | -0.085816 | 0.029223 | south | N | 0.029223 | 0
8507 | VAL #2 | 2 | 25 | -0.13207 | south | N | -0.23426 | 0.029223 | -0.22799 | -0.085816 | 0.029223 | south | N | 0.029223 | 0
8511 | OXY_CC0A | 1 | 38 | -0.1322 | south | N | -0.23439 | 0.029096 | -0.22812 | -0.085943 | 0.029096 | south | N | 0.029096 | 0
8517 | CELANEBI | 1 | 29 | -0.13279 | south | N | -0.23498 | 0.028507 | -0.22871 | -0.086532 | 0.028507 | south | N | 0.028507 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.13178 | south | N | -0.23397 | 0.029511 | -0.2277 | -0.085528 | 0.029511 | south | N | 0.029511 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.13178 | south | N | -0.23397 | 0.029511 | -0.2277 | -0.085528 | 0.029511 | south | N | 0.029511 | 0
8562 | CNOPST1 | 3 | 153 | -0.13178 | south | N | -0.23397 | 0.029511 | -0.2277 | -0.085528 | 0.029511 | south | N | 0.029511 | 0
8926 | LGE_GT10 | 1 | 158 | -0.13054 | south | N | -0.23273 | 0.030749 | -0.22646 | -0.08429 | 0.030749 | south | N | 0.030749 | 0
8927 | LGE_GT20 | 2 | 153 | -0.13054 | south | N | -0.23273 | 0.030749 | -0.22646 | -0.08429 | 0.030749 | south | N | 0.030749 | 0
8928 | LGE_STG0 | 3 | 100 | -0.13054 | south | N | -0.23273 | 0.030749 | -0.22646 | -0.08429 | 0.030749 | south | N | 0.030749 | 0
8930 | ICPGN10A | 1 | 145 | -0.13054 | south | N | -0.23273 | 0.030749 | -0.22646 | -0.08429 | 0.030749 | south | N | 0.030749 | 0
8931 | ICPGN20A | 2 | 147 | -0.13054 | south | N | -0.23273 | 0.030749 | -0.22646 | -0.08429 | 0.030749 | south | N | 0.030749 | 0
8932 | ICPGN30A | 3 | 127 | -0.13054 | south | N | -0.23273 | 0.030749 | -0.22646 | -0.08429 | 0.030749 | south | N | 0.030749 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.13349 | south | Y | -0.23568 | 0.027799 | -0.22941 | -0.08724 | 0.027799 | south | N | 0.027799 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.13349 | south | Y | -0.23568 | 0.027799 | -0.22941 | -0.08724 | 0.027799 | south | N | 0.027799 | 0
8935 | FGNTS201 | 3 | 173 | -0.13349 | south | Y | -0.23568 | 0.027799 | -0.22941 | -0.08724 | 0.027799 | south | N | 0.027799 | 0
8936 | MVGN#1 | 1 | 207 | -0.13328 | south | Y | -0.23547 | 0.028013 | -0.2292 | -0.087026 | 0.028013 | south | N | 0.028013 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.13328 | south | Y | -0.23547 | 0.028013 | -0.2292 | -0.087026 | 0.028013 | south | N | 0.028013 | 0
8938 | MVGN#3 | 3 | 242 | -0.13328 | south | Y | -0.23547 | 0.028013 | -0.2292 | -0.087026 | 0.028013 | south | N | 0.028013 | 0
8981 | HECN1 | 1 | 144 | -0.13328 | south | Y | -0.23547 | 0.028017 | -0.2292 | -0.087022 | 0.028017 | south | N | 0.028017 | 0
8982 | HECN2 | 2 | 144 | -0.13328 | south | Y | -0.23547 | 0.028017 | -0.2292 | -0.087022 | 0.028017 | south | N | 0.028017 | 0
8983 | HECN3 | 3 | 171 | -0.13328 | south | Y | -0.23547 | 0.028017 | -0.2292 | -0.087022 | 0.028017 | south | N | 0.028017 | 0
9000 | DECKR_G1 | 1 | 310 | -0.15418 | south | Y | -0.25637 | 0.0071161 | -0.2501 | -0.10792 | 0.0071161 | south | N | 0.0071161 | 0
9001 | DECKR_G2 | 2 | 413 | -0.15418 | south | Y | -0.25637 | 0.0071161 | -0.2501 | -0.10792 | 0.0071161 | south | N | 0.0071161 | 0
9002 | DECKR_G3 | 3 | 42 | -0.15707 | south | Y | -0.25926 | 0.0042281 | -0.25299 | -0.11081 | 0.0042281 | south | N | 0.0042281 | 0
9003 | DECKR_G4 | 4 | 44 | -0.15707 | south | Y | -0.25926 | 0.0042281 | -0.25299 | -0.11081 | 0.0042281 | south | N | 0.0042281 | 0
9004 | DECKR_G5 | 5 | 44 | -0.15707 | south | Y | -0.25926 | 0.0042281 | -0.25299 | -0.11081 | 0.0042281 | south | N | 0.0042281 | 0
9005 | DECKR_G6 | 6 | 47 | -0.15707 | south | Y | -0.25926 | 0.0042281 | -0.25299 | -0.11081 | 0.0042281 | south | N | 0.0042281 | 0
9016 | SANDH_G1 | 1 | 49 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
9017 | SANDH_G2 | 2 | 46 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
9018 | SANDH_G3 | 3 | 46 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
9019 | SANDH_G4 | 4 | 47 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
9020 | SANDHG5A | 5A | 154 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
9021 | SANDHG5C | 5C | 148 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
9022 | SANDH_G6 | 6 | 48 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
9023 | SANDH_G7 | 7 | 48 | -0.15935 | south | Y | -0.26154 | 0.0019441 | -0.25527 | -0.11309 | 0.0019441 | south | N | 0.0019441 | 0
11001 | NAV1CT | 1 | 70 | 0.095963 | west | Y | -0.0062274 | 0.25726 | 4.2537e-05 | 0.14222 | 4.2537e-05 | west | N | 4.2537e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.095963 | west | Y | -0.0062274 | 0.25726 | 4.2537e-05 | 0.14222 | 4.2537e-05 | west | N | 4.2537e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.095963 | west | Y | -0.0062274 | 0.25726 | 4.2537e-05 | 0.14222 | 4.2537e-05 | west | N | 4.2537e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.095963 | west | Y | -0.0062274 | 0.25726 | 4.2537e-05 | 0.14222 | 4.2537e-05 | west | N | 4.2537e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.095963 | west | Y | -0.0062274 | 0.25726 | 4.2537e-05 | 0.14222 | 4.2537e-05 | west | N | 4.2537e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.095963 | west | Y | -0.0062274 | 0.25726 | 4.2537e-05 | 0.14222 | 4.2537e-05 | west | N | 4.2537e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.095947 | west | Y | -0.0062434 | 0.25724 | 2.6537e-05 | 0.1422 | 2.6537e-05 | west | N | 2.6537e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.095947 | west | Y | -0.0062434 | 0.25724 | 2.6537e-05 | 0.1422 | 2.6537e-05 | west | N | 2.6537e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.095947 | west | Y | -0.0062434 | 0.25724 | 2.6537e-05 | 0.1422 | 2.6537e-05 | west | N | 2.6537e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.095947 | west | Y | -0.0062434 | 0.25724 | 2.6537e-05 | 0.1422 | 2.6537e-05 | west | N | 2.6537e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.095947 | west | Y | -0.0062434 | 0.25724 | 2.6537e-05 | 0.1422 | 2.6537e-05 | west | N | 2.6537e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.095947 | west | Y | -0.0062434 | 0.25724 | 2.6537e-05 | 0.1422 | 2.6537e-05 | west | N | 2.6537e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.09894 | west | Y | -0.0032504 | 0.26023 | 0.0030195 | 0.14519 | 0.0030195 | west | N | 0.0030195 | 0
11057 | CHAMPION | 1 | 126.5 | 0.09894 | west | Y | -0.0032504 | 0.26023 | 0.0030195 | 0.14519 | 0.0030195 | west | N | 0.0030195 | 0
11058 | PYRON_1G | 1 | 249 | 0.09894 | west | Y | -0.0032504 | 0.26023 | 0.0030195 | 0.14519 | 0.0030195 | west | N | 0.0030195 | 0
11059 | INADALE_ | 1 | 197 | 0.09894 | west | Y | -0.0032504 | 0.26023 | 0.0030195 | 0.14519 | 0.0030195 | west | N | 0.0030195 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.097481 | west | Y | -0.0047094 | 0.25877 | 0.0015605 | 0.14374 | 0.0015605 | west | N | 0.0015605 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.097481 | west | Y | -0.0047094 | 0.25877 | 0.0015605 | 0.14374 | 0.0015605 | west | N | 0.0015605 | 0
11147 | NOTREES_ | 1 | 149 | 0.094604 | west | Y | -0.0075864 | 0.2559 | -0.0013165 | 0.14086 | 0.0013165 | west | N | 0.0013165 | 0
11309 | BULLCREK | 1 | 180 | 0.097258 | west | Y | -0.0049324 | 0.25855 | 0.0013375 | 0.14351 | 0.0013375 | west | N | 0.0013375 | 0
11310 | BULLCREK | 1 | 180 | 0.097258 | west | Y | -0.0049324 | 0.25855 | 0.0013375 | 0.14351 | 0.0013375 | west | N | 0.0013375 | 0
11320 | COYOTE_1 | 1 | 225 | 0.097166 | west | Y | -0.0050244 | 0.25846 | 0.0012455 | 0.14342 | 0.0012455 | west | N | 0.0012455 | 0
11415 | LORAINE_ | 1 | 125 | 0.098364 | west | Y | -0.0038264 | 0.25966 | 0.0024435 | 0.14462 | 0.0024435 | west | N | 0.0024435 | 0
11416 | LORAINE_ | 1 | 125 | 0.098364 | west | Y | -0.0038264 | 0.25966 | 0.0024435 | 0.14462 | 0.0024435 | west | N | 0.0024435 | 0
11691 | KMICHICT | 1 | 140 | 0.10677 | north | N | 0.0045816 | 0.26807 | 0.010852 | 0.15303 | 0.0045816 | North | N | 0.0045816 | 0
11692 | KMICHICT | 2 | 141 | 0.10677 | north | N | 0.0045816 | 0.26807 | 0.010852 | 0.15303 | 0.0045816 | North | N | 0.0045816 | 0
11693 | KMICHIST | 3 | 309 | 0.10677 | north | N | 0.0045816 | 0.26807 | 0.010852 | 0.15303 | 0.0045816 | North | N | 0.0045816 | 0
11694 | KMICHICT | 4 | 143 | 0.10677 | north | N | 0.0045816 | 0.26807 | 0.010852 | 0.15303 | 0.0045816 | North | N | 0.0045816 | 0
11695 | KMICHICT | 5 | 144 | 0.10677 | north | N | 0.0045816 | 0.26807 | 0.010852 | 0.15303 | 0.0045816 | North | N | 0.0045816 | 0
11696 | KMICHIST | 6 | 310 | 0.10677 | north | N | 0.0045816 | 0.26807 | 0.010852 | 0.15303 | 0.0045816 | North | N | 0.0045816 | 0
12322 | ENNSTRAC | 1 | 196 | 0.11045 | north | Y | 0.0082586 | 0.27174 | 0.014529 | 0.1567 | 0.0082586 | North | N | 0.0082586 | 0
12323 | ENNSTRAC | 2 | 111 | 0.11045 | north | Y | 0.0082586 | 0.27174 | 0.014529 | 0.1567 | 0.0082586 | North | N | 0.0082586 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.1076 | north | N | 0.0054126 | 0.2689 | 0.011683 | 0.15386 | 0.0054126 | North | N | 0.0054126 | 0
12411 | FPLEFR1A | 1 | 161 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12412 | FPLEFR1B | 2 | 164 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12413 | FPLEFR1C | 3 | 164 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12414 | FPLEFR1S | 4 | 414 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12421 | FPLEFR2A | 1 | 162 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12422 | FPLEFR2B | 2 | 161 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12423 | FPLEFR2C | 3 | 163 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12424 | FPLEFR2S | 4 | 409 | 0.10542 | north | Y | 0.0032306 | 0.26671 | 0.0095005 | 0.15168 | 0.0032306 | North | N | 0.0032306 | 0
12440 | PARKD_1S | 1 | 0 | 0.10684 | north | N | 0.0046466 | 0.26813 | 0.010917 | 0.15309 | 0.0046466 | North | N | 0.0046466 | 0
12449 | PARKD_2S | 1 | 0 | 0.10684 | north | N | 0.0046466 | 0.26813 | 0.010917 | 0.15309 | 0.0046466 | North | N | 0.0046466 | 0
13116 | TGATEWAY | 1 | 148 | 0.10062 | north | N | -0.0015664 | 0.26192 | 0.0047035 | 0.14688 | 0.0015664 | North | N | 0.0015664 | 0
13117 | TGATEWAY | 2 | 130 | 0.10062 | north | N | -0.0015664 | 0.26192 | 0.0047035 | 0.14688 | 0.0015664 | North | N | 0.0015664 | 0
13118 | TGATEWAY | 3 | 145 | 0.10062 | north | N | -0.0015664 | 0.26192 | 0.0047035 | 0.14688 | 0.0015664 | North | N | 0.0015664 | 0
13119 | TGATEWAY | 4 | 399 | 0.10062 | north | N | -0.0015664 | 0.26192 | 0.0047035 | 0.14688 | 0.0015664 | North | N | 0.0015664 | 0
13131 | CALFREST | 1 | 150.7 | 0.093977 | north | Y | -0.0082134 | 0.25527 | -0.0019435 | 0.14023 | 0.0019435 | west | Y | 0.0082134 | 0.94488
13132 | CALFREST | 2 | 151 | 0.093977 | north | Y | -0.0082134 | 0.25527 | -0.0019435 | 0.14023 | 0.0019435 | west | Y | 0.0082134 | 0.94676
13133 | CALFREST | 3 | 177.4 | 0.093977 | north | Y | -0.0082134 | 0.25527 | -0.0019435 | 0.14023 | 0.0019435 | west | Y | 0.0082134 | 1.1123
13134 | CALFREST | 4 | 151.5 | 0.094238 | north | Y | -0.0079524 | 0.25553 | -0.0016825 | 0.14049 | 0.0016825 | west | Y | 0.0079524 | 0.94989
13135 | CALFREST | 5 | 152.3 | 0.094238 | north | Y | -0.0079524 | 0.25553 | -0.0016825 | 0.14049 | 0.0016825 | west | Y | 0.0079524 | 0.95491
13136 | CALFREST | 6 | 177.5 | 0.094238 | north | Y | -0.0079524 | 0.25553 | -0.0016825 | 0.14049 | 0.0016825 | west | Y | 0.0079524 | 1.1129
13432 | SANDOW_5 | 5 | 581 | -0.26215 | south | Y | -0.36434 | -0.10086 | -0.35807 | -0.2159 | 0.10086 | south | N | 0.10086 | 0
13691 | OAKGROVE | 1 | 855 | 0.060706 | north | Y | -0.041484 | 0.222 | -0.035214 | 0.10696 | 0.035214 | west | Y | 0.041484 | 5.3608
13692 | OAKGROVE | 2 | 855 | 0.060706 | north | Y | -0.041484 | 0.222 | -0.035214 | 0.10696 | 0.035214 | west | Y | 0.041484 | 5.3608
32798 | BRYN_TAM | 1 | 32 | 0.02359 | north | N | -0.0786 | 0.18488 | -0.07233 | 0.069844 | 0.069844 | houston | Y | 0.0786 | 0
32883 | BRYN_DNS | 1 | 48 | 0.020745 | north | Y | -0.081445 | 0.18204 | -0.075175 | 0.066999 | 0.066999 | houston | Y | 0.081445 | 0.69342
32884 | BRYN_DNS | 1 | 46 | 0.020745 | north | Y | -0.081445 | 0.18204 | -0.075175 | 0.066999 | 0.066999 | houston | Y | 0.081445 | 0.66453
32886 | BRYN_ATK | MB | 12 | 0.023678 | north | Y | -0.078512 | 0.18497 | -0.072242 | 0.069932 | 0.069932 | houston | Y | 0.078512 | 0
32887 | BRYN_ATK | MB | 51 | 0.023678 | north | Y | -0.078512 | 0.18497 | -0.072242 | 0.069932 | 0.069932 | houston | Y | 0.078512 | 0
32888 | BRYN_ATK | 1 | 17 | 0.023678 | north | Y | -0.078512 | 0.18497 | -0.072242 | 0.069932 | 0.069932 | houston | Y | 0.078512 | 0.14586
32890 | BRYN_ATK | MB | 22 | 0.023678 | north | Y | -0.078512 | 0.18497 | -0.072242 | 0.069932 | 0.069932 | houston | Y | 0.078512 | 0
32891 | BRYN_ATK | MB | 25 | 0.023678 | north | Y | -0.078512 | 0.18497 | -0.072242 | 0.069932 | 0.069932 | houston | Y | 0.078512 | 0
32892 | BRYN_DNS | 1 | 105 | 0.020745 | north | Y | -0.081445 | 0.18204 | -0.075175 | 0.066999 | 0.066999 | houston | Y | 0.081445 | 1.5169
36998 | RDCNYNG1 | 1 | 84 | 0.0982 | west | Y | -0.0039904 | 0.25949 | 0.0022795 | 0.14445 | 0.0022795 | west | N | 0.0022795 | 0
38332 | WDWRDU2 | 1 | 80 | 0.08427 | west | Y | -0.01792 | 0.24556 | -0.01165 | 0.13052 | 0.01165 | west | N | 0.01165 | 0
38437 | TNSRBNMS | 1 | 150 | 0.08418 | west | Y | -0.01801 | 0.24547 | -0.01174 | 0.13043 | 0.01174 | west | N | 0.01174 | 0
38438 | TNSRBNMS | 1 | 150 | 0.08418 | west | Y | -0.01801 | 0.24547 | -0.01174 | 0.13043 | 0.01174 | west | N | 0.01174 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38600 | TNBP_CGN | 5 | 53 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38614 | TNBPAMCG | 4 | 96 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38615 | TNBPAMCG | 1 | 244 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38690 | TNBP_CGN | 3 | 40 | -0.048031 | houston | N | -0.15022 | 0.11326 | -0.14395 | -0.0017768 | 0.0017768 | houston | N | 0.0017768 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.048057 | houston | N | -0.15025 | 0.11324 | -0.14398 | -0.0018028 | 0.0018028 | houston | N | 0.0018028 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.048057 | houston | N | -0.15025 | 0.11324 | -0.14398 | -0.0018028 | 0.0018028 | houston | N | 0.0018028 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.048057 | houston | N | -0.15025 | 0.11324 | -0.14398 | -0.0018028 | 0.0018028 | houston | N | 0.0018028 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.048057 | houston | N | -0.15025 | 0.11324 | -0.14398 | -0.0018028 | 0.0018028 | houston | N | 0.0018028 | 0
39470 | TNDOWCGN | 1 | 32 | -0.048056 | houston | N | -0.15025 | 0.11324 | -0.14398 | -0.0018018 | 0.0018018 | houston | N | 0.0018018 | 0
39480 | TNDOWCGN | 1 | 30 | -0.048056 | houston | N | -0.15025 | 0.11324 | -0.14398 | -0.0018018 | 0.0018018 | houston | N | 0.0018018 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.064162 | houston | N | -0.16635 | 0.097131 | -0.16008 | -0.017908 | 0.017908 | houston | N | 0.017908 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.064162 | houston | N | -0.16635 | 0.097131 | -0.16008 | -0.017908 | 0.017908 | houston | N | 0.017908 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.064162 | houston | N | -0.16635 | 0.097131 | -0.16008 | -0.017908 | 0.017908 | houston | N | 0.017908 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.064162 | houston | N | -0.16635 | 0.097131 | -0.16008 | -0.017908 | 0.017908 | houston | N | 0.017908 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.060706 | north | Y | -0.041484 | 0.222 | -0.035214 | 0.10696 | 0.035214 | west | Y | 0.041484 | 0.95491
39970 | TNTNPONE | 1 | 153 | 0.060706 | north | Y | -0.041484 | 0.222 | -0.035214 | 0.10696 | 0.035214 | west | Y | 0.041484 | 0.9593
48500 | APD_GT1_ | 1 | 136 | -0.038116 | houston | N | -0.14031 | 0.12318 | -0.13404 | 0.0081382 | 0.0081382 | houston | N | 0.0081382 | 0
48510 | AK_GT1__ | 1 | 33 | -0.053408 | houston | N | -0.1556 | 0.10789 | -0.14933 | -0.0071538 | 0.0071538 | houston | N | 0.0071538 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.038055 | houston | Y | -0.14025 | 0.12324 | -0.13398 | 0.0081992 | 0.0081992 | houston | N | 0.0081992 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.038055 | houston | Y | -0.14025 | 0.12324 | -0.13398 | 0.0081992 | 0.0081992 | houston | N | 0.0081992 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.038055 | houston | Y | -0.14025 | 0.12324 | -0.13398 | 0.0081992 | 0.0081992 | houston | N | 0.0081992 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.038055 | houston | Y | -0.14025 | 0.12324 | -0.13398 | 0.0081992 | 0.0081992 | houston | N | 0.0081992 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.066819 | houston | N | -0.16901 | 0.094474 | -0.16274 | -0.020565 | 0.020565 | houston | N | 0.020565 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.066819 | houston | N | -0.16901 | 0.094474 | -0.16274 | -0.020565 | 0.020565 | houston | N | 0.020565 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.054498 | houston | N | -0.15669 | 0.1068 | -0.15042 | -0.0082438 | 0.0082438 | houston | N | 0.0082438 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.054498 | houston | N | -0.15669 | 0.1068 | -0.15042 | -0.0082438 | 0.0082438 | houston | N | 0.0082438 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.054498 | houston | N | -0.15669 | 0.1068 | -0.15042 | -0.0082438 | 0.0082438 | houston | N | 0.0082438 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.041816 | houston | N | -0.14401 | 0.11948 | -0.13774 | 0.0044382 | 0.0044382 | houston | N | 0.0044382 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.041816 | houston | N | -0.14401 | 0.11948 | -0.13774 | 0.0044382 | 0.0044382 | houston | N | 0.0044382 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.041816 | houston | N | -0.14401 | 0.11948 | -0.13774 | 0.0044382 | 0.0044382 | houston | N | 0.0044382 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.041816 | houston | N | -0.14401 | 0.11948 | -0.13774 | 0.0044382 | 0.0044382 | houston | N | 0.0044382 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.0394 | houston | N | -0.14159 | 0.12189 | -0.13532 | 0.0068542 | 0.0068542 | houston | N | 0.0068542 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.0394 | houston | N | -0.14159 | 0.12189 | -0.13532 | 0.0068542 | 0.0068542 | houston | N | 0.0068542 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.042543 | houston | N | -0.14473 | 0.11875 | -0.13846 | 0.0037112 | 0.0037112 | houston | N | 0.0037112 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.042543 | houston | N | -0.14473 | 0.11875 | -0.13846 | 0.0037112 | 0.0037112 | houston | N | 0.0037112 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.042543 | houston | N | -0.14473 | 0.11875 | -0.13846 | 0.0037112 | 0.0037112 | houston | N | 0.0037112 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.042543 | houston | N | -0.14473 | 0.11875 | -0.13846 | 0.0037112 | 0.0037112 | houston | N | 0.0037112 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.042543 | houston | N | -0.14473 | 0.11875 | -0.13846 | 0.0037112 | 0.0037112 | houston | N | 0.0037112 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.035024 | houston | Y | -0.13721 | 0.12627 | -0.13094 | 0.01123 | 0.01123 | houston | N | 0.01123 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.036254 | houston | Y | -0.13844 | 0.12504 | -0.13217 | 0.01 | 0.01 | houston | N | 0.01 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.034653 | houston | Y | -0.13684 | 0.12664 | -0.13057 | 0.011601 | 0.011601 | houston | N | 0.011601 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.034653 | houston | Y | -0.13684 | 0.12664 | -0.13057 | 0.011601 | 0.011601 | houston | N | 0.011601 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.034653 | houston | Y | -0.13684 | 0.12664 | -0.13057 | 0.011601 | 0.011601 | houston | N | 0.011601 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.027826 | houston | N | -0.13002 | 0.13347 | -0.12375 | 0.018428 | 0.018428 | houston | N | 0.018428 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.037872 | houston | N | -0.14006 | 0.12342 | -0.13379 | 0.0083822 | 0.0083822 | houston | N | 0.0083822 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.037872 | houston | N | -0.14006 | 0.12342 | -0.13379 | 0.0083822 | 0.0083822 | houston | N | 0.0083822 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.033783 | houston | N | -0.13597 | 0.12751 | -0.1297 | 0.012471 | 0.012471 | houston | N | 0.012471 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.033783 | houston | N | -0.13597 | 0.12751 | -0.1297 | 0.012471 | 0.012471 | houston | N | 0.012471 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.033783 | houston | N | -0.13597 | 0.12751 | -0.1297 | 0.012471 | 0.012471 | houston | N | 0.012471 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.033783 | houston | N | -0.13597 | 0.12751 | -0.1297 | 0.012471 | 0.012471 | houston | N | 0.012471 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.039319 | houston | N | -0.14151 | 0.12197 | -0.13524 | 0.0069352 | 0.0069352 | houston | N | 0.0069352 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.039319 | houston | N | -0.14151 | 0.12197 | -0.13524 | 0.0069352 | 0.0069352 | houston | N | 0.0069352 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.039319 | houston | N | -0.14151 | 0.12197 | -0.13524 | 0.0069352 | 0.0069352 | houston | N | 0.0069352 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.039319 | houston | N | -0.14151 | 0.12197 | -0.13524 | 0.0069352 | 0.0069352 | houston | N | 0.0069352 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.040091 | houston | N | -0.14228 | 0.1212 | -0.13601 | 0.0061632 | 0.0061632 | houston | N | 0.0061632 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.040091 | houston | N | -0.14228 | 0.1212 | -0.13601 | 0.0061632 | 0.0061632 | houston | N | 0.0061632 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.040091 | houston | N | -0.14228 | 0.1212 | -0.13601 | 0.0061632 | 0.0061632 | houston | N | 0.0061632 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.040091 | houston | N | -0.14228 | 0.1212 | -0.13601 | 0.0061632 | 0.0061632 | houston | N | 0.0061632 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.040091 | houston | N | -0.14228 | 0.1212 | -0.13601 | 0.0061632 | 0.0061632 | houston | N | 0.0061632 | 0
48651 | EP_1_2 | 1 | 5 | -0.035089 | houston | N | -0.13728 | 0.1262 | -0.13101 | 0.011165 | 0.011165 | houston | N | 0.011165 | 0
48651 | EP_1_2 | 2 | 21 | -0.035089 | houston | N | -0.13728 | 0.1262 | -0.13101 | 0.011165 | 0.011165 | houston | N | 0.011165 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.020341 | north | N | -0.081849 | 0.18163 | -0.075579 | 0.066595 | 0.066595 | houston | Y | 0.081849 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.020341 | north | N | -0.081849 | 0.18163 | -0.075579 | 0.066595 | 0.066595 | houston | Y | 0.081849 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.020341 | north | N | -0.081849 | 0.18163 | -0.075579 | 0.066595 | 0.066595 | houston | Y | 0.081849 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.020341 | north | N | -0.081849 | 0.18163 | -0.075579 | 0.066595 | 0.066595 | houston | Y | 0.081849 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.033483 | houston | Y | -0.13567 | 0.12781 | -0.1294 | 0.012771 | 0.012771 | houston | N | 0.012771 | 0
48691 | GBY_7374 | A | 46 | -0.040743 | houston | Y | -0.14293 | 0.12055 | -0.13666 | 0.0055112 | 0.0055112 | houston | N | 0.0055112 | 0
48691 | GBY_7374 | B | 46 | -0.040743 | houston | Y | -0.14293 | 0.12055 | -0.13666 | 0.0055112 | 0.0055112 | houston | N | 0.0055112 | 0
48692 | GBY_8182 | C | 46 | -0.040743 | houston | Y | -0.14293 | 0.12055 | -0.13666 | 0.0055112 | 0.0055112 | houston | N | 0.0055112 | 0
48692 | GBY_8182 | D | 55 | -0.040743 | houston | Y | -0.14293 | 0.12055 | -0.13666 | 0.0055112 | 0.0055112 | houston | N | 0.0055112 | 0
48693 | GBY_8384 | E | 55 | -0.040743 | houston | Y | -0.14293 | 0.12055 | -0.13666 | 0.0055112 | 0.0055112 | houston | N | 0.0055112 | 0
48693 | GBY_8384 | F | 54 | -0.040743 | houston | Y | -0.14293 | 0.12055 | -0.13666 | 0.0055112 | 0.0055112 | houston | N | 0.0055112 | 0
48721 | LEG_1___ | 1 | 827 | 0.073917 | north | Y | -0.028273 | 0.23521 | -0.022003 | 0.12017 | 0.022003 | west | Y | 0.028273 | 5.1852
48722 | LEG_2___ | 2 | 819 | 0.073917 | north | Y | -0.028273 | 0.23521 | -0.022003 | 0.12017 | 0.022003 | west | Y | 0.028273 | 5.1351
48730 | MNS_GT | 1 | 46.1 | -0.054812 | houston | N | -0.157 | 0.10648 | -0.15073 | -0.0085578 | 0.0085578 | houston | N | 0.0085578 | 0
48731 | CBE_GT1 | 1 | 76 | -0.087632 | houston | Y | -0.18982 | 0.073661 | -0.18355 | -0.041378 | 0.041378 | houston | N | 0.041378 | 0
48732 | CBE_GT2 | 1 | 76 | -0.087632 | houston | Y | -0.18982 | 0.073661 | -0.18355 | -0.041378 | 0.041378 | houston | N | 0.041378 | 0
48733 | CBE_ST12 | 1 | 105 | -0.087632 | houston | Y | -0.18982 | 0.073661 | -0.18355 | -0.041378 | 0.041378 | houston | N | 0.041378 | 0
48734 | CBE_GT3 | 1 | 74 | -0.087632 | houston | Y | -0.18982 | 0.073661 | -0.18355 | -0.041378 | 0.041378 | houston | N | 0.041378 | 0
48735 | CBE_GT4 | 1 | 74 | -0.087632 | houston | Y | -0.18982 | 0.073661 | -0.18355 | -0.041378 | 0.041378 | houston | N | 0.041378 | 0
48736 | CBE_ST34 | 1 | 102 | -0.087632 | houston | Y | -0.18982 | 0.073661 | -0.18355 | -0.041378 | 0.041378 | houston | N | 0.041378 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.039297 | houston | N | -0.14149 | 0.122 | -0.13522 | 0.0069572 | 0.0069572 | houston | N | 0.0069572 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.039297 | houston | N | -0.14149 | 0.122 | -0.13522 | 0.0069572 | 0.0069572 | houston | N | 0.0069572 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.039297 | houston | N | -0.14149 | 0.122 | -0.13522 | 0.0069572 | 0.0069572 | houston | N | 0.0069572 | 0
48761 | PR_GT1__ | 1 | 35 | -0.039788 | houston | N | -0.14198 | 0.12151 | -0.13571 | 0.0064662 | 0.0064662 | houston | N | 0.0064662 | 0
48772 | PHR_GN2_ | MB | 459 | -0.0444 | houston | Y | -0.14659 | 0.11689 | -0.14032 | 0.0018542 | 0.0018542 | houston | N | 0.0018542 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.035081 | houston | N | -0.13727 | 0.12621 | -0.131 | 0.011173 | 0.011173 | houston | N | 0.011173 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.035081 | houston | N | -0.13727 | 0.12621 | -0.131 | 0.011173 | 0.011173 | houston | N | 0.011173 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.035081 | houston | N | -0.13727 | 0.12621 | -0.131 | 0.011173 | 0.011173 | houston | N | 0.011173 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.035081 | houston | N | -0.13727 | 0.12621 | -0.131 | 0.011173 | 0.011173 | houston | N | 0.011173 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.035081 | houston | N | -0.13727 | 0.12621 | -0.131 | 0.011173 | 0.011173 | houston | N | 0.011173 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.035081 | houston | N | -0.13727 | 0.12621 | -0.131 | 0.011173 | 0.011173 | houston | N | 0.011173 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.035081 | houston | N | -0.13727 | 0.12621 | -0.131 | 0.011173 | 0.011173 | houston | N | 0.011173 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.027826 | houston | N | -0.13002 | 0.13347 | -0.12375 | 0.018428 | 0.018428 | houston | N | 0.018428 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.027826 | houston | N | -0.13002 | 0.13347 | -0.12375 | 0.018428 | 0.018428 | houston | N | 0.018428 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.027826 | houston | N | -0.13002 | 0.13347 | -0.12375 | 0.018428 | 0.018428 | houston | N | 0.018428 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.027826 | houston | N | -0.13002 | 0.13347 | -0.12375 | 0.018428 | 0.018428 | houston | N | 0.018428 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.0348 | houston | N | -0.13699 | 0.12649 | -0.13072 | 0.011454 | 0.011454 | houston | N | 0.011454 | 0
48820 | SHELLG1_ | 1 | 71 | -0.038839 | houston | N | -0.14103 | 0.12245 | -0.13476 | 0.0074152 | 0.0074152 | houston | N | 0.0074152 | 0
48821 | SHELLG2 | 2 | 72 | -0.038839 | houston | N | -0.14103 | 0.12245 | -0.13476 | 0.0074152 | 0.0074152 | houston | N | 0.0074152 | 0
48822 | SHELLG3_ | 1 | 39 | -0.038839 | houston | N | -0.14103 | 0.12245 | -0.13476 | 0.0074152 | 0.0074152 | houston | N | 0.0074152 | 0
48822 | SHELLG3_ | 2 | 30 | -0.038839 | houston | N | -0.14103 | 0.12245 | -0.13476 | 0.0074152 | 0.0074152 | houston | N | 0.0074152 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.040464 | houston | N | -0.14265 | 0.12083 | -0.13638 | 0.0057902 | 0.0057902 | houston | N | 0.0057902 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.040464 | houston | N | -0.14265 | 0.12083 | -0.13638 | 0.0057902 | 0.0057902 | houston | N | 0.0057902 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.039325 | houston | N | -0.14152 | 0.12197 | -0.13525 | 0.0069292 | 0.0069292 | houston | N | 0.0069292 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.03942 | houston | Y | -0.14161 | 0.12187 | -0.13534 | 0.0068342 | 0.0068342 | houston | N | 0.0068342 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.039445 | houston | Y | -0.14164 | 0.12185 | -0.13537 | 0.0068092 | 0.0068092 | houston | N | 0.0068092 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.039333 | houston | Y | -0.14152 | 0.12196 | -0.13525 | 0.0069212 | 0.0069212 | houston | N | 0.0069212 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.039308 | houston | Y | -0.1415 | 0.12199 | -0.13523 | 0.0069462 | 0.0069462 | houston | N | 0.0069462 | 0
48855 | SRB_GT21 | B2 | 12 | -0.039464 | houston | Y | -0.14165 | 0.12183 | -0.13538 | 0.0067902 | 0.0067902 | houston | N | 0.0067902 | 0
48855 | SRB_GT21 | MB | 18 | -0.039464 | houston | Y | -0.14165 | 0.12183 | -0.13538 | 0.0067902 | 0.0067902 | houston | N | 0.0067902 | 0
48865 | TECO_GT1 | 1 | 50 | -0.045996 | houston | Y | -0.14819 | 0.1153 | -0.14192 | 0.00025818 | 0.00025818 | houston | N | 0.00025818 | 0
48873 | THW_ST3_ | 3 | 104 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48874 | THW_ST4_ | 4 | 104 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48875 | THW_3132 | A | 54 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48875 | THW_3132 | B | 53 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48877 | THW_3334 | C | 54 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48877 | THW_3334 | D | 57 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48879 | THW_4142 | E | 54 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48879 | THW_4142 | F | 54 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48881 | THW_4344 | G | 58 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48881 | THW_4344 | H | 58 | -0.036712 | houston | Y | -0.1389 | 0.12458 | -0.13263 | 0.0095422 | 0.0095422 | houston | N | 0.0095422 | 0
48883 | THW_GT1_ | B2 | 12 | -0.03558 | houston | Y | -0.13777 | 0.12571 | -0.1315 | 0.010674 | 0.010674 | houston | N | 0.010674 | 0
48885 | THW_5152 | A | 56 | -0.03296 | houston | Y | -0.13515 | 0.12833 | -0.12888 | 0.013294 | 0.013294 | houston | N | 0.013294 | 0
48885 | THW_5152 | B | 59 | -0.03296 | houston | Y | -0.13515 | 0.12833 | -0.12888 | 0.013294 | 0.013294 | houston | N | 0.013294 | 0
48886 | THW_5354 | C | 56 | -0.03296 | houston | Y | -0.13515 | 0.12833 | -0.12888 | 0.013294 | 0.013294 | houston | N | 0.013294 | 0
48886 | THW_5354 | D | 56 | -0.03296 | houston | Y | -0.13515 | 0.12833 | -0.12888 | 0.013294 | 0.013294 | houston | N | 0.013294 | 0
48887 | THW_5556 | E | 59 | -0.03296 | houston | Y | -0.13515 | 0.12833 | -0.12888 | 0.013294 | 0.013294 | houston | N | 0.013294 | 0
48887 | THW_5556 | F | 56 | -0.03296 | houston | Y | -0.13515 | 0.12833 | -0.12888 | 0.013294 | 0.013294 | houston | N | 0.013294 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.083293 | houston | Y | -0.18548 | 0.078 | -0.17921 | -0.037039 | 0.037039 | houston | N | 0.037039 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.053001 | houston | Y | -0.15519 | 0.10829 | -0.14892 | -0.0067468 | 0.0067468 | houston | N | 0.0067468 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.053001 | houston | Y | -0.15519 | 0.10829 | -0.14892 | -0.0067468 | 0.0067468 | houston | N | 0.0067468 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.053001 | houston | Y | -0.15519 | 0.10829 | -0.14892 | -0.0067468 | 0.0067468 | houston | N | 0.0067468 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.053001 | houston | Y | -0.15519 | 0.10829 | -0.14892 | -0.0067468 | 0.0067468 | houston | N | 0.0067468 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.053001 | houston | N | -0.15519 | 0.10829 | -0.14892 | -0.0067468 | 0.0067468 | houston | N | 0.0067468 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.054578 | houston | Y | -0.15677 | 0.10672 | -0.1505 | -0.0083238 | 0.0083238 | houston | N | 0.0083238 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.054578 | houston | Y | -0.15677 | 0.10672 | -0.1505 | -0.0083238 | 0.0083238 | houston | N | 0.0083238 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.054578 | houston | Y | -0.15677 | 0.10672 | -0.1505 | -0.0083238 | 0.0083238 | houston | N | 0.0083238 | 0
48929 | WAPGT21_ | B1 | 13 | -0.053001 | houston | Y | -0.15519 | 0.10829 | -0.14892 | -0.0067468 | 0.0067468 | houston | N | 0.0067468 | 0
48940 | WARVUE_G | G1 | 12 | -0.035058 | houston | Y | -0.13725 | 0.12624 | -0.13098 | 0.011196 | 0.011196 | houston | N | 0.011196 | 0
49803 | EXN_15GT | 1 | 34 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49826 | EXN938GT | 5 | 45.9 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49828 | EXN941GT | 10 | 17.7 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49829 | EXN942GT | 11 | 20.4 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49830 | EXN943GT | 12 | 19.9 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49831 | EXN944GT | 13 | 35 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49832 | EXN945GT | 9 | 18 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49837 | EXN_GT | 4 | 85.4 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49838 | EXN_14GT | 14 | 148 | -0.035955 | houston | N | -0.13815 | 0.12534 | -0.13188 | 0.010299 | 0.010299 | houston | N | 0.010299 | 0
49851 | DOW17000 | 37 | 62 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49858 | DOW38100 | 31 | 71.4 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49859 | DOW38200 | 33 | 45 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49860 | DOW38300 | 32 | 101 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49862 | DOW39100 | 36 | 86 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49863 | DOW39200 | 35 | 88 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49865 | DOW41000 | 41 | 50 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49866 | DOW42000 | 42 | 18 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49869 | DOW49000 | 45 | 94 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49870 | DOW61000 | 61 | 70 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49871 | DOW62000 | 62 | 63 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49872 | DOW63000 | 63 | 72 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49873 | DOW64000 | 64 | 64.8 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49876 | DOW65000 | 65 | 101 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49877 | DOW66000 | 66 | 97 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49878 | DOW67000 | 67 | 103 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49882 | DOW81000 | 81 | 76 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49884 | DOW82000 | 82 | 80 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49885 | DOW83000 | 83 | 80 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
49886 | DOW84000 | 84 | 171 | -0.070173 | houston | N | -0.17236 | 0.09112 | -0.16609 | -0.023919 | 0.023919 | houston | N | 0.023919 | 0
58909 | PEARSALL | 1 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58909 | PEARSALL | 2 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58909 | PEARSALL | 3 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58909 | PEARSALL | 4 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58909 | PEARSALL | 5 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58909 | PEARSALL | 6 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58919 | PEARSALL | 1 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58919 | PEARSALL | 2 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58919 | PEARSALL | 3 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58919 | PEARSALL | 4 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58919 | PEARSALL | 5 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58919 | PEARSALL | 6 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58929 | PEARSALL | 1 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58929 | PEARSALL | 2 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58929 | PEARSALL | 3 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58929 | PEARSALL | 4 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58929 | PEARSALL | 5 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58929 | PEARSALL | 6 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58949 | PEARSALL | 1 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58949 | PEARSALL | 2 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58949 | PEARSALL | 3 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58949 | PEARSALL | 4 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58949 | PEARSALL | 5 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
58949 | PEARSALL | 6 | 8.4 | -0.13784 | south | Y | -0.24003 | 0.023451 | -0.23376 | -0.091588 | 0.023451 | south | N | 0.023451 | 0
60000 | DSKY2 | 1 | 76.5 | 0.080012 | west | Y | -0.022178 | 0.24131 | -0.015908 | 0.12627 | 0.015908 | west | N | 0.015908 | 0
60003 | KING_NE1 | 1 | 80 | 0.084448 | west | Y | -0.017742 | 0.24574 | -0.011472 | 0.1307 | 0.011472 | west | N | 0.011472 | 0
60005 | KING_SE1 | 1 | 40 | 0.084448 | west | Y | -0.017742 | 0.24574 | -0.011472 | 0.1307 | 0.011472 | west | N | 0.011472 | 0
60007 | KING_SW1 | 1 | 80 | 0.085165 | west | Y | -0.017025 | 0.24646 | -0.010755 | 0.13142 | 0.010755 | west | N | 0.010755 | 0
60016 | WOODWRD1 | 1 | 80 | 0.084291 | west | Y | -0.017899 | 0.24558 | -0.011629 | 0.13055 | 0.011629 | west | N | 0.011629 | 0
60017 | ORNNWP1 | 1 | 80 | 0.080601 | west | Y | -0.021589 | 0.24189 | -0.015319 | 0.12686 | 0.015319 | west | N | 0.015319 | 0
60018 | DSKY1 | 1 | 84 | 0.079394 | west | Y | -0.022796 | 0.24069 | -0.016526 | 0.12565 | 0.016526 | west | N | 0.016526 | 0
60019 | KING_NW1 | 1 | 80 | 0.085165 | west | Y | -0.017025 | 0.24646 | -0.010755 | 0.13142 | 0.010755 | west | N | 0.010755 | 0
60057 | CALLAHAN | 1 | 114 | -0.15859 | south | Y | -0.26078 | 0.0027081 | -0.25451 | -0.11233 | 0.0027081 | south | N | 0.0027081 | 0
60058 | BUFF_GAP | 1 | 120 | 0.097363 | west | Y | -0.0048274 | 0.25866 | 0.0014425 | 0.14362 | 0.0014425 | west | N | 0.0014425 | 0
60060 | CIRELLO | 1 | 233 | 0.097363 | west | Y | -0.0048274 | 0.25866 | 0.0014425 | 0.14362 | 0.0014425 | west | N | 0.0014425 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.097363 | west | Y | -0.0048274 | 0.25866 | 0.0014425 | 0.14362 | 0.0014425 | west | N | 0.0014425 | 0
60066 | H_HOLLOW | 1 | 222 | -0.15859 | south | Y | -0.26078 | 0.0027081 | -0.25451 | -0.11233 | 0.0027081 | south | N | 0.0027081 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.15859 | south | Y | -0.26078 | 0.0027081 | -0.25451 | -0.11233 | 0.0027081 | south | N | 0.0027081 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.15859 | south | Y | -0.26078 | 0.0027081 | -0.25451 | -0.11233 | 0.0027081 | south | N | 0.0027081 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.15859 | south | Y | -0.26078 | 0.0027081 | -0.25451 | -0.11233 | 0.0027081 | south | N | 0.0027081 | 0
60074 | HORSH5 | 1 | 100 | -0.15859 | south | Y | -0.26078 | 0.0027081 | -0.25451 | -0.11233 | 0.0027081 | south | N | 0.0027081 | 0
60081 | WHRLWIND | 1 | 60 | 0.10058 | west | Y | -0.0016084 | 0.26188 | 0.0046615 | 0.14684 | 0.0016084 | North | Y | 0.0046615 | 0.18319
60201 | RIO DRCS | F | 0 | -0.056041 | south | N | -0.15823 | 0.10525 | -0.15196 | -0.0097868 | 0.0097868 | houston | Y | 0.10525 | 0
60202 | FRIEND_R | F | 0 | 0.060136 | west | N | -0.042054 | 0.22143 | -0.035784 | 0.10639 | 0.035784 | west | N | 0.035784 | 0
60203 | PRES0A | BT | 4.8 | 0.087809 | west | N | -0.014381 | 0.2491 | -0.0081115 | 0.13406 | 0.0081115 | west | N | 0.0081115 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.09889 | west | Y | -0.0033004 | 0.26018 | 0.0029695 | 0.14514 | 0.0029695 | west | N | 0.0029695 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.09889 | west | Y | -0.0033004 | 0.26018 | 0.0029695 | 0.14514 | 0.0029695 | west | N | 0.0029695 | 0
71057 | L_SWEETW | W1 | 135 | 0.09889 | west | Y | -0.0033004 | 0.26018 | 0.0029695 | 0.14514 | 0.0029695 | west | N | 0.0029695 | 0
71059 | L_SWEETW | W1 | 119 | 0.09889 | west | Y | -0.0033004 | 0.26018 | 0.0029695 | 0.14514 | 0.0029695 | west | N | 0.0029695 | 0
71060 | L_SWEETW | W1 | 105 | 0.09889 | west | Y | -0.0033004 | 0.26018 | 0.0029695 | 0.14514 | 0.0029695 | west | N | 0.0029695 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.09889 | west | Y | -0.0033004 | 0.26018 | 0.0029695 | 0.14514 | 0.0029695 | west | N | 0.0029695 | 0
76031 | L_GASCCR | W1 | 150 | 0.096223 | west | Y | -0.0059674 | 0.25752 | 0.00030254 | 0.14248 | 0.00030254 | west | N | 0.00030254 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.095899 | west | Y | -0.0062914 | 0.25719 | -2.1463e-05 | 0.14215 | 2.1463e-05 | west | N | 2.1463e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.095899 | west | Y | -0.0062914 | 0.25719 | -2.1463e-05 | 0.14215 | 2.1463e-05 | west | N | 2.1463e-05 | 0
76096 | L_CAPRSI | W1 | 186 | 0.095899 | west | Y | -0.0062914 | 0.25719 | -2.1463e-05 | 0.14215 | 2.1463e-05 | west | N | 2.1463e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.095899 | west | Y | -0.0062914 | 0.25719 | -2.1463e-05 | 0.14215 | 2.1463e-05 | west | N | 2.1463e-05 | 0
80003 | MILHWYS | F | 0 | -0.13306 | south | N | -0.23525 | 0.028235 | -0.22898 | -0.086804 | 0.028235 | south | N | 0.028235 | 0
80010 | EPLVT1 | F | 0 | -0.10115 | south | N | -0.20334 | 0.060141 | -0.19707 | -0.054898 | 0.054898 | houston | Y | 0.060141 | 0
80012 | LAR | F | 0 | -0.1392 | south | N | -0.24139 | 0.022098 | -0.23512 | -0.092941 | 0.022098 | south | N | 0.022098 | 0
80051 | FORPVCM0 | 8 | 28 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
80053 | FOR69CG0 | 10 | 74 | -0.12207 | south | N | -0.22426 | 0.03922 | -0.21799 | -0.075819 | 0.03922 | south | N | 0.03922 | 0
80080 | GWINDT11 | 1 | 94 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80080 | GWINDT11 | 2 | 41 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80080 | GWINDT11 | 3 | 38 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80080 | GWINDT11 | 4 | 19 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80081 | GWINDT21 | 1 | 94 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80081 | GWINDT21 | 2 | 36 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80081 | GWINDT21 | 3 | 43 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80081 | GWINDT21 | 4 | 22 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80137 | CSDR89 | 8 | 39 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
80137 | CSDR89 | 9 | 15 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
80138 | CSDR7 | 7 | 7 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
80139 | CSDR56 | 5 | 15 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
80139 | CSDR56 | 6 | 39 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
80140 | CSDR11 | 11 | 39 | -0.12607 | south | N | -0.22826 | 0.035226 | -0.22199 | -0.079813 | 0.035226 | south | N | 0.035226 | 0
80180 | PNSCALT1 | 1 | 148 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80180 | PNSCALT1 | 2 | 50 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80181 | PNSCALT2 | 1 | 55 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80181 | PNSCALT2 | 2 | 50 | -0.13298 | south | Y | -0.23517 | 0.028312 | -0.2289 | -0.086727 | 0.028312 | south | N | 0.028312 | 0
80223 | REYSHR G | 1 | 12 | -0.13054 | south | N | -0.23273 | 0.030749 | -0.22646 | -0.08429 | 0.030749 | south | N | 0.030749 | 0
80224 | VISTRONG | 1 | 15 | -0.12732 | south | N | -0.22951 | 0.033978 | -0.22324 | -0.081061 | 0.033978 | south | N | 0.033978 | 0
80225 | VISTRONG | 2 | 23 | -0.12732 | south | N | -0.22951 | 0.033978 | -0.22324 | -0.081061 | 0.033978 | south | N | 0.033978 | 0
80226 | ALCOA G | 1 | 48 | -0.12301 | south | N | -0.2252 | 0.038286 | -0.21893 | -0.076753 | 0.038286 | south | N | 0.038286 | 0
80227 | AIRCO G | 1 | 8 | -0.12653 | south | N | -0.22872 | 0.034759 | -0.22245 | -0.08028 | 0.034759 | south | N | 0.034759 | 0
80261 | NBEC81A | 1 | 180 | -0.13181 | south | Y | -0.234 | 0.029488 | -0.22773 | -0.085551 | 0.029488 | south | N | 0.029488 | 0
80262 | NBEC91A | 1 | 180 | -0.13177 | south | Y | -0.23396 | 0.029525 | -0.22769 | -0.085514 | 0.029525 | south | N | 0.029525 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.13204 | south | Y | -0.23423 | 0.02925 | -0.22796 | -0.085789 | 0.02925 | south | N | 0.02925 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.13204 | south | Y | -0.23423 | 0.02925 | -0.22796 | -0.085789 | 0.02925 | south | N | 0.02925 | 0
80265 | LARECU40 | 4 | 100 | -0.13921 | south | Y | -0.2414 | 0.022086 | -0.23513 | -0.092953 | 0.022086 | south | N | 0.022086 | 0
80266 | LARECU50 | 5 | 100 | -0.13921 | south | Y | -0.2414 | 0.022086 | -0.23513 | -0.092953 | 0.022086 | south | N | 0.022086 | 0
80291 | PAPALOTE | 1 | 25 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
80291 | PAPALOTE | 2 | 25 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
80291 | PAPALOTE | 3 | 25 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
80291 | PAPALOTE | 4 | 16 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
80294 | PAPALOTE | 5 | 25 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
80294 | PAPALOTE | 6 | 25 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
80294 | PAPALOTE | 7 | 25 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
80294 | PAPALOTE | 8 | 15 | -0.13103 | south | Y | -0.23322 | 0.03026 | -0.22695 | -0.084779 | 0.03026 | south | N | 0.03026 | 0
86104 | CID-138 | EQ | 0 | -0.13921 | south | N | -0.2414 | 0.022086 | -0.23513 | -0.092953 | 0.022086 | south | N | 0.022086 | 0
86105 | CID-230 | EQ | 500 | -0.13921 | south | N | -0.2414 | 0.022086 | -0.23513 | -0.092953 | 0.022086 | south | N | 0.022086 | 0
86106 | CUF-230 | EQ | 500 | -0.13921 | south | N | -0.2414 | 0.022086 | -0.23513 | -0.092953 | 0.022086 | south | N | 0.022086 | 0
86107 | CUF-138 | EQ | 0 | -0.13921 | south | N | -0.2414 | 0.022086 | -0.23513 | -0.092953 | 0.022086 | south | N | 0.022086 | 0
88198 | BEEVILLE | F | 0 | -0.13798 | south | N | -0.24017 | 0.023316 | -0.2339 | -0.091723 | 0.023316 | south | N | 0.023316 | 0
88253 | HAMILTON | F | 0 | -0.077259 | south | N | -0.17945 | 0.084034 | -0.17318 | -0.031005 | 0.031005 | houston | Y | 0.084034 | 0
88299 | ZAPATA | F | 0 | -0.13612 | south | N | -0.23831 | 0.025175 | -0.23204 | -0.089864 | 0.025175 | south | N | 0.025175 | 0
88508 | FALFURRI | F | 0 | -0.13498 | south | N | -0.23717 | 0.026317 | -0.2309 | -0.088722 | 0.026317 | south | N | 0.026317 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: 3413 TEMP_SS_ to 3429 SANDOW_ C: 3414 TEMP_SS_ to 3429 SANDOW_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0 | Weighted Shift Factors
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0 | South | -0.16129
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0 | North | 0.11234
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0 |  | -0.27364
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16129 | 0 | 0 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8139 | 0 | 0.13347 | 0 | 0 | 0 | Line Rating | 1072
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3409 | 0 | 0.13347 | 0 | 0 | 0 | Conc Gen | 2023
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2852 | 0 | 0.13347 | 0 | 0 | 0 | Weighted Imp. | 256.9459
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2852 | 0 | 0.13347 | 0 | 0 | 0 | PTDF | 0.12701
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.027826 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5078 | 0 | 0.13347 | 0 | 0 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867 | 56 | 7.1867 | Concentration | -0.46417
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9446 | 59 | 0.12833 | 7.5717 | 115 | 14.7583
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867 | 171 | 21.945
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867 | 227 | 29.1316
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9446 | 59 | 0.12833 | 7.5717 | 286 | 36.7033
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867 | 342 | 43.8899
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.033483 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.3262 | 398 | 0.12781 | 50.8684 | 740 | 94.7583
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4999 | 0 | 0.12751 | 0 | 740 | 94.7583
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4526 | 0 | 0.12751 | 0 | 740 | 94.7583
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3681 | 0 | 0.12751 | 0 | 740 | 94.7583
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0944 | 0 | 0.12751 | 0 | 740 | 94.7583
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9603 | 172 | 0.12664 | 21.7821 | 912 | 116.5404
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9603 | 172 | 0.12664 | 21.7821 | 1084 | 138.3225
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9603 | 172 | 0.12664 | 21.7821 | 1256 | 160.1046
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.0348 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.4636 | 0 | 0.12649 | 0 | 1256 | 160.1046
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.035024 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.0228 | 743 | 0.12627 | 93.8179 | 1999 | 253.9225
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.035058 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.4207 | 12 | 0.12624 | 1.5148 | 2011 | 255.4373
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2803 | 0 | 0.12621 | 0 | 2011 | 255.4373
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3153 | 0 | 0.12621 | 0 | 2011 | 255.4373
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4557 | 0 | 0.12621 | 0 | 2011 | 255.4373
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2101 | 0 | 0.12621 | 0 | 2011 | 255.4373
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.175 | 0 | 0.12621 | 0 | 2011 | 255.4373
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6484 | 0 | 0.12621 | 0 | 2011 | 255.4373
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0698 | 0 | 0.12621 | 0 | 2011 | 255.4373
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.035089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17544 | 0 | 0.1262 | 0 | 2011 | 255.4373
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.035089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73687 | 0 | 0.1262 | 0 | 2011 | 255.4373
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.03558 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42696 | 12 | 0.12571 | 1.5086 | 2023 | 256.9459
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2225 | 0 | 0.12534 | 0 | 2023 | 256.9459
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2476 | 0 | 0.12534 | 0 | 2023 | 256.9459
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1757 | 0 | 0.12534 | 0 | 2023 | 256.9459
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6503 | 0 | 0.12534 | 0 | 2023 | 256.9459
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6364 | 0 | 0.12534 | 0 | 2023 | 256.9459
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73348 | 0 | 0.12534 | 0 | 2023 | 256.9459
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7155 | 0 | 0.12534 | 0 | 2023 | 256.9459
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2584 | 0 | 0.12534 | 0 | 2023 | 256.9459
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64719 | 0 | 0.12534 | 0 | 2023 | 256.9459
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0706 | 0 | 0.12534 | 0 | 2023 | 256.9459
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3213 | 0 | 0.12534 | 0 | 2023 | 256.9459
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.036254 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.6467 | 735 | 0.12504 | 91.9037
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.818 | 104 | 0.12458 | 12.9564
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.818 | 104 | 0.12458 | 12.9564
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9457 | 53 | 0.12458 | 6.6028
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0926 | 57 | 0.12458 | 7.1011
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1293 | 58 | 0.12458 | 7.2257
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1293 | 58 | 0.12458 | 7.2257
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.037872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5519 | 0 | 0.12342 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.037872 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1127 | 0 | 0.12342 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 42 | 0.12324 | 5.176
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 42 | 0.12324 | 5.176
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4461 | 38 | 0.12324 | 4.683
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4461 | 38 | 0.12324 | 4.683
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.038116 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1838 | 0 | 0.12318 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7576 | 0 | 0.12245 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7964 | 0 | 0.12245 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5147 | 0 | 0.12245 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1652 | 0 | 0.12245 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0735 | 0 | 0.122 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2325 | 0 | 0.122 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1696 | 0 | 0.122 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039308 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.9622 | 228 | 0.12199 | 27.8126
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5164 | 0 | 0.12197 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.485 | 0 | 0.12197 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2477 | 0 | 0.12197 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8939 | 0 | 0.12197 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63706 | 0 | 0.12197 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039333 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.3779 | 213 | 0.12196 | 25.9775
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.0394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8706 | 0 | 0.12189 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.0394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5649 | 0 | 0.12189 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.03942 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.5043 | 165 | 0.12187 | 20.1091
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039445 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.6662 | 169 | 0.12185 | 20.5923
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039464 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47357 | 12 | 0.12183 | 1.4619
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039464 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.12183 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039788 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3926 | 0 | 0.12151 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.5429 | 0 | 0.1212 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2983 | 0 | 0.1212 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3143 | 0 | 0.1212 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2943 | 0 | 0.1212 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.7845 | 0 | 0.1212 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.040464 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.1562 | 0 | 0.12083 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.040464 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2371 | 0 | 0.12083 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8742 | 46 | 0.12055 | 5.5453
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8742 | 46 | 0.12055 | 5.5453
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8742 | 46 | 0.12055 | 5.5453
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2409 | 55 | 0.12055 | 6.6303
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2409 | 55 | 0.12055 | 6.6303
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2001 | 54 | 0.12055 | 6.5097
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.718 | 0 | 0.11948 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.509 | 0 | 0.11948 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.718 | 0 | 0.11948 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.718 | 0 | 0.11948 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8714 | 0 | 0.11875 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7268 | 0 | 0.11875 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7012 | 0 | 0.11875 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3186 | 0 | 0.11875 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51902 | 0 | 0.11875 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.0444 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.11689 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.045996 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2998 | 50 | 0.1153 | 5.7649
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4006 | 0 | 0.11326 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2037 | 0 | 0.11326 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5456 | 0 | 0.11326 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3583 | 0 | 0.11326 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3728 | 0 | 0.11326 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3151 | 0 | 0.11326 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.611 | 0 | 0.11326 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.7196 | 0 | 0.11326 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9212 | 0 | 0.11326 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.048056 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5378 | 0 | 0.11324 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.048056 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4417 | 0 | 0.11324 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8201 | 0 | 0.11324 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.4645 | 0 | 0.11324 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9355 | 0 | 0.11324 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9018 | 0 | 0.11324 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.5332 | 161 | 0.10829 | 17.435
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.7982 | 166 | 0.10829 | 17.9765
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.1442 | 248 | 0.10829 | 26.8564
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.053001 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -28.9385 | 546 | 0.10829 | 59.1275
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.053001 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -34.0796 | 0 | 0.10829 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.053001 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.68901 | 13 | 0.10829 | 1.4078
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.053408 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7625 | 0 | 0.10789 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8832 | 0 | 0.1068 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8832 | 0 | 0.1068 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.352 | 0 | 0.1068 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -35.5303 | 651 | 0.10672 | 69.4715
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -30.782 | 564 | 0.10672 | 60.1873
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.7468 | 600 | 0.10672 | 64.029
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.054812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5268 | 0 | 0.10648 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.122 | 0 | 0.097131 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.122 | 0 | 0.097131 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.6353 | 0 | 0.097131 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0257 | 0 | 0.097131 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.066819 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7441 | 0 | 0.094474 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.066819 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66819 | 0 | 0.094474 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3507 | 0 | 0.09112 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0104 | 0 | 0.09112 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1578 | 0 | 0.09112 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0875 | 0 | 0.09112 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0349 | 0 | 0.09112 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1752 | 0 | 0.09112 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5086 | 0 | 0.09112 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2631 | 0 | 0.09112 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5963 | 0 | 0.09112 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9121 | 0 | 0.09112 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4209 | 0 | 0.09112 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0525 | 0 | 0.09112 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5472 | 0 | 0.09112 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0875 | 0 | 0.09112 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8068 | 0 | 0.09112 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2278 | 0 | 0.09112 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3331 | 0 | 0.09112 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6138 | 0 | 0.09112 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6138 | 0 | 0.09112 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.9996 | 0 | 0.09112 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.077259 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5495 | 0 | 0.084034 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.077259 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9315 | 0 | 0.084034 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.077259 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.084034 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3978 | 0 | 0.083638 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3978 | 0 | 0.083638 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1648 | 0 | 0.083638 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.082934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1362 | 0 | 0.078359 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.083293 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.4973 | 66 | 0.078 | 5.148
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.66 | 76 | 0.073661 | 5.5982
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.66 | 76 | 0.073661 | 5.5982
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2014 | 105 | 0.073661 | 7.7344
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4848 | 74 | 0.073661 | 5.4509
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4848 | 74 | 0.073661 | 5.4509
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.9385 | 102 | 0.073661 | 7.5134
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.088576 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.0718 | 0 | 0.072717 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.088576 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -117.6289 | 0 | 0.072717 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.096644 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.57986 | 0 | 0.064649 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.17291 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.060567 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.17291 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 136.0794 | 787 | 0.060567 | 47.6659
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.10115 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.060141 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.10185 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8518 | 0 | 0.059443 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.10185 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9537 | 0 | 0.059443 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.10207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -43.0748 | 422 | 0.05922 | 24.9909
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.16815 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055812 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.16815 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055812 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.11043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9877 | 0 | 0.050867 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.11043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9877 | 0 | 0.050867 | 0
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.16306 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.579 | 255 | 0.050713 | 12.9317
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.16306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.2952 | 149 | 0.050713 | 7.5562
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.16306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.9474 | 153 | 0.050713 | 7.759
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.15555 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3319 | 150 | 0.043204 | 6.4805
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.15555 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.4437 | 80 | 0.043204 | 3.4563
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6438 | 0 | 0.03922 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.8879 | 0 | 0.03922 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6438 | 0 | 0.03922 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.7658 | 0 | 0.03922 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.5705 | 0 | 0.03922 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0518 | 0 | 0.03922 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6154 | 0 | 0.03922 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.418 | 0 | 0.03922 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3224 | 0 | 0.03922 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.0334 | 0 | 0.03922 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.12301 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9043 | 0 | 0.038286 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.14766 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.215 | 0 | 0.035322 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.14766 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.215 | 0 | 0.035322 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5299 | 0 | 0.035226 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.88247 | 0 | 0.035226 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9166 | 0 | 0.035226 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.891 | 0 | 0.035226 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.88247 | 0 | 0.035226 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.891 | 0 | 0.035226 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9166 | 0 | 0.035226 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9166 | 0 | 0.035226 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.12653 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0123 | 0 | 0.034759 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.12732 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9097 | 0 | 0.033978 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.12732 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9282 | 0 | 0.033978 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.1284 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8249 | 22 | 0.032888 | 0.72354
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4125 | 11 | 0.032888 | 0.36177
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4125 | 11 | 0.032888 | 0.36177
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5279 | 0 | 0.031925 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.3985 | 0 | 0.031925 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5279 | 0 | 0.031925 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1721 | 47.7 | 0.031898 | 1.5215
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8264 | 37.3 | 0.031898 | 1.1898
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9522 | 46 | 0.031898 | 1.4673
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.211 | 48 | 0.031898 | 1.5311
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.12948 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.4523 | 0 | 0.03181 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.626 | 0 | 0.030749 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.9732 | 0 | 0.030749 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -13.0544 | 0 | 0.030749 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.9289 | 0 | 0.030749 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.19 | 0 | 0.030749 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -16.5791 | 0 | 0.030749 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.13054 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5665 | 0 | 0.030749 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.13074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -18.8263 | 144 | 0.030555 | 4.3999
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.13074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.5787 | 188 | 0.030555 | 5.7444
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 25 | 0.03026 | 0.7565
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 25 | 0.03026 | 0.7565
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 25 | 0.03026 | 0.7565
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0965 | 16 | 0.03026 | 0.48416
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 25 | 0.03026 | 0.7565
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 25 | 0.03026 | 0.7565
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 25 | 0.03026 | 0.7565
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9655 | 15 | 0.03026 | 0.4539
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.13177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.274 | 336 | 0.029525 | 9.9204
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7182 | 180 | 0.029525 | 5.3145
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.5433 | 0 | 0.029511 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.5828 | 0 | 0.029511 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.1626 | 0 | 0.029511 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7249 | 180 | 0.029488 | 5.3079
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.13204 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.1024 | 334 | 0.02925 | 9.7695
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.13204 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.8946 | 340 | 0.02925 | 9.945
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7677 | 180 | 0.02925 | 5.265
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7677 | 180 | 0.02925 | 5.265
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.13207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3018 | 0 | 0.029223 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.13207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3018 | 0 | 0.029223 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.13219 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0232 | 0 | 0.029103 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.1322 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0235 | 0 | 0.029096 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.13279 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8508 | 0 | 0.028507 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5002 | 94 | 0.028312 | 2.6613
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4522 | 41 | 0.028312 | 1.1608
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.0533 | 38 | 0.028312 | 1.0759
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.5266 | 19 | 0.028312 | 0.53793
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5002 | 94 | 0.028312 | 2.6613
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7873 | 36 | 0.028312 | 1.0192
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7182 | 43 | 0.028312 | 1.2174
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9256 | 22 | 0.028312 | 0.62287
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.6812 | 148 | 0.028312 | 4.1902
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.649 | 50 | 0.028312 | 1.4156
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.314 | 55 | 0.028312 | 1.5572
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.649 | 50 | 0.028312 | 1.4156
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0562 | 38 | 0.028235 | 1.0729
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.568 | 19.3 | 0.028235 | 0.54494
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9959 | 15 | 0.028235 | 0.42353
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.13306 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.2537 | 47 | 0.028235 | 1.327
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.13306 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028235 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.1917 | 144 | 0.028017 | 4.0345
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.1917 | 144 | 0.028017 | 4.0345
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.7902 | 171 | 0.028017 | 4.7909
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.589 | 207 | 0.028013 | 5.7987
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.8818 | 216.7 | 0.028013 | 6.0704
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.2538 | 242 | 0.028013 | 6.7792
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.5569 | 146.5 | 0.027799 | 4.0726
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.7438 | 147.9 | 0.027799 | 4.1115
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.0945 | 173 | 0.027799 | 4.8092
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.618 | 0 | 0.026458 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4832 | 0 | 0.026458 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.618 | 0 | 0.026458 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.13498 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.026317 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.13612 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.025175 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.1366 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.9201 | 629 | 0.024695 | 15.5332
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.13798 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023316 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.1392 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022098 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.13921 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9207 | 100 | 0.022086 | 2.2086
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.13921 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9207 | 100 | 0.022086 | 2.2086
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13943 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3463 | 24 | 0.021863 | 0.52471
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13943 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.3463 | 24 | 0.021863 | 0.52471
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.13943 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.2069 | 23 | 0.021863 | 0.50285
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.14694 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1755 | 0 | 0.01435 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.14694 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1755 | 0 | 0.01435 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.14841 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -58.7704 | 396 | 0.012883 | 5.1017
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.1514 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8168 | 0 | 0.0098921 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.15418 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.7949 | 310 | 0.0071161 | 2.206
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.15418 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.6751 | 413 | 0.0071161 | 2.9389
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.15513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.9977 | 58 | 0.0061611 | 0.35734
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.15513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.8067 | 89 | 0.0061611 | 0.54834
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8258 | 44 | 0.0061611 | 0.27109
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8258 | 44 | 0.0061611 | 0.27109
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6707 | 43 | 0.0061611 | 0.26493
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9809 | 45 | 0.0061611 | 0.27725
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.15569 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.0051 | 546 | 0.0056061 | 3.0609
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.15569 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -116.7652 | 750 | 0.0056061 | 4.2046
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.1561 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.5323 | 407 | 0.0051941 | 2.114
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.1961 | 155 | 0.0051891 | 0.80431
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.5377 | 170 | 0.0051891 | 0.88214
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.1961 | 155 | 0.0051891 | 0.80431
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.15615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -32.6347 | 209 | 0.0051461 | 1.0755
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.15615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -33.7278 | 216 | 0.0051461 | 1.1116
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1828 | 46 | 0.0051461 | 0.23672
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3389 | 47 | 0.0051461 | 0.24187
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1828 | 46 | 0.0051461 | 0.23672
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1828 | 46 | 0.0051461 | 0.23672
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11743 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7287 | 168 | 0.0050905 | 0.85521
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11743 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.569 | 90 | 0.0050905 | 0.45815
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.15633 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -64.4071 | 412 | 0.0049651 | 2.0456
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.15633 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -62.5312 | 400 | 0.0049651 | 1.986
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.15655 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.3768 | 424 | 0.0047441 | 2.0115
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.15655 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.5333 | 425 | 0.0047441 | 2.0162
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.5967 | 42 | 0.0042281 | 0.17758
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9109 | 44 | 0.0042281 | 0.18604
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9109 | 44 | 0.0042281 | 0.18604
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3821 | 47 | 0.0042281 | 0.19872
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.0891 | 224 | 0.0041265 | 0.92434
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.322 | 226 | 0.0041265 | 0.9326
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.6914 | 212 | 0.0041265 | 0.87483
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.575 | 211 | 0.0041265 | 0.8707
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0041101 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0041101 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0041101 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.11588 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0773 | 216.4 | 0.0035415 | 0.76639
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.11588 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0425 | 216.1 | 0.0035415 | 0.76533
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.0787 | 114 | 0.0027081 | 0.30872
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.2059 | 222 | 0.0027081 | 0.60119
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -29.1796 | 184 | 0.0027081 | 0.49829
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.523 | 224 | 0.0027081 | 0.60661
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.2373 | 115 | 0.0027081 | 0.31143
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8081 | 49 | 0.0019441 | 0.09526
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3301 | 46 | 0.0019441 | 0.089427
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3301 | 46 | 0.0019441 | 0.089427
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.4894 | 47 | 0.0019441 | 0.091371
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.15935 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.5397 | 154 | 0.0019441 | 0.29939
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.15935 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.5837 | 148 | 0.0019441 | 0.28772
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6488 | 48 | 0.0019441 | 0.093316
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6488 | 48 | 0.0019441 | 0.093316
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.15961 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38307 | 0 | 0.0016811 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.15961 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38307 | 0 | 0.0016811 | 0
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.9743 | 70 | 0.0015755 | 0.11029
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8603 | 69 | 0.0015755 | 0.10871
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8603 | 69 | 0.0015755 | 0.10871
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7464 | 68 | 0.0015755 | 0.10714
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11249 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.2118 | 73 | 0.00014853 | 0.010843
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11249 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.3864 | 119 | 0.00014853 | 0.017676
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11249 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.0607 | 205 | 0.00014853 | 0.03045
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11249 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.4741 | 102 | 0.00014853 | 0.015151
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11249 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.7991 | 96 | 0.00014853 | 0.014259
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11197 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 44.2297 | 395 | -0.00036847 | -0.14554
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.7087 | 435 | -0.00036847 | -0.16028
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.11193 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00041247 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11174 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.6082 | 435 | -0.00059947 | -0.26077
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.11172 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.703 | 60 | -0.00062647 | -0.037588
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8097 | 147 | -0.00067793 | -0.099655
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.352 | 138 | -0.00067793 | -0.093554
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.6759 | 140 | -0.00067793 | -0.09491
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8097 | 147 | -0.00067793 | -0.099655
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.4787 | 182 | -0.00067793 | -0.12338
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.0703 | 198 | -0.00067793 | -0.13423
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2642 | 217.3 | -0.00068047 | -0.14787
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8907 | 205 | -0.00068047 | -0.1395
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.4167 | 272.4 | -0.00068047 | -0.18536
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11145 | north | 3 | N | N | Nnorth | Nnorth | 1 | 128.95 | 0 | -0.00089047 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11145 | north | 3 | N | N | Nnorth | Nnorth | 1 | 129.0614 | 0 | -0.00089047 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0012 | 18 | -0.0011665 | -0.020996
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0012 | 18 | -0.0011665 | -0.020996
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.2247 | 38 | -0.0011665 | -0.044326
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.16316 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65262 | 0 | -0.0018629 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.648 | 196 | -0.0018935 | -0.37112
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2598 | 111 | -0.0018935 | -0.21017
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.11023 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0021115 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.11023 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0021115 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.11023 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0021115 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.6662 | 288 | -0.0023905 | -0.68845
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1629 | 147 | -0.0023905 | -0.3514
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1629 | 147 | -0.0023905 | -0.3514
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39297 | 0 | -0.0024459 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39297 | 0 | -0.0024459 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45847 | 0 | -0.0024459 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.16465 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.98787 | 0 | -0.0033519 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.10892 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.307 | 0 | -0.0034255 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.10892 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.307 | 0 | -0.0034255 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.10891 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.0694 | 120 | -0.0034305 | -0.41166
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.10866 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 12.2238 | 112.5 | -0.0036865 | -0.41473
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.10852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.5111 | 60 | -0.0038235 | -0.22941
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.10852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.8367 | 63 | -0.0038235 | -0.24088
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.10851 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.8039 | 118 | -0.0038345 | -0.45247
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.10851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.4784 | 115 | -0.0038345 | -0.44096
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.10851 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.3304 | 556 | -0.0038345 | -2.132
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0577 | 204 | -0.0042165 | -0.86016
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7333 | 201 | -0.0042165 | -0.84751
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.1665 | 242 | -0.0042165 | -1.0204
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.10764 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047035 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.1076 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0047395 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.10706 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2824 | 0 | -0.0052825 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.10706 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2824 | 0 | -0.0052825 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.10693 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 18.1774 | 170 | -0.0054165 | -0.9208
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.10693 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 55.6015 | 520 | -0.0054165 | -2.8166
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.10684 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0055055 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.10684 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0055055 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.10677 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 39.5056 | 370 | -0.0055705 | -2.0611
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.9481 | 0 | -0.0055705 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.0549 | 0 | -0.0055705 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.9925 | 0 | -0.0055705 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.2684 | 0 | -0.0055705 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.3752 | 0 | -0.0055705 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 33.0993 | 0 | -0.0055705 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0688 | 160 | -0.0056625 | -0.90599
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6421 | 156 | -0.0056625 | -0.88334
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9093 | 196 | -0.0056625 | -1.1098
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6421 | 156 | -0.0056625 | -0.88334
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7488 | 157 | -0.0056625 | -0.88901
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.1226 | 198 | -0.0056625 | -1.1212
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | 1 | 7.9947 | 0 | -0.0057465 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | 1 | 8.485 | 0 | -0.0057465 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.4231 | 0 | -0.0057465 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.10658 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.2633 | 40 | -0.0057595 | -0.23038
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4171 | 79 | -0.0057965 | -0.45792
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.2939 | 106 | -0.0057965 | -0.61443
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.5557 | 146 | -0.0057965 | -0.84628
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.10655 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.0975 | 76 | -0.0057965 | -0.44053
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 59.4432 | 558 | -0.0058135 | -3.2439
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.6803 | 579 | -0.0058135 | -3.366
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 86.0754 | 808 | -0.0058135 | -4.6973
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.10643 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 41.2945 | 388 | -0.0059135 | -2.2944
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.10643 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.8109 | 515 | -0.0059135 | -3.0454
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6595 | 25 | -0.0059615 | -0.14904
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3616 | 41 | -0.0059615 | -0.24442
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1276 | 20 | -0.0059615 | -0.11923
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.10632 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.7282 | 242 | -0.0060275 | -1.4586
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1235 | 20 | -0.0061695 | -0.12339
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1235 | 20 | -0.0061695 | -0.12339
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1235 | 20 | -0.0061695 | -0.12339
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.8049 | 17 | -0.0061695 | -0.10488
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.1204 | 132 | -0.0062859 | -0.82974
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.4556 | 134 | -0.0062859 | -0.84231
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -54.128 | 323 | -0.0062859 | -2.0304
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.10601 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.7467 | 224 | -0.0063305 | -1.418
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.10596 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 38.7825 | 366 | -0.0063795 | -2.3349
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8669 | 142 | -0.0067839 | -0.96332
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.3712 | 145 | -0.0067839 | -0.98367
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.3796 | 151 | -0.0067839 | -1.0244
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.7423 | 290 | -0.0067839 | -1.9673
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.9728 | 161 | -0.0069215 | -1.1144
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.289 | 164 | -0.0069215 | -1.1351
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.289 | 164 | -0.0069215 | -1.1351
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.6443 | 414 | -0.0069215 | -2.8655
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0782 | 162 | -0.0069215 | -1.1213
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.9728 | 161 | -0.0069215 | -1.1144
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1836 | 163 | -0.0069215 | -1.1282
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.1172 | 409 | -0.0069215 | -2.8309
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.1037 | west | 4 | Y | N | Ywest | Nwest | 1 | 67.3726 | 649.7 | -0.0086445 | -5.6163
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.1029 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.979 | 165 | -0.0094395 | -1.5575
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.10194 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.0569 | 236 | -0.010406 | -2.4559
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10193 | west | 6 | Y | N | Ywest | Nwest | 1 | 40.7724 | 400 | -0.010411 | -4.1646
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.4302 | 785 | -0.011157 | -8.7586
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.4421 | 795 | -0.011157 | -8.8702
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.9243 | 780 | -0.011157 | -8.7028
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.8924 | 0 | -0.011718 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.0811 | 0 | -0.011718 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.5905 | 0 | -0.011718 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 40.149 | 0 | -0.011718 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10058 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0349 | 60 | -0.01176 | -0.70563
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.099958 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.012384 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.099907 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.9954 | 50 | -0.012435 | -0.62177
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.099488 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.1068 | 182 | -0.012854 | -2.3395
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.099488 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.1522 | 484 | -0.012854 | -6.2216
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.099307 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8961 | 150 | -0.013035 | -1.9553
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6785 | 209 | -0.013402 | -2.8011
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5159 | 126.5 | -0.013402 | -1.6954
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6361 | 249 | -0.013402 | -3.3372
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4912 | 197 | -0.013402 | -2.6403
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7084 | 37.5 | -0.013452 | -0.50447
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6307 | 107.5 | -0.013452 | -1.4461
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3501 | 135 | -0.013452 | -1.8161
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7679 | 119 | -0.013452 | -1.6008
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3834 | 105 | -0.013452 | -1.4125
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9606 | 80.5 | -0.013452 | -1.0829
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.1366 | 223.9 | -0.013502 | -3.0231
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.3289 | 225 | -0.013502 | -3.0379
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.259 | 224.6 | -0.013502 | -3.0325
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.626 | 226.7 | -0.013502 | -3.0609
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.098626 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7939 | 150 | -0.013716 | -2.0575
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.098626 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9612 | 101 | -0.013716 | -1.3854
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098364 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2955 | 125 | -0.013978 | -1.7473
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098364 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2955 | 125 | -0.013978 | -1.7473
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.0982 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2488 | 84 | -0.014142 | -1.188
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.097947 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6968 | 99 | -0.014395 | -1.4252
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.097947 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9748 | 61 | -0.014395 | -0.87812
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4487 | 0 | -0.014395 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4762 | 0 | -0.014395 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4762 | 0 | -0.014395 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.097919 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8066 | 141 | -0.014423 | -2.0337
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.097919 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7503 | 120 | -0.014423 | -1.7308
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.097848 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1644 | 63 | -0.014494 | -0.91315
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.4509 | 66 | -0.014601 | -0.9637
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.7441 | 69 | -0.014601 | -1.0075
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.7441 | 69 | -0.014601 | -1.0075
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5486 | 67 | -0.014601 | -0.9783
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5486 | 67 | -0.014601 | -0.9783
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3532 | 65 | -0.014601 | -0.9491
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6221 | 150 | -0.014861 | -2.2292
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.4458 | 220 | -0.014861 | -3.2695
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4962 | 200 | -0.014861 | -2.9723
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8829 | 121.9 | -0.014861 | -1.8116
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6836 | 120 | -0.014979 | -1.7975
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6856 | 233 | -0.014979 | -3.4902
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5712 | 170.2 | -0.014979 | -2.5495
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097258 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5064 | 180 | -0.015084 | -2.7152
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097258 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5064 | 180 | -0.015084 | -2.7152
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 1 | 6.8041 | 0 | -0.01514 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 1 | 7.1346 | 0 | -0.01514 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 1 | 6.843 | 0 | -0.01514 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.097166 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.8623 | 225 | -0.015176 | -3.4147
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.097002 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6402 | 120 | -0.01534 | -1.8409
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.09696 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6352 | 120 | -0.015382 | -1.8459
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.096445 | west | 8 | N | N | Nwest | Nwest | 1 | 2.4883 | 0 | -0.015897 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.096281 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6234 | 214.2 | -0.016061 | -3.4404
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.096223 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.4335 | 150 | -0.016119 | -2.4179
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.096074 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6554 | 100.5 | -0.016268 | -1.635
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.096043 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5705 | 58 | -0.016299 | -0.94537
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7174 | 70 | -0.016379 | -1.1466
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7174 | 70 | -0.016379 | -1.1466
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.9054 | 92.8 | -0.016379 | -1.52
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.677 | 80 | -0.016379 | -1.3104
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.677 | 80 | -0.016379 | -1.3104
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0357 | 115 | -0.016379 | -1.8836
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 19.9762 | 208.2 | -0.016395 | -3.4135
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.6341 | 142.1 | -0.016395 | -2.3298
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.7034 | 132.4 | -0.016395 | -2.1708
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.0488 | 136 | -0.016395 | -2.2298
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.1042 | 147 | -0.016395 | -2.4101
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.1489 | 210 | -0.016395 | -3.443
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7886 | 112.5 | -0.016443 | -1.8499
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3369 | 149.5 | -0.016443 | -2.4583
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8372 | 186 | -0.016443 | -3.0585
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5703 | 214.5 | -0.016443 | -3.5271
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.095289 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.62891 | 6.6 | -0.017053 | -0.11255
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.095289 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2684 | 34.3 | -0.017053 | -0.58493
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.094741 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0586 | 169.5 | -0.017601 | -2.9834
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.094604 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.096 | 149 | -0.017738 | -2.643
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.094301 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3005 | 35 | -0.018041 | -0.63145
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.094301 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.829 | 30 | -0.018041 | -0.54124
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.2771 | 151.5 | -0.018104 | -2.7428
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3524 | 152.3 | -0.018104 | -2.7573
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7272 | 177.5 | -0.018104 | -3.2135
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.218 | 66 | -0.01813 | -1.1966
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.1238 | 65 | -0.01813 | -1.1785
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3122 | 67 | -0.01813 | -1.2147
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3122 | 67 | -0.01813 | -1.2147
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3122 | 67 | -0.01813 | -1.2147
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.094212 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.01813 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.094212 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.01813 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1623 | 150.7 | -0.018365 | -2.7677
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1905 | 151 | -0.018365 | -2.7732
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6715 | 177.4 | -0.018365 | -3.258
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.092557 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.9226 | 615 | -0.019785 | -12.1681
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.092557 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 54.331 | 587 | -0.019785 | -11.6141
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.087809 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.42148 | 0 | -0.024533 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.18586 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -80.4791 | 433 | -0.024571 | -10.6392
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.1861 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -108.6818 | 584 | -0.024806 | -14.4867
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.1861 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -110.7289 | 595 | -0.024806 | -14.7595
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085165 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8132 | 80 | -0.027177 | -2.1742
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085165 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8132 | 80 | -0.027177 | -2.1742
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3336 | 75 | -0.027894 | -2.0921
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7558 | 80 | -0.027894 | -2.2316
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3779 | 40 | -0.027894 | -1.1158
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084291 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7433 | 80 | -0.028051 | -2.2441
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.08427 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7416 | 80 | -0.028072 | -2.2458
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.08418 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.627 | 150 | -0.028162 | -4.2244
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.08418 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.627 | 150 | -0.028162 | -4.2244
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.080601 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4481 | 80 | -0.031741 | -2.5393
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.080012 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1209 | 76.5 | -0.03233 | -2.4733
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.079394 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6691 | 84 | -0.032948 | -2.7677
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.073917 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.1294 | 827 | -0.038425 | -31.7779
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.073917 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 60.538 | 819 | -0.038425 | -31.4705
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.054 | 152.5 | -0.048897 | -7.4568
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.4234 | 149.5 | -0.048897 | -7.3101
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.8902 | 232.6 | -0.048897 | -11.3734
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 51.9036 | 855 | -0.051636 | -44.1492
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 51.9036 | 855 | -0.051636 | -44.1492
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.2455 | 152.3 | -0.051636 | -7.8642
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.288 | 153 | -0.051636 | -7.9004
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.060136 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.052206 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.2195 | 158 | -0.055286 | -8.7352
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6526 | 160 | -0.055286 | -8.8457
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.9013 | 175 | -0.055286 | -9.675
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.04495 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7425 | 150 | -0.067392 | -10.1089
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.029493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.6553 | 463 | -0.082849 | -38.3593
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.023678 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.40253 | 17 | -0.088664 | -1.5073
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.02359 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.75488 | 0 | -0.088752 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.020745 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.99576 | 48 | -0.091597 | -4.3967
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.020745 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.95427 | 46 | -0.091597 | -4.2135
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.020745 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1782 | 105 | -0.091597 | -9.6177
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1366 | 0 | -0.092001 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1732 | 0 | -0.092001 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1732 | 0 | -0.092001 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.7296 | 0 | -0.092001 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.26215 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -149.1656 | 569 | -0.10086 | -57.3899
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.26215 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -152.3115 | 581 | -0.10086 | -58.6002
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.11234 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.11234 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.056041 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.16838 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -15.8585 | 100 | -0.27093 | -27.0927

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: 3413 TEMP_SS_ to 3429 SANDOW_ C: 3414 TEMP_SS_ to 3429 SANDOW_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -15.8585 | 0 | -0.27093 | 0 | 0 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.056041 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | -0.16838 | 0 | 0 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.11234 | 0 | 0 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.11234 | 0 | 0 | 0 | Weighted Shift Factors
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.26215 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -149.1656 | 0 | -0.10086 | 0 | 0 | 0 | South | -0.16129
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.26215 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -152.3115 | 0 | -0.10086 | 0 | 0 | 0 | North | 0.11234
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1366 | 0 | -0.092001 | 0 | 0 | 0 |  | -0.27364
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1732 | 0 | -0.092001 | 0 | 0 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1732 | 0 | -0.092001 | 0 | 0 | 0 | Line Rating | 1072
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.020341 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.7296 | 0 | -0.092001 | 0 | 0 | 0 | Conc Gen | 2054.7
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.020745 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.99576 | 48 | -0.091597 | -4.3967 | 48 | 4.3967 | Weighted Imp. | 87.9497
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.020745 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.95427 | 46 | -0.091597 | -4.2135 | 94 | 8.6102 | PTDF | 0.042804
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.020745 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1782 | 105 | -0.091597 | -9.6177 | 199 | 18.2279
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.02359 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.75488 | 0 | -0.088752 | 0 | 199 | 18.2279 | Concentration | -0.15643
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0 | 199 | 18.2279
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0 | 199 | 18.2279
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.023678 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.40253 | 17 | -0.088664 | -1.5073 | 216 | 19.7352
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0 | 216 | 19.7352
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.023678 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.088664 | 0 | 216 | 19.7352
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.029493 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.6553 | 0 | -0.082849 | 0 | 216 | 19.7352
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.04495 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7425 | 0 | -0.067392 | 0 | 216 | 19.7352
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.2195 | 158 | -0.055286 | -8.7352 | 374 | 28.4704
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.6526 | 160 | -0.055286 | -8.8457 | 534 | 37.3161
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21658 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.9013 | 175 | -0.055286 | -9.675 | 709 | 46.9912
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.060136 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | -0.052206 | 0 | 709 | 46.9912
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 51.9036 | 0 | -0.051636 | 0 | 709 | 46.9912
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 51.9036 | 0 | -0.051636 | 0 | 709 | 46.9912
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.2455 | 0 | -0.051636 | 0 | 709 | 46.9912
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.060706 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.288 | 0 | -0.051636 | 0 | 709 | 46.9912
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.054 | 152.5 | -0.048897 | -7.4568 | 861.5 | 54.4479
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.4234 | 149.5 | -0.048897 | -7.3101 | 1011 | 61.758
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.21019 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.8902 | 232.6 | -0.048897 | -11.3734 | 1243.6 | 73.1314
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.073917 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.1294 | 0 | -0.038425 | 0 | 1243.6 | 73.1314
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.073917 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 60.538 | 0 | -0.038425 | 0 | 1243.6 | 73.1314
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.079394 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6691 | 0 | -0.032948 | 0 | 1243.6 | 73.1314
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.080012 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1209 | 0 | -0.03233 | 0 | 1243.6 | 73.1314
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.080601 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4481 | 0 | -0.031741 | 0 | 1243.6 | 73.1314
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.08418 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.627 | 0 | -0.028162 | 0 | 1243.6 | 73.1314
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.08418 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.627 | 0 | -0.028162 | 0 | 1243.6 | 73.1314
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.08427 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7416 | 0 | -0.028072 | 0 | 1243.6 | 73.1314
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084291 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7433 | 0 | -0.028051 | 0 | 1243.6 | 73.1314
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3336 | 0 | -0.027894 | 0 | 1243.6 | 73.1314
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7558 | 0 | -0.027894 | 0 | 1243.6 | 73.1314
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.084448 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3779 | 0 | -0.027894 | 0 | 1243.6 | 73.1314
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085165 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8132 | 0 | -0.027177 | 0 | 1243.6 | 73.1314
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085165 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8132 | 0 | -0.027177 | 0 | 1243.6 | 73.1314
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.1861 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -108.6818 | 0 | -0.024806 | 0 | 1243.6 | 73.1314
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.1861 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -110.7289 | 0 | -0.024806 | 0 | 1243.6 | 73.1314
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.18586 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -80.4791 | 0 | -0.024571 | 0 | 1243.6 | 73.1314
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.087809 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.42148 | 0 | -0.024533 | 0 | 1243.6 | 73.1314
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.092557 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 56.9226 | 0 | -0.019785 | 0 | 1243.6 | 73.1314
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.092557 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 54.331 | 0 | -0.019785 | 0 | 1243.6 | 73.1314
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1623 | 150.7 | -0.018365 | -2.7677 | 1394.3 | 75.8991
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1905 | 151 | -0.018365 | -2.7732 | 1545.3 | 78.6723
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.093977 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6715 | 177.4 | -0.018365 | -3.258 | 1722.7 | 81.9303
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.218 | 66 | -0.01813 | -1.1966 | 1788.7 | 83.127
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.1238 | 65 | -0.01813 | -1.1785 | 1853.7 | 84.3054
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3122 | 67 | -0.01813 | -1.2147 | 1920.7 | 85.5202
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3122 | 67 | -0.01813 | -1.2147 | 1987.7 | 86.7349
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.094212 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3122 | 67 | -0.01813 | -1.2147 | 2054.7 | 87.9497
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.094212 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.01813 | 0 | 2054.7 | 87.9497
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.094212 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.01813 | 0 | 2054.7 | 87.9497
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.2771 | 151.5 | -0.018104 | -2.7428
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3524 | 152.3 | -0.018104 | -2.7573
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.094238 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7272 | 177.5 | -0.018104 | -3.2135
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.094301 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3005 | 0 | -0.018041 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.094301 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.829 | 0 | -0.018041 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.094604 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.096 | 0 | -0.017738 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.094741 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0586 | 0 | -0.017601 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.095289 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.62891 | 0 | -0.017053 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.095289 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2684 | 0 | -0.017053 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7886 | 0 | -0.016443 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3369 | 0 | -0.016443 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8372 | 0 | -0.016443 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.095899 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.5703 | 0 | -0.016443 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 19.9762 | 208.2 | -0.016395 | -3.4135
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.6341 | 142.1 | -0.016395 | -2.3298
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.7034 | 132.4 | -0.016395 | -2.1708
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.0488 | 136 | -0.016395 | -2.2298
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.1042 | 147 | -0.016395 | -2.4101
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.095947 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.1489 | 210 | -0.016395 | -3.443
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7174 | 70 | -0.016379 | -1.1466
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7174 | 70 | -0.016379 | -1.1466
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.9054 | 92.8 | -0.016379 | -1.52
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.677 | 80 | -0.016379 | -1.3104
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.677 | 80 | -0.016379 | -1.3104
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.095963 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0357 | 115 | -0.016379 | -1.8836
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.096043 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5705 | 0 | -0.016299 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.096074 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6554 | 0 | -0.016268 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.096223 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.4335 | 0 | -0.016119 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.096281 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6234 | 0 | -0.016061 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.096445 | west | 8 | N | N | Nwest | Nwest | 1 | 2.4883 | 0 | -0.015897 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.09696 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6352 | 0 | -0.015382 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.097002 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6402 | 0 | -0.01534 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.097166 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.8623 | 0 | -0.015176 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 1 | 6.8041 | 0 | -0.01514 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 1 | 7.1346 | 0 | -0.01514 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.097202 | west | 8 | N | N | Nwest | Nwest | 1 | 6.843 | 0 | -0.01514 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097258 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5064 | 0 | -0.015084 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097258 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5064 | 0 | -0.015084 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6836 | 0 | -0.014979 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6856 | 0 | -0.014979 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.097363 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.5712 | 0 | -0.014979 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6221 | 0 | -0.014861 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.4458 | 0 | -0.014861 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4962 | 0 | -0.014861 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.097481 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8829 | 0 | -0.014861 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.4509 | 66 | -0.014601 | -0.9637
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.7441 | 69 | -0.014601 | -1.0075
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.7441 | 69 | -0.014601 | -1.0075
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5486 | 67 | -0.014601 | -0.9783
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5486 | 67 | -0.014601 | -0.9783
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.097741 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3532 | 65 | -0.014601 | -0.9491
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.097848 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1644 | 0 | -0.014494 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.097919 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8066 | 0 | -0.014423 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.097919 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7503 | 0 | -0.014423 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.097947 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6968 | 0 | -0.014395 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.097947 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9748 | 0 | -0.014395 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4487 | 0 | -0.014395 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4762 | 0 | -0.014395 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.097947 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4762 | 0 | -0.014395 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.0982 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2488 | 0 | -0.014142 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098364 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2955 | 0 | -0.013978 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098364 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.2955 | 0 | -0.013978 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.098626 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.7939 | 0 | -0.013716 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.098626 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9612 | 0 | -0.013716 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.1366 | 223.9 | -0.013502 | -3.0231
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.3289 | 225 | -0.013502 | -3.0379
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.259 | 224.6 | -0.013502 | -3.0325
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.1748 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.626 | 226.7 | -0.013502 | -3.0609
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7084 | 0 | -0.013452 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6307 | 0 | -0.013452 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3501 | 0 | -0.013452 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7679 | 0 | -0.013452 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.3834 | 0 | -0.013452 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.09889 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9606 | 0 | -0.013452 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6785 | 0 | -0.013402 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5159 | 0 | -0.013402 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6361 | 0 | -0.013402 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.09894 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.4912 | 0 | -0.013402 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.099307 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8961 | 0 | -0.013035 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.099488 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.1068 | 182 | -0.012854 | -2.3395
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.099488 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.1522 | 484 | -0.012854 | -6.2216
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.099907 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 4.9954 | 0 | -0.012435 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.099958 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | -0.012384 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10058 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0349 | 0 | -0.01176 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.8924 | 0 | -0.011718 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.0811 | 0 | -0.011718 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.5905 | 0 | -0.011718 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.10062 | north | 1 | N | N | Nnorth | Nnorth | 1 | 40.149 | 0 | -0.011718 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.4302 | 0 | -0.011157 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.4421 | 0 | -0.011157 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.10118 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 78.9243 | 0 | -0.011157 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10193 | west | 6 | Y | N | Ywest | Nwest | 1 | 40.7724 | 0 | -0.010411 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.10194 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.0569 | 0 | -0.010406 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.1029 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.979 | 0 | -0.0094395 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.1037 | west | 4 | Y | N | Ywest | Nwest | 1 | 67.3726 | 0 | -0.0086445 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.9728 | 161 | -0.0069215 | -1.1144
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.289 | 164 | -0.0069215 | -1.1351
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.289 | 164 | -0.0069215 | -1.1351
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.6443 | 414 | -0.0069215 | -2.8655
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0782 | 162 | -0.0069215 | -1.1213
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.9728 | 161 | -0.0069215 | -1.1144
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1836 | 163 | -0.0069215 | -1.1282
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.10542 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.1172 | 409 | -0.0069215 | -2.8309
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8669 | 142 | -0.0067839 | -0.96332
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.3712 | 145 | -0.0067839 | -0.98367
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.3796 | 151 | -0.0067839 | -1.0244
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.16808 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.7423 | 290 | -0.0067839 | -1.9673
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.10596 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 38.7825 | 366 | -0.0063795 | -2.3349
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.16764 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.382 | 50 | -0.0063469 | -0.31735
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.10601 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.7467 | 224 | -0.0063305 | -1.418
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.1204 | 132 | -0.0062859 | -0.82974
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.4556 | 134 | -0.0062859 | -0.84231
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.16758 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -54.128 | 323 | -0.0062859 | -2.0304
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1235 | 20 | -0.0061695 | -0.12339
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1235 | 20 | -0.0061695 | -0.12339
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1235 | 20 | -0.0061695 | -0.12339
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.10617 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.8049 | 17 | -0.0061695 | -0.10488
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.10632 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.7282 | 242 | -0.0060275 | -1.4586
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1276 | 20 | -0.0059615 | -0.11923
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.6595 | 25 | -0.0059615 | -0.14904
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.10638 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3616 | 41 | -0.0059615 | -0.24442
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.10643 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 41.2945 | 388 | -0.0059135 | -2.2944
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.10643 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.8109 | 515 | -0.0059135 | -3.0454
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 59.4432 | 0 | -0.0058135 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.6803 | 0 | -0.0058135 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.10653 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 86.0754 | 0 | -0.0058135 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4171 | 79 | -0.0057965 | -0.45792
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.2939 | 106 | -0.0057965 | -0.61443
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.10655 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.5557 | 146 | -0.0057965 | -0.84628
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.10655 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.0975 | 76 | -0.0057965 | -0.44053
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.10658 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.2633 | 40 | -0.0057595 | -0.23038
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | 1 | 7.9947 | 0 | -0.0057465 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | 1 | 8.485 | 0 | -0.0057465 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.1066 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.4231 | 0 | -0.0057465 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0688 | 160 | -0.0056625 | -0.90599
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6421 | 156 | -0.0056625 | -0.88334
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9093 | 196 | -0.0056625 | -1.1098
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6421 | 156 | -0.0056625 | -0.88334
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7488 | 157 | -0.0056625 | -0.88901
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.10668 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.1226 | 198 | -0.0056625 | -1.1212
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.10677 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 39.5056 | 370 | -0.0055705 | -2.0611
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.9481 | 0 | -0.0055705 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.0549 | 0 | -0.0055705 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 32.9925 | 0 | -0.0055705 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.2684 | 0 | -0.0055705 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.3752 | 0 | -0.0055705 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.10677 | north | 1 | N | N | Nnorth | Nnorth | 1 | 33.0993 | 0 | -0.0055705 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.10684 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0055055 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.10684 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0055055 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.10693 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 18.1774 | 170 | -0.0054165 | -0.9208
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.10693 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 55.6015 | 520 | -0.0054165 | -2.8166
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.10706 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2824 | 0 | -0.0052825 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.10706 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2824 | 0 | -0.0052825 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.1076 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | -0.0047395 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.10764 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0047035 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.0577 | 204 | -0.0042165 | -0.86016
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7333 | 201 | -0.0042165 | -0.84751
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.10813 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.1665 | 242 | -0.0042165 | -1.0204
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.10851 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.8039 | 118 | -0.0038345 | -0.45247
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.10851 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.4784 | 115 | -0.0038345 | -0.44096
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.10851 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.3304 | 556 | -0.0038345 | -2.132
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.10852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.5111 | 60 | -0.0038235 | -0.22941
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.10852 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.8367 | 63 | -0.0038235 | -0.24088
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.10866 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 12.2238 | 0 | -0.0036865 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.10891 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.0694 | 0 | -0.0034305 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.10892 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.307 | 0 | -0.0034255 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.10892 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.307 | 0 | -0.0034255 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.16465 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.98787 | 0 | -0.0033519 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39297 | 0 | -0.0024459 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39297 | 0 | -0.0024459 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.16374 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45847 | 0 | -0.0024459 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.6662 | 288 | -0.0023905 | -0.68845
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1629 | 147 | -0.0023905 | -0.3514
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.10995 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.1629 | 147 | -0.0023905 | -0.3514
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.11023 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0021115 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.11023 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0021115 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.11023 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.0021115 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.648 | 196 | -0.0018935 | -0.37112
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11045 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2598 | 111 | -0.0018935 | -0.21017
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.16316 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65262 | 0 | -0.0018629 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0012 | 18 | -0.0011665 | -0.020996
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0012 | 18 | -0.0011665 | -0.020996
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11118 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.2247 | 38 | -0.0011665 | -0.044326
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11145 | north | 3 | N | N | Nnorth | Nnorth | 1 | 128.95 | 0 | -0.00089047 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11145 | north | 3 | N | N | Nnorth | Nnorth | 1 | 129.0614 | 0 | -0.00089047 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.2642 | 217.3 | -0.00068047 | -0.14787
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.8907 | 205 | -0.00068047 | -0.1395
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11166 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.4167 | 272.4 | -0.00068047 | -0.18536
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8097 | 147 | -0.00067793 | -0.099655
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.352 | 138 | -0.00067793 | -0.093554
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.6759 | 140 | -0.00067793 | -0.09491
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8097 | 147 | -0.00067793 | -0.099655
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.4787 | 182 | -0.00067793 | -0.12338
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.16197 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.0703 | 198 | -0.00067793 | -0.13423
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.11172 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.703 | 0 | -0.00062647 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11174 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.6082 | 435 | -0.00059947 | -0.26077
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.11193 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | -0.00041247 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11197 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 44.2297 | 395 | -0.00036847 | -0.14554
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11197 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.7087 | 435 | -0.00036847 | -0.16028
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11249 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.2118 | 73 | 0.00014853 | 0.010843
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11249 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.3864 | 119 | 0.00014853 | 0.017676
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11249 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.0607 | 205 | 0.00014853 | 0.03045
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11249 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.4741 | 102 | 0.00014853 | 0.015151
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11249 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.7991 | 96 | 0.00014853 | 0.014259
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.9743 | 70 | 0.0015755 | 0.11029
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8603 | 69 | 0.0015755 | 0.10871
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8603 | 69 | 0.0015755 | 0.10871
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11392 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7464 | 68 | 0.0015755 | 0.10714
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.15961 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38307 | 0 | 0.0016811 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.15961 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38307 | 0 | 0.0016811 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8081 | 49 | 0.0019441 | 0.09526
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3301 | 46 | 0.0019441 | 0.089427
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3301 | 46 | 0.0019441 | 0.089427
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.4894 | 47 | 0.0019441 | 0.091371
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.15935 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.5397 | 154 | 0.0019441 | 0.29939
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.15935 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.5837 | 148 | 0.0019441 | 0.28772
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6488 | 48 | 0.0019441 | 0.093316
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.15935 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6488 | 48 | 0.0019441 | 0.093316
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.0787 | 0 | 0.0027081 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.2059 | 0 | 0.0027081 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -29.1796 | 0 | 0.0027081 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.523 | 0 | 0.0027081 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.15859 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.2373 | 0 | 0.0027081 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.11588 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0773 | 216.4 | 0.0035415 | 0.76639
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.11588 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0425 | 216.1 | 0.0035415 | 0.76533
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0041101 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0041101 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.15718 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.0041101 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.0891 | 224 | 0.0041265 | 0.92434
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.322 | 226 | 0.0041265 | 0.9326
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.6914 | 212 | 0.0041265 | 0.87483
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11647 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.575 | 211 | 0.0041265 | 0.8707
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.5967 | 42 | 0.0042281 | 0.17758
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9109 | 44 | 0.0042281 | 0.18604
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9109 | 44 | 0.0042281 | 0.18604
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.15707 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3821 | 47 | 0.0042281 | 0.19872
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.15655 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.3768 | 0 | 0.0047441 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.15655 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.5333 | 0 | 0.0047441 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.15633 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -64.4071 | 412 | 0.0049651 | 2.0456
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.15633 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -62.5312 | 400 | 0.0049651 | 1.986
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11743 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7287 | 168 | 0.0050905 | 0.85521
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11743 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.569 | 90 | 0.0050905 | 0.45815
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.15615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -32.6347 | 209 | 0.0051461 | 1.0755
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.15615 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -33.7278 | 216 | 0.0051461 | 1.1116
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1828 | 46 | 0.0051461 | 0.23672
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3389 | 47 | 0.0051461 | 0.24187
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1828 | 46 | 0.0051461 | 0.23672
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.15615 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1828 | 46 | 0.0051461 | 0.23672
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.1961 | 155 | 0.0051891 | 0.80431
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.5377 | 170 | 0.0051891 | 0.88214
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.1561 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.1961 | 155 | 0.0051891 | 0.80431
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.1561 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.5323 | 407 | 0.0051941 | 2.114
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.15569 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.0051 | 0 | 0.0056061 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.15569 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -116.7652 | 0 | 0.0056061 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.15513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -8.9977 | 58 | 0.0061611 | 0.35734
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.15513 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.8067 | 89 | 0.0061611 | 0.54834
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8258 | 44 | 0.0061611 | 0.27109
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8258 | 44 | 0.0061611 | 0.27109
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6707 | 43 | 0.0061611 | 0.26493
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.15513 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9809 | 45 | 0.0061611 | 0.27725
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.15418 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.7949 | 310 | 0.0071161 | 2.206
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.15418 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.6751 | 413 | 0.0071161 | 2.9389
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.1514 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8168 | 0 | 0.0098921 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.14841 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -58.7704 | 0 | 0.012883 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.14694 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1755 | 0 | 0.01435 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.14694 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1755 | 0 | 0.01435 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13943 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3463 | 24 | 0.021863 | 0.52471
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13943 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.3463 | 24 | 0.021863 | 0.52471
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.13943 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.2069 | 23 | 0.021863 | 0.50285
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.13921 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9207 | 100 | 0.022086 | 2.2086
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.13921 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9207 | 100 | 0.022086 | 2.2086
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.13921 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022086 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.1392 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.022098 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.13798 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.023316 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13784 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1579 | 8.4 | 0.023451 | 0.19699
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.1366 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.9201 | 0 | 0.024695 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.13612 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.025175 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.13498 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.026317 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.618 | 0 | 0.026458 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4832 | 0 | 0.026458 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.13484 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.618 | 0 | 0.026458 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.5569 | 146.5 | 0.027799 | 4.0726
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.7438 | 147.9 | 0.027799 | 4.1115
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.13349 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.0945 | 173 | 0.027799 | 4.8092
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.589 | 207 | 0.028013 | 5.7987
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.8818 | 216.7 | 0.028013 | 6.0704
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.2538 | 242 | 0.028013 | 6.7792
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.1917 | 144 | 0.028017 | 4.0345
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.1917 | 144 | 0.028017 | 4.0345
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.13328 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.7902 | 171 | 0.028017 | 4.7909
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.13306 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.028235 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0562 | 38 | 0.028235 | 1.0729
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.568 | 19.3 | 0.028235 | 0.54494
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.13306 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.9959 | 15 | 0.028235 | 0.42353
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.13306 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.2537 | 47 | 0.028235 | 1.327
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5002 | 0 | 0.028312 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4522 | 0 | 0.028312 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.0533 | 0 | 0.028312 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.5266 | 0 | 0.028312 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5002 | 0 | 0.028312 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7873 | 0 | 0.028312 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7182 | 0 | 0.028312 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9256 | 0 | 0.028312 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.6812 | 0 | 0.028312 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.649 | 0 | 0.028312 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.314 | 0 | 0.028312 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13298 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.649 | 0 | 0.028312 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.13279 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8508 | 0 | 0.028507 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.1322 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0235 | 0 | 0.029096 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.13219 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0232 | 0 | 0.029103 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.13207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3018 | 0 | 0.029223 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.13207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3018 | 0 | 0.029223 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.13204 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.1024 | 334 | 0.02925 | 9.7695
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.13204 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.8946 | 340 | 0.02925 | 9.945
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7677 | 180 | 0.02925 | 5.265
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7677 | 180 | 0.02925 | 5.265
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13181 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7249 | 180 | 0.029488 | 5.3079
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.5433 | 0 | 0.029511 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.5828 | 0 | 0.029511 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.13178 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.1626 | 0 | 0.029511 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.13177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.274 | 336 | 0.029525 | 9.9204
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7182 | 180 | 0.029525 | 5.3145
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 0 | 0.03026 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 0 | 0.03026 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 0 | 0.03026 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.0965 | 0 | 0.03026 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 0 | 0.03026 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 0 | 0.03026 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2758 | 0 | 0.03026 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.13103 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9655 | 0 | 0.03026 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.13074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -18.8263 | 144 | 0.030555 | 4.3999
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.13074 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.5787 | 188 | 0.030555 | 5.7444
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.626 | 0 | 0.030749 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.9732 | 0 | 0.030749 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -13.0544 | 0 | 0.030749 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.9289 | 0 | 0.030749 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.19 | 0 | 0.030749 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.13054 | south | 8 | N | N | Nsouth | Nsouth | -1 | -16.5791 | 0 | 0.030749 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.13054 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5665 | 0 | 0.030749 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.12948 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.4523 | 0 | 0.03181 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1721 | 47.7 | 0.031898 | 1.5215
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8264 | 37.3 | 0.031898 | 1.1898
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9522 | 46 | 0.031898 | 1.4673
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.1294 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.211 | 48 | 0.031898 | 1.5311
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5279 | 0 | 0.031925 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.3985 | 0 | 0.031925 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.12937 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5279 | 0 | 0.031925 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.1284 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8249 | 22 | 0.032888 | 0.72354
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4125 | 11 | 0.032888 | 0.36177
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.1284 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4125 | 11 | 0.032888 | 0.36177
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.12732 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9097 | 0 | 0.033978 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.12732 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9282 | 0 | 0.033978 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.12653 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0123 | 0 | 0.034759 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5299 | 0 | 0.035226 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.88247 | 0 | 0.035226 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9166 | 0 | 0.035226 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.891 | 0 | 0.035226 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.88247 | 0 | 0.035226 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.891 | 0 | 0.035226 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9166 | 0 | 0.035226 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.12607 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9166 | 0 | 0.035226 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.14766 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.215 | 0 | 0.035322 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.14766 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.215 | 0 | 0.035322 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.12301 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9043 | 0 | 0.038286 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6438 | 0 | 0.03922 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.8879 | 0 | 0.03922 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6438 | 0 | 0.03922 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.7658 | 0 | 0.03922 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.5705 | 0 | 0.03922 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0518 | 0 | 0.03922 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6154 | 0 | 0.03922 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.418 | 0 | 0.03922 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3224 | 0 | 0.03922 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.12207 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.0334 | 0 | 0.03922 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.15555 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3319 | 150 | 0.043204 | 6.4805
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.15555 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.4437 | 80 | 0.043204 | 3.4563
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.16306 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.579 | 255 | 0.050713 | 12.9317
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.16306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.2952 | 149 | 0.050713 | 7.5562
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.16306 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.9474 | 153 | 0.050713 | 7.759
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.11043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9877 | 0 | 0.050867 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.11043 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9877 | 0 | 0.050867 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.16815 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055812 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.16815 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.055812 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.10207 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -43.0748 | 422 | 0.05922 | 24.9909
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.10185 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8518 | 0 | 0.059443 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.10185 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9537 | 0 | 0.059443 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.10115 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.060141 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.17291 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.060567 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.17291 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 136.0794 | 787 | 0.060567 | 47.6659
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.096644 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.57986 | 0 | 0.064649 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.088576 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.0718 | 0 | 0.072717 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.088576 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -117.6289 | 0 | 0.072717 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.66 | 76 | 0.073661 | 5.5982
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.66 | 76 | 0.073661 | 5.5982
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2014 | 105 | 0.073661 | 7.7344
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4848 | 74 | 0.073661 | 5.4509
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4848 | 74 | 0.073661 | 5.4509
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.087632 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.9385 | 102 | 0.073661 | 7.5134
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.083293 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.4973 | 66 | 0.078 | 5.148
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.082934 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1362 | 0 | 0.078359 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3978 | 0 | 0.083638 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.3978 | 0 | 0.083638 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.077655 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1648 | 0 | 0.083638 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.077259 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5495 | 0 | 0.084034 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.077259 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9315 | 0 | 0.084034 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.077259 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.084034 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3507 | 0 | 0.09112 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0104 | 0 | 0.09112 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1578 | 0 | 0.09112 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0875 | 0 | 0.09112 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0349 | 0 | 0.09112 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1752 | 0 | 0.09112 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5086 | 0 | 0.09112 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2631 | 0 | 0.09112 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5963 | 0 | 0.09112 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9121 | 0 | 0.09112 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4209 | 0 | 0.09112 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0525 | 0 | 0.09112 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5472 | 0 | 0.09112 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.0875 | 0 | 0.09112 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8068 | 0 | 0.09112 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2278 | 0 | 0.09112 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3331 | 0 | 0.09112 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6138 | 0 | 0.09112 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6138 | 0 | 0.09112 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.070173 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.9996 | 0 | 0.09112 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.066819 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7441 | 0 | 0.094474 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.066819 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66819 | 0 | 0.094474 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.122 | 0 | 0.097131 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.122 | 0 | 0.097131 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.6353 | 0 | 0.097131 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.064162 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0257 | 0 | 0.097131 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.054812 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5268 | 0 | 0.10648 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -35.5303 | 0 | 0.10672 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -30.782 | 0 | 0.10672 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.054578 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.7468 | 0 | 0.10672 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8832 | 0 | 0.1068 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8832 | 0 | 0.1068 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.054498 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.352 | 0 | 0.1068 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.053408 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7625 | 0 | 0.10789 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.5332 | 161 | 0.10829 | 17.435
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.7982 | 166 | 0.10829 | 17.9765
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.053001 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.1442 | 248 | 0.10829 | 26.8564
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.053001 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -28.9385 | 546 | 0.10829 | 59.1275
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.053001 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -34.0796 | 0 | 0.10829 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.053001 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.68901 | 13 | 0.10829 | 1.4078
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8201 | 0 | 0.11324 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.4645 | 0 | 0.11324 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9355 | 0 | 0.11324 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.048057 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9018 | 0 | 0.11324 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.048056 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5378 | 0 | 0.11324 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.048056 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4417 | 0 | 0.11324 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4006 | 0 | 0.11326 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2037 | 0 | 0.11326 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5456 | 0 | 0.11326 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3583 | 0 | 0.11326 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3728 | 0 | 0.11326 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3151 | 0 | 0.11326 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.611 | 0 | 0.11326 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.048031 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.7196 | 0 | 0.11326 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.048031 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9212 | 0 | 0.11326 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.045996 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2998 | 50 | 0.1153 | 5.7649
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.0444 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.11689 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8714 | 0 | 0.11875 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7268 | 0 | 0.11875 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7012 | 0 | 0.11875 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3186 | 0 | 0.11875 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.042543 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51902 | 0 | 0.11875 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.718 | 0 | 0.11948 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.509 | 0 | 0.11948 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.718 | 0 | 0.11948 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.041816 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.718 | 0 | 0.11948 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8742 | 46 | 0.12055 | 5.5453
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8742 | 46 | 0.12055 | 5.5453
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8742 | 46 | 0.12055 | 5.5453
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2409 | 55 | 0.12055 | 6.6303
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2409 | 55 | 0.12055 | 6.6303
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.040743 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2001 | 54 | 0.12055 | 6.5097
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.040464 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.1562 | 0 | 0.12083 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.040464 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2371 | 0 | 0.12083 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.5429 | 0 | 0.1212 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2983 | 0 | 0.1212 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3143 | 0 | 0.1212 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2943 | 0 | 0.1212 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.040091 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.7845 | 0 | 0.1212 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039788 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3926 | 0 | 0.12151 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039464 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47357 | 12 | 0.12183 | 1.4619
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039464 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.12183 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039445 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.6662 | 169 | 0.12185 | 20.5923
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.03942 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.5043 | 165 | 0.12187 | 20.1091
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.0394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8706 | 0 | 0.12189 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.0394 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5649 | 0 | 0.12189 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039333 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.3779 | 213 | 0.12196 | 25.9775
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039325 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63706 | 0 | 0.12197 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5164 | 0 | 0.12197 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.485 | 0 | 0.12197 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2477 | 0 | 0.12197 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.039319 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8939 | 0 | 0.12197 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039308 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.9622 | 228 | 0.12199 | 27.8126
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0735 | 0 | 0.122 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2325 | 0 | 0.122 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039297 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1696 | 0 | 0.122 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7576 | 0 | 0.12245 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7964 | 0 | 0.12245 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5147 | 0 | 0.12245 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.038839 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1652 | 0 | 0.12245 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.038116 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1838 | 0 | 0.12318 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 42 | 0.12324 | 5.176
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.5983 | 42 | 0.12324 | 5.176
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4461 | 38 | 0.12324 | 4.683
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.038055 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4461 | 38 | 0.12324 | 4.683
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.037872 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5519 | 0 | 0.12342 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.037872 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1127 | 0 | 0.12342 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.818 | 104 | 0.12458 | 12.9564
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.818 | 104 | 0.12458 | 12.9564
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9457 | 53 | 0.12458 | 6.6028
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0926 | 57 | 0.12458 | 7.1011
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9824 | 54 | 0.12458 | 6.7274
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1293 | 58 | 0.12458 | 7.2257
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.036712 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1293 | 58 | 0.12458 | 7.2257
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.036254 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.6467 | 735 | 0.12504 | 91.9037
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2225 | 0 | 0.12534 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2476 | 0 | 0.12534 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1757 | 0 | 0.12534 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6503 | 0 | 0.12534 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.6364 | 0 | 0.12534 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73348 | 0 | 0.12534 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.7155 | 0 | 0.12534 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2584 | 0 | 0.12534 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64719 | 0 | 0.12534 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0706 | 0 | 0.12534 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.035955 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3213 | 0 | 0.12534 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.03558 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42696 | 12 | 0.12571 | 1.5086
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.035089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17544 | 0 | 0.1262 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.035089 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73687 | 0 | 0.1262 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2803 | 0 | 0.12621 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3153 | 0 | 0.12621 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4557 | 0 | 0.12621 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2101 | 0 | 0.12621 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.175 | 0 | 0.12621 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6484 | 0 | 0.12621 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.035081 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0698 | 0 | 0.12621 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.035058 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.4207 | 0 | 0.12624 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.035024 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.0228 | 743 | 0.12627 | 93.8179
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.0348 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.4636 | 0 | 0.12649 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9603 | 172 | 0.12664 | 21.7821
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9603 | 172 | 0.12664 | 21.7821
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.034653 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9603 | 172 | 0.12664 | 21.7821
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4999 | 0 | 0.12751 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4526 | 0 | 0.12751 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3681 | 0 | 0.12751 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.033783 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.0944 | 0 | 0.12751 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.033483 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.3262 | 398 | 0.12781 | 50.8684
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9446 | 59 | 0.12833 | 7.5717
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9446 | 59 | 0.12833 | 7.5717
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.03296 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8458 | 56 | 0.12833 | 7.1867
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8139 | 0 | 0.13347 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3409 | 0 | 0.13347 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2852 | 0 | 0.13347 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027826 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2852 | 0 | 0.13347 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.027826 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5078 | 0 | 0.13347 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | 0.16129 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16129 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | 0.16129 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown