## test results
CRE test for: |  | Singleton - Roans Prairie [ 44645 - 40600] | [5 empty] | PASS
Line Rating: |  | 1710
Direction |  | North | → | Houston |  | N-H
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Singleton - Roans Prairie [ 44645 - 40600]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.12411
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.032486
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.10571
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.14851
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | Singleton - Roans Prairie [ 44645 - 40600]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.11649
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.034516
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.10595
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.15269
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | Singleton - Roans Prairie [ 44645 - 40600]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.15863
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.018158
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.2768
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.13844
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | 0.11602
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.25839
PTDF tests
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.2768 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.2768 | 0.15863
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.31243
[6 empty] | Concentration |  | 1.1287 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.29141
[6 empty] | Concentration |  | 1.0528 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 45.2915
| Percent of line rating => | [6 empty] | 2.649% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.2426
[7 empty] | B1(N-S) | 0.031236 | 0.22835 | 0.19712 | 0.031236
[7 empty] | B2 (N-W) | 0.0035687 | 0.026133 | 0.022564 | 0.0035687
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B4 (S-W) | -0.027259 | -0.19929 | -0.17203 | -0.027259
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.025633 | 0.11854 | 0.14417 | -0.025633
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.0036173 | 0.31747 | 0.32109 | -0.0036173
[7 empty] | test | 0 | 0.34396 | 0.34396 | 0
[7 empty] | B1 | 9.081%
Deployment Error Percent | [6 empty] | B2 | 1.038%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | 0%
[7 empty] | B4 | -7.925%
[7 empty] | B5 | -7.452%
[7 empty] | B6 | -1.052%
[7 empty] | Max Abs Error | 9.081% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N- H
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: Singleton - Roans Prairie [ 44645 - 40600] C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: Singleton - Roans Prairie [ 44645 - 40600] C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.090878 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 23.1739
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.090878 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 13.5408
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.096462 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.4469
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.096462 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.4469
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.090878 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 13.9043
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.09258 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 13.887
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.09258 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 7.4064
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11112 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 8.1116
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11112 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 13.223
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11112 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 22.7792
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11112 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 11.334
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11112 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 10.6673
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.11228 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.3474
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.11228 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.3474
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11184 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 18.79
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11184 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 10.0661
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0385
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0385
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 4.3036
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 32.9988
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.8431
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.8431
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.11616 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 13.068
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 4.8189
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 9.5171
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 12.7697
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 17.5885
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.12047 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 9.1556
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.11735 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 7.041
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.11735 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 7.393
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.4124
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 3.0155
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 4.9454
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.1782 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 82.5071
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 6.9073
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 6.8026
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.012
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.012
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 7.012
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10466 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 11.9308
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.10466 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 53.8978
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 7.0448
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 7.365
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 7.365
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.1515
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 7.1515
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 6.938
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 7.4513
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 7.8132
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 7.4939
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 15.9923
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 23.4553
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10684 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 10.577
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10684 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 6.5171
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.10682 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 15.0618
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 2.6709
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.8825
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.8825
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.10682 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 12.8185
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.10594 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 2.7331
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.10575 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 10.628
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.10626 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 12.7513
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.10573 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 6.1326
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.10587 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 22.6782
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.10704 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 16.0561
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.1052 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.69431
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.1052 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 3.6083
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.10704 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 10.8111
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.10628 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 12.7541
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.11224 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 41.0787
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.11159 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 27.0048
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.10949 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 43.798
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.1095 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 25.8415
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.11016 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 18.1757
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 23.2431
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 22.9013
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 27.5728
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.2472
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.2472
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.2472
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 1.9101
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.11214 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 13.4567
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.10759 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 6.4553
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 9.0184
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 9.5716
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 10.6297
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 19.2282
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 18.7475
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 23.5545
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 18.7475
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 18.8676
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 23.7948
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.11986 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 20.376
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.11986 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 62.3267
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12008 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 44.4296
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 67.1525
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 69.6798
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 97.2388
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11574 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 12.9624
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11574 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 11.5736
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.11574 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 43.7482
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 24.7405
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 23.3401
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 31.0138
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.11411 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 87.8632
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 7.8811
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.7685
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.7685
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 7.6559
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11357 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 131.4005
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11357 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 131.5141
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 25.6771
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 25.9064
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.11579 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 25.057
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.11579 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 25.0222
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 24.3016
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 24.1869
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11599 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 45.8157
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.11623 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 50.5609
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11599 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 50.4552
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.11915 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 16.4431
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.11944 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 14.0938
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.11944 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 13.7355
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.11944 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 66.4081
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.12076 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 46.8557
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.12076 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 62.1924
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 98.0763
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 99.3257
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 97.4516
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.12599 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 22.9307
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.12599 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 60.9806
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.12167 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 27.2543
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.12593 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 6.2963
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.12587 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 5.2867
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.13244 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 81.4506
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.13244 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 77.7423
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.088923 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 47.7517
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.088923 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 69.9824
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.087612 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 6.5709
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.087612 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 19.4499
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.029157 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | 16.5903
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.036971 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -7.7269
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.036971 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -7.9857
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.036794 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -14.9752
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.7007
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -1.7376
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.7007
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -1.7007
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.036862 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -15.6295
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.036862 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -15.6663
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.036821 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -2.1356
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.036821 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -3.2771
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.6201
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -1.6201
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -1.5833
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -1.6569
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.036837 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -15.1768
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.036837 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -14.7348
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.03883 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -21.2012
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.03883 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -29.1225
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -2.258
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -3.5166
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -5.5896
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -5.8847
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -6.4542
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -5.8847
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.063137 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.389
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.063137 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.69451
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.063137 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.69451
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -2.9811
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.3311
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -2.8748
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -2.9998
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.64026
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.58691
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.037952 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.91085
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.037952 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -0.91085
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.037952 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -0.8729
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.044368 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -17.5697
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.10396 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -138.5773
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.10396 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -138.0576
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.2187
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.1269
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -0.87582
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.058388 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -2.7442
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 7.4126
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.10758 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 16.1375
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.1048 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 17.7644
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.076243 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 11.4365
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.10678 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 6.7271
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.11072 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 71.9328
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.11968 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.7873
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.11968 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.7873
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | 0.003035 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | 1.2808
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -1.4212
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -1.4428
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -3.4777
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -2.026
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -2.0517
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -2.244
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.02789 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -16.2878
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.02789 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -16.5946
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.028025 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -12.1348
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -6.1752
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -6.2055
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -6.1945
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -6.2524
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.002969 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.023752
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.002969 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.023752
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.19622
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | 0.19622
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | 0.16351
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | 0.009505 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | 0.13022
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.001843 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.033174
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | 0.001843 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | 0.033174
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.03003
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -0.029172
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -0.03003
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003371 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | 0.094388
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | 0.003371 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | 0.097759
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.10471 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 3.6648
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.10471 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 3.1412
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.2167
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.2167
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.2167
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -1.2167
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.022345 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.13407
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.074201
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.074201
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.086568
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.032326 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.1293
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.033006 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.079214
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.033006 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.079214
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.2777
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -4.9546
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -5.0264
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -5.2777
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -6.5343
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -7.1088
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -1.6543
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -1.6218
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -2.5232
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -4.524
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -4.6196
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -4.8107
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -9.2391
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.00032 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | 0.01056
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.00032 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | 0.008
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.64026
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.062505 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -4.5629
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.5188
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -5.6585
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -1.8441
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.46101
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.5188
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -5.5886
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -5.4769
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.7465
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.2135
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.055549 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -34.9403
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.061266 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -8.8223
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.061266 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -11.518
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.040629 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -0.48755
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.012179 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.073074
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.059937 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -20.1388
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.059659 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -19.9261
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.059659 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -20.2841
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.059447 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.259
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.059587 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.4897
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.059587 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.4897
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.059488 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.2605
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.058846 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -1.7065
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -8.8866
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -8.9046
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -9.1682
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -9.6734
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -9.3673
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -6.1224
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -8.8775
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -8.9999
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -7.7754
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -8.3914
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -8.4716
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -9.9093
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -11.9903
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -12.5521
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -14.0176
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -8.3416
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -8.3416
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -9.9057
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.003099 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -0.96069
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.003099 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -1.2799
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -0.080808
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.084656
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -0.084656
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -0.090428
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -0.24108
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.22632
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -0.22632
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -0.23124
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -0.75768
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -0.72816
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.23616
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -0.23616
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 7.3994
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 7.3994
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 9.8094
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 8.4564
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 8.4564
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 12.1561
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 22.0057
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 15.0193
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 13.994
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 14.3745
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 15.5372
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 22.1959
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 22.48
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 13.6063
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 26.7824
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 21.1893
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 21.323
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 12.9964
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.10489 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 15.6279
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.10644 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 19.1587
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.10644 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 19.1587
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.10638 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 23.9362
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.10717 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 13.3961
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.10717 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 13.3961
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 16.8112
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 16.9313
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 37.1047
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 17.1714
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 17.2915
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 37.2248
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11847 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 23.2207
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11847 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 13.1505
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.11941 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 19.5638
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 19.9283
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 19.9283
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 50.3068
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 19.6853
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 19.5638
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 19.8068
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 49.6992
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.12053 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.12053 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 18.5647
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 16.3068
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 18.1884
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 50.0494
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 19.7803
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 19.8197
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 23.2848
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 19.8515
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 19.9563
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 23.2584
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | 0.029157 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | 16.9402
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 132.7439
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 132.7439
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.16595 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 5.3103
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.16178 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 7.7656
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.16178 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 7.442
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 1.987
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 8.4446
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.16558 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 2.8149
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 3.6428
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 4.1395
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.16178 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 16.9872
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.10698 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 8.986
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.098728 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 7.8982
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.098674 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 14.8011
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.098674 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 14.8011
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -10.4461
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -9.8412
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -7.8198
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -22.6037
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -22.648
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -22.471
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -14.1642
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -36.0007
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -5.9018
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -14.7949
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -13.7033
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -15.1489
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -15.0456
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.14751 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -4.7202
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.14751 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -4.4252
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -14.0159
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -14.0159
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -15.026
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -13.8265
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 23.6455
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 23.7542
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.16232 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -22.075
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.1403 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -4.63
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -6.8935
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -6.8935
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.237
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -6.237
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.12436 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -8.8298
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.12436 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -1.2436
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -21.7951
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -21.7951
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -32.7594
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -10.2365
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -9.449
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -10.2365
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -10.2365
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.16156 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -24.0718
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.16156 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -10.5173
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -14.2177
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -13.6865
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -13.5928
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -8.515
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -1.9061
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.16985 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -126.1971
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.1676 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -123.1838
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -29.4965
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -29.4965
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -29.4965
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -32.8873
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.16293 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -28.1872
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.16293 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -21.9958
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -28.3137
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -28.0702
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -27.6354
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -46.8185
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -10.3487
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -10.2194
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -13.3563
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -11.901
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -26.4449
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -25.4565
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -25.5213
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -25.4403
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -43.5888
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.16803 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.84014
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.16803 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -3.5286
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | -118.6327
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -120.0175
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | -120.0175
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | -292.3503
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.17066 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -67.9223
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.019
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.019
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -7.019
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -8.3923
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -8.3923
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -8.2398
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.14627 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 120.9678
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.14627 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 119.7976
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.13845 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -6.3823
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -7.7349
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -7.7349
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -10.6864
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -7.5313
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -7.5313
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -10.3811
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -29.1116
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -25.6505
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -25.3918
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.16068 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -5.6239
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.15351 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -70.462
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -10.875
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -11.0423
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -11.7115
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -10.5403
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -10.373
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -17.3999
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -9.8711
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -29.6556
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -29.2754
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -29.2754
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.1901 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -30.7962
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.1679 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -26.3597
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -11.5462
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -11.7088
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -6.3423
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -4.8787
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.15963 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -12.4515
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.15963 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -12.7707
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.16169 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -2.6193
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.16151 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -26.6483
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.16145 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -27.2859
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.16167 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -34.4363
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.16172 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -36.8724
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.16142 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -1.937
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.16142 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -2.9056
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.14701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -7.3503
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -15.4656
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -15.4656
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.0302
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -7.8815
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.0302
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -8.4764
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.0302
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -8.0302
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -8.6251
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -8.6251
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -1.818
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7447
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -9.2131
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7447
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7447
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -9.2131
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -8.7447
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.10701 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -7.0627
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -21.9047
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -22.585
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -33.7414
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13605 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -74.2855
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13605 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -87.4827
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -86.9905
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -75.3651
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -80.1756
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.13605 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -1.7687
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.1689 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -2.0268
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -5.6904
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -5.8076
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -5.4729
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -7.6821
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -2.9624
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -3.4143
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -3.3306
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -5.8578
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -3.0126
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -14.2931
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -24.7702
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -7.5347
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -8.6771
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -5.4688
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -12.2743
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -10.4514
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -10.6945
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -6.0764
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -2.1875
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -11.4236
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -8.507
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -7.6563
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -8.75
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -7.875
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -12.2743
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -11.7882
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -12.5174
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -9.2361
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -9.7222
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -9.7222
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -20.7813
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.30687
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.096188 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 7.3584
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 7.9067
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 3.9534
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.09926 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 7.9408
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.098741 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 7.8993
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.096544 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 7.7235
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.095825 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 8.0493
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.09926 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 7.9408
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -3.3212
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 12.7636
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 24.7826
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 18.103
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -6.4675
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -5.3605
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -6.5258
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -3.3503
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -2.9133
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.10837 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 6.5019
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | 0.025303 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.084364 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.10084 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.48402
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 4.0302
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 11.5531
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 14.5086
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 12.789
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 11.2845
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 8.6514
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.10572 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 15.8584
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 11.8689
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 15.7724
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 19.6232
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 22.63
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.058388 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.015087 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.043988 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -1.956
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -3.0458
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -5.1695
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -5.5049
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -2.4011
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.2254
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.1127
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -5.5049
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.1083
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -2.5182
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.2884
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.5685
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.98789
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.46101
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -0.98789
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.5685
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.5685
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -8.6673
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -2.9282
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -3.221
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -2.9282
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.061224 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.73469
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.064631 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -0.96947
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.064631 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.4865
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.068928 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.3085
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.06539 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.52312
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.059898 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -10.7816
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.059937 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -10.7887
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.059659 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -10.7386
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.059659 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -10.7386
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.043984 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -4.3984
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.043984 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -4.3984
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.5178
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.5178
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.5178
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -0.97139
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.5178
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.5178
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.5178
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -0.91068
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.043984 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.043984 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -21.992
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.043984 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -21.992
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.043984 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.052658 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | 0.00032 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.049602 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.055465 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: Singleton - Roans Prairie [ 44645 - 40600] C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | [7 empty] | 45.2915
Number of Bus | Name of Bus | ID | Max MW | L: Singleton - Roans Prairie [ 44645 - 40600] C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.090878 | north | Y | -0.033234 | 0.12336 | -0.014828 | 0.23938 | 0.014828 | west | Y | 0.033234 | 4.6935
239 | BOSQUESW | 1 | 149 | 0.090878 | north | Y | -0.033234 | 0.12336 | -0.014828 | 0.23938 | 0.014828 | west | Y | 0.033234 | 2.7424
244 | WHITNYDM | 1 | 15 | 0.096462 | north | N | -0.02765 | 0.12895 | -0.0092443 | 0.24497 | 0.0092443 | west | Y | 0.02765 | 0
245 | WHITNYDM | 2 | 15 | 0.096462 | north | N | -0.02765 | 0.12895 | -0.0092443 | 0.24497 | 0.0092443 | west | Y | 0.02765 | 0
247 | BOSQUESW | 2 | 153 | 0.090878 | north | Y | -0.033234 | 0.12336 | -0.014828 | 0.23938 | 0.014828 | west | Y | 0.033234 | 2.8161
251 | BOSQUESW | 2 | 150 | 0.09258 | north | Y | -0.031532 | 0.12507 | -0.013126 | 0.24109 | 0.013126 | west | Y | 0.031532 | 2.7609
253 | BOSQUESW | 2 | 80 | 0.09258 | north | Y | -0.031532 | 0.12507 | -0.013126 | 0.24109 | 0.013126 | west | Y | 0.031532 | 1.4725
332 | RWMILLER | 1 | 73 | 0.11112 | north | Y | -0.012994 | 0.1436 | 0.0054117 | 0.25962 | 0.0054117 | west | Y | 0.012994 | 0.55351
333 | RWMILLER | 2 | 119 | 0.11112 | north | Y | -0.012994 | 0.1436 | 0.0054117 | 0.25962 | 0.0054117 | west | Y | 0.012994 | 0.90229
334 | RWMILLER | 3 | 205 | 0.11112 | north | Y | -0.012994 | 0.1436 | 0.0054117 | 0.25962 | 0.0054117 | west | Y | 0.012994 | 1.5544
335 | RWMILLER | 4 | 102 | 0.11112 | north | Y | -0.012994 | 0.1436 | 0.0054117 | 0.25962 | 0.0054117 | west | Y | 0.012994 | 0.77339
336 | RWMILLER | 5 | 96 | 0.11112 | north | Y | -0.012994 | 0.1436 | 0.0054117 | 0.25962 | 0.0054117 | west | Y | 0.012994 | 0.7279
344 | MRSSHPRD | 1 | 12 | 0.11228 | north | N | -0.011827 | 0.14477 | 0.0065787 | 0.26079 | 0.0065787 | west | Y | 0.011827 | 0
345 | MRSSHPRD | 2 | 12 | 0.11228 | north | N | -0.011827 | 0.14477 | 0.0065787 | 0.26079 | 0.0065787 | west | Y | 0.011827 | 0
366 | JNSNCNTY | 1 | 168 | 0.11184 | north | Y | -0.012267 | 0.14433 | 0.0061387 | 0.26035 | 0.0061387 | west | Y | 0.012267 | 1.0296
367 | JNSNCNTY | 2 | 90 | 0.11184 | north | Y | -0.012267 | 0.14433 | 0.0061387 | 0.26035 | 0.0061387 | west | Y | 0.012267 | 0.55154
503 | NTHTEXAS | 1 | 18 | 0.11325 | north | Y | -0.01086 | 0.14574 | 0.0075457 | 0.26176 | 0.0075457 | west | Y | 0.01086 | 0.059657
504 | NTHTEXAS | 2 | 18 | 0.11325 | north | Y | -0.01086 | 0.14574 | 0.0075457 | 0.26176 | 0.0075457 | west | Y | 0.01086 | 0.059657
505 | NTHTEXAS | 3 | 38 | 0.11325 | north | Y | -0.01086 | 0.14574 | 0.0075457 | 0.26176 | 0.0075457 | west | Y | 0.01086 | 0.12594
580 | JCKCNTY8 | 1 | 288 | 0.11458 | north | Y | -0.009533 | 0.14707 | 0.0088727 | 0.26308 | 0.0088727 | west | Y | 0.009533 | 0.19016
581 | JCKCNTY8 | 2 | 147 | 0.11458 | north | Y | -0.009533 | 0.14707 | 0.0088727 | 0.26308 | 0.0088727 | west | Y | 0.009533 | 0.097061
582 | JCKCNTY8 | 3 | 147 | 0.11458 | north | Y | -0.009533 | 0.14707 | 0.0088727 | 0.26308 | 0.0088727 | west | Y | 0.009533 | 0.097061
728 | WOLFRIDG | 1 | 112.5 | 0.11616 | north | Y | -0.007952 | 0.14865 | 0.010454 | 0.26467 | 0.007952 | North | N | 0.007952 | 0
837 | NEWMAN_G | 1 | 40 | 0.12047 | north | Y | -0.003639 | 0.15296 | 0.014767 | 0.26898 | 0.003639 | North | N | 0.003639 | 0
842 | OLINGER_ | 1 | 79 | 0.12047 | north | Y | -0.003643 | 0.15296 | 0.014763 | 0.26897 | 0.003643 | North | N | 0.003643 | 0
843 | OLINGER_ | 1 | 106 | 0.12047 | north | Y | -0.003643 | 0.15296 | 0.014763 | 0.26897 | 0.003643 | North | N | 0.003643 | 0
844 | OLINGER_ | 1 | 146 | 0.12047 | north | Y | -0.003643 | 0.15296 | 0.014763 | 0.26897 | 0.003643 | North | N | 0.003643 | 0
845 | OLINGER_ | 1 | 76 | 0.12047 | north | Y | -0.003643 | 0.15296 | 0.014763 | 0.26897 | 0.003643 | North | N | 0.003643 | 0
923 | SPENCER_ | 1 | 60 | 0.11735 | north | Y | -0.006762 | 0.14984 | 0.011644 | 0.26586 | 0.006762 | North | N | 0.006762 | 0
924 | SPENCER_ | 1 | 63 | 0.11735 | north | Y | -0.006762 | 0.14984 | 0.011644 | 0.26586 | 0.006762 | North | N | 0.006762 | 0
948 | STEAM1 | 1 | 20 | 0.12062 | north | Y | -0.003492 | 0.15311 | 0.014914 | 0.26913 | 0.003492 | North | N | 0.003492 | 0
949 | STEAM2 | 1 | 25 | 0.12062 | north | Y | -0.003493 | 0.15311 | 0.014913 | 0.26912 | 0.003493 | North | N | 0.003493 | 0
950 | STEAM3 | 1 | 41 | 0.12062 | north | Y | -0.003493 | 0.15311 | 0.014913 | 0.26912 | 0.003493 | North | N | 0.003493 | 0
990 | GIBN_CRE | 1 | 463 | 0.1782 | north | Y | 0.054089 | 0.21069 | 0.072495 | 0.32671 | 0.054089 | North | N | 0.054089 | 0
1002 | PBCTAGE_ | A | 66 | 0.10466 | west | Y | -0.019456 | 0.13714 | -0.0010503 | 0.25316 | 0.0010503 | west | N | 0.0010503 | 0
1003 | PBCTBGE_ | B | 65 | 0.10466 | west | Y | -0.019456 | 0.13714 | -0.0010503 | 0.25316 | 0.0010503 | west | N | 0.0010503 | 0
1004 | PBCTCGE_ | C | 67 | 0.10466 | west | Y | -0.019456 | 0.13714 | -0.0010503 | 0.25316 | 0.0010503 | west | N | 0.0010503 | 0
1005 | PBCTDGE_ | D | 67 | 0.10466 | west | Y | -0.019456 | 0.13714 | -0.0010503 | 0.25316 | 0.0010503 | west | N | 0.0010503 | 0
1006 | PBCTEGE_ | E | 67 | 0.10466 | west | Y | -0.019456 | 0.13714 | -0.0010503 | 0.25316 | 0.0010503 | west | N | 0.0010503 | 0
1007 | PB5GEN_6 | MB | 114 | 0.10466 | west | Y | -0.019456 | 0.13714 | -0.0010503 | 0.25316 | 0.0010503 | west | N | 0.0010503 | 0
1008 | PB6GEN_7 | MB | 515 | 0.10466 | west | Y | -0.019456 | 0.13714 | -0.0010503 | 0.25316 | 0.0010503 | west | N | 0.0010503 | 0
1039 | MRGNAG_1 | A | 66 | 0.10674 | west | Y | -0.017373 | 0.13923 | 0.0010327 | 0.25524 | 0.0010327 | west | N | 0.0010327 | 0
1040 | MRGNBG_2 | B | 69 | 0.10674 | west | Y | -0.017373 | 0.13923 | 0.0010327 | 0.25524 | 0.0010327 | west | N | 0.0010327 | 0
1041 | MRGNCG_3 | C | 69 | 0.10674 | west | Y | -0.017373 | 0.13923 | 0.0010327 | 0.25524 | 0.0010327 | west | N | 0.0010327 | 0
1042 | MRGNDG_4 | D | 67 | 0.10674 | west | Y | -0.017373 | 0.13923 | 0.0010327 | 0.25524 | 0.0010327 | west | N | 0.0010327 | 0
1043 | MRGNEG_5 | E | 67 | 0.10674 | west | Y | -0.017373 | 0.13923 | 0.0010327 | 0.25524 | 0.0010327 | west | N | 0.0010327 | 0
1044 | MRGNFG_6 | F | 65 | 0.10674 | west | Y | -0.017373 | 0.13923 | 0.0010327 | 0.25524 | 0.0010327 | west | N | 0.0010327 | 0
1045 | CALENG1G | 1 | 70 | 0.10645 | west | N | -0.017665 | 0.13893 | 0.00074071 | 0.25495 | 0.00074071 | west | N | 0.00074071 | 0
1046 | CALENG2G | 2 | 73.4 | 0.10645 | west | N | -0.017665 | 0.13893 | 0.00074071 | 0.25495 | 0.00074071 | west | N | 0.00074071 | 0
1047 | CALENG3G | 3 | 70.4 | 0.10645 | west | N | -0.017665 | 0.13893 | 0.00074071 | 0.25495 | 0.00074071 | west | N | 0.00074071 | 0
1058 | LONGSHOR | 1 | 150 | 0.10662 | west | Y | -0.017497 | 0.1391 | 0.00090871 | 0.25512 | 0.00090871 | west | N | 0.00090871 | 0
1058 | LONGSHOR | 2 | 220 | 0.10662 | west | Y | -0.017497 | 0.1391 | 0.00090871 | 0.25512 | 0.00090871 | west | N | 0.00090871 | 0
1061 | CIELOGEN | 1 | 99 | 0.10684 | west | Y | -0.017274 | 0.13932 | 0.0011317 | 0.25534 | 0.0011317 | west | N | 0.0011317 | 0
1062 | CIELOGEN | 1 | 61 | 0.10684 | west | Y | -0.017274 | 0.13932 | 0.0011317 | 0.25534 | 0.0011317 | west | N | 0.0011317 | 0
1068 | SCURRYCW | 1 | 141 | 0.10682 | west | Y | -0.017291 | 0.13931 | 0.0011147 | 0.25533 | 0.0011147 | west | N | 0.0011147 | 0
1069 | KINDERMG | 1 | 25 | 0.10684 | west | N | -0.017274 | 0.13932 | 0.0011317 | 0.25534 | 0.0011317 | west | N | 0.0011317 | 0
1070 | KINDERMG | 1 | 45.7 | 0.10684 | west | N | -0.017274 | 0.13932 | 0.0011317 | 0.25534 | 0.0011317 | west | N | 0.0011317 | 0
1071 | KINDERMG | 1 | 45.7 | 0.10684 | west | N | -0.017274 | 0.13932 | 0.0011317 | 0.25534 | 0.0011317 | west | N | 0.0011317 | 0
1073 | SCURRYCW | 2 | 120 | 0.10682 | west | Y | -0.017291 | 0.13931 | 0.0011147 | 0.25533 | 0.0011147 | west | N | 0.0011147 | 0
1320 | BSP 1 | 1 | 25.8 | 0.10594 | west | N | -0.018176 | 0.13842 | 0.00022971 | 0.25444 | 0.00022971 | west | N | 0.00022971 | 0
1326 | STANTONW | 1 | 100.5 | 0.10575 | west | Y | -0.018361 | 0.13824 | 4.4706e-05 | 0.25426 | 4.4706e-05 | west | N | 4.4706e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.10626 | west | Y | -0.017851 | 0.13875 | 0.00055471 | 0.25477 | 0.00055471 | west | N | 0.00055471 | 0
1328 | OCOTILLO | 1 | 58 | 0.10573 | west | Y | -0.018378 | 0.13822 | 2.7706e-05 | 0.25424 | 2.7706e-05 | west | N | 2.7706e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.10587 | west | Y | -0.018238 | 0.13836 | 0.00016771 | 0.25438 | 0.00016771 | west | N | 0.00016771 | 0
1343 | TRENTIPP | 1 | 150 | 0.10704 | west | Y | -0.017071 | 0.13953 | 0.0013347 | 0.25555 | 0.0013347 | west | N | 0.0013347 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.1052 | west | Y | -0.018913 | 0.13769 | -0.00050729 | 0.2537 | 0.00050729 | west | N | 0.00050729 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.1052 | west | Y | -0.018913 | 0.13769 | -0.00050729 | 0.2537 | 0.00050729 | west | N | 0.00050729 | 0
1354 | AEPWIND_ | 1 | 101 | 0.10704 | west | Y | -0.017071 | 0.13953 | 0.0013347 | 0.25555 | 0.0013347 | west | N | 0.0013347 | 0
1360 | GUNSIGHT | 1 | 120 | 0.10628 | west | Y | -0.017828 | 0.13877 | 0.00057771 | 0.25479 | 0.00057771 | west | N | 0.00057771 | 0
1432 | GRHAMSES | 2 | 366 | 0.11224 | north | Y | -0.011875 | 0.14472 | 0.0065307 | 0.26074 | 0.0065307 | west | Y | 0.011875 | 1.956
1433 | GRHAMSES | 1 | 242 | 0.11159 | north | Y | -0.012522 | 0.14408 | 0.0058837 | 0.2601 | 0.0058837 | west | Y | 0.012522 | 1.6065
1437 | MESQUITW | 1 | 400 | 0.10949 | west | Y | -0.014617 | 0.14198 | 0.0037887 | 0.258 | 0.0037887 | west | N | 0.0037887 | 0
1438 | MESQUITW | 1 | 236 | 0.1095 | west | Y | -0.014614 | 0.14198 | 0.0037917 | 0.258 | 0.0037917 | west | N | 0.0037917 | 0
1442 | COKFIELD | 1 | 165 | 0.11016 | west | Y | -0.013956 | 0.14264 | 0.0044497 | 0.25866 | 0.0044497 | west | N | 0.0044497 | 0
1453 | WCPWRCO_ | 1 | 204 | 0.11394 | north | Y | -0.010175 | 0.14642 | 0.0082307 | 0.26244 | 0.0082307 | west | Y | 0.010175 | 0.39663
1454 | WCPWRCO_ | 2 | 201 | 0.11394 | north | Y | -0.010175 | 0.14642 | 0.0082307 | 0.26244 | 0.0082307 | west | Y | 0.010175 | 0.3908
1455 | WCPWRCO_ | 3 | 242 | 0.11394 | north | Y | -0.010175 | 0.14642 | 0.0082307 | 0.26244 | 0.0082307 | west | Y | 0.010175 | 0.47051
1479 | WFCOGEN_ | 1 | 20 | 0.11236 | west | Y | -0.011754 | 0.14484 | 0.0066517 | 0.26086 | 0.0066517 | west | N | 0.0066517 | 0
1479 | WFCOGEN_ | 2 | 20 | 0.11236 | west | Y | -0.011754 | 0.14484 | 0.0066517 | 0.26086 | 0.0066517 | west | N | 0.0066517 | 0
1482 | WFCOGEN_ | 1 | 20 | 0.11236 | west | Y | -0.011754 | 0.14484 | 0.0066517 | 0.26086 | 0.0066517 | west | N | 0.0066517 | 0
1482 | WFCOGEN_ | 2 | 17 | 0.11236 | west | Y | -0.011754 | 0.14484 | 0.0066517 | 0.26086 | 0.0066517 | west | N | 0.0066517 | 0
1600 | BARTNWND | 1 | 120 | 0.11214 | north | Y | -0.011973 | 0.14463 | 0.0064327 | 0.26064 | 0.0064327 | west | Y | 0.011973 | 0.66483
1643 | SLSTR1PP | 1 | 60 | 0.10759 | north | Y | -0.016523 | 0.14008 | 0.0018827 | 0.25609 | 0.0018827 | west | Y | 0.016523 | 0.87842
1675 | PEC_1G | 1 | 75 | 0.12025 | north | N | -0.003866 | 0.15273 | 0.01454 | 0.26875 | 0.003866 | North | N | 0.003866 | 0
1676 | PEC_2G | 2 | 79.6 | 0.12025 | north | N | -0.003866 | 0.15273 | 0.01454 | 0.26875 | 0.003866 | North | N | 0.003866 | 0
1677 | PEC_3G | 3 | 88.4 | 0.12025 | north | N | -0.003866 | 0.15273 | 0.01454 | 0.26875 | 0.003866 | North | N | 0.003866 | 0
1678 | LAMARPWR | 1 | 160 | 0.12018 | north | Y | -0.003936 | 0.15266 | 0.01447 | 0.26868 | 0.003936 | North | N | 0.003936 | 0
1679 | LAMARPWR | 2 | 156 | 0.12018 | north | Y | -0.003936 | 0.15266 | 0.01447 | 0.26868 | 0.003936 | North | N | 0.003936 | 0
1680 | LAMARPWR | 3 | 196 | 0.12018 | north | Y | -0.003936 | 0.15266 | 0.01447 | 0.26868 | 0.003936 | North | N | 0.003936 | 0
1681 | LAMARPWR | 4 | 156 | 0.12018 | north | Y | -0.003936 | 0.15266 | 0.01447 | 0.26868 | 0.003936 | North | N | 0.003936 | 0
1682 | LAMARPWR | 5 | 157 | 0.12018 | north | Y | -0.003936 | 0.15266 | 0.01447 | 0.26868 | 0.003936 | North | N | 0.003936 | 0
1683 | LAMARPWR | 6 | 198 | 0.12018 | north | Y | -0.003936 | 0.15266 | 0.01447 | 0.26868 | 0.003936 | North | N | 0.003936 | 0
1687 | VALLEY_1 | 1 | 170 | 0.11986 | north | Y | -0.004253 | 0.15235 | 0.014153 | 0.26836 | 0.004253 | North | N | 0.004253 | 0
1688 | VALLEY_2 | 2 | 520 | 0.11986 | north | Y | -0.004253 | 0.15235 | 0.014153 | 0.26836 | 0.004253 | North | N | 0.004253 | 0
1689 | VALLEY_3 | 3 | 370 | 0.12008 | north | Y | -0.004032 | 0.15257 | 0.014374 | 0.26859 | 0.004032 | North | N | 0.004032 | 0
1701 | MOSES_1G | 1 | 558 | 0.12034 | north | Y | -0.003767 | 0.15283 | 0.014639 | 0.26885 | 0.003767 | North | N | 0.003767 | 0
1702 | MOSES_2G | 2 | 579 | 0.12034 | north | Y | -0.003767 | 0.15283 | 0.014639 | 0.26885 | 0.003767 | North | N | 0.003767 | 0
1703 | MOSES_3G | 3 | 808 | 0.12034 | north | Y | -0.003767 | 0.15283 | 0.014639 | 0.26885 | 0.003767 | North | N | 0.003767 | 0
1861 | EAGLEMNT | MB | 112 | 0.11574 | north | Y | -0.008376 | 0.14822 | 0.01003 | 0.26424 | 0.008376 | North | N | 0.008376 | 0
1862 | EAGLEMNT | MB | 100 | 0.11574 | north | Y | -0.008376 | 0.14822 | 0.01003 | 0.26424 | 0.008376 | North | N | 0.008376 | 0
1863 | EAGLEMNT | MB | 378 | 0.11574 | north | Y | -0.008376 | 0.14822 | 0.01003 | 0.26424 | 0.008376 | North | N | 0.008376 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.11385 | north | Y | -0.010258 | 0.14634 | 0.0081477 | 0.26236 | 0.0081477 | west | Y | 0.010258 | 0.45856
1878 | WLFHOLW_ | 2 | 205 | 0.11385 | north | Y | -0.010258 | 0.14634 | 0.0081477 | 0.26236 | 0.0081477 | west | Y | 0.010258 | 0.43261
1879 | WLFHOLW_ | 3 | 272.4 | 0.11385 | north | Y | -0.010258 | 0.14634 | 0.0081477 | 0.26236 | 0.0081477 | west | Y | 0.010258 | 0.57484
1889 | DECRDOVA | MB | 770 | 0.11411 | north | Y | -0.010004 | 0.14659 | 0.0084017 | 0.26261 | 0.0084017 | west | Y | 0.010004 | 0
1892 | DECRDOVA | A | 70 | 0.11259 | north | Y | -0.011525 | 0.14507 | 0.0068807 | 0.26109 | 0.0068807 | west | Y | 0.011525 | 0.3251
1893 | DECRDOVA | B | 69 | 0.11259 | north | Y | -0.011525 | 0.14507 | 0.0068807 | 0.26109 | 0.0068807 | west | Y | 0.011525 | 0.32046
1894 | DECRDOVA | C | 69 | 0.11259 | north | Y | -0.011525 | 0.14507 | 0.0068807 | 0.26109 | 0.0068807 | west | Y | 0.011525 | 0.32046
1895 | DECRDOVA | D | 68 | 0.11259 | north | Y | -0.011525 | 0.14507 | 0.0068807 | 0.26109 | 0.0068807 | west | Y | 0.011525 | 0.31581
1898 | COMCHEPK | 1 | 1157 | 0.11357 | north | N | -0.010542 | 0.14606 | 0.0078637 | 0.26208 | 0.0078637 | west | Y | 0.010542 | 0
1899 | COMCHEPK | 2 | 1158 | 0.11357 | north | N | -0.010542 | 0.14606 | 0.0078637 | 0.26208 | 0.0078637 | west | Y | 0.010542 | 0
1937 | MDLTHELP | 5 | 224 | 0.11463 | north | Y | -0.009482 | 0.14712 | 0.0089237 | 0.26314 | 0.0089237 | west | Y | 0.009482 | 0.12505
1938 | MDLTHELP | 6 | 226 | 0.11463 | north | Y | -0.009482 | 0.14712 | 0.0089237 | 0.26314 | 0.0089237 | west | Y | 0.009482 | 0.12617
1941 | MDLTHELP | 1 | 216.4 | 0.11579 | north | Y | -0.008322 | 0.14828 | 0.010084 | 0.2643 | 0.008322 | North | N | 0.008322 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.11579 | north | Y | -0.008322 | 0.14828 | 0.010084 | 0.2643 | 0.008322 | North | N | 0.008322 | 0
1943 | MDLTHELP | 3 | 212 | 0.11463 | north | Y | -0.009482 | 0.14712 | 0.0089237 | 0.26314 | 0.0089237 | west | Y | 0.009482 | 0.11835
1944 | MDLTHELP | 4 | 211 | 0.11463 | north | Y | -0.009482 | 0.14712 | 0.0089237 | 0.26314 | 0.0089237 | west | Y | 0.009482 | 0.1178
1947 | HANDLEY_ | 3 | 395 | 0.11599 | north | Y | -0.008123 | 0.14848 | 0.010283 | 0.26449 | 0.008123 | North | N | 0.008123 | 0
1948 | HANDLEY_ | 4 | 435 | 0.11623 | north | Y | -0.00788 | 0.14872 | 0.010526 | 0.26474 | 0.00788 | North | N | 0.00788 | 0
1949 | HANDLEY_ | 5 | 435 | 0.11599 | north | Y | -0.008123 | 0.14848 | 0.010283 | 0.26449 | 0.008123 | North | N | 0.008123 | 0
2371 | COLLIN_1 | MB | 138 | 0.11915 | north | Y | -0.004959 | 0.15164 | 0.013447 | 0.26766 | 0.004959 | North | N | 0.004959 | 0
2413 | MTCK6_G | 6 | 118 | 0.11944 | north | Y | -0.004673 | 0.15193 | 0.013733 | 0.26794 | 0.004673 | North | N | 0.004673 | 0
2414 | MTCK7_G | 7 | 115 | 0.11944 | north | Y | -0.004673 | 0.15193 | 0.013733 | 0.26794 | 0.004673 | North | N | 0.004673 | 0
2417 | MTCK8_G | 8 | 556 | 0.11944 | north | Y | -0.004673 | 0.15193 | 0.013733 | 0.26794 | 0.004673 | North | N | 0.004673 | 0
2451 | LKHB1_G | 1 | 388 | 0.12076 | north | Y | -0.00335 | 0.15325 | 0.015056 | 0.26927 | 0.00335 | North | N | 0.00335 | 0
2452 | LKHB2_G | 2 | 515 | 0.12076 | north | Y | -0.00335 | 0.15325 | 0.015056 | 0.26927 | 0.00335 | North | N | 0.00335 | 0
3097 | MARTLAKE | 1 | 785 | 0.12494 | north | Y | 0.00082602 | 0.15742 | 0.019232 | 0.27344 | 0.00082602 | North | N | 0.00082602 | 0
3098 | MARTLAKE | 2 | 795 | 0.12494 | north | Y | 0.00082602 | 0.15742 | 0.019232 | 0.27344 | 0.00082602 | North | N | 0.00082602 | 0
3099 | MARTLAKE | 3 | 780 | 0.12494 | north | Y | 0.00082602 | 0.15742 | 0.019232 | 0.27344 | 0.00082602 | North | N | 0.00082602 | 0
3107 | STRYKER_ | 1 | 182 | 0.12599 | north | Y | 0.001881 | 0.15848 | 0.020287 | 0.2745 | 0.001881 | North | N | 0.001881 | 0
3108 | STRYKER_ | 2 | 484 | 0.12599 | north | Y | 0.001881 | 0.15848 | 0.020287 | 0.2745 | 0.001881 | North | N | 0.001881 | 0
3126 | TRINIDAD | 1 | 224 | 0.12167 | north | Y | -0.002441 | 0.15416 | 0.015965 | 0.27018 | 0.002441 | North | N | 0.002441 | 0
3309 | ASPN_G | 1 | 50 | 0.12593 | north | Y | 0.001814 | 0.15841 | 0.02022 | 0.27443 | 0.001814 | North | N | 0.001814 | 0
3348 | CHAMPION | MB | 42 | 0.12587 | north | N | 0.001762 | 0.15836 | 0.020168 | 0.27438 | 0.001762 | North | N | 0.001762 | 0
3381 | BBRN_1G | 1 | 615 | 0.13244 | north | Y | 0.008328 | 0.16493 | 0.026734 | 0.28095 | 0.008328 | North | N | 0.008328 | 0
3382 | BBRN_2G | 2 | 587 | 0.13244 | north | Y | 0.008328 | 0.16493 | 0.026734 | 0.28095 | 0.008328 | North | N | 0.008328 | 0
3403 | THOUSE_1 | MB | 537 | 0.088923 | north | Y | -0.035189 | 0.12141 | -0.016783 | 0.23743 | 0.016783 | west | Y | 0.035189 | 0
3404 | THOUSE_2 | 2 | 787 | 0.088923 | north | Y | -0.035189 | 0.12141 | -0.016783 | 0.23743 | 0.016783 | west | Y | 0.035189 | 14.4853
3416 | LAKE_CRK | MB | 75 | 0.087612 | north | Y | -0.0365 | 0.1201 | -0.018094 | 0.23612 | 0.018094 | west | Y | 0.0365 | 0
3417 | LAKE_CRK | MB | 222 | 0.087612 | north | Y | -0.0365 | 0.1201 | -0.018094 | 0.23612 | 0.018094 | west | Y | 0.0365 | 0
3432 | SANDOW_4 | 4 | 569 | 0.029157 | south | Y | -0.094955 | 0.061643 | -0.076549 | 0.17766 | 0.061643 | south | N | 0.061643 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.036971 | south | Y | -0.16108 | -0.0044846 | -0.14268 | 0.11153 | 0.0044846 | south | N | 0.0044846 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.036971 | south | Y | -0.16108 | -0.0044846 | -0.14268 | 0.11153 | 0.0044846 | south | N | 0.0044846 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.036794 | south | Y | -0.16091 | -0.0043076 | -0.1425 | 0.11171 | 0.0043076 | south | N | 0.0043076 | 0
5031 | BRA_VHBC | 1 | 46 | -0.036971 | south | Y | -0.16108 | -0.0044846 | -0.14268 | 0.11153 | 0.0044846 | south | N | 0.0044846 | 0
5032 | BRA_VHBC | 2 | 47 | -0.036971 | south | Y | -0.16108 | -0.0044846 | -0.14268 | 0.11153 | 0.0044846 | south | N | 0.0044846 | 0
5033 | BRA_VHBC | 3 | 46 | -0.036971 | south | Y | -0.16108 | -0.0044846 | -0.14268 | 0.11153 | 0.0044846 | south | N | 0.0044846 | 0
5034 | BRA_VHBC | 4 | 46 | -0.036971 | south | Y | -0.16108 | -0.0044846 | -0.14268 | 0.11153 | 0.0044846 | south | N | 0.0044846 | 0
5111 | CALAVER_ | 1 | 424 | -0.036862 | south | Y | -0.16097 | -0.0043756 | -0.14257 | 0.11164 | 0.0043756 | south | N | 0.0043756 | 0
5112 | CALAVER_ | 2 | 425 | -0.036862 | south | Y | -0.16097 | -0.0043756 | -0.14257 | 0.11164 | 0.0043756 | south | N | 0.0043756 | 0
5264 | LEON_LCP | 3 | 58 | -0.036821 | south | Y | -0.16093 | -0.0043346 | -0.14253 | 0.11168 | 0.0043346 | south | N | 0.0043346 | 0
5265 | LEON_LCP | 4 | 89 | -0.036821 | south | Y | -0.16093 | -0.0043346 | -0.14253 | 0.11168 | 0.0043346 | south | N | 0.0043346 | 0
5266 | LEON_LCP | 1 | 44 | -0.036821 | south | Y | -0.16093 | -0.0043346 | -0.14253 | 0.11168 | 0.0043346 | south | N | 0.0043346 | 0
5267 | LEON_LCP | 2 | 44 | -0.036821 | south | Y | -0.16093 | -0.0043346 | -0.14253 | 0.11168 | 0.0043346 | south | N | 0.0043346 | 0
5268 | LEON_LCP | 3 | 43 | -0.036821 | south | Y | -0.16093 | -0.0043346 | -0.14253 | 0.11168 | 0.0043346 | south | N | 0.0043346 | 0
5269 | LEON_LCP | 4 | 45 | -0.036821 | south | Y | -0.16093 | -0.0043346 | -0.14253 | 0.11168 | 0.0043346 | south | N | 0.0043346 | 0
5396 | CALAVER_ | 1 | 412 | -0.036837 | south | Y | -0.16095 | -0.0043506 | -0.14254 | 0.11167 | 0.0043506 | south | N | 0.0043506 | 0
5397 | CALAVER_ | 2 | 400 | -0.036837 | south | Y | -0.16095 | -0.0043506 | -0.14254 | 0.11167 | 0.0043506 | south | N | 0.0043506 | 0
5401 | CALAVER_ | 1 | 546 | -0.03883 | south | Y | -0.16294 | -0.0063436 | -0.14454 | 0.10968 | 0.0063436 | south | N | 0.0063436 | 0
5402 | CALAVER_ | 2 | 750 | -0.03883 | south | Y | -0.16294 | -0.0063436 | -0.14454 | 0.10968 | 0.0063436 | south | N | 0.0063436 | 0
5436 | TUTTL_WB | MB | 61 | -0.037017 | south | Y | -0.16113 | -0.0045306 | -0.14272 | 0.11149 | 0.0045306 | south | N | 0.0045306 | 0
5438 | TUTTL_WB | MB | 95 | -0.037017 | south | Y | -0.16113 | -0.0045306 | -0.14272 | 0.11149 | 0.0045306 | south | N | 0.0045306 | 0
5439 | TUTTL_WB | MB | 151 | -0.037017 | south | Y | -0.16113 | -0.0045306 | -0.14272 | 0.11149 | 0.0045306 | south | N | 0.0045306 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.037966 | south | Y | -0.16208 | -0.0054796 | -0.14367 | 0.11054 | 0.0054796 | south | N | 0.0054796 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.037966 | south | Y | -0.16208 | -0.0054796 | -0.14367 | 0.11054 | 0.0054796 | south | N | 0.0054796 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.037966 | south | Y | -0.16208 | -0.0054796 | -0.14367 | 0.11054 | 0.0054796 | south | N | 0.0054796 | 0
5503 | RAYBURNG | 1 | 22 | -0.063137 | south | Y | -0.18725 | -0.030651 | -0.16884 | 0.085369 | 0.030651 | south | N | 0.030651 | 0
5505 | RAYBURNG | 1 | 11 | -0.063137 | south | Y | -0.18725 | -0.030651 | -0.16884 | 0.085369 | 0.030651 | south | N | 0.030651 | 0
5506 | RAYBURNG | 1 | 11 | -0.063137 | south | Y | -0.18725 | -0.030651 | -0.16884 | 0.085369 | 0.030651 | south | N | 0.030651 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.062496 | south | Y | -0.18661 | -0.03001 | -0.1682 | 0.08601 | 0.03001 | south | N | 0.03001 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.062496 | south | Y | -0.18661 | -0.03001 | -0.1682 | 0.08601 | 0.03001 | south | N | 0.03001 | 0
5511 | RAYBURNC | 1 | 46 | -0.062496 | south | Y | -0.18661 | -0.03001 | -0.1682 | 0.08601 | 0.03001 | south | N | 0.03001 | 0
5512 | RAYBURNC | 1 | 48 | -0.062496 | south | Y | -0.18661 | -0.03001 | -0.1682 | 0.08601 | 0.03001 | south | N | 0.03001 | 0
5728 | FALCONHY | 2 | 12 | -0.053355 | south | N | -0.17747 | -0.020869 | -0.15906 | 0.095151 | 0.020869 | south | N | 0.020869 | 0
5729 | FALCONHY | 3 | 11 | -0.053355 | south | N | -0.17747 | -0.020869 | -0.15906 | 0.095151 | 0.020869 | south | N | 0.020869 | 0
5890 | PEARSALL | 1 | 24 | -0.037952 | south | Y | -0.16206 | -0.0054656 | -0.14366 | 0.11055 | 0.0054656 | south | N | 0.0054656 | 0
5891 | PEARSALL | 1 | 24 | -0.037952 | south | Y | -0.16206 | -0.0054656 | -0.14366 | 0.11055 | 0.0054656 | south | N | 0.0054656 | 0
5892 | PEARSALL | 1 | 23 | -0.037952 | south | Y | -0.16206 | -0.0054656 | -0.14366 | 0.11055 | 0.0054656 | south | N | 0.0054656 | 0
5903 | SANMIGUE | 1 | 396 | -0.044368 | south | Y | -0.16848 | -0.011882 | -0.15007 | 0.10414 | 0.011882 | south | N | 0.011882 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.10396 | houston | N | -0.22807 | -0.071473 | -0.20967 | 0.044547 | 0.044547 | houston | N | 0.044547 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.10396 | houston | N | -0.22807 | -0.071473 | -0.20967 | 0.044547 | 0.044547 | houston | N | 0.044547 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | Y | 0.12411 | 0
5932 | SI_RAY9 | 9 | 38 | -0.058388 | south | Y | -0.1825 | -0.025902 | -0.16409 | 0.090118 | 0.025902 | south | N | 0.025902 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.058388 | south | Y | -0.1825 | -0.025902 | -0.16409 | 0.090118 | 0.025902 | south | N | 0.025902 | 0
5934 | SI_RAY5 | 5 | 15 | -0.058388 | south | Y | -0.1825 | -0.025902 | -0.16409 | 0.090118 | 0.025902 | south | N | 0.025902 | 0
5935 | SI_RAY10 | 10 | 47 | -0.058388 | south | Y | -0.1825 | -0.025902 | -0.16409 | 0.090118 | 0.025902 | south | N | 0.025902 | 0
6016 | SWMESA | 1 | 75 | 0.098834 | west | Y | -0.025278 | 0.13132 | -0.0068723 | 0.24734 | 0.0068723 | west | N | 0.0068723 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | Y | 0.10571 | 0
6144 | MCADOO1A | 1 | 150 | 0.10758 | west | Y | -0.016529 | 0.14007 | 0.0018767 | 0.25609 | 0.0018767 | west | N | 0.0018767 | 0
6407 | TURKTRAK | 1 | 169.5 | 0.1048 | west | Y | -0.019307 | 0.13729 | -0.00090129 | 0.25331 | 0.00090129 | west | N | 0.00090129 | 0
6476 | LANGFORD | 1 | 150 | 0.076243 | west | Y | -0.047869 | 0.10873 | -0.029463 | 0.22475 | 0.029463 | west | N | 0.029463 | 0
6637 | SNYDERW1 | 1 | 63 | 0.10678 | west | Y | -0.017333 | 0.13927 | 0.0010727 | 0.25528 | 0.0010727 | west | N | 0.0010727 | 0
6752 | OKLA0A | 1 | 649.7 | 0.11072 | west | Y | -0.013395 | 0.1432 | 0.0050107 | 0.25922 | 0.0050107 | west | N | 0.0050107 | 0
6948 | DENISNDM | 1 | 40 | 0.11968 | north | N | -0.004429 | 0.15217 | 0.013977 | 0.26819 | 0.004429 | North | N | 0.004429 | 0
6948 | DENISNDM | 2 | 40 | 0.11968 | north | N | -0.004429 | 0.15217 | 0.013977 | 0.26819 | 0.004429 | North | N | 0.004429 | 0
7000 | L_FERGUS | 1 | 422 | 0.003035 | south | Y | -0.12108 | 0.035521 | -0.10267 | 0.15154 | 0.035521 | south | N | 0.035521 | 0
7004 | L_SIMGID | 1 | 132 | -0.010767 | south | Y | -0.13488 | 0.021719 | -0.11647 | 0.13774 | 0.021719 | south | N | 0.021719 | 0
7005 | L_SIMGID | 2 | 134 | -0.010767 | south | Y | -0.13488 | 0.021719 | -0.11647 | 0.13774 | 0.021719 | south | N | 0.021719 | 0
7006 | L_SIMGID | 3 | 323 | -0.010767 | south | Y | -0.13488 | 0.021719 | -0.11647 | 0.13774 | 0.021719 | south | N | 0.021719 | 0
7007 | L_LOSTPI | 1 | 158 | -0.012823 | south | Y | -0.13693 | 0.019663 | -0.11853 | 0.13568 | 0.019663 | south | N | 0.019663 | 0
7008 | L_LOSTPI | 2 | 160 | -0.012823 | south | Y | -0.13693 | 0.019663 | -0.11853 | 0.13568 | 0.019663 | south | N | 0.019663 | 0
7009 | L_LOSTPI | 3 | 175 | -0.012823 | south | Y | -0.13693 | 0.019663 | -0.11853 | 0.13568 | 0.019663 | south | N | 0.019663 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.02789 | south | Y | -0.152 | 0.0045964 | -0.1336 | 0.12062 | 0.0045964 | south | N | 0.0045964 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.02789 | south | Y | -0.152 | 0.0045964 | -0.1336 | 0.12062 | 0.0045964 | south | N | 0.0045964 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.028025 | south | Y | -0.15214 | 0.0044614 | -0.13373 | 0.12048 | 0.0044614 | south | N | 0.0044614 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.02758 | south | Y | -0.15169 | 0.0049064 | -0.13329 | 0.12093 | 0.0049064 | south | N | 0.0049064 | 0
7015 | L_HAYSEN | 2 | 225 | -0.02758 | south | Y | -0.15169 | 0.0049064 | -0.13329 | 0.12093 | 0.0049064 | south | N | 0.0049064 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.02758 | south | Y | -0.15169 | 0.0049064 | -0.13329 | 0.12093 | 0.0049064 | south | N | 0.0049064 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.02758 | south | Y | -0.15169 | 0.0049064 | -0.13329 | 0.12093 | 0.0049064 | south | N | 0.0049064 | 0
7020 | L_AUSTPL | 1 | 8 | -0.002969 | south | N | -0.12708 | 0.029517 | -0.10868 | 0.14554 | 0.029517 | south | N | 0.029517 | 0
7020 | L_AUSTPL | 2 | 8 | -0.002969 | south | N | -0.12708 | 0.029517 | -0.10868 | 0.14554 | 0.029517 | south | N | 0.029517 | 0
7022 | L_BUCHAN | 1 | 18 | 0.010901 | south | N | -0.11321 | 0.043387 | -0.094805 | 0.15941 | 0.043387 | south | N | 0.043387 | 0
7023 | L_BUCHAN | 2 | 18 | 0.010901 | south | N | -0.11321 | 0.043387 | -0.094805 | 0.15941 | 0.043387 | south | N | 0.043387 | 0
7024 | L_BUCHAN | 3 | 15 | 0.010901 | south | N | -0.11321 | 0.043387 | -0.094805 | 0.15941 | 0.043387 | south | N | 0.043387 | 0
7026 | L_INKSDA | 1 | 13.7 | 0.009505 | south | N | -0.11461 | 0.041991 | -0.096201 | 0.15801 | 0.041991 | south | N | 0.041991 | 0
7028 | L_MARBFA | 1 | 18 | 0.001843 | south | N | -0.12227 | 0.034329 | -0.10386 | 0.15035 | 0.034329 | south | N | 0.034329 | 0
7029 | L_MARBFA | 2 | 18 | 0.001843 | south | N | -0.12227 | 0.034329 | -0.10386 | 0.15035 | 0.034329 | south | N | 0.034329 | 0
7031 | L_MARSFO | 1 | 35 | -0.000858 | south | N | -0.12497 | 0.031628 | -0.10656 | 0.14765 | 0.031628 | south | N | 0.031628 | 0
7032 | L_MARSFO | 2 | 34 | -0.000858 | south | N | -0.12497 | 0.031628 | -0.10656 | 0.14765 | 0.031628 | south | N | 0.031628 | 0
7033 | L_MARSFO | 3 | 35 | -0.000858 | south | N | -0.12497 | 0.031628 | -0.10656 | 0.14765 | 0.031628 | south | N | 0.031628 | 0
7035 | L_WIRTZ_ | 1 | 28 | 0.003371 | south | N | -0.12074 | 0.035857 | -0.10234 | 0.15188 | 0.035857 | south | N | 0.035857 | 0
7036 | L_WIRTZ_ | 2 | 29 | 0.003371 | south | N | -0.12074 | 0.035857 | -0.10234 | 0.15188 | 0.035857 | south | N | 0.035857 | 0
7038 | L_DELAWA | 1 | 35 | 0.10471 | west | Y | -0.019404 | 0.13719 | -0.00099829 | 0.25321 | 0.00099829 | west | N | 0.00099829 | 0
7038 | L_DELAWA | 2 | 30 | 0.10471 | west | Y | -0.019404 | 0.13719 | -0.00099829 | 0.25321 | 0.00099829 | west | N | 0.00099829 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.024333 | south | Y | -0.14844 | 0.0081534 | -0.13004 | 0.12417 | 0.0081534 | south | N | 0.0081534 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.024333 | south | Y | -0.14844 | 0.0081534 | -0.13004 | 0.12417 | 0.0081534 | south | N | 0.0081534 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.024333 | south | Y | -0.14844 | 0.0081534 | -0.13004 | 0.12417 | 0.0081534 | south | N | 0.0081534 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.024333 | south | Y | -0.14844 | 0.0081534 | -0.13004 | 0.12417 | 0.0081534 | south | N | 0.0081534 | 0
7487 | L_CANYHY | 1 | 6 | -0.022345 | south | N | -0.14646 | 0.010141 | -0.12805 | 0.12616 | 0.010141 | south | N | 0.010141 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.030917 | south | N | -0.15503 | 0.0015694 | -0.13662 | 0.11759 | 0.0015694 | south | N | 0.0015694 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.030917 | south | N | -0.15503 | 0.0015694 | -0.13662 | 0.11759 | 0.0015694 | south | N | 0.0015694 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.030917 | south | N | -0.15503 | 0.0015694 | -0.13662 | 0.11759 | 0.0015694 | south | N | 0.0015694 | 0
7609 | L_SCHUMA | 1 | 4 | -0.032326 | south | N | -0.15644 | 0.00016043 | -0.13803 | 0.11618 | 0.00016043 | south | N | 0.00016043 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.033006 | south | N | -0.15712 | -0.00051957 | -0.13871 | 0.1155 | 0.00051957 | south | N | 0.00051957 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.033006 | south | N | -0.15712 | -0.00051957 | -0.13871 | 0.1155 | 0.00051957 | south | N | 0.00051957 | 0
7800 | L_GUADGE | 1 | 147 | -0.035903 | south | Y | -0.16001 | -0.0034166 | -0.14161 | 0.1126 | 0.0034166 | south | N | 0.0034166 | 0
7801 | L_GUADGE | 2 | 138 | -0.035903 | south | Y | -0.16001 | -0.0034166 | -0.14161 | 0.1126 | 0.0034166 | south | N | 0.0034166 | 0
7802 | L_GUADGE | 3 | 140 | -0.035903 | south | Y | -0.16001 | -0.0034166 | -0.14161 | 0.1126 | 0.0034166 | south | N | 0.0034166 | 0
7803 | L_GUADGE | 4 | 147 | -0.035903 | south | Y | -0.16001 | -0.0034166 | -0.14161 | 0.1126 | 0.0034166 | south | N | 0.0034166 | 0
7804 | L_GUADGE | 5 | 182 | -0.035903 | south | Y | -0.16001 | -0.0034166 | -0.14161 | 0.1126 | 0.0034166 | south | N | 0.0034166 | 0
7805 | L_GUADGE | 6 | 198 | -0.035903 | south | Y | -0.16001 | -0.0034166 | -0.14161 | 0.1126 | 0.0034166 | south | N | 0.0034166 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.010848 | south | Y | -0.13496 | 0.021638 | -0.11655 | 0.13766 | 0.021638 | south | N | 0.021638 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.010848 | south | Y | -0.13496 | 0.021638 | -0.11655 | 0.13766 | 0.021638 | south | N | 0.021638 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.010848 | south | Y | -0.13496 | 0.021638 | -0.11655 | 0.13766 | 0.021638 | south | N | 0.021638 | 0
7810 | L_RIONOG | 1 | 142 | -0.031859 | south | Y | -0.15597 | 0.00062743 | -0.13757 | 0.11665 | 0.00062743 | south | N | 0.00062743 | 0
7811 | L_RIONOG | 2 | 145 | -0.031859 | south | Y | -0.15597 | 0.00062743 | -0.13757 | 0.11665 | 0.00062743 | south | N | 0.00062743 | 0
7812 | L_RIONOG | 3 | 151 | -0.031859 | south | Y | -0.15597 | 0.00062743 | -0.13757 | 0.11665 | 0.00062743 | south | N | 0.00062743 | 0
7813 | L_RIONOG | 4 | 290 | -0.031859 | south | Y | -0.15597 | 0.00062743 | -0.13757 | 0.11665 | 0.00062743 | south | N | 0.00062743 | 0
8032 | AMISTADH | 1 | 33 | 0.00032 | south | N | -0.12379 | 0.032806 | -0.10539 | 0.14883 | 0.032806 | south | N | 0.032806 | 0
8033 | AMISTADH | 2 | 25 | 0.00032 | south | N | -0.12379 | 0.032806 | -0.10539 | 0.14883 | 0.032806 | south | N | 0.032806 | 0
8048 | FALCONHY | 1 | 12 | -0.053355 | south | N | -0.17747 | -0.020869 | -0.15906 | 0.095151 | 0.020869 | south | N | 0.020869 | 0
8066 | DUP1V#1 | 1 | 73 | -0.062505 | south | N | -0.18662 | -0.030019 | -0.16821 | 0.086001 | 0.030019 | south | N | 0.030019 | 0
8134 | FOR69CG0 | 1 | 79 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
8138 | FOR69CG0 | 2 | 81 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8147 | UCAR #2 | 10 | 28 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
8148 | UCAR #1 | 2 | 7 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
8153 | FOR69CG0 | 3 | 79 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
8154 | FOR69CG0 | 4 | 80 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
8156 | FOR69CG0 | 6 | 25 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
8157 | FOR69CG0 | 7 | 46 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
8161 | COLETOU1 | 1 | 629 | -0.055549 | south | Y | -0.17966 | -0.023063 | -0.16126 | 0.092957 | 0.023063 | south | N | 0.023063 | 0
8173 | VICEC51A | 5 | 144 | -0.061266 | south | Y | -0.18538 | -0.02878 | -0.16697 | 0.08724 | 0.02878 | south | N | 0.02878 | 0
8174 | VICEC61A | 6 | 188 | -0.061266 | south | Y | -0.18538 | -0.02878 | -0.16697 | 0.08724 | 0.02878 | south | N | 0.02878 | 0
8189 | CUERO 2 | 1 | 12 | -0.040629 | south | N | -0.16474 | -0.0081426 | -0.14634 | 0.10788 | 0.0081426 | south | N | 0.0081426 | 0
8262 | ELPS | 1 | 6 | -0.012179 | south | N | -0.13629 | 0.020307 | -0.11789 | 0.13633 | 0.020307 | south | N | 0.020307 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8442 | NBEC71A | 1 | 336 | -0.059937 | south | Y | -0.18405 | -0.027451 | -0.16564 | 0.088569 | 0.027451 | south | N | 0.027451 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.12411 | 0.032486 | -0.10571 | 0.14851 | 0.032486 | south | N | 0.032486 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.059659 | south | Y | -0.18377 | -0.027173 | -0.16537 | 0.088847 | 0.027173 | south | N | 0.027173 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.059659 | south | Y | -0.18377 | -0.027173 | -0.16537 | 0.088847 | 0.027173 | south | N | 0.027173 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.059447 | south | N | -0.18356 | -0.026961 | -0.16515 | 0.089059 | 0.026961 | south | N | 0.026961 | 0
8506 | VAL #1 | 1 | 25 | -0.059587 | south | N | -0.1837 | -0.027101 | -0.16529 | 0.088919 | 0.027101 | south | N | 0.027101 | 0
8507 | VAL #2 | 2 | 25 | -0.059587 | south | N | -0.1837 | -0.027101 | -0.16529 | 0.088919 | 0.027101 | south | N | 0.027101 | 0
8511 | OXY_CC0A | 1 | 38 | -0.059488 | south | N | -0.1836 | -0.027002 | -0.16519 | 0.089018 | 0.027002 | south | N | 0.027002 | 0
8517 | CELANEBI | 1 | 29 | -0.058846 | south | N | -0.18296 | -0.02636 | -0.16455 | 0.08966 | 0.02636 | south | N | 0.02636 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.059923 | south | N | -0.18403 | -0.027437 | -0.16563 | 0.088583 | 0.027437 | south | N | 0.027437 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.059923 | south | N | -0.18403 | -0.027437 | -0.16563 | 0.088583 | 0.027437 | south | N | 0.027437 | 0
8562 | CNOPST1 | 3 | 153 | -0.059923 | south | N | -0.18403 | -0.027437 | -0.16563 | 0.088583 | 0.027437 | south | N | 0.027437 | 0
8926 | LGE_GT10 | 1 | 158 | -0.061224 | south | N | -0.18534 | -0.028738 | -0.16693 | 0.087282 | 0.028738 | south | N | 0.028738 | 0
8927 | LGE_GT20 | 2 | 153 | -0.061224 | south | N | -0.18534 | -0.028738 | -0.16693 | 0.087282 | 0.028738 | south | N | 0.028738 | 0
8928 | LGE_STG0 | 3 | 100 | -0.061224 | south | N | -0.18534 | -0.028738 | -0.16693 | 0.087282 | 0.028738 | south | N | 0.028738 | 0
8930 | ICPGN10A | 1 | 145 | -0.061224 | south | N | -0.18534 | -0.028738 | -0.16693 | 0.087282 | 0.028738 | south | N | 0.028738 | 0
8931 | ICPGN20A | 2 | 147 | -0.061224 | south | N | -0.18534 | -0.028738 | -0.16693 | 0.087282 | 0.028738 | south | N | 0.028738 | 0
8932 | ICPGN30A | 3 | 127 | -0.061224 | south | N | -0.18534 | -0.028738 | -0.16693 | 0.087282 | 0.028738 | south | N | 0.028738 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.057279 | south | Y | -0.18139 | -0.024793 | -0.16299 | 0.091227 | 0.024793 | south | N | 0.024793 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.057279 | south | Y | -0.18139 | -0.024793 | -0.16299 | 0.091227 | 0.024793 | south | N | 0.024793 | 0
8935 | FGNTS201 | 3 | 173 | -0.057279 | south | Y | -0.18139 | -0.024793 | -0.16299 | 0.091227 | 0.024793 | south | N | 0.024793 | 0
8936 | MVGN#1 | 1 | 207 | -0.057924 | south | Y | -0.18204 | -0.025438 | -0.16363 | 0.090582 | 0.025438 | south | N | 0.025438 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.057924 | south | Y | -0.18204 | -0.025438 | -0.16363 | 0.090582 | 0.025438 | south | N | 0.025438 | 0
8938 | MVGN#3 | 3 | 242 | -0.057924 | south | Y | -0.18204 | -0.025438 | -0.16363 | 0.090582 | 0.025438 | south | N | 0.025438 | 0
8981 | HECN1 | 1 | 144 | -0.057928 | south | Y | -0.18204 | -0.025442 | -0.16363 | 0.090578 | 0.025442 | south | N | 0.025442 | 0
8982 | HECN2 | 2 | 144 | -0.057928 | south | Y | -0.18204 | -0.025442 | -0.16363 | 0.090578 | 0.025442 | south | N | 0.025442 | 0
8983 | HECN3 | 3 | 171 | -0.057928 | south | Y | -0.18204 | -0.025442 | -0.16363 | 0.090578 | 0.025442 | south | N | 0.025442 | 0
9000 | DECKR_G1 | 1 | 310 | -0.003099 | south | Y | -0.12721 | 0.029387 | -0.10881 | 0.14541 | 0.029387 | south | N | 0.029387 | 0
9001 | DECKR_G2 | 2 | 413 | -0.003099 | south | Y | -0.12721 | 0.029387 | -0.10881 | 0.14541 | 0.029387 | south | N | 0.029387 | 0
9002 | DECKR_G3 | 3 | 42 | -0.001924 | south | Y | -0.12604 | 0.030562 | -0.10763 | 0.14658 | 0.030562 | south | N | 0.030562 | 0
9003 | DECKR_G4 | 4 | 44 | -0.001924 | south | Y | -0.12604 | 0.030562 | -0.10763 | 0.14658 | 0.030562 | south | N | 0.030562 | 0
9004 | DECKR_G5 | 5 | 44 | -0.001924 | south | Y | -0.12604 | 0.030562 | -0.10763 | 0.14658 | 0.030562 | south | N | 0.030562 | 0
9005 | DECKR_G6 | 6 | 47 | -0.001924 | south | Y | -0.12604 | 0.030562 | -0.10763 | 0.14658 | 0.030562 | south | N | 0.030562 | 0
9016 | SANDH_G1 | 1 | 49 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
9017 | SANDH_G2 | 2 | 46 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
9018 | SANDH_G3 | 3 | 46 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
9019 | SANDH_G4 | 4 | 47 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
9020 | SANDHG5A | 5A | 154 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
9021 | SANDHG5C | 5C | 148 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
9022 | SANDH_G6 | 6 | 48 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
9023 | SANDH_G7 | 7 | 48 | -0.00492 | south | Y | -0.12903 | 0.027566 | -0.11063 | 0.14359 | 0.027566 | south | N | 0.027566 | 0
11001 | NAV1CT | 1 | 70 | 0.1057 | west | Y | -0.018407 | 0.13819 | -1.2945e-06 | 0.25421 | 1.2945e-06 | west | N | 1.2945e-06 | 0
11009 | NAV2CT | 1 | 70 | 0.1057 | west | Y | -0.018407 | 0.13819 | -1.2945e-06 | 0.25421 | 1.2945e-06 | west | N | 1.2945e-06 | 0
11011 | NAV3ST | 1 | 92.8 | 0.1057 | west | Y | -0.018407 | 0.13819 | -1.2945e-06 | 0.25421 | 1.2945e-06 | west | N | 1.2945e-06 | 0
11012 | NAV4CT | 1 | 80 | 0.1057 | west | Y | -0.018407 | 0.13819 | -1.2945e-06 | 0.25421 | 1.2945e-06 | west | N | 1.2945e-06 | 0
11013 | NAV5CT | 1 | 80 | 0.1057 | west | Y | -0.018407 | 0.13819 | -1.2945e-06 | 0.25421 | 1.2945e-06 | west | N | 1.2945e-06 | 0
11014 | NAV6ST | 1 | 115 | 0.1057 | west | Y | -0.018407 | 0.13819 | -1.2945e-06 | 0.25421 | 1.2945e-06 | west | N | 1.2945e-06 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.10569 | west | Y | -0.018417 | 0.13818 | -1.1294e-05 | 0.2542 | 1.1294e-05 | west | N | 1.1294e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.10569 | west | Y | -0.018417 | 0.13818 | -1.1294e-05 | 0.2542 | 1.1294e-05 | west | N | 1.1294e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.10569 | west | Y | -0.018417 | 0.13818 | -1.1294e-05 | 0.2542 | 1.1294e-05 | west | N | 1.1294e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.10569 | west | Y | -0.018417 | 0.13818 | -1.1294e-05 | 0.2542 | 1.1294e-05 | west | N | 1.1294e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.10569 | west | Y | -0.018417 | 0.13818 | -1.1294e-05 | 0.2542 | 1.1294e-05 | west | N | 1.1294e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.10569 | west | Y | -0.018417 | 0.13818 | -1.1294e-05 | 0.2542 | 1.1294e-05 | west | N | 1.1294e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.10756 | west | Y | -0.016552 | 0.14005 | 0.0018537 | 0.25607 | 0.0018537 | west | N | 0.0018537 | 0
11057 | CHAMPION | 1 | 126.5 | 0.10756 | west | Y | -0.016552 | 0.14005 | 0.0018537 | 0.25607 | 0.0018537 | west | N | 0.0018537 | 0
11058 | PYRON_1G | 1 | 249 | 0.10756 | west | Y | -0.016552 | 0.14005 | 0.0018537 | 0.25607 | 0.0018537 | west | N | 0.0018537 | 0
11059 | INADALE_ | 1 | 197 | 0.10756 | west | Y | -0.016552 | 0.14005 | 0.0018537 | 0.25607 | 0.0018537 | west | N | 0.0018537 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.10662 | west | Y | -0.017497 | 0.1391 | 0.00090871 | 0.25512 | 0.00090871 | west | N | 0.00090871 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.10662 | west | Y | -0.017497 | 0.1391 | 0.00090871 | 0.25512 | 0.00090871 | west | N | 0.00090871 | 0
11147 | NOTREES_ | 1 | 149 | 0.10489 | west | Y | -0.019227 | 0.13737 | -0.00082129 | 0.25339 | 0.00082129 | west | N | 0.00082129 | 0
11309 | BULLCREK | 1 | 180 | 0.10644 | west | Y | -0.017675 | 0.13892 | 0.00073071 | 0.25494 | 0.00073071 | west | N | 0.00073071 | 0
11310 | BULLCREK | 1 | 180 | 0.10644 | west | Y | -0.017675 | 0.13892 | 0.00073071 | 0.25494 | 0.00073071 | west | N | 0.00073071 | 0
11320 | COYOTE_1 | 1 | 225 | 0.10638 | west | Y | -0.017729 | 0.13887 | 0.00067671 | 0.25489 | 0.00067671 | west | N | 0.00067671 | 0
11415 | LORAINE_ | 1 | 125 | 0.10717 | west | Y | -0.016943 | 0.13966 | 0.0014627 | 0.25567 | 0.0014627 | west | N | 0.0014627 | 0
11416 | LORAINE_ | 1 | 125 | 0.10717 | west | Y | -0.016943 | 0.13966 | 0.0014627 | 0.25567 | 0.0014627 | west | N | 0.0014627 | 0
11691 | KMICHICT | 1 | 140 | 0.12008 | north | N | -0.004032 | 0.15257 | 0.014374 | 0.26859 | 0.004032 | North | N | 0.004032 | 0
11692 | KMICHICT | 2 | 141 | 0.12008 | north | N | -0.004032 | 0.15257 | 0.014374 | 0.26859 | 0.004032 | North | N | 0.004032 | 0
11693 | KMICHIST | 3 | 309 | 0.12008 | north | N | -0.004032 | 0.15257 | 0.014374 | 0.26859 | 0.004032 | North | N | 0.004032 | 0
11694 | KMICHICT | 4 | 143 | 0.12008 | north | N | -0.004032 | 0.15257 | 0.014374 | 0.26859 | 0.004032 | North | N | 0.004032 | 0
11695 | KMICHICT | 5 | 144 | 0.12008 | north | N | -0.004032 | 0.15257 | 0.014374 | 0.26859 | 0.004032 | North | N | 0.004032 | 0
11696 | KMICHIST | 6 | 310 | 0.12008 | north | N | -0.004032 | 0.15257 | 0.014374 | 0.26859 | 0.004032 | North | N | 0.004032 | 0
12322 | ENNSTRAC | 1 | 196 | 0.11847 | north | Y | -0.005639 | 0.15096 | 0.012767 | 0.26698 | 0.005639 | North | N | 0.005639 | 0
12323 | ENNSTRAC | 2 | 111 | 0.11847 | north | Y | -0.005639 | 0.15096 | 0.012767 | 0.26698 | 0.005639 | North | N | 0.005639 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.11941 | north | N | -0.004704 | 0.15189 | 0.013702 | 0.26791 | 0.004704 | North | N | 0.004704 | 0
12411 | FPLEFR1A | 1 | 161 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12412 | FPLEFR1B | 2 | 164 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12413 | FPLEFR1C | 3 | 164 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12414 | FPLEFR1S | 4 | 414 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12421 | FPLEFR2A | 1 | 162 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12422 | FPLEFR2B | 2 | 161 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12423 | FPLEFR2C | 3 | 163 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12424 | FPLEFR2S | 4 | 409 | 0.12151 | north | Y | -0.002598 | 0.154 | 0.015808 | 0.27002 | 0.002598 | North | N | 0.002598 | 0
12440 | PARKD_1S | 1 | 0 | 0.12053 | north | N | -0.003579 | 0.15302 | 0.014827 | 0.26904 | 0.003579 | North | N | 0.003579 | 0
12449 | PARKD_2S | 1 | 0 | 0.12053 | north | N | -0.003579 | 0.15302 | 0.014827 | 0.26904 | 0.003579 | North | N | 0.003579 | 0
13116 | TGATEWAY | 1 | 148 | 0.12544 | north | N | 0.001325 | 0.15792 | 0.019731 | 0.27394 | 0.001325 | North | N | 0.001325 | 0
13117 | TGATEWAY | 2 | 130 | 0.12544 | north | N | 0.001325 | 0.15792 | 0.019731 | 0.27394 | 0.001325 | North | N | 0.001325 | 0
13118 | TGATEWAY | 3 | 145 | 0.12544 | north | N | 0.001325 | 0.15792 | 0.019731 | 0.27394 | 0.001325 | North | N | 0.001325 | 0
13119 | TGATEWAY | 4 | 399 | 0.12544 | north | N | 0.001325 | 0.15792 | 0.019731 | 0.27394 | 0.001325 | North | N | 0.001325 | 0
13131 | CALFREST | 1 | 150.7 | 0.13126 | north | Y | 0.007144 | 0.16374 | 0.02555 | 0.27976 | 0.007144 | North | N | 0.007144 | 0
13132 | CALFREST | 2 | 151 | 0.13126 | north | Y | 0.007144 | 0.16374 | 0.02555 | 0.27976 | 0.007144 | North | N | 0.007144 | 0
13133 | CALFREST | 3 | 177.4 | 0.13126 | north | Y | 0.007144 | 0.16374 | 0.02555 | 0.27976 | 0.007144 | North | N | 0.007144 | 0
13134 | CALFREST | 4 | 151.5 | 0.13103 | north | Y | 0.006921 | 0.16352 | 0.025327 | 0.27954 | 0.006921 | North | N | 0.006921 | 0
13135 | CALFREST | 5 | 152.3 | 0.13103 | north | Y | 0.006921 | 0.16352 | 0.025327 | 0.27954 | 0.006921 | North | N | 0.006921 | 0
13136 | CALFREST | 6 | 177.5 | 0.13103 | north | Y | 0.006921 | 0.16352 | 0.025327 | 0.27954 | 0.006921 | North | N | 0.006921 | 0
13432 | SANDOW_5 | 5 | 581 | 0.029157 | south | Y | -0.094955 | 0.061643 | -0.076549 | 0.17766 | 0.061643 | south | N | 0.061643 | 0
13691 | OAKGROVE | 1 | 855 | 0.15526 | north | Y | 0.031144 | 0.18774 | 0.04955 | 0.30376 | 0.031144 | North | N | 0.031144 | 0
13692 | OAKGROVE | 2 | 855 | 0.15526 | north | Y | 0.031144 | 0.18774 | 0.04955 | 0.30376 | 0.031144 | North | N | 0.031144 | 0
32798 | BRYN_TAM | 1 | 32 | 0.16595 | north | N | 0.041835 | 0.19843 | 0.060241 | 0.31445 | 0.041835 | North | N | 0.041835 | 0
32883 | BRYN_DNS | 1 | 48 | 0.16178 | north | Y | 0.037671 | 0.19427 | 0.056077 | 0.31029 | 0.037671 | North | N | 0.037671 | 0
32884 | BRYN_DNS | 1 | 46 | 0.16178 | north | Y | 0.037671 | 0.19427 | 0.056077 | 0.31029 | 0.037671 | North | N | 0.037671 | 0
32886 | BRYN_ATK | MB | 12 | 0.16558 | north | Y | 0.041469 | 0.19807 | 0.059875 | 0.31409 | 0.041469 | North | N | 0.041469 | 0
32887 | BRYN_ATK | MB | 51 | 0.16558 | north | Y | 0.041469 | 0.19807 | 0.059875 | 0.31409 | 0.041469 | North | N | 0.041469 | 0
32888 | BRYN_ATK | 1 | 17 | 0.16558 | north | Y | 0.041469 | 0.19807 | 0.059875 | 0.31409 | 0.041469 | North | N | 0.041469 | 0
32890 | BRYN_ATK | MB | 22 | 0.16558 | north | Y | 0.041469 | 0.19807 | 0.059875 | 0.31409 | 0.041469 | North | N | 0.041469 | 0
32891 | BRYN_ATK | MB | 25 | 0.16558 | north | Y | 0.041469 | 0.19807 | 0.059875 | 0.31409 | 0.041469 | North | N | 0.041469 | 0
32892 | BRYN_DNS | 1 | 105 | 0.16178 | north | Y | 0.037671 | 0.19427 | 0.056077 | 0.31029 | 0.037671 | North | N | 0.037671 | 0
36998 | RDCNYNG1 | 1 | 84 | 0.10698 | west | Y | -0.017136 | 0.13946 | 0.0012697 | 0.25548 | 0.0012697 | west | N | 0.0012697 | 0
38332 | WDWRDU2 | 1 | 80 | 0.098728 | west | Y | -0.025384 | 0.13121 | -0.0069783 | 0.24723 | 0.0069783 | west | N | 0.0069783 | 0
38437 | TNSRBNMS | 1 | 150 | 0.098674 | west | Y | -0.025438 | 0.13116 | -0.0070323 | 0.24718 | 0.0070323 | west | N | 0.0070323 | 0
38438 | TNSRBNMS | 1 | 150 | 0.098674 | west | Y | -0.025438 | 0.13116 | -0.0070323 | 0.24718 | 0.0070323 | west | N | 0.0070323 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38600 | TNBP_CGN | 5 | 53 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38614 | TNBPAMCG | 4 | 96 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38615 | TNBPAMCG | 1 | 244 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38690 | TNBP_CGN | 3 | 40 | -0.14754 | houston | N | -0.27166 | -0.11506 | -0.25325 | 0.00096183 | 0.00096183 | houston | N | 0.00096183 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.14751 | houston | N | -0.27162 | -0.11502 | -0.25321 | 0.00099983 | 0.00099983 | houston | N | 0.00099983 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.14751 | houston | N | -0.27162 | -0.11502 | -0.25321 | 0.00099983 | 0.00099983 | houston | N | 0.00099983 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.14751 | houston | N | -0.27162 | -0.11502 | -0.25321 | 0.00099983 | 0.00099983 | houston | N | 0.00099983 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.14751 | houston | N | -0.27162 | -0.11502 | -0.25321 | 0.00099983 | 0.00099983 | houston | N | 0.00099983 | 0
39470 | TNDOWCGN | 1 | 32 | -0.14751 | houston | N | -0.27162 | -0.11502 | -0.25321 | 0.00099883 | 0.00099883 | houston | N | 0.00099883 | 0
39480 | TNDOWCGN | 1 | 30 | -0.14751 | houston | N | -0.27162 | -0.11502 | -0.25321 | 0.00099883 | 0.00099883 | houston | N | 0.00099883 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.12627 | houston | N | -0.25038 | -0.093783 | -0.23198 | 0.022237 | 0.022237 | houston | N | 0.022237 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.12627 | houston | N | -0.25038 | -0.093783 | -0.23198 | 0.022237 | 0.022237 | houston | N | 0.022237 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.12627 | houston | N | -0.25038 | -0.093783 | -0.23198 | 0.022237 | 0.022237 | houston | N | 0.022237 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.12627 | houston | N | -0.25038 | -0.093783 | -0.23198 | 0.022237 | 0.022237 | houston | N | 0.022237 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.15526 | north | Y | 0.031144 | 0.18774 | 0.04955 | 0.30376 | 0.031144 | North | N | 0.031144 | 0
39970 | TNTNPONE | 1 | 153 | 0.15526 | north | Y | 0.031144 | 0.18774 | 0.04955 | 0.30376 | 0.031144 | North | N | 0.031144 | 0
48500 | APD_GT1_ | 1 | 136 | -0.16232 | houston | N | -0.28643 | -0.12983 | -0.26802 | -0.01381 | 0.01381 | houston | N | 0.01381 | 0
48510 | AK_GT1__ | 1 | 33 | -0.1403 | houston | N | -0.26441 | -0.10782 | -0.24601 | 0.0082038 | 0.0082038 | houston | N | 0.0082038 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.16413 | houston | Y | -0.28824 | -0.13164 | -0.26984 | -0.015625 | 0.015625 | houston | N | 0.015625 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.16413 | houston | Y | -0.28824 | -0.13164 | -0.26984 | -0.015625 | 0.015625 | houston | N | 0.015625 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.16413 | houston | Y | -0.28824 | -0.13164 | -0.26984 | -0.015625 | 0.015625 | houston | N | 0.015625 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.16413 | houston | Y | -0.28824 | -0.13164 | -0.26984 | -0.015625 | 0.015625 | houston | N | 0.015625 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.12436 | houston | N | -0.24847 | -0.091877 | -0.23007 | 0.024143 | 0.024143 | houston | N | 0.024143 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.12436 | houston | N | -0.24847 | -0.091877 | -0.23007 | 0.024143 | 0.024143 | houston | N | 0.024143 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.13371 | houston | N | -0.25782 | -0.10123 | -0.23942 | 0.014794 | 0.014794 | houston | N | 0.014794 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.13371 | houston | N | -0.25782 | -0.10123 | -0.23942 | 0.014794 | 0.014794 | houston | N | 0.014794 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.13371 | houston | N | -0.25782 | -0.10123 | -0.23942 | 0.014794 | 0.014794 | houston | N | 0.014794 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.15748 | houston | N | -0.2816 | -0.125 | -0.26319 | -0.0089782 | 0.0089782 | houston | N | 0.0089782 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.15748 | houston | N | -0.2816 | -0.125 | -0.26319 | -0.0089782 | 0.0089782 | houston | N | 0.0089782 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.15748 | houston | N | -0.2816 | -0.125 | -0.26319 | -0.0089782 | 0.0089782 | houston | N | 0.0089782 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.15748 | houston | N | -0.2816 | -0.125 | -0.26319 | -0.0089782 | 0.0089782 | houston | N | 0.0089782 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.16156 | houston | N | -0.28567 | -0.12907 | -0.26726 | -0.01305 | 0.01305 | houston | N | 0.01305 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.16156 | houston | N | -0.28567 | -0.12907 | -0.26726 | -0.01305 | 0.01305 | houston | N | 0.01305 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.15624 | houston | N | -0.28035 | -0.12375 | -0.26195 | -0.0077332 | 0.0077332 | houston | N | 0.0077332 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.15624 | houston | N | -0.28035 | -0.12375 | -0.26195 | -0.0077332 | 0.0077332 | houston | N | 0.0077332 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.15624 | houston | N | -0.28035 | -0.12375 | -0.26195 | -0.0077332 | 0.0077332 | houston | N | 0.0077332 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.15624 | houston | N | -0.28035 | -0.12375 | -0.26195 | -0.0077332 | 0.0077332 | houston | N | 0.0077332 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.15624 | houston | N | -0.28035 | -0.12375 | -0.26195 | -0.0077332 | 0.0077332 | houston | N | 0.0077332 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.16985 | houston | Y | -0.29396 | -0.13736 | -0.27555 | -0.021342 | 0.021342 | houston | N | 0.021342 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.1676 | houston | Y | -0.29171 | -0.13511 | -0.2733 | -0.019091 | 0.019091 | houston | N | 0.019091 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.17149 | houston | Y | -0.2956 | -0.139 | -0.2772 | -0.022985 | 0.022985 | houston | N | 0.022985 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.17149 | houston | Y | -0.2956 | -0.139 | -0.2772 | -0.022985 | 0.022985 | houston | N | 0.022985 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.17149 | houston | Y | -0.2956 | -0.139 | -0.2772 | -0.022985 | 0.022985 | houston | N | 0.022985 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.1901 | houston | N | -0.31421 | -0.15761 | -0.29581 | -0.041594 | 0.041594 | houston | N | 0.041594 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.16293 | houston | N | -0.28704 | -0.13045 | -0.26864 | -0.014426 | 0.014426 | houston | N | 0.014426 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.16293 | houston | N | -0.28704 | -0.13045 | -0.26864 | -0.014426 | 0.014426 | houston | N | 0.014426 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.17392 | houston | N | -0.29803 | -0.14143 | -0.27962 | -0.025411 | 0.025411 | houston | N | 0.025411 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.17392 | houston | N | -0.29803 | -0.14143 | -0.27962 | -0.025411 | 0.025411 | houston | N | 0.025411 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.17392 | houston | N | -0.29803 | -0.14143 | -0.27962 | -0.025411 | 0.025411 | houston | N | 0.025411 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.17392 | houston | N | -0.29803 | -0.14143 | -0.27962 | -0.025411 | 0.025411 | houston | N | 0.025411 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.1617 | houston | N | -0.28581 | -0.12921 | -0.26741 | -0.013193 | 0.013193 | houston | N | 0.013193 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.1617 | houston | N | -0.28581 | -0.12921 | -0.26741 | -0.013193 | 0.013193 | houston | N | 0.013193 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.1617 | houston | N | -0.28581 | -0.12921 | -0.26741 | -0.013193 | 0.013193 | houston | N | 0.013193 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.1617 | houston | N | -0.28581 | -0.12921 | -0.26741 | -0.013193 | 0.013193 | houston | N | 0.013193 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.16204 | houston | N | -0.28615 | -0.12955 | -0.26775 | -0.013534 | 0.013534 | houston | N | 0.013534 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.16204 | houston | N | -0.28615 | -0.12955 | -0.26775 | -0.013534 | 0.013534 | houston | N | 0.013534 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.16204 | houston | N | -0.28615 | -0.12955 | -0.26775 | -0.013534 | 0.013534 | houston | N | 0.013534 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.16204 | houston | N | -0.28615 | -0.12955 | -0.26775 | -0.013534 | 0.013534 | houston | N | 0.013534 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.16204 | houston | N | -0.28615 | -0.12955 | -0.26775 | -0.013534 | 0.013534 | houston | N | 0.013534 | 0
48651 | EP_1_2 | 1 | 5 | -0.16803 | houston | N | -0.29214 | -0.13554 | -0.27373 | -0.019522 | 0.019522 | houston | N | 0.019522 | 0
48651 | EP_1_2 | 2 | 21 | -0.16803 | houston | N | -0.29214 | -0.13554 | -0.27373 | -0.019522 | 0.019522 | houston | N | 0.019522 | 0
48671 | FTR_GT1_ | 1 | 154.2 | -0.76934 | north | N | -0.89345 | -0.73686 | -0.87505 | -0.62084 | 0.62084 | houston | Y | 0.89345 | 0
48672 | FTR_GT2_ | 2 | 156 | -0.76934 | north | N | -0.89345 | -0.73686 | -0.87505 | -0.62084 | 0.62084 | houston | Y | 0.89345 | 0
48673 | FTR_GT3_ | 3 | 156 | -0.76934 | north | N | -0.89345 | -0.73686 | -0.87505 | -0.62084 | 0.62084 | houston | Y | 0.89345 | 0
48674 | FTR_CN4_ | 4 | 380 | -0.76934 | north | N | -0.89345 | -0.73686 | -0.87505 | -0.62084 | 0.62084 | houston | Y | 0.89345 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.17066 | houston | Y | -0.29477 | -0.13817 | -0.27637 | -0.022153 | 0.022153 | houston | N | 0.022153 | 0
48691 | GBY_7374 | A | 46 | -0.15259 | houston | Y | -0.2767 | -0.1201 | -0.25829 | -0.0040822 | 0.0040822 | houston | N | 0.0040822 | 0
48691 | GBY_7374 | B | 46 | -0.15259 | houston | Y | -0.2767 | -0.1201 | -0.25829 | -0.0040822 | 0.0040822 | houston | N | 0.0040822 | 0
48692 | GBY_8182 | C | 46 | -0.15259 | houston | Y | -0.2767 | -0.1201 | -0.25829 | -0.0040822 | 0.0040822 | houston | N | 0.0040822 | 0
48692 | GBY_8182 | D | 55 | -0.15259 | houston | Y | -0.2767 | -0.1201 | -0.25829 | -0.0040822 | 0.0040822 | houston | N | 0.0040822 | 0
48693 | GBY_8384 | E | 55 | -0.15259 | houston | Y | -0.2767 | -0.1201 | -0.25829 | -0.0040822 | 0.0040822 | houston | N | 0.0040822 | 0
48693 | GBY_8384 | F | 54 | -0.15259 | houston | Y | -0.2767 | -0.1201 | -0.25829 | -0.0040822 | 0.0040822 | houston | N | 0.0040822 | 0
48721 | LEG_1___ | 1 | 827 | 0.14627 | north | Y | 0.022161 | 0.17876 | 0.040567 | 0.29478 | 0.022161 | North | N | 0.022161 | 0
48722 | LEG_2___ | 2 | 819 | 0.14627 | north | Y | 0.022161 | 0.17876 | 0.040567 | 0.29478 | 0.022161 | North | N | 0.022161 | 0
48730 | MNS_GT | 1 | 46.1 | -0.13845 | houston | N | -0.26256 | -0.10596 | -0.24415 | 0.010061 | 0.010061 | houston | N | 0.010061 | 0
48731 | CBE_GT1 | 1 | 76 | -0.10178 | houston | Y | -0.22589 | -0.069289 | -0.20748 | 0.046731 | 0.046731 | houston | N | 0.046731 | 0
48732 | CBE_GT2 | 1 | 76 | -0.10178 | houston | Y | -0.22589 | -0.069289 | -0.20748 | 0.046731 | 0.046731 | houston | N | 0.046731 | 0
48733 | CBE_ST12 | 1 | 105 | -0.10178 | houston | Y | -0.22589 | -0.069289 | -0.20748 | 0.046731 | 0.046731 | houston | N | 0.046731 | 0
48734 | CBE_GT3 | 1 | 74 | -0.10178 | houston | Y | -0.22589 | -0.069289 | -0.20748 | 0.046731 | 0.046731 | houston | N | 0.046731 | 0
48735 | CBE_GT4 | 1 | 74 | -0.10178 | houston | Y | -0.22589 | -0.069289 | -0.20748 | 0.046731 | 0.046731 | houston | N | 0.046731 | 0
48736 | CBE_ST34 | 1 | 102 | -0.10178 | houston | Y | -0.22589 | -0.069289 | -0.20748 | 0.046731 | 0.046731 | houston | N | 0.046731 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.16173 | houston | N | -0.28584 | -0.12924 | -0.26744 | -0.013225 | 0.013225 | houston | N | 0.013225 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.16173 | houston | N | -0.28584 | -0.12924 | -0.26744 | -0.013225 | 0.013225 | houston | N | 0.013225 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.16173 | houston | N | -0.28584 | -0.12924 | -0.26744 | -0.013225 | 0.013225 | houston | N | 0.013225 | 0
48761 | PR_GT1__ | 1 | 35 | -0.16068 | houston | N | -0.2848 | -0.1282 | -0.26639 | -0.012178 | 0.012178 | houston | N | 0.012178 | 0
48772 | PHR_GN2_ | MB | 459 | -0.15351 | houston | Y | -0.27762 | -0.12103 | -0.25922 | -0.0050062 | 0.0050062 | houston | N | 0.0050062 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.16731 | houston | N | -0.29142 | -0.13482 | -0.27301 | -0.018801 | 0.018801 | houston | N | 0.018801 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.16731 | houston | N | -0.29142 | -0.13482 | -0.27301 | -0.018801 | 0.018801 | houston | N | 0.018801 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.16731 | houston | N | -0.29142 | -0.13482 | -0.27301 | -0.018801 | 0.018801 | houston | N | 0.018801 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.16731 | houston | N | -0.29142 | -0.13482 | -0.27301 | -0.018801 | 0.018801 | houston | N | 0.018801 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.16731 | houston | N | -0.29142 | -0.13482 | -0.27301 | -0.018801 | 0.018801 | houston | N | 0.018801 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.16731 | houston | N | -0.29142 | -0.13482 | -0.27301 | -0.018801 | 0.018801 | houston | N | 0.018801 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.16731 | houston | N | -0.29142 | -0.13482 | -0.27301 | -0.018801 | 0.018801 | houston | N | 0.018801 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.1901 | houston | N | -0.31421 | -0.15761 | -0.29581 | -0.041594 | 0.041594 | houston | N | 0.041594 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.1901 | houston | N | -0.31421 | -0.15761 | -0.29581 | -0.041594 | 0.041594 | houston | N | 0.041594 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.1901 | houston | N | -0.31421 | -0.15761 | -0.29581 | -0.041594 | 0.041594 | houston | N | 0.041594 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.1901 | houston | N | -0.31421 | -0.15761 | -0.29581 | -0.041594 | 0.041594 | houston | N | 0.041594 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.1679 | houston | N | -0.29201 | -0.13541 | -0.2736 | -0.01939 | 0.01939 | houston | N | 0.01939 | 0
48820 | SHELLG1_ | 1 | 71 | -0.16262 | houston | N | -0.28673 | -0.13014 | -0.26833 | -0.014116 | 0.014116 | houston | N | 0.014116 | 0
48821 | SHELLG2 | 2 | 72 | -0.16262 | houston | N | -0.28673 | -0.13014 | -0.26833 | -0.014116 | 0.014116 | houston | N | 0.014116 | 0
48822 | SHELLG3_ | 1 | 39 | -0.16262 | houston | N | -0.28673 | -0.13014 | -0.26833 | -0.014116 | 0.014116 | houston | N | 0.014116 | 0
48822 | SHELLG3_ | 2 | 30 | -0.16262 | houston | N | -0.28673 | -0.13014 | -0.26833 | -0.014116 | 0.014116 | houston | N | 0.014116 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.15963 | houston | N | -0.28375 | -0.12715 | -0.26534 | -0.011128 | 0.011128 | houston | N | 0.011128 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.15963 | houston | N | -0.28375 | -0.12715 | -0.26534 | -0.011128 | 0.011128 | houston | N | 0.011128 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.16169 | houston | N | -0.2858 | -0.1292 | -0.26739 | -0.013182 | 0.013182 | houston | N | 0.013182 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.16151 | houston | Y | -0.28562 | -0.12902 | -0.26721 | -0.012999 | 0.012999 | houston | N | 0.012999 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.16145 | houston | Y | -0.28557 | -0.12897 | -0.26716 | -0.012949 | 0.012949 | houston | N | 0.012949 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.16167 | houston | Y | -0.28578 | -0.12919 | -0.26738 | -0.013167 | 0.013167 | houston | N | 0.013167 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.16172 | houston | Y | -0.28583 | -0.12923 | -0.26743 | -0.013215 | 0.013215 | houston | N | 0.013215 | 0
48855 | SRB_GT21 | B2 | 12 | -0.16142 | houston | Y | -0.28553 | -0.12893 | -0.26713 | -0.012914 | 0.012914 | houston | N | 0.012914 | 0
48855 | SRB_GT21 | MB | 18 | -0.16142 | houston | Y | -0.28553 | -0.12893 | -0.26713 | -0.012914 | 0.012914 | houston | N | 0.012914 | 0
48865 | TECO_GT1 | 1 | 50 | -0.14701 | houston | Y | -0.27112 | -0.11452 | -0.25271 | 0.0014988 | 0.0014988 | houston | N | 0.0014988 | 0
48873 | THW_ST3_ | 3 | 104 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48874 | THW_ST4_ | 4 | 104 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48875 | THW_3132 | A | 54 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48875 | THW_3132 | B | 53 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48877 | THW_3334 | C | 54 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48877 | THW_3334 | D | 57 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48879 | THW_4142 | E | 54 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48879 | THW_4142 | F | 54 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48881 | THW_4344 | G | 58 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48881 | THW_4344 | H | 58 | -0.14871 | houston | Y | -0.27282 | -0.11622 | -0.25441 | -0.00020217 | 0.00020217 | houston | N | 0.00020217 | 0
48883 | THW_GT1_ | B2 | 12 | -0.1515 | houston | Y | -0.27561 | -0.11902 | -0.25721 | -0.0029972 | 0.0029972 | houston | N | 0.0029972 | 0
48885 | THW_5152 | A | 56 | -0.15615 | houston | Y | -0.28027 | -0.12367 | -0.26186 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48885 | THW_5152 | B | 59 | -0.15615 | houston | Y | -0.28027 | -0.12367 | -0.26186 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48886 | THW_5354 | C | 56 | -0.15615 | houston | Y | -0.28027 | -0.12367 | -0.26186 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48886 | THW_5354 | D | 56 | -0.15615 | houston | Y | -0.28027 | -0.12367 | -0.26186 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48887 | THW_5556 | E | 59 | -0.15615 | houston | Y | -0.28027 | -0.12367 | -0.26186 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48887 | THW_5556 | F | 56 | -0.15615 | houston | Y | -0.28027 | -0.12367 | -0.26186 | -0.0076492 | 0.0076492 | houston | N | 0.0076492 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.10701 | houston | Y | -0.23112 | -0.074525 | -0.21272 | 0.041495 | 0.041495 | houston | N | 0.041495 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.13605 | houston | Y | -0.26017 | -0.10357 | -0.24176 | 0.012452 | 0.012452 | houston | N | 0.012452 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.13605 | houston | Y | -0.26017 | -0.10357 | -0.24176 | 0.012452 | 0.012452 | houston | N | 0.012452 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.13605 | houston | Y | -0.26017 | -0.10357 | -0.24176 | 0.012452 | 0.012452 | houston | N | 0.012452 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.13605 | houston | Y | -0.26017 | -0.10357 | -0.24176 | 0.012452 | 0.012452 | houston | N | 0.012452 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.13605 | houston | N | -0.26017 | -0.10357 | -0.24176 | 0.012452 | 0.012452 | houston | N | 0.012452 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.13363 | houston | Y | -0.25774 | -0.10114 | -0.23933 | 0.01488 | 0.01488 | houston | N | 0.01488 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.13363 | houston | Y | -0.25774 | -0.10114 | -0.23933 | 0.01488 | 0.01488 | houston | N | 0.01488 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.13363 | houston | Y | -0.25774 | -0.10114 | -0.23933 | 0.01488 | 0.01488 | houston | N | 0.01488 | 0
48929 | WAPGT21_ | B1 | 13 | -0.13605 | houston | Y | -0.26017 | -0.10357 | -0.24176 | 0.012452 | 0.012452 | houston | N | 0.012452 | 0
48940 | WARVUE_G | G1 | 12 | -0.1689 | houston | Y | -0.29301 | -0.13641 | -0.2746 | -0.020391 | 0.020391 | houston | N | 0.020391 | 0
49803 | EXN_15GT | 1 | 34 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49826 | EXN938GT | 5 | 45.9 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49828 | EXN941GT | 10 | 17.7 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49829 | EXN942GT | 11 | 20.4 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49830 | EXN943GT | 12 | 19.9 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49831 | EXN944GT | 13 | 35 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49832 | EXN945GT | 9 | 18 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49837 | EXN_GT | 4 | 85.4 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49838 | EXN_14GT | 14 | 148 | -0.16737 | houston | N | -0.29148 | -0.13488 | -0.27307 | -0.01886 | 0.01886 | houston | N | 0.01886 | 0
49851 | DOW17000 | 37 | 62 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49858 | DOW38100 | 31 | 71.4 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49859 | DOW38200 | 33 | 45 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49860 | DOW38300 | 32 | 101 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49862 | DOW39100 | 36 | 86 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49863 | DOW39200 | 35 | 88 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49865 | DOW41000 | 41 | 50 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49866 | DOW42000 | 42 | 18 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49869 | DOW49000 | 45 | 94 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49870 | DOW61000 | 61 | 70 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49871 | DOW62000 | 62 | 63 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49872 | DOW63000 | 63 | 72 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49873 | DOW64000 | 64 | 64.8 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49876 | DOW65000 | 65 | 101 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49877 | DOW66000 | 66 | 97 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49878 | DOW67000 | 67 | 103 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49882 | DOW81000 | 81 | 76 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49884 | DOW82000 | 82 | 80 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49885 | DOW83000 | 83 | 80 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
49886 | DOW84000 | 84 | 171 | -0.12153 | houston | N | -0.24564 | -0.089042 | -0.22723 | 0.026978 | 0.026978 | houston | N | 0.026978 | 0
58909 | PEARSALL | 1 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58909 | PEARSALL | 2 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58909 | PEARSALL | 3 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58909 | PEARSALL | 4 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58909 | PEARSALL | 5 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58909 | PEARSALL | 6 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58919 | PEARSALL | 1 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58919 | PEARSALL | 2 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58919 | PEARSALL | 3 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58919 | PEARSALL | 4 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58919 | PEARSALL | 5 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58919 | PEARSALL | 6 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58929 | PEARSALL | 1 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58929 | PEARSALL | 2 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58929 | PEARSALL | 3 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58929 | PEARSALL | 4 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58929 | PEARSALL | 5 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58929 | PEARSALL | 6 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58949 | PEARSALL | 1 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58949 | PEARSALL | 2 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58949 | PEARSALL | 3 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58949 | PEARSALL | 4 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58949 | PEARSALL | 5 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
58949 | PEARSALL | 6 | 8.4 | -0.036532 | south | Y | -0.16064 | -0.0040456 | -0.14224 | 0.11197 | 0.0040456 | south | N | 0.0040456 | 0
60000 | DSKY2 | 1 | 76.5 | 0.096188 | west | Y | -0.027924 | 0.12867 | -0.0095183 | 0.24469 | 0.0095183 | west | N | 0.0095183 | 0
60003 | KING_NE1 | 1 | 80 | 0.098834 | west | Y | -0.025278 | 0.13132 | -0.0068723 | 0.24734 | 0.0068723 | west | N | 0.0068723 | 0
60005 | KING_SE1 | 1 | 40 | 0.098834 | west | Y | -0.025278 | 0.13132 | -0.0068723 | 0.24734 | 0.0068723 | west | N | 0.0068723 | 0
60007 | KING_SW1 | 1 | 80 | 0.09926 | west | Y | -0.024852 | 0.13175 | -0.0064463 | 0.24777 | 0.0064463 | west | N | 0.0064463 | 0
60016 | WOODWRD1 | 1 | 80 | 0.098741 | west | Y | -0.025371 | 0.13123 | -0.0069653 | 0.24725 | 0.0069653 | west | N | 0.0069653 | 0
60017 | ORNNWP1 | 1 | 80 | 0.096544 | west | Y | -0.027568 | 0.12903 | -0.0091623 | 0.24505 | 0.0091623 | west | N | 0.0091623 | 0
60018 | DSKY1 | 1 | 84 | 0.095825 | west | Y | -0.028287 | 0.12831 | -0.0098813 | 0.24433 | 0.0098813 | west | N | 0.0098813 | 0
60019 | KING_NW1 | 1 | 80 | 0.09926 | west | Y | -0.024852 | 0.13175 | -0.0064463 | 0.24777 | 0.0064463 | west | N | 0.0064463 | 0
60057 | CALLAHAN | 1 | 114 | -0.029133 | south | Y | -0.15324 | 0.0033534 | -0.13484 | 0.11937 | 0.0033534 | south | N | 0.0033534 | 0
60058 | BUFF_GAP | 1 | 120 | 0.10636 | west | Y | -0.017749 | 0.13885 | 0.00065671 | 0.25487 | 0.00065671 | west | N | 0.00065671 | 0
60060 | CIRELLO | 1 | 233 | 0.10636 | west | Y | -0.017749 | 0.13885 | 0.00065671 | 0.25487 | 0.00065671 | west | N | 0.00065671 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.10636 | west | Y | -0.017749 | 0.13885 | 0.00065671 | 0.25487 | 0.00065671 | west | N | 0.00065671 | 0
60066 | H_HOLLOW | 1 | 222 | -0.029133 | south | Y | -0.15324 | 0.0033534 | -0.13484 | 0.11937 | 0.0033534 | south | N | 0.0033534 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.029133 | south | Y | -0.15324 | 0.0033534 | -0.13484 | 0.11937 | 0.0033534 | south | N | 0.0033534 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.029133 | south | Y | -0.15324 | 0.0033534 | -0.13484 | 0.11937 | 0.0033534 | south | N | 0.0033534 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.029133 | south | Y | -0.15324 | 0.0033534 | -0.13484 | 0.11937 | 0.0033534 | south | N | 0.0033534 | 0
60074 | HORSH5 | 1 | 100 | -0.029133 | south | Y | -0.15324 | 0.0033534 | -0.13484 | 0.11937 | 0.0033534 | south | N | 0.0033534 | 0
60081 | WHRLWIND | 1 | 60 | 0.10837 | west | Y | -0.015747 | 0.14085 | 0.0026587 | 0.25687 | 0.0026587 | west | N | 0.0026587 | 0
60201 | RIO DRCS | F | 0 | 0.025303 | south | N | -0.098809 | 0.057789 | -0.080403 | 0.17381 | 0.057789 | south | N | 0.057789 | 0
60202 | FRIEND_R | F | 0 | 0.084364 | west | N | -0.039748 | 0.11685 | -0.021342 | 0.23287 | 0.021342 | west | N | 0.021342 | 0
60203 | PRES0A | BT | 4.8 | 0.10084 | west | N | -0.023274 | 0.13332 | -0.0048683 | 0.24934 | 0.0048683 | west | N | 0.0048683 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.10747 | west | Y | -0.016641 | 0.13996 | 0.0017647 | 0.25598 | 0.0017647 | west | N | 0.0017647 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.10747 | west | Y | -0.016641 | 0.13996 | 0.0017647 | 0.25598 | 0.0017647 | west | N | 0.0017647 | 0
71057 | L_SWEETW | W1 | 135 | 0.10747 | west | Y | -0.016641 | 0.13996 | 0.0017647 | 0.25598 | 0.0017647 | west | N | 0.0017647 | 0
71059 | L_SWEETW | W1 | 119 | 0.10747 | west | Y | -0.016641 | 0.13996 | 0.0017647 | 0.25598 | 0.0017647 | west | N | 0.0017647 | 0
71060 | L_SWEETW | W1 | 105 | 0.10747 | west | Y | -0.016641 | 0.13996 | 0.0017647 | 0.25598 | 0.0017647 | west | N | 0.0017647 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.10747 | west | Y | -0.016641 | 0.13996 | 0.0017647 | 0.25598 | 0.0017647 | west | N | 0.0017647 | 0
76031 | L_GASCCR | W1 | 150 | 0.10572 | west | Y | -0.018389 | 0.13821 | 1.6706e-05 | 0.25423 | 1.6706e-05 | west | N | 1.6706e-05 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.1055 | west | Y | -0.018611 | 0.13799 | -0.00020529 | 0.25401 | 0.00020529 | west | N | 0.00020529 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.1055 | west | Y | -0.018611 | 0.13799 | -0.00020529 | 0.25401 | 0.00020529 | west | N | 0.00020529 | 0
76096 | L_CAPRSI | W1 | 186 | 0.1055 | west | Y | -0.018611 | 0.13799 | -0.00020529 | 0.25401 | 0.00020529 | west | N | 0.00020529 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.1055 | west | Y | -0.018611 | 0.13799 | -0.00020529 | 0.25401 | 0.00020529 | west | N | 0.00020529 | 0
80003 | MILHWYS | F | 0 | -0.058388 | south | N | -0.1825 | -0.025902 | -0.16409 | 0.090118 | 0.025902 | south | N | 0.025902 | 0
80010 | EPLVT1 | F | 0 | -0.015087 | south | N | -0.1392 | 0.017399 | -0.12079 | 0.13342 | 0.017399 | south | N | 0.017399 | 0
80012 | LAR | F | 0 | -0.043988 | south | N | -0.1681 | -0.011502 | -0.14969 | 0.10452 | 0.011502 | south | N | 0.011502 | 0
80051 | FORPVCM0 | 8 | 28 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
80053 | FOR69CG0 | 10 | 74 | -0.069858 | south | N | -0.19397 | -0.037372 | -0.17556 | 0.078648 | 0.037372 | south | N | 0.037372 | 0
80080 | GWINDT11 | 1 | 94 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80080 | GWINDT11 | 2 | 41 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80080 | GWINDT11 | 3 | 38 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80080 | GWINDT11 | 4 | 19 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80081 | GWINDT21 | 1 | 94 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80081 | GWINDT21 | 2 | 36 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80081 | GWINDT21 | 3 | 43 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80081 | GWINDT21 | 4 | 22 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80137 | CSDR89 | 8 | 39 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
80137 | CSDR89 | 9 | 15 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
80138 | CSDR7 | 7 | 7 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
80139 | CSDR56 | 5 | 15 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
80139 | CSDR56 | 6 | 39 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
80140 | CSDR11 | 11 | 39 | -0.065859 | south | N | -0.18997 | -0.033373 | -0.17157 | 0.082647 | 0.033373 | south | N | 0.033373 | 0
80180 | PNSCALT1 | 1 | 148 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80180 | PNSCALT1 | 2 | 50 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80181 | PNSCALT2 | 1 | 55 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80181 | PNSCALT2 | 2 | 50 | -0.058563 | south | Y | -0.18267 | -0.026077 | -0.16427 | 0.089943 | 0.026077 | south | N | 0.026077 | 0
80223 | REYSHR G | 1 | 12 | -0.061224 | south | N | -0.18534 | -0.028738 | -0.16693 | 0.087282 | 0.028738 | south | N | 0.028738 | 0
80224 | VISTRONG | 1 | 15 | -0.064631 | south | N | -0.18874 | -0.032145 | -0.17034 | 0.083875 | 0.032145 | south | N | 0.032145 | 0
80225 | VISTRONG | 2 | 23 | -0.064631 | south | N | -0.18874 | -0.032145 | -0.17034 | 0.083875 | 0.032145 | south | N | 0.032145 | 0
80226 | ALCOA G | 1 | 48 | -0.068928 | south | N | -0.19304 | -0.036442 | -0.17463 | 0.079578 | 0.036442 | south | N | 0.036442 | 0
80227 | AIRCO G | 1 | 8 | -0.06539 | south | N | -0.1895 | -0.032904 | -0.1711 | 0.083116 | 0.032904 | south | N | 0.032904 | 0
80261 | NBEC81A | 1 | 180 | -0.059898 | south | Y | -0.18401 | -0.027412 | -0.1656 | 0.088608 | 0.027412 | south | N | 0.027412 | 0
80262 | NBEC91A | 1 | 180 | -0.059937 | south | Y | -0.18405 | -0.027451 | -0.16564 | 0.088569 | 0.027451 | south | N | 0.027451 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.059659 | south | Y | -0.18377 | -0.027173 | -0.16537 | 0.088847 | 0.027173 | south | N | 0.027173 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.059659 | south | Y | -0.18377 | -0.027173 | -0.16537 | 0.088847 | 0.027173 | south | N | 0.027173 | 0
80265 | LARECU40 | 4 | 100 | -0.043984 | south | Y | -0.1681 | -0.011498 | -0.14969 | 0.10452 | 0.011498 | south | N | 0.011498 | 0
80266 | LARECU50 | 5 | 100 | -0.043984 | south | Y | -0.1681 | -0.011498 | -0.14969 | 0.10452 | 0.011498 | south | N | 0.011498 | 0
80291 | PAPALOTE | 1 | 25 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
80291 | PAPALOTE | 2 | 25 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
80291 | PAPALOTE | 3 | 25 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
80291 | PAPALOTE | 4 | 16 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
80294 | PAPALOTE | 5 | 25 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
80294 | PAPALOTE | 6 | 25 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
80294 | PAPALOTE | 7 | 25 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
80294 | PAPALOTE | 8 | 15 | -0.060712 | south | Y | -0.18482 | -0.028226 | -0.16642 | 0.087794 | 0.028226 | south | N | 0.028226 | 0
86104 | CID-138 | EQ | 0 | -0.043984 | south | N | -0.1681 | -0.011498 | -0.14969 | 0.10452 | 0.011498 | south | N | 0.011498 | 0
86105 | CID-230 | EQ | 500 | -0.043984 | south | N | -0.1681 | -0.011498 | -0.14969 | 0.10452 | 0.011498 | south | N | 0.011498 | 0
86106 | CUF-230 | EQ | 500 | -0.043984 | south | N | -0.1681 | -0.011498 | -0.14969 | 0.10452 | 0.011498 | south | N | 0.011498 | 0
86107 | CUF-138 | EQ | 0 | -0.043984 | south | N | -0.1681 | -0.011498 | -0.14969 | 0.10452 | 0.011498 | south | N | 0.011498 | 0
88198 | BEEVILLE | F | 0 | -0.052658 | south | N | -0.17677 | -0.020172 | -0.15836 | 0.095848 | 0.020172 | south | N | 0.020172 | 0
88253 | HAMILTON | F | 0 | 0.00032 | south | N | -0.12379 | 0.032806 | -0.10539 | 0.14883 | 0.032806 | south | N | 0.032806 | 0
88299 | ZAPATA | F | 0 | -0.049602 | south | N | -0.17371 | -0.017116 | -0.15531 | 0.098904 | 0.017116 | south | N | 0.017116 | 0
88508 | FALFURRI | F | 0 | -0.055465 | south | N | -0.17958 | -0.022979 | -0.16117 | 0.093041 | 0.022979 | south | N | 0.022979 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Singleton - Roans Prairie [ 44645 - 40600] C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.1782 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.5071 | 463 | 0.33089 | 153.2007 | 463 | 153.2007
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.16595 | north | 7 | N | N | Nnorth | Nnorth | 1 | 5.3103 | 0 | 0.31863 | 0 | 463 | 153.2007
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0 | 463 | 153.2007
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0 | 463 | 153.2007 | Weighted Shift Factors
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.16558 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8149 | 17 | 0.31827 | 5.4105 | 480 | 158.6113 | North | 0.12411
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0 | 480 | 158.6113 | Houston | -0.15269
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0 | 480 | 158.6113 |  | 0.2768
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.16178 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7656 | 48 | 0.31447 | 15.0945 | 528 | 173.7058
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.16178 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.442 | 46 | 0.31447 | 14.4656 | 574 | 188.1714 | Line Rating | 1710
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.16178 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.9872 | 105 | 0.31447 | 33.0193 | 679 | 221.1906 | Conc Gen | 2694.3
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 132.7439 | 855 | 0.30794 | 263.2905 | 1534 | 484.4811 | Weighted Imp. | 841.7864
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 132.7439 | 855 | 0.30794 | 263.2905 | 2389 | 747.7716 | PTDF | 0.31243
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.6455 | 152.3 | 0.30794 | 46.8996 | 2541.3 | 794.6712
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.7542 | 153 | 0.30794 | 47.1151 | 2694.3 | 841.7864 | Concentration | 1.1287
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.14627 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 120.9678 | 827 | 0.29896 | 247.2392
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.14627 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 119.7976 | 819 | 0.29896 | 244.8475
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.13244 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.4506 | 615 | 0.28513 | 175.3526
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.13244 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.7423 | 587 | 0.28513 | 167.369
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7803 | 150.7 | 0.28394 | 42.7901
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8197 | 151 | 0.28394 | 42.8753
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2848 | 177.4 | 0.28394 | 50.3713
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8515 | 151.5 | 0.28372 | 42.9834
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9563 | 152.3 | 0.28372 | 43.2104
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2584 | 177.5 | 0.28372 | 50.3601
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.12599 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.9307 | 182 | 0.27868 | 50.7196
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.12599 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.9806 | 484 | 0.27868 | 134.8807
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.12593 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.2963 | 50 | 0.27861 | 13.9306
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.12587 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.27856 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.5647 | 0 | 0.27812 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.3068 | 0 | 0.27812 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.1884 | 0 | 0.27812 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 50.0494 | 0 | 0.27812 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 98.0763 | 785 | 0.27762 | 217.9349
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 99.3257 | 795 | 0.27762 | 220.7112
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 97.4516 | 780 | 0.27762 | 216.5468
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.12167 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.2543 | 224 | 0.27436 | 61.456
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.5638 | 161 | 0.2742 | 44.1462
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9283 | 164 | 0.2742 | 44.9688
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9283 | 164 | 0.2742 | 44.9688
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 50.3068 | 414 | 0.2742 | 113.5188
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.6853 | 162 | 0.2742 | 44.4204
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.5638 | 161 | 0.2742 | 44.1462
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8068 | 163 | 0.2742 | 44.6946
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 49.6992 | 409 | 0.2742 | 112.1478
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.12076 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 46.8557 | 388 | 0.27345 | 106.0979
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.12076 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.1924 | 515 | 0.27345 | 140.8258
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.4124 | 20 | 0.27331 | 5.4661
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0155 | 25 | 0.27331 | 6.8326
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.9454 | 41 | 0.27331 | 11.2055
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12053 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27322 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12053 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27322 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8189 | 40 | 0.27316 | 10.9264
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.5171 | 79 | 0.27316 | 21.5793
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.7697 | 106 | 0.27316 | 28.9544
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 17.5885 | 146 | 0.27316 | 39.8806
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.12047 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1556 | 76 | 0.27316 | 20.7598
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.1525 | 558 | 0.27303 | 152.3514
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 69.6798 | 579 | 0.27303 | 158.085
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 97.2388 | 808 | 0.27303 | 220.6091
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.0184 | 0 | 0.27293 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.5716 | 0 | 0.27293 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6297 | 0 | 0.27293 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2282 | 160 | 0.27286 | 43.6579
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7475 | 156 | 0.27286 | 42.5665
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5545 | 196 | 0.27286 | 53.481
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7475 | 156 | 0.27286 | 42.5665
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.8676 | 157 | 0.27286 | 42.8394
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.7948 | 198 | 0.27286 | 54.0267
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.12008 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 44.4296 | 370 | 0.27277 | 100.9235
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.8112 | 0 | 0.27277 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.9313 | 0 | 0.27277 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.1047 | 0 | 0.27277 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.1714 | 0 | 0.27277 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.2915 | 0 | 0.27277 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.2248 | 0 | 0.27277 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.11986 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.376 | 170 | 0.27255 | 46.3327
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.11986 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.3267 | 520 | 0.27255 | 141.7235
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.11968 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7873 | 0 | 0.27237 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.11968 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7873 | 0 | 0.27237 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.11944 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.0938 | 118 | 0.27213 | 32.1108
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.11944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 13.7355 | 115 | 0.27213 | 31.2944
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.11944 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.4081 | 556 | 0.27213 | 151.3016
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.11941 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27209 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.11915 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27184 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11847 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2207 | 196 | 0.27116 | 53.1472
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11847 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.1505 | 111 | 0.27116 | 30.0987
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.11735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.041 | 60 | 0.27004 | 16.2022
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.11735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.393 | 63 | 0.27004 | 17.0123
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11623 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.5609 | 435 | 0.26892 | 116.9794
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.11616 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.068 | 112.5 | 0.26885 | 30.2452
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11599 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.8157 | 395 | 0.26868 | 106.1267
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11599 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.4552 | 435 | 0.26868 | 116.8737
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.11579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.057 | 216.4 | 0.26848 | 58.0982
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.11579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0222 | 216.1 | 0.26848 | 58.0177
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.11574 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26842 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.11574 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26842 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.11574 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26842 | 0
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.6771 | 224 | 0.26732 | 59.8788
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.9064 | 226 | 0.26732 | 60.4134
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3016 | 212 | 0.26732 | 56.671
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.1869 | 211 | 0.26732 | 56.4037
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.9988 | 288 | 0.26727 | 76.9724
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.8431 | 147 | 0.26727 | 39.288
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.8431 | 147 | 0.26727 | 39.288
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.11411 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26679 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2431 | 204 | 0.26662 | 54.3911
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9013 | 201 | 0.26662 | 53.5912
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.5728 | 242 | 0.26662 | 64.5228
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.7405 | 217.3 | 0.26654 | 57.9192
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3401 | 205 | 0.26654 | 54.6407
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.0138 | 272.4 | 0.26654 | 72.6055
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11357 | north | 3 | N | N | Nnorth | Nnorth | 1 | 131.4005 | 0 | 0.26626 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11357 | north | 3 | N | N | Nnorth | Nnorth | 1 | 131.5141 | 0 | 0.26626 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0385 | 18 | 0.26594 | 4.7869
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0385 | 18 | 0.26594 | 4.7869
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.3036 | 38 | 0.26594 | 10.1056
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8811 | 70 | 0.26527 | 18.5691
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7685 | 69 | 0.26527 | 18.3038
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7685 | 69 | 0.26527 | 18.3038
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.6559 | 68 | 0.26527 | 18.0386
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2472 | 20 | 0.26504 | 5.3009
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2472 | 20 | 0.26504 | 5.3009
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2472 | 20 | 0.26504 | 5.3009
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.9101 | 17 | 0.26504 | 4.5057
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.11228 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3474 | 0 | 0.26497 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.11228 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3474 | 0 | 0.26497 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.11224 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 41.0787 | 366 | 0.26492 | 96.9619
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.11214 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.4567 | 120 | 0.26483 | 31.779
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11184 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.79 | 168 | 0.26453 | 44.4412
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11184 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.0661 | 90 | 0.26453 | 23.8078
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.11159 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.0048 | 242 | 0.26428 | 63.9548
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11112 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.1116 | 73 | 0.2638 | 19.2577
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.223 | 119 | 0.2638 | 31.3927
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.7792 | 205 | 0.2638 | 54.0798
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.334 | 102 | 0.2638 | 26.908
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.6673 | 96 | 0.2638 | 25.3252
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.11072 | west | 4 | Y | N | Ywest | Nwest | 1 | 71.9328 | 649.7 | 0.2634 | 171.133
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.11016 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.1757 | 165 | 0.26284 | 43.3689
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.1095 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.8415 | 236 | 0.26218 | 61.8755
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10949 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.798 | 400 | 0.26218 | 104.8724
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10837 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5019 | 60 | 0.26105 | 15.6631
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.10759 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.4553 | 60 | 0.26028 | 15.6165
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.10758 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1375 | 150 | 0.26027 | 39.0404
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.48 | 209 | 0.26025 | 54.3914
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6063 | 126.5 | 0.26025 | 32.9211
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.7824 | 249 | 0.26025 | 64.8013
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1893 | 197 | 0.26025 | 51.2685
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0302 | 37.5 | 0.26016 | 9.7559
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5531 | 107.5 | 0.26016 | 27.9669
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.5086 | 135 | 0.26016 | 35.1212
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.789 | 119 | 0.26016 | 30.9587
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.2845 | 105 | 0.26016 | 27.3165
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6514 | 80.5 | 0.26016 | 20.9426
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10717 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3961 | 125 | 0.25986 | 32.4819
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10717 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3961 | 125 | 0.25986 | 32.4819
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.10704 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0561 | 150 | 0.25973 | 38.9591
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.10704 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8111 | 101 | 0.25973 | 26.2324
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.10698 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.986 | 84 | 0.25966 | 21.8116
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.10684 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.577 | 99 | 0.25952 | 25.6929
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.10684 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5171 | 61 | 0.25952 | 15.831
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 1 | 2.6709 | 0 | 0.25952 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8825 | 0 | 0.25952 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8825 | 0 | 0.25952 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.10682 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0618 | 141 | 0.25951 | 36.5905
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.10682 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8185 | 120 | 0.25951 | 31.1409
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.10678 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7271 | 63 | 0.25947 | 16.3463
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.0448 | 66 | 0.25943 | 17.1221
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.365 | 69 | 0.25943 | 17.9003
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.365 | 69 | 0.25943 | 17.9003
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.1515 | 67 | 0.25943 | 17.3815
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.1515 | 67 | 0.25943 | 17.3815
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.938 | 65 | 0.25943 | 16.8626
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9923 | 150 | 0.2593 | 38.8952
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.4553 | 220 | 0.2593 | 57.0462
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.323 | 200 | 0.2593 | 51.8602
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.9964 | 121.9 | 0.2593 | 31.6088
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 1 | 7.4513 | 0 | 0.25913 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 1 | 7.8132 | 0 | 0.25913 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 1 | 7.4939 | 0 | 0.25913 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10644 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1587 | 180 | 0.25912 | 46.6422
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10644 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1587 | 180 | 0.25912 | 46.6422
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.10638 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.9362 | 225 | 0.25907 | 58.2906
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7636 | 120 | 0.25905 | 31.0859
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.7826 | 233 | 0.25905 | 60.3584
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.103 | 170.2 | 0.25905 | 44.0902
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.10628 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7541 | 120 | 0.25897 | 31.0764
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.10626 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7513 | 120 | 0.25895 | 31.0737
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.10594 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7331 | 0 | 0.25862 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.10587 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6782 | 214.2 | 0.25856 | 55.3836
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.10575 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.628 | 100.5 | 0.25844 | 25.9729
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.10573 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1326 | 58 | 0.25842 | 14.9884
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.10572 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.8584 | 150 | 0.25841 | 38.7614
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3994 | 70 | 0.25839 | 18.0874
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3994 | 70 | 0.25839 | 18.0874
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.8094 | 92.8 | 0.25839 | 23.9787
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.4564 | 80 | 0.25839 | 20.6713
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.4564 | 80 | 0.25839 | 20.6713
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.1561 | 115 | 0.25839 | 29.715
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.0057 | 208.2 | 0.25838 | 53.7949
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.0193 | 142.1 | 0.25838 | 36.716
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.994 | 132.4 | 0.25838 | 34.2097
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3745 | 136 | 0.25838 | 35.1398
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.5372 | 147 | 0.25838 | 37.982
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.1959 | 210 | 0.25838 | 54.26
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8689 | 112.5 | 0.25819 | 29.0461
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7724 | 149.5 | 0.25819 | 38.599
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.6232 | 186 | 0.25819 | 48.0228
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.63 | 214.5 | 0.25819 | 55.3811
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.1052 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69431 | 6.6 | 0.25789 | 1.702
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.1052 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6083 | 34.3 | 0.25789 | 8.8455
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.10489 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.6279 | 149 | 0.25757 | 38.3781
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1048 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.7644 | 169.5 | 0.25749 | 43.6447
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.10471 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6648 | 35 | 0.25739 | 9.0088
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.10471 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1412 | 30 | 0.25739 | 7.7218
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9073 | 66 | 0.25734 | 16.9846
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.8026 | 65 | 0.25734 | 16.7272
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.012 | 67 | 0.25734 | 17.2419
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.012 | 67 | 0.25734 | 17.2419
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.012 | 67 | 0.25734 | 17.2419
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.10466 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25734 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.10466 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25734 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.10084 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.48402 | 0 | 0.25352 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.09926 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9408 | 80 | 0.25195 | 20.1557
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.09926 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9408 | 80 | 0.25195 | 20.1557
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4126 | 75 | 0.25152 | 18.864
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9067 | 80 | 0.25152 | 20.1216
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9534 | 40 | 0.25152 | 10.0608
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098741 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8993 | 80 | 0.25143 | 20.1142
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.098728 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8982 | 80 | 0.25141 | 20.1131
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.098674 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8011 | 150 | 0.25136 | 37.704
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.098674 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8011 | 150 | 0.25136 | 37.704
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.096544 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7235 | 80 | 0.24923 | 19.9384
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.096462 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4469 | 0 | 0.24915 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.096462 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4469 | 0 | 0.24915 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.096188 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3584 | 76.5 | 0.24887 | 19.0389
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.095825 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0493 | 84 | 0.24851 | 20.8749
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.09258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.887 | 150 | 0.24527 | 36.7899
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.09258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4064 | 80 | 0.24527 | 19.6213
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.090878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1739 | 255 | 0.24356 | 62.1088
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.090878 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.5408 | 149 | 0.24356 | 36.2911
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.090878 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9043 | 153 | 0.24356 | 37.2653
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.088923 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.24161 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.088923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.9824 | 787 | 0.24161 | 190.1464
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.087612 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2403 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.087612 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2403 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.084364 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.23705 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.076243 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4365 | 150 | 0.22893 | 34.3394
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.025303 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.17799 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.15269 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.15269 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.9133 | 100 | 0.12355 | 12.3553
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.029157 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 16.5903 | 569 | -0.094955 | -54.0294
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.029157 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 16.9402 | 581 | -0.094955 | -55.1688
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19622 | 0 | -0.11321 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19622 | 0 | -0.11321 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16351 | 0 | -0.11321 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.009505 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13022 | 0 | -0.11461 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003371 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.094388 | 0 | -0.12074 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003371 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.097759 | 0 | -0.12074 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.003035 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2808 | 422 | -0.12108 | -51.0945
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001843 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033174 | 0 | -0.12227 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001843 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033174 | 0 | -0.12227 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.00032 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01056 | 0 | -0.12379 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.00032 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008 | 0 | -0.12379 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.00032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12379 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12411 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12411 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03003 | 0 | -0.12497 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.029172 | 0 | -0.12497 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03003 | 0 | -0.12497 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.080808 | 42 | -0.12604 | -5.2935
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.084656 | 44 | -0.12604 | -5.5456
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.084656 | 44 | -0.12604 | -5.5456
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.090428 | 47 | -0.12604 | -5.9237
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.002969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.023752 | 0 | -0.12708 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.002969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.023752 | 0 | -0.12708 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.003099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.96069 | 310 | -0.12721 | -39.4354
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.003099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2799 | 413 | -0.12721 | -52.5381
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24108 | 49 | -0.12903 | -6.3226
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22632 | 46 | -0.12903 | -5.9355
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22632 | 46 | -0.12903 | -5.9355
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23124 | 47 | -0.12903 | -6.0645
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.00492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.75768 | 154 | -0.12903 | -19.8709
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.00492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.72816 | 148 | -0.12903 | -19.0967
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23616 | 48 | -0.12903 | -6.1935
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23616 | 48 | -0.12903 | -6.1935
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4212 | 132 | -0.13488 | -17.804
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4428 | 134 | -0.13488 | -18.0738
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.4777 | 323 | -0.13488 | -43.5659
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6543 | 152.5 | -0.13496 | -20.5814
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6218 | 149.5 | -0.13496 | -20.1765
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5232 | 232.6 | -0.13496 | -31.3917
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.012179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.073074 | 0 | -0.13629 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.026 | 158 | -0.13693 | -21.6357
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0517 | 160 | -0.13693 | -21.9096
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.244 | 175 | -0.13693 | -23.9636
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.015087 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1392 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.022345 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13407 | 0 | -0.14646 | 0
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1752 | 223.9 | -0.15169 | -33.9638
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2055 | 225 | -0.15169 | -34.1307
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1945 | 224.6 | -0.15169 | -34.07
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2524 | 226.7 | -0.15169 | -34.3886
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.02789 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.2878 | 584 | -0.152 | -88.7692
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.02789 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.5946 | 595 | -0.152 | -90.4412
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.028025 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.1348 | 433 | -0.15214 | -65.8753
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3212 | 114 | -0.15324 | -17.4699
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.4675 | 222 | -0.15324 | -34.0204
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.3605 | 184 | -0.15324 | -28.1971
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5258 | 224 | -0.15324 | -34.3269
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3503 | 115 | -0.15324 | -17.6232
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.074201 | 0 | -0.15503 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.074201 | 0 | -0.15503 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086568 | 0 | -0.15503 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.524 | 142 | -0.15597 | -22.1479
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6196 | 145 | -0.15597 | -22.6158
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8107 | 151 | -0.15597 | -23.5516
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2391 | 290 | -0.15597 | -45.2316
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.032326 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1293 | 0 | -0.15644 | 0
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.033006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.079214 | 0 | -0.15712 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.033006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.079214 | 0 | -0.15712 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.2777 | 147 | -0.16001 | -23.5222
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.9546 | 138 | -0.16001 | -22.0821
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.0264 | 140 | -0.16001 | -22.4021
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.2777 | 147 | -0.16001 | -23.5222
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.5343 | 182 | -0.16001 | -29.1227
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1088 | 198 | -0.16001 | -31.683
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.036794 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -14.9752 | 407 | -0.16091 | -65.4887
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.036821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1356 | 58 | -0.16093 | -9.3341
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.036821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.2771 | 89 | -0.16093 | -14.323
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6201 | 44 | -0.16093 | -7.0811
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6201 | 44 | -0.16093 | -7.0811
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5833 | 43 | -0.16093 | -6.9201
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6569 | 45 | -0.16093 | -7.242
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.036837 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.1768 | 412 | -0.16095 | -66.311
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.036837 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -14.7348 | 400 | -0.16095 | -64.3796
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.036862 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.6295 | 424 | -0.16097 | -68.253
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.036862 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.6663 | 425 | -0.16097 | -68.4139
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.036971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.7269 | 209 | -0.16108 | -33.6663
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.036971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.9857 | 216 | -0.16108 | -34.7939
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7007 | 46 | -0.16108 | -7.4098
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7376 | 47 | -0.16108 | -7.5709
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7007 | 46 | -0.16108 | -7.4098
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7007 | 46 | -0.16108 | -7.4098
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16113 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16113 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16113 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.037952 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.91085 | 24 | -0.16206 | -3.8895
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.037952 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.91085 | 24 | -0.16206 | -3.8895
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.037952 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.8729 | 23 | -0.16206 | -3.7275
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8847 | 155 | -0.16208 | -25.1221
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4542 | 170 | -0.16208 | -27.5533
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8847 | 155 | -0.16208 | -25.1221
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.03883 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.2012 | 546 | -0.16294 | -88.9663
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.03883 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -29.1225 | 750 | -0.16294 | -122.2065
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.040629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.48755 | 0 | -0.16474 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.043984 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3984 | 100 | -0.1681 | -16.8096
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.043984 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3984 | 100 | -0.1681 | -16.8096
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.043988 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.044368 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.5697 | 396 | -0.16848 | -66.7181
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.049602 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17371 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.052658 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17677 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64026 | 0 | -0.17747 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.58691 | 0 | -0.17747 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64026 | 0 | -0.17747 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.055465 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17958 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.055549 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -34.9403 | 629 | -0.17966 | -113.0068
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3914 | 146.5 | -0.18139 | -26.5738
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.4716 | 147.9 | -0.18139 | -26.8277
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9093 | 173 | -0.18139 | -31.3806
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.9903 | 207 | -0.18204 | -37.6814
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5521 | 216.7 | -0.18204 | -39.4472
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.0176 | 242 | -0.18204 | -44.0527
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3416 | 144 | -0.18204 | -26.2138
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3416 | 144 | -0.18204 | -26.2138
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9057 | 171 | -0.18204 | -31.1288
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.058388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1825 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2187 | 38 | -0.1825 | -6.935
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1269 | 19.3 | -0.1825 | -3.5222
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.87582 | 15 | -0.1825 | -2.7375
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.058388 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7442 | 47 | -0.1825 | -8.5775
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5049 | 94 | -0.18267 | -17.1714
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4011 | 41 | -0.18267 | -7.4897
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2254 | 38 | -0.18267 | -6.9416
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1127 | 19 | -0.18267 | -3.4708
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5049 | 94 | -0.18267 | -17.1714
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.1083 | 36 | -0.18267 | -6.5763
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.5182 | 43 | -0.18267 | -7.855
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2884 | 22 | -0.18267 | -4.0188
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.6673 | 148 | -0.18267 | -27.0359
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9282 | 50 | -0.18267 | -9.1337
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.221 | 55 | -0.18267 | -10.0471
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9282 | 50 | -0.18267 | -9.1337
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.058846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7065 | 0 | -0.18296 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.059447 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.259 | 0 | -0.18356 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.059488 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2605 | 0 | -0.1836 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.059587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4897 | 0 | -0.1837 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.059587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4897 | 0 | -0.1837 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.059659 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.9261 | 334 | -0.18377 | -61.3795
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.059659 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.2841 | 340 | -0.18377 | -62.4821
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.059659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7386 | 180 | -0.18377 | -33.0788
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.059659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7386 | 180 | -0.18377 | -33.0788
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.059898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7816 | 180 | -0.18401 | -33.1218
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.8866 | 0 | -0.18403 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.9046 | 0 | -0.18403 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.1682 | 0 | -0.18403 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.059937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.1388 | 336 | -0.18405 | -61.8405
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.059937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7887 | 180 | -0.18405 | -33.1288
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 25 | -0.18482 | -4.6206
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 25 | -0.18482 | -4.6206
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 25 | -0.18482 | -4.6206
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.97139 | 16 | -0.18482 | -2.9572
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 25 | -0.18482 | -4.6206
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 25 | -0.18482 | -4.6206
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 25 | -0.18482 | -4.6206
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91068 | 15 | -0.18482 | -2.7724
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6734 | 0 | -0.18534 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.3673 | 0 | -0.18534 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.1224 | 0 | -0.18534 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.8775 | 0 | -0.18534 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.9999 | 0 | -0.18534 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.7754 | 0 | -0.18534 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.061224 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.73469 | 0 | -0.18534 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.061266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8223 | 144 | -0.18538 | -26.6944
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.061266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.518 | 188 | -0.18538 | -34.8511
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9811 | 47.7 | -0.18661 | -8.9012
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3311 | 37.3 | -0.18661 | -6.9605
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8748 | 46 | -0.18661 | -8.584
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9998 | 48 | -0.18661 | -8.9572
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.062505 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.5629 | 0 | -0.18662 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.063137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.389 | 22 | -0.18725 | -4.1195
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.063137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.69451 | 11 | -0.18725 | -2.0597
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.063137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.69451 | 11 | -0.18725 | -2.0597
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.064631 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.96947 | 0 | -0.18874 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.064631 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4865 | 0 | -0.18874 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.06539 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.52312 | 0 | -0.1895 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8441 | 0 | -0.18997 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46101 | 0 | -0.18997 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.5685 | 0 | -0.18997 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98789 | 0 | -0.18997 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46101 | 0 | -0.18997 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98789 | 0 | -0.18997 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.5685 | 0 | -0.18997 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.5685 | 0 | -0.18997 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.068928 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3085 | 0 | -0.19304 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5188 | 0 | -0.19397 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6585 | 0 | -0.19397 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5188 | 0 | -0.19397 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5886 | 0 | -0.19397 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4769 | 0 | -0.19397 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7465 | 0 | -0.19397 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2135 | 0 | -0.19397 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.956 | 0 | -0.19397 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0458 | 0 | -0.19397 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.1695 | 0 | -0.19397 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.7349 | 76 | -0.22589 | -17.1674
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.7349 | 76 | -0.22589 | -17.1674
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.6864 | 105 | -0.22589 | -23.7181
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.5313 | 74 | -0.22589 | -16.7156
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.5313 | 74 | -0.22589 | -16.7156
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.3811 | 102 | -0.22589 | -23.0405
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.10396 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -138.5773 | 0 | -0.22807 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.10396 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -138.0576 | 0 | -0.22807 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.10701 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.0627 | 66 | -0.23112 | -15.2541
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5347 | 0 | -0.24564 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6771 | 0 | -0.24564 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4688 | 0 | -0.24564 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.2743 | 0 | -0.24564 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4514 | 0 | -0.24564 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6945 | 0 | -0.24564 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0764 | 0 | -0.24564 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1875 | 0 | -0.24564 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4236 | 0 | -0.24564 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.507 | 0 | -0.24564 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6563 | 0 | -0.24564 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.75 | 0 | -0.24564 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.875 | 0 | -0.24564 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.2743 | 0 | -0.24564 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7882 | 0 | -0.24564 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5174 | 0 | -0.24564 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2361 | 0 | -0.24564 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7222 | 0 | -0.24564 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7222 | 0 | -0.24564 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -20.7813 | 0 | -0.24564 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.12436 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8298 | 0 | -0.24847 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.12436 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2436 | 0 | -0.24847 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.0159 | 0 | -0.25038 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.0159 | 0 | -0.25038 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.026 | 0 | -0.25038 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8265 | 0 | -0.25038 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -86.9905 | 651 | -0.25774 | -167.7874
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -75.3651 | 564 | -0.25774 | -145.3642
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -80.1756 | 600 | -0.25774 | -154.6428
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.7951 | 0 | -0.25782 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.7951 | 0 | -0.25782 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.7594 | 0 | -0.25782 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.9047 | 161 | -0.26017 | -41.8867
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -22.585 | 166 | -0.26017 | -43.1876
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -33.7414 | 248 | -0.26017 | -64.5212
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.13605 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -74.2855 | 546 | -0.26017 | -142.0506
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.13605 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -87.4827 | 0 | -0.26017 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.13605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7687 | 13 | -0.26017 | -3.3822
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.13845 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3823 | 0 | -0.26256 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.1403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.63 | 0 | -0.26441 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.14701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.3503 | 50 | -0.27112 | -13.5559
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.7949 | 0 | -0.27162 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.7033 | 0 | -0.27162 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.1489 | 0 | -0.27162 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.0456 | 0 | -0.27162 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.14751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7202 | 0 | -0.27162 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.14751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4252 | 0 | -0.27162 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4461 | 0 | -0.27166 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.8412 | 0 | -0.27166 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8198 | 0 | -0.27166 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.6037 | 0 | -0.27166 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.648 | 0 | -0.27166 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.471 | 0 | -0.27166 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.1642 | 0 | -0.27166 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -36.0007 | 0 | -0.27166 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9018 | 0 | -0.27166 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.4656 | 104 | -0.27282 | -28.3733
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.4656 | 104 | -0.27282 | -28.3733
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.8815 | 53 | -0.27282 | -14.4595
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4764 | 57 | -0.27282 | -15.5507
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6251 | 58 | -0.27282 | -15.8236
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6251 | 58 | -0.27282 | -15.8236
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.818 | 12 | -0.27561 | -3.3074
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.019 | 46 | -0.2767 | -12.7282
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.019 | 46 | -0.2767 | -12.7282
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.019 | 46 | -0.2767 | -12.7282
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3923 | 55 | -0.2767 | -15.2185
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3923 | 55 | -0.2767 | -15.2185
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2398 | 54 | -0.2767 | -14.9418
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.15351 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.27762 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.2131 | 59 | -0.28027 | -16.5358
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.2131 | 59 | -0.28027 | -16.5358
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.2177 | 0 | -0.28035 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.6865 | 0 | -0.28035 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5928 | 0 | -0.28035 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.515 | 0 | -0.28035 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9061 | 0 | -0.28035 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2365 | 0 | -0.2816 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.449 | 0 | -0.2816 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2365 | 0 | -0.2816 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2365 | 0 | -0.2816 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.15963 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.4515 | 0 | -0.28375 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.15963 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.7707 | 0 | -0.28375 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.16068 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6239 | 0 | -0.2848 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.16142 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.937 | 12 | -0.28553 | -3.4264
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.16142 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.28553 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.16145 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -27.2859 | 169 | -0.28557 | -48.2608
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.16151 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.6483 | 165 | -0.28562 | -47.1268
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.16156 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.0718 | 0 | -0.28567 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.16156 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5173 | 0 | -0.28567 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.16167 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -34.4363 | 213 | -0.28578 | -60.8722
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.16169 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6193 | 0 | -0.2858 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.3487 | 0 | -0.28581 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2194 | 0 | -0.28581 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.3563 | 0 | -0.28581 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.901 | 0 | -0.28581 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.16172 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -36.8724 | 228 | -0.28583 | -65.1699
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.1116 | 0 | -0.28584 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.6505 | 0 | -0.28584 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.3918 | 0 | -0.28584 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.4449 | 0 | -0.28615 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.4565 | 0 | -0.28615 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.5213 | 0 | -0.28615 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.4403 | 0 | -0.28615 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -43.5888 | 0 | -0.28615 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.16232 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.075 | 0 | -0.28643 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5462 | 0 | -0.28673 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7088 | 0 | -0.28673 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3423 | 0 | -0.28673 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8787 | 0 | -0.28673 | 0
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.16293 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.1872 | 0 | -0.28704 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.16293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.9958 | 0 | -0.28704 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8935 | 42 | -0.28824 | -12.1062
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8935 | 42 | -0.28824 | -12.1062
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.237 | 38 | -0.28824 | -10.9532
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.237 | 38 | -0.28824 | -10.9532
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.875 | 0 | -0.29142 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0423 | 0 | -0.29142 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7115 | 0 | -0.29142 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5403 | 0 | -0.29142 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.373 | 0 | -0.29142 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -17.3999 | 0 | -0.29142 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.8711 | 0 | -0.29142 | 0
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6904 | 0 | -0.29148 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8076 | 0 | -0.29148 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4729 | 0 | -0.29148 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6821 | 0 | -0.29148 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9624 | 0 | -0.29148 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4143 | 0 | -0.29148 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3306 | 0 | -0.29148 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8578 | 0 | -0.29148 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0126 | 0 | -0.29148 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.2931 | 0 | -0.29148 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.7702 | 0 | -0.29148 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.1676 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -123.1838 | 735 | -0.29171 | -214.4061
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.1679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.3597 | 0 | -0.29201 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.16803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84014 | 0 | -0.29214 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.16803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5286 | 0 | -0.29214 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.1689 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.0268 | 12 | -0.29301 | -3.5161
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.16985 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -126.1971 | 743 | -0.29396 | -218.4123
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.17066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -67.9223 | 398 | -0.29477 | -117.3189
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -29.4965 | 172 | -0.2956 | -50.8437
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -29.4965 | 172 | -0.2956 | -50.8437
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -29.4965 | 172 | -0.2956 | -50.8437
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.3137 | 0 | -0.29803 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.0702 | 0 | -0.29803 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.6354 | 0 | -0.29803 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -46.8185 | 0 | -0.29803 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.8873 | 0 | -0.31421 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.6556 | 0 | -0.31421 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.2754 | 0 | -0.31421 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.2754 | 0 | -0.31421 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.1901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.7962 | 0 | -0.31421 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -118.6327 | 0 | -0.61666 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -120.0175 | 0 | -0.61666 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -120.0175 | 0 | -0.61666 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -292.3503 | 0 | -0.61666 | 0

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: Singleton - Roans Prairie [ 44645 - 40600] C:44645 SNGLTN - 45500 T_H_W__345B C:44645 SNGLTN - 44500 OBRIEN__345A | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -118.6327 | 0 | -0.61666 | 0 | 0 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -120.0175 | 0 | -0.61666 | 0 | 0 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -120.0175 | 0 | -0.61666 | 0 | 0 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.76934 | north | 1 | N | N | Nnorth | Nnorth | 1 | -292.3503 | 0 | -0.61666 | 0 | 0 | 0 | Weighted Shift Factors
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.8873 | 0 | -0.31421 | 0 | 0 | 0 | North | 0.12411
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.6556 | 0 | -0.31421 | 0 | 0 | 0 | Houston | -0.15269
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.2754 | 0 | -0.31421 | 0 | 0 | 0 |  | 0.2768
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.1901 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.2754 | 0 | -0.31421 | 0 | 0 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.1901 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -30.7962 | 0 | -0.31421 | 0 | 0 | 0 | Line Rating | 1710
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.3137 | 0 | -0.29803 | 0 | 0 | 0 | Conc Gen | 3395
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.0702 | 0 | -0.29803 | 0 | 0 | 0 | Weighted Imp. | 989.3383
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -27.6354 | 0 | -0.29803 | 0 | 0 | 0 | PTDF | 0.29141
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.17392 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -46.8185 | 0 | -0.29803 | 0 | 0 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -29.4965 | 172 | -0.2956 | -50.8437 | 172 | 50.8437 | Concentration | 1.0528
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -29.4965 | 172 | -0.2956 | -50.8437 | 344 | 101.6874
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.17149 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -29.4965 | 172 | -0.2956 | -50.8437 | 516 | 152.5311
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.17066 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -67.9223 | 398 | -0.29477 | -117.3189 | 914 | 269.85
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.16985 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -126.1971 | 743 | -0.29396 | -218.4123 | 1657 | 488.2623
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.1689 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -2.0268 | 0 | -0.29301 | 0 | 1657 | 488.2623
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.16803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.84014 | 0 | -0.29214 | 0 | 1657 | 488.2623
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.16803 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5286 | 0 | -0.29214 | 0 | 1657 | 488.2623
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.1679 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.3597 | 0 | -0.29201 | 0 | 1657 | 488.2623
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.1676 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -123.1838 | 735 | -0.29171 | -214.4061 | 2392 | 702.6684
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6904 | 0 | -0.29148 | 0 | 2392 | 702.6684
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8076 | 0 | -0.29148 | 0 | 2392 | 702.6684
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4729 | 0 | -0.29148 | 0 | 2392 | 702.6684
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6821 | 0 | -0.29148 | 0 | 2392 | 702.6684
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.9624 | 0 | -0.29148 | 0 | 2392 | 702.6684
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4143 | 0 | -0.29148 | 0 | 2392 | 702.6684
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.3306 | 0 | -0.29148 | 0 | 2392 | 702.6684
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8578 | 0 | -0.29148 | 0 | 2392 | 702.6684
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0126 | 0 | -0.29148 | 0 | 2392 | 702.6684
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.2931 | 0 | -0.29148 | 0 | 2392 | 702.6684
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.16737 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.7702 | 0 | -0.29148 | 0 | 2392 | 702.6684
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.875 | 0 | -0.29142 | 0 | 2392 | 702.6684
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.0423 | 0 | -0.29142 | 0 | 2392 | 702.6684
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7115 | 0 | -0.29142 | 0 | 2392 | 702.6684
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5403 | 0 | -0.29142 | 0 | 2392 | 702.6684
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.373 | 0 | -0.29142 | 0 | 2392 | 702.6684
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -17.3999 | 0 | -0.29142 | 0 | 2392 | 702.6684
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.16731 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.8711 | 0 | -0.29142 | 0 | 2392 | 702.6684
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8935 | 42 | -0.28824 | -12.1062 | 2434 | 714.7746
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.8935 | 42 | -0.28824 | -12.1062 | 2476 | 726.8808
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.237 | 38 | -0.28824 | -10.9532 | 2514 | 737.834
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.16413 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -6.237 | 38 | -0.28824 | -10.9532 | 2552 | 748.7872
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.16293 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -28.1872 | 0 | -0.28704 | 0 | 2552 | 748.7872
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.16293 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.9958 | 0 | -0.28704 | 0 | 2552 | 748.7872
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.5462 | 0 | -0.28673 | 0 | 2552 | 748.7872
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7088 | 0 | -0.28673 | 0 | 2552 | 748.7872
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3423 | 0 | -0.28673 | 0 | 2552 | 748.7872
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.16262 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.8787 | 0 | -0.28673 | 0 | 2552 | 748.7872
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.16232 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.075 | 0 | -0.28643 | 0 | 2552 | 748.7872
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -26.4449 | 0 | -0.28615 | 0 | 2552 | 748.7872
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.4565 | 0 | -0.28615 | 0 | 2552 | 748.7872
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.5213 | 0 | -0.28615 | 0 | 2552 | 748.7872
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.4403 | 0 | -0.28615 | 0 | 2552 | 748.7872
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.16204 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -43.5888 | 0 | -0.28615 | 0 | 2552 | 748.7872
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -29.1116 | 0 | -0.28584 | 0 | 2552 | 748.7872
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.6505 | 0 | -0.28584 | 0 | 2552 | 748.7872
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.16173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -25.3918 | 0 | -0.28584 | 0 | 2552 | 748.7872
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.16172 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -36.8724 | 228 | -0.28583 | -65.1699 | 2780 | 813.9572
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.3487 | 0 | -0.28581 | 0 | 2780 | 813.9572
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.2194 | 0 | -0.28581 | 0 | 2780 | 813.9572
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.3563 | 0 | -0.28581 | 0 | 2780 | 813.9572
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.1617 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.901 | 0 | -0.28581 | 0 | 2780 | 813.9572
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.16169 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.6193 | 0 | -0.2858 | 0 | 2780 | 813.9572
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.16167 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -34.4363 | 213 | -0.28578 | -60.8722 | 2993 | 874.8294
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.16156 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -24.0718 | 0 | -0.28567 | 0 | 2993 | 874.8294
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.16156 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.5173 | 0 | -0.28567 | 0 | 2993 | 874.8294
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.16151 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -26.6483 | 165 | -0.28562 | -47.1268 | 3158 | 921.9562
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.16145 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -27.2859 | 169 | -0.28557 | -48.2608 | 3327 | 970.217
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.16142 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.937 | 12 | -0.28553 | -3.4264 | 3339 | 973.6434
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.16142 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.28553 | 0 | 3339 | 973.6434
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.16068 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6239 | 0 | -0.2848 | 0 | 3339 | 973.6434
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.15963 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.4515 | 0 | -0.28375 | 0 | 3339 | 973.6434
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.15963 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -12.7707 | 0 | -0.28375 | 0 | 3339 | 973.6434
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2365 | 0 | -0.2816 | 0 | 3339 | 973.6434
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -9.449 | 0 | -0.2816 | 0 | 3339 | 973.6434
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2365 | 0 | -0.2816 | 0 | 3339 | 973.6434
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.15748 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.2365 | 0 | -0.2816 | 0 | 3339 | 973.6434
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -14.2177 | 0 | -0.28035 | 0 | 3339 | 973.6434
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.6865 | 0 | -0.28035 | 0 | 3339 | 973.6434
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -13.5928 | 0 | -0.28035 | 0 | 3339 | 973.6434
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.515 | 0 | -0.28035 | 0 | 3339 | 973.6434
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.15624 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9061 | 0 | -0.28035 | 0 | 3339 | 973.6434
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695 | 3395 | 989.3383
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.2131 | 59 | -0.28027 | -16.5358
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -9.2131 | 59 | -0.28027 | -16.5358
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.15615 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.7447 | 56 | -0.28027 | -15.695
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.15351 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.27762 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.019 | 46 | -0.2767 | -12.7282
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.019 | 46 | -0.2767 | -12.7282
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.019 | 46 | -0.2767 | -12.7282
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3923 | 55 | -0.2767 | -15.2185
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.3923 | 55 | -0.2767 | -15.2185
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.15259 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -8.2398 | 54 | -0.2767 | -14.9418
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.1515 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.818 | 12 | -0.27561 | -3.3074
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.4656 | 104 | -0.27282 | -28.3733
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -15.4656 | 104 | -0.27282 | -28.3733
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.8815 | 53 | -0.27282 | -14.4595
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.4764 | 57 | -0.27282 | -15.5507
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.0302 | 54 | -0.27282 | -14.7323
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6251 | 58 | -0.27282 | -15.8236
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.14871 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.6251 | 58 | -0.27282 | -15.8236
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4461 | 0 | -0.27166 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.8412 | 0 | -0.27166 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.8198 | 0 | -0.27166 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.6037 | 0 | -0.27166 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.648 | 0 | -0.27166 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -22.471 | 0 | -0.27166 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.1642 | 0 | -0.27166 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.14754 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -36.0007 | 0 | -0.27166 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.14754 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.9018 | 0 | -0.27166 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.14751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7202 | 0 | -0.27162 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.14751 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.4252 | 0 | -0.27162 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.7949 | 0 | -0.27162 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.7033 | 0 | -0.27162 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.1489 | 0 | -0.27162 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.14751 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.0456 | 0 | -0.27162 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.14701 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.3503 | 50 | -0.27112 | -13.5559
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.1403 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.63 | 0 | -0.26441 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.13845 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.3823 | 0 | -0.26256 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -21.9047 | 161 | -0.26017 | -41.8867
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -22.585 | 166 | -0.26017 | -43.1876
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.13605 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -33.7414 | 248 | -0.26017 | -64.5212
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.13605 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -74.2855 | 546 | -0.26017 | -142.0506
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.13605 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -87.4827 | 0 | -0.26017 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.13605 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.7687 | 13 | -0.26017 | -3.3822
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.7951 | 0 | -0.25782 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -21.7951 | 0 | -0.25782 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.13371 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -32.7594 | 0 | -0.25782 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -86.9905 | 0 | -0.25774 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -75.3651 | 0 | -0.25774 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.13363 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -80.1756 | 0 | -0.25774 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.0159 | 0 | -0.25038 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -14.0159 | 0 | -0.25038 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -15.026 | 0 | -0.25038 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.12627 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.8265 | 0 | -0.25038 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.12436 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.8298 | 0 | -0.24847 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.12436 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2436 | 0 | -0.24847 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.5347 | 0 | -0.24564 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.6771 | 0 | -0.24564 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4688 | 0 | -0.24564 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.2743 | 0 | -0.24564 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.4514 | 0 | -0.24564 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -10.6945 | 0 | -0.24564 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.0764 | 0 | -0.24564 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1875 | 0 | -0.24564 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.4236 | 0 | -0.24564 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.507 | 0 | -0.24564 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.6563 | 0 | -0.24564 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -8.75 | 0 | -0.24564 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.875 | 0 | -0.24564 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.2743 | 0 | -0.24564 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -11.7882 | 0 | -0.24564 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.5174 | 0 | -0.24564 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.2361 | 0 | -0.24564 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7222 | 0 | -0.24564 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.7222 | 0 | -0.24564 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.12153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -20.7813 | 0 | -0.24564 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.10701 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -7.0627 | 66 | -0.23112 | -15.2541
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.10396 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -138.5773 | 0 | -0.22807 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.10396 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -138.0576 | 0 | -0.22807 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.7349 | 76 | -0.22589 | -17.1674
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.7349 | 76 | -0.22589 | -17.1674
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.6864 | 105 | -0.22589 | -23.7181
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.5313 | 74 | -0.22589 | -16.7156
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -7.5313 | 74 | -0.22589 | -16.7156
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.10178 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -10.3811 | 102 | -0.22589 | -23.0405
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5188 | 0 | -0.19397 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6585 | 0 | -0.19397 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5188 | 0 | -0.19397 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5886 | 0 | -0.19397 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4769 | 0 | -0.19397 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7465 | 0 | -0.19397 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.2135 | 0 | -0.19397 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.956 | 0 | -0.19397 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0458 | 0 | -0.19397 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.069858 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.1695 | 0 | -0.19397 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.068928 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3085 | 0 | -0.19304 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8441 | 0 | -0.18997 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46101 | 0 | -0.18997 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.5685 | 0 | -0.18997 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98789 | 0 | -0.18997 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.46101 | 0 | -0.18997 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.98789 | 0 | -0.18997 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.5685 | 0 | -0.18997 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.065859 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.5685 | 0 | -0.18997 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.06539 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.52312 | 0 | -0.1895 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.064631 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.96947 | 0 | -0.18874 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.064631 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4865 | 0 | -0.18874 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.063137 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.389 | 22 | -0.18725 | -4.1195
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.063137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.69451 | 11 | -0.18725 | -2.0597
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.063137 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.69451 | 11 | -0.18725 | -2.0597
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.062505 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.5629 | 0 | -0.18662 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9811 | 47.7 | -0.18661 | -8.9012
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.3311 | 37.3 | -0.18661 | -6.9605
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.8748 | 46 | -0.18661 | -8.584
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.062496 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.9998 | 48 | -0.18661 | -8.9572
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.061266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.8223 | 144 | -0.18538 | -26.6944
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.061266 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.518 | 188 | -0.18538 | -34.8511
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.6734 | 0 | -0.18534 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.3673 | 0 | -0.18534 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -6.1224 | 0 | -0.18534 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.8775 | 0 | -0.18534 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.9999 | 0 | -0.18534 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.061224 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.7754 | 0 | -0.18534 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.061224 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.73469 | 0 | -0.18534 | 0
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 0 | -0.18482 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 0 | -0.18482 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 0 | -0.18482 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.97139 | 0 | -0.18482 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 0 | -0.18482 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 0 | -0.18482 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.5178 | 0 | -0.18482 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.060712 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -0.91068 | 0 | -0.18482 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.059937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -20.1388 | 336 | -0.18405 | -61.8405
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.059937 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7887 | 180 | -0.18405 | -33.1288
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.8866 | 0 | -0.18403 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -1 | -8.9046 | 0 | -0.18403 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.059923 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.1682 | 0 | -0.18403 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.059898 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7816 | 180 | -0.18401 | -33.1218
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.059659 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -19.9261 | 334 | -0.18377 | -61.3795
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.059659 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -20.2841 | 340 | -0.18377 | -62.4821
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.059659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7386 | 180 | -0.18377 | -33.0788
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.059659 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7386 | 180 | -0.18377 | -33.0788
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.059587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4897 | 0 | -0.1837 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.059587 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.4897 | 0 | -0.1837 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.059488 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.2605 | 0 | -0.1836 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.059447 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.259 | 0 | -0.18356 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.058846 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7065 | 0 | -0.18296 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5049 | 0 | -0.18267 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.4011 | 0 | -0.18267 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.2254 | 0 | -0.18267 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1127 | 0 | -0.18267 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.5049 | 0 | -0.18267 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.1083 | 0 | -0.18267 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.5182 | 0 | -0.18267 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.2884 | 0 | -0.18267 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -8.6673 | 0 | -0.18267 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9282 | 0 | -0.18267 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.221 | 0 | -0.18267 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.058563 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9282 | 0 | -0.18267 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.2187 | 38 | -0.1825 | -6.935
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1269 | 19.3 | -0.1825 | -3.5222
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.058388 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.87582 | 15 | -0.1825 | -2.7375
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.058388 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -2.7442 | 47 | -0.1825 | -8.5775
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.058388 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1825 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3416 | 144 | -0.18204 | -26.2138
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3416 | 144 | -0.18204 | -26.2138
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.057928 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9057 | 171 | -0.18204 | -31.1288
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.9903 | 207 | -0.18204 | -37.6814
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.5521 | 216.7 | -0.18204 | -39.4472
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.057924 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.0176 | 242 | -0.18204 | -44.0527
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.3914 | 146.5 | -0.18139 | -26.5738
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -8.4716 | 147.9 | -0.18139 | -26.8277
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.057279 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.9093 | 173 | -0.18139 | -31.3806
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.055549 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -34.9403 | 0 | -0.17966 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.055465 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17958 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64026 | 0 | -0.17747 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.58691 | 0 | -0.17747 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.053355 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.64026 | 0 | -0.17747 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.052658 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17677 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.049602 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17371 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.044368 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -17.5697 | 0 | -0.16848 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.043988 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.043984 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3984 | 100 | -0.1681 | -16.8096
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.043984 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.3984 | 100 | -0.1681 | -16.8096
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.043984 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1681 | 0
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.040629 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.48755 | 0 | -0.16474 | 0
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.03883 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -21.2012 | 0 | -0.16294 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.03883 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -29.1225 | 0 | -0.16294 | 0
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8847 | 155 | -0.16208 | -25.1221
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.4542 | 170 | -0.16208 | -27.5533
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.037966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.8847 | 155 | -0.16208 | -25.1221
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.037952 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.91085 | 24 | -0.16206 | -3.8895
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.037952 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.91085 | 24 | -0.16206 | -3.8895
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.037952 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -0.8729 | 23 | -0.16206 | -3.7275
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16113 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16113 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.037017 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.16113 | 0
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.036971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.7269 | 209 | -0.16108 | -33.6663
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.036971 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.9857 | 216 | -0.16108 | -34.7939
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7007 | 46 | -0.16108 | -7.4098
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7376 | 47 | -0.16108 | -7.5709
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7007 | 46 | -0.16108 | -7.4098
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.036971 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.7007 | 46 | -0.16108 | -7.4098
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.036862 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.6295 | 0 | -0.16097 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.036862 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -15.6663 | 0 | -0.16097 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.036837 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -15.1768 | 412 | -0.16095 | -66.311
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.036837 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -14.7348 | 400 | -0.16095 | -64.3796
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.036821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.1356 | 58 | -0.16093 | -9.3341
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.036821 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.2771 | 89 | -0.16093 | -14.323
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6201 | 44 | -0.16093 | -7.0811
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6201 | 44 | -0.16093 | -7.0811
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.5833 | 43 | -0.16093 | -6.9201
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.036821 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.6569 | 45 | -0.16093 | -7.242
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.036794 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -14.9752 | 407 | -0.16091 | -65.4887
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.036532 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.30687 | 8.4 | -0.16064 | -1.3494
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.2777 | 147 | -0.16001 | -23.5222
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.9546 | 138 | -0.16001 | -22.0821
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.0264 | 140 | -0.16001 | -22.4021
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.2777 | 147 | -0.16001 | -23.5222
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.5343 | 182 | -0.16001 | -29.1227
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.035903 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -7.1088 | 198 | -0.16001 | -31.683
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.033006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.079214 | 0 | -0.15712 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.033006 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.079214 | 0 | -0.15712 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.032326 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.1293 | 0 | -0.15644 | 0
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.524 | 142 | -0.15597 | -22.1479
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.6196 | 145 | -0.15597 | -22.6158
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8107 | 151 | -0.15597 | -23.5516
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.031859 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -9.2391 | 290 | -0.15597 | -45.2316
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.074201 | 0 | -0.15503 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.074201 | 0 | -0.15503 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.030917 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.086568 | 0 | -0.15503 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3212 | 0 | -0.15324 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.4675 | 0 | -0.15324 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.3605 | 0 | -0.15324 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.5258 | 0 | -0.15324 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.3503 | 0 | -0.15324 | 0
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.028025 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -12.1348 | 0 | -0.15214 | 0
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.02789 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.2878 | 0 | -0.152 | 0
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.02789 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -16.5946 | 0 | -0.152 | 0
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1752 | 223.9 | -0.15169 | -33.9638
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2055 | 225 | -0.15169 | -34.1307
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.1945 | 224.6 | -0.15169 | -34.07
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.02758 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2524 | 226.7 | -0.15169 | -34.3886
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.024333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.2167 | 50 | -0.14844 | -7.4222
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.022345 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.13407 | 0 | -0.14646 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.015087 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.1392 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.026 | 158 | -0.13693 | -21.6357
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.0517 | 160 | -0.13693 | -21.9096
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.012823 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.244 | 175 | -0.13693 | -23.9636
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.012179 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.073074 | 0 | -0.13629 | 0
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6543 | 152.5 | -0.13496 | -20.5814
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -1.6218 | 149.5 | -0.13496 | -20.1765
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.010848 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.5232 | 232.6 | -0.13496 | -31.3917
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4212 | 132 | -0.13488 | -17.804
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4428 | 134 | -0.13488 | -18.0738
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.010767 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.4777 | 323 | -0.13488 | -43.5659
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.24108 | 49 | -0.12903 | -6.3226
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22632 | 46 | -0.12903 | -5.9355
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.22632 | 46 | -0.12903 | -5.9355
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23124 | 47 | -0.12903 | -6.0645
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.00492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.75768 | 154 | -0.12903 | -19.8709
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.00492 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -0.72816 | 148 | -0.12903 | -19.0967
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23616 | 48 | -0.12903 | -6.1935
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.00492 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.23616 | 48 | -0.12903 | -6.1935
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.003099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -0.96069 | 310 | -0.12721 | -39.4354
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.003099 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.2799 | 413 | -0.12721 | -52.5381
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.002969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.023752 | 0 | -0.12708 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.002969 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.023752 | 0 | -0.12708 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.080808 | 42 | -0.12604 | -5.2935
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.084656 | 44 | -0.12604 | -5.5456
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.084656 | 44 | -0.12604 | -5.5456
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.001924 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.090428 | 47 | -0.12604 | -5.9237
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03003 | 0 | -0.12497 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.029172 | 0 | -0.12497 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.000858 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.03003 | 0 | -0.12497 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.12411 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12411 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12411 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.00032 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.01056 | 0 | -0.12379 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.00032 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.008 | 0 | -0.12379 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.00032 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.12379 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | 0.001843 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033174 | 0 | -0.12227 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | 0.001843 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.033174 | 0 | -0.12227 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.003035 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | 1.2808 | 422 | -0.12108 | -51.0945
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | 0.003371 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.094388 | 0 | -0.12074 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | 0.003371 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.097759 | 0 | -0.12074 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.009505 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.13022 | 0 | -0.11461 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19622 | 0 | -0.11321 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.19622 | 0 | -0.11321 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | 0.010901 | south | 5 | N | N | Nsouth | Nsouth | -1 | 0.16351 | 0 | -0.11321 | 0
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | 0.029157 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 16.5903 | 0 | -0.094955 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | 0.029157 | south | 4 | Y | N | Ysouth | Nsouth | -1 | 16.9402 | 0 | -0.094955 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.029133 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -2.9133 | 0 | 0.12355 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.15269 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.15269 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.025303 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.17799 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.076243 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4365 | 0 | 0.22893 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.084364 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.23705 | 0
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.087612 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2403 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.087612 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.2403 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.088923 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.24161 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.088923 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 69.9824 | 787 | 0.24161 | 190.1464
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.090878 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.1739 | 255 | 0.24356 | 62.1088
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.090878 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.5408 | 149 | 0.24356 | 36.2911
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.090878 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.9043 | 153 | 0.24356 | 37.2653
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.09258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.887 | 150 | 0.24527 | 36.7899
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.09258 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.4064 | 80 | 0.24527 | 19.6213
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.095825 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0493 | 0 | 0.24851 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.096188 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3584 | 0 | 0.24887 | 0
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.096462 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4469 | 0 | 0.24915 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.096462 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.4469 | 0 | 0.24915 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.096544 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.7235 | 0 | 0.24923 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.098674 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8011 | 0 | 0.25136 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.098674 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8011 | 0 | 0.25136 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.098728 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8982 | 0 | 0.25141 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098741 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.8993 | 0 | 0.25143 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.4126 | 0 | 0.25152 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9067 | 0 | 0.25152 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.098834 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.9534 | 0 | 0.25152 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.09926 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9408 | 0 | 0.25195 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.09926 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9408 | 0 | 0.25195 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.10084 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.48402 | 0 | 0.25352 | 0
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.9073 | 66 | 0.25734 | 16.9846
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.8026 | 65 | 0.25734 | 16.7272
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.012 | 67 | 0.25734 | 17.2419
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.012 | 67 | 0.25734 | 17.2419
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.10466 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.012 | 67 | 0.25734 | 17.2419
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.10466 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25734 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.10466 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.25734 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.10471 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6648 | 0 | 0.25739 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.10471 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.1412 | 0 | 0.25739 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.1048 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.7644 | 0 | 0.25749 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.10489 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.6279 | 0 | 0.25757 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.1052 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.69431 | 0 | 0.25789 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.1052 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6083 | 0 | 0.25789 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8689 | 0 | 0.25819 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.7724 | 0 | 0.25819 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.6232 | 0 | 0.25819 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.1055 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.63 | 0 | 0.25819 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.0057 | 208.2 | 0.25838 | 53.7949
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.0193 | 142.1 | 0.25838 | 36.716
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.994 | 132.4 | 0.25838 | 34.2097
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.3745 | 136 | 0.25838 | 35.1398
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 15.5372 | 147 | 0.25838 | 37.982
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.10569 | west | 9 | Y | Y | Ywest | Ywest | 1 | 22.1959 | 210 | 0.25838 | 54.26
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3994 | 70 | 0.25839 | 18.0874
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.3994 | 70 | 0.25839 | 18.0874
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 9.8094 | 92.8 | 0.25839 | 23.9787
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.4564 | 80 | 0.25839 | 20.6713
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.4564 | 80 | 0.25839 | 20.6713
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.1057 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.1561 | 115 | 0.25839 | 29.715
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.10572 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.8584 | 0 | 0.25841 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.10573 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1326 | 0 | 0.25842 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.10575 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.628 | 0 | 0.25844 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.10587 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.6782 | 0 | 0.25856 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.10594 | west | 8 | N | N | Nwest | Nwest | 1 | 2.7331 | 0 | 0.25862 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.10626 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7513 | 0 | 0.25895 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.10628 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7541 | 0 | 0.25897 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.7636 | 0 | 0.25905 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.7826 | 0 | 0.25905 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.10636 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.103 | 0 | 0.25905 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.10638 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.9362 | 0 | 0.25907 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10644 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1587 | 0 | 0.25912 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.10644 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.1587 | 0 | 0.25912 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 1 | 7.4513 | 0 | 0.25913 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 1 | 7.8132 | 0 | 0.25913 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.10645 | west | 8 | N | N | Nwest | Nwest | 1 | 7.4939 | 0 | 0.25913 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.9923 | 0 | 0.2593 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 23.4553 | 0 | 0.2593 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.323 | 0 | 0.2593 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.10662 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.9964 | 0 | 0.2593 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.0448 | 66 | 0.25943 | 17.1221
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.365 | 69 | 0.25943 | 17.9003
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.365 | 69 | 0.25943 | 17.9003
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.1515 | 67 | 0.25943 | 17.3815
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 7.1515 | 67 | 0.25943 | 17.3815
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.10674 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.938 | 65 | 0.25943 | 16.8626
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.10678 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7271 | 0 | 0.25947 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.10682 | west | 6 | Y | N | Ywest | Nwest | 1 | 15.0618 | 0 | 0.25951 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.10682 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.8185 | 0 | 0.25951 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.10684 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.577 | 0 | 0.25952 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.10684 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5171 | 0 | 0.25952 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 1 | 2.6709 | 0 | 0.25952 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8825 | 0 | 0.25952 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.10684 | west | 7 | N | N | Nwest | Nwest | 1 | 4.8825 | 0 | 0.25952 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.10698 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.986 | 0 | 0.25966 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.10704 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0561 | 0 | 0.25973 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.10704 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8111 | 0 | 0.25973 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10717 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3961 | 0 | 0.25986 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.10717 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3961 | 0 | 0.25986 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.0302 | 0 | 0.26016 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.5531 | 0 | 0.26016 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.5086 | 0 | 0.26016 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.789 | 0 | 0.26016 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.2845 | 0 | 0.26016 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.10747 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.6514 | 0 | 0.26016 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.48 | 0 | 0.26025 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6063 | 0 | 0.26025 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 26.7824 | 0 | 0.26025 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.10756 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.1893 | 0 | 0.26025 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.10758 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.1375 | 0 | 0.26027 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.10759 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.4553 | 0 | 0.26028 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10837 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5019 | 0 | 0.26105 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10949 | west | 6 | Y | N | Ywest | Nwest | 1 | 43.798 | 0 | 0.26218 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.1095 | west | 6 | Y | N | Ywest | Nwest | 1 | 25.8415 | 0 | 0.26218 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.11016 | west | 6 | Y | N | Ywest | Nwest | 1 | 18.1757 | 0 | 0.26284 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.11072 | west | 4 | Y | N | Ywest | Nwest | 1 | 71.9328 | 0 | 0.2634 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11112 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.1116 | 73 | 0.2638 | 19.2577
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.223 | 119 | 0.2638 | 31.3927
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11112 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.7792 | 205 | 0.2638 | 54.0798
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.334 | 102 | 0.2638 | 26.908
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11112 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.6673 | 96 | 0.2638 | 25.3252
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.11159 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.0048 | 242 | 0.26428 | 63.9548
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11184 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.79 | 168 | 0.26453 | 44.4412
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11184 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.0661 | 90 | 0.26453 | 23.8078
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.11214 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.4567 | 0 | 0.26483 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.11224 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 41.0787 | 366 | 0.26492 | 96.9619
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.11228 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3474 | 0 | 0.26497 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.11228 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3474 | 0 | 0.26497 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2472 | 20 | 0.26504 | 5.3009
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2472 | 20 | 0.26504 | 5.3009
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.2472 | 20 | 0.26504 | 5.3009
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.11236 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.9101 | 17 | 0.26504 | 4.5057
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8811 | 70 | 0.26527 | 18.5691
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7685 | 69 | 0.26527 | 18.3038
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7685 | 69 | 0.26527 | 18.3038
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11259 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.6559 | 68 | 0.26527 | 18.0386
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0385 | 18 | 0.26594 | 4.7869
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0385 | 18 | 0.26594 | 4.7869
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11325 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.3036 | 38 | 0.26594 | 10.1056
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11357 | north | 3 | N | N | Nnorth | Nnorth | 1 | 131.4005 | 0 | 0.26626 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11357 | north | 3 | N | N | Nnorth | Nnorth | 1 | 131.5141 | 0 | 0.26626 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.7405 | 217.3 | 0.26654 | 57.9192
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3401 | 205 | 0.26654 | 54.6407
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11385 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.0138 | 272.4 | 0.26654 | 72.6055
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2431 | 204 | 0.26662 | 54.3911
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9013 | 201 | 0.26662 | 53.5912
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.11394 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 27.5728 | 242 | 0.26662 | 64.5228
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.11411 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26679 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 32.9988 | 288 | 0.26727 | 76.9724
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.8431 | 147 | 0.26727 | 39.288
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.11458 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.8431 | 147 | 0.26727 | 39.288
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.6771 | 224 | 0.26732 | 59.8788
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.9064 | 226 | 0.26732 | 60.4134
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3016 | 212 | 0.26732 | 56.671
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11463 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.1869 | 211 | 0.26732 | 56.4037
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.11574 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26842 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.11574 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26842 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.11574 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26842 | 0
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.11579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.057 | 216.4 | 0.26848 | 58.0982
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.11579 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.0222 | 216.1 | 0.26848 | 58.0177
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11599 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 45.8157 | 395 | 0.26868 | 106.1267
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11599 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.4552 | 435 | 0.26868 | 116.8737
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.11616 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.068 | 0 | 0.26885 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11623 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 50.5609 | 435 | 0.26892 | 116.9794
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.11735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.041 | 60 | 0.27004 | 16.2022
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.11735 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 7.393 | 63 | 0.27004 | 17.0123
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11847 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2207 | 196 | 0.27116 | 53.1472
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11847 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.1505 | 111 | 0.27116 | 30.0987
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.11915 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.27184 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.11941 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27209 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.11944 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.0938 | 118 | 0.27213 | 32.1108
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.11944 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 13.7355 | 115 | 0.27213 | 31.2944
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.11944 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 66.4081 | 556 | 0.27213 | 151.3016
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.11968 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7873 | 0 | 0.27237 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.11968 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.7873 | 0 | 0.27237 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.11986 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 20.376 | 170 | 0.27255 | 46.3327
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.11986 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.3267 | 520 | 0.27255 | 141.7235
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.12008 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 44.4296 | 370 | 0.27277 | 100.9235
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.8112 | 0 | 0.27277 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.9313 | 0 | 0.27277 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.1047 | 0 | 0.27277 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.1714 | 0 | 0.27277 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 17.2915 | 0 | 0.27277 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.12008 | north | 1 | N | N | Nnorth | Nnorth | 1 | 37.2248 | 0 | 0.27277 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.2282 | 160 | 0.27286 | 43.6579
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7475 | 156 | 0.27286 | 42.5665
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5545 | 196 | 0.27286 | 53.481
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.7475 | 156 | 0.27286 | 42.5665
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 18.8676 | 157 | 0.27286 | 42.8394
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.12018 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.7948 | 198 | 0.27286 | 54.0267
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.0184 | 0 | 0.27293 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.5716 | 0 | 0.27293 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.12025 | north | 8 | N | N | Nnorth | Nnorth | 1 | 10.6297 | 0 | 0.27293 | 0
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 67.1525 | 0 | 0.27303 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 69.6798 | 0 | 0.27303 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.12034 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 97.2388 | 0 | 0.27303 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.5171 | 79 | 0.27316 | 21.5793
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.7697 | 106 | 0.27316 | 28.9544
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 17.5885 | 146 | 0.27316 | 39.8806
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.12047 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 9.1556 | 76 | 0.27316 | 20.7598
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.12047 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.8189 | 40 | 0.27316 | 10.9264
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12053 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27322 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.12053 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.27322 | 0
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.0155 | 25 | 0.27331 | 6.8326
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.9454 | 41 | 0.27331 | 11.2055
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.12062 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.4124 | 20 | 0.27331 | 5.4661
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.12076 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 46.8557 | 388 | 0.27345 | 106.0979
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.12076 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 62.1924 | 515 | 0.27345 | 140.8258
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.5638 | 161 | 0.2742 | 44.1462
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9283 | 164 | 0.2742 | 44.9688
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9283 | 164 | 0.2742 | 44.9688
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 50.3068 | 414 | 0.2742 | 113.5188
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.6853 | 162 | 0.2742 | 44.4204
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.5638 | 161 | 0.2742 | 44.1462
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8068 | 163 | 0.2742 | 44.6946
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.12151 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 49.6992 | 409 | 0.2742 | 112.1478
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.12167 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 27.2543 | 224 | 0.27436 | 61.456
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 98.0763 | 0 | 0.27762 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 99.3257 | 0 | 0.27762 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.12494 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 97.4516 | 0 | 0.27762 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.5647 | 0 | 0.27812 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 16.3068 | 0 | 0.27812 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.1884 | 0 | 0.27812 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.12544 | north | 1 | N | N | Nnorth | Nnorth | 1 | 50.0494 | 0 | 0.27812 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.12587 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.27856 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.12593 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.2963 | 0 | 0.27861 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.12599 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 22.9307 | 182 | 0.27868 | 50.7196
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.12599 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.9806 | 484 | 0.27868 | 134.8807
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8515 | 151.5 | 0.28372 | 42.9834
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.9563 | 152.3 | 0.28372 | 43.2104
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.13103 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2584 | 177.5 | 0.28372 | 50.3601
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7803 | 150.7 | 0.28394 | 42.7901
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.8197 | 151 | 0.28394 | 42.8753
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.13126 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.2848 | 177.4 | 0.28394 | 50.3713
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.13244 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 81.4506 | 0 | 0.28513 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.13244 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 77.7423 | 0 | 0.28513 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.14627 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 120.9678 | 0 | 0.29896 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.14627 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 119.7976 | 0 | 0.29896 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 132.7439 | 0 | 0.30794 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 132.7439 | 0 | 0.30794 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.6455 | 0 | 0.30794 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.15526 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 23.7542 | 0 | 0.30794 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.16178 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7656 | 48 | 0.31447 | 15.0945
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.16178 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.442 | 46 | 0.31447 | 14.4656
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.16178 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 16.9872 | 105 | 0.31447 | 33.0193
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.16558 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 2.8149 | 17 | 0.31827 | 5.4105
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.16558 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.31827 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.16595 | north | 7 | N | N | Nnorth | Nnorth | 1 | 5.3103 | 0 | 0.31863 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.1782 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 82.5071 | 0 | 0.33089 | 0

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown