## test results
CRE test for: |  | 3414 TEMP_SS_ to 3429 SANDOW_ | [5 empty] | PASS
Line Rating: |  | 1072
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3414 TEMP_SS_ to 3429 SANDOW_
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.10244
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.16164
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.096146
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.046329
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | 3414 TEMP_SS_ to 3429 SANDOW_
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.11262
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.15445
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.096584
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.043985
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | 3414 TEMP_SS_ to 3429 SANDOW_
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.25689
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.0058579
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.14643
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.25822
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.11531
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.14013
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.25689 | PASS
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.25689 | 0.25689
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.31001
[6 empty] | Concentration |  | 1.2068 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.29626
[6 empty] | Concentration |  | 1.1532 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 53.4232
| Percent of line rating => | [6 empty] | 4.984% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 1.5646
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.0074488 | 0.016614 | 0.0091651 | 0.0074488
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.0099424 | 0.21915 | 0.22909 | -0.0099424
[7 empty] | B4 (S-W) | 0.014423 | -0.38958 | -0.40401 | 0.014423
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0066356 | -0.18705 | -0.18041 | -0.0066356
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.01745 | 0.20179 | 0.21924 | -0.01745
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 1.853%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -2.474%
[7 empty] | B4 | 3.588%
[7 empty] | B5 | -1.651%
[7 empty] | B6 | -4.342%
[7 empty] | Max Abs Error | 4.342% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: 3414 TEMP_SS_ to 3429 SANDOW_ C: 3413 TEMP_SS_ to 3429 SANDOW_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: 3414 TEMP_SS_ to 3429 SANDOW_ C: 3413 TEMP_SS_ to 3429 SANDOW_
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.16343 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 41.6757
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.16343 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 24.3517
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.148 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.2199
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.148 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 2.2199
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.16343 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 25.0054
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.15589 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 23.3839
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.15589 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 12.4714
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11276 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 8.2313
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11276 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 13.4181
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11276 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 23.1152
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11276 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 11.5012
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.11276 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 10.8247
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.10918 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.3101
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.10918 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 1.3101
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11771 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 19.7758
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.11771 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 10.5942
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0059
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 2.0059
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 4.2348
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 31.7422
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.2018
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 16.2018
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.10892 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 12.2534
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.10684 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 4.2738
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 8.4378
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 11.3215
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 15.5938
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.10681 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 8.1173
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.10878 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 6.527
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.10878 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 6.8533
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 2.1328
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 2.666
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 4.3723
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.029588 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 13.6992
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 6.2326
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 6.1382
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.3271
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.3271
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 6.3271
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094434 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 10.7655
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.094434 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 48.6335
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 6.4661
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 6.76
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 6.76
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 6.5641
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 6.5641
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 6.3681
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 6.8202
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 7.1514
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 6.8591
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 14.6567
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 21.4964
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.098178 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 9.7196
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.098178 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 5.9889
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.09815 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 13.8392
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 2.4545
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.4867
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 4.4867
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.09815 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 11.778
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.096671 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 2.4941
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.0963 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 9.6782
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.097188 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 11.6626
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.096269 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 5.5836
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.096507 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 20.6718
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.098858 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 14.8287
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.095512 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.63038
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.095512 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 3.2761
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.098858 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 9.9847
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.09723 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 11.6676
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.10622 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 38.8754
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.10657 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 25.7895
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.10217 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 40.8692
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.10218 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 24.114
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.10315 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 17.0193
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 22.1107
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 21.7856
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 26.2294
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.1285
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.1285
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 2.1285
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 1.8093
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.10917 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 13.1005
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.11197 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 6.7184
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 8.0143
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 8.5058
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 9.4462
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 17.1106
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 16.6828
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 20.9604
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 16.6828
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 16.7897
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 21.1743
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.10719 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 18.222
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.10719 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 55.7378
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10703 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 39.6022
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 59.5888
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 61.8314
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 86.2863
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1105 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 12.3757
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1105 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 11.0497
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.1105 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 41.7679
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 24.3224
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 22.9457
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 30.4897
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.1122 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 86.394
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 7.9933
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.8791
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 7.8791
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 7.7649
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11172 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 129.2589
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.11172 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 129.3706
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 26.1524
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 26.386
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.11617 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 25.1385
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.11617 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 25.1037
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 24.7514
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 24.6347
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11225 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 44.3372
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.11202 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 48.7265
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.11225 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 48.827
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.1079 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 14.8905
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.10877 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 12.8353
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.10877 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 12.509
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.10877 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 60.4783
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.10669 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 41.3957
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.10669 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 54.9453
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 79.6265
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 80.6408
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 79.1193
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.099735 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 18.1518
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.099735 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 48.2717
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.10627 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 23.8047
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.10015 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 5.0077
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.10021 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 4.2087
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.09279 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 57.0658
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.09279 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 54.4677
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.17333 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 93.0787
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.17333 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 136.4115
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.16854 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 12.6407
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.16854 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 37.4165
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.26261 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -149.424
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15648 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -32.7043
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15648 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -33.7997
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.15643 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -63.6674
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.1981
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -7.3546
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.1981
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -7.1981
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.15688 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -66.518
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.15688 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -66.6749
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15546 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -9.0168
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15546 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -13.8361
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -6.8403
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -6.8403
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -6.6849
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -6.9958
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.15666 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -64.5443
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.15666 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -62.6644
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.15602 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -85.1853
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.15602 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -117.0127
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -9.6085
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -14.9641
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -23.7851
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -24.2474
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -26.5939
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -24.2474
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.12867 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -2.8308
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.12867 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.4154
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.12867 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -1.4154
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -6.185
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -4.8365
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -5.9645
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -6.2239
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.6214
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -1.4863
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.13972 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.3534
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.13972 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -3.3534
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.13972 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -3.2137
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.14872 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -58.8939
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.088747 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -118.2998
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.088747 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -117.856
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -5.0667
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -2.5733
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -2
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.13333 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -6.2667
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 6.3484
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.099541 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 14.9312
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.094962 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 16.0961
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.045049 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 6.7573
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.098078 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 6.1789
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.10394 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 67.5331
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.10732 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.2929
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.10732 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 4.2929
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.10246 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -43.2398
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -22.1776
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -22.5136
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -54.2679
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -34.2849
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -34.7189
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -37.9738
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.18647 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -108.8991
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.18647 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -110.9502
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.18624 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -80.6402
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -39.2185
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -39.4112
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -39.3412
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -39.709
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.14741 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.1793
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.14741 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -1.1793
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.4048
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -1.4048
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -1.1707
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.083315 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -1.1414
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.11083 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.995
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.11083 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.995
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -4.5435
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -4.4136
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -4.5435
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.10224 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -2.8628
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.10224 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -2.9651
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.094523 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 3.3083
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.094523 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 2.8357
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.4014
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.4014
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.4014
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -8.4014
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.16503 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.99016
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.39383
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.39383
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.45947
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.16351 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.65403
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.15996 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.38392
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.15996 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.38392
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -23.8599
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -22.3991
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -22.7237
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -23.8599
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -29.5408
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -32.1378
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -32.118
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -31.4862
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -48.9879
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -23.9171
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -24.4224
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -25.4329
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -48.8447
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.077419 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -2.5548
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.077419 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.9355
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -1.6214
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.12975 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -9.472
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -9.6637
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -9.9083
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -3.5372
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.8843
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -9.6637
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -9.786
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -9.5903
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -3.0581
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -5.6269
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.13688 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -86.1
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.13101 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -18.8656
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.13101 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -24.6301
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.15173 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -1.8208
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.096846 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.58108
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -44.3661
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13232 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -44.1939
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13232 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -44.9878
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.13246 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -5.0337
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.13234 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.3086
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.13234 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -3.3086
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.13247 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -5.0339
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.13306 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -3.8588
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -19.5839
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -19.6235
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -20.2046
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -20.6688
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -20.0147
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -13.0815
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -18.9682
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -19.2298
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -16.6135
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -19.5976
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -19.7849
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -23.1426
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -27.6463
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -28.9418
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -32.3208
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -19.2318
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -19.2318
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -22.8377
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.15464 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -47.9381
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.15464 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -63.8659
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -6.6163
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -6.9314
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -6.9314
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -7.404
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -7.8303
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -7.3509
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -7.3509
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -7.5107
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -24.6095
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -23.6507
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -7.6705
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -7.6705
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 6.7332
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 6.7332
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 8.9263
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 7.6951
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 7.6951
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 11.0617
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 20.023
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 13.666
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 12.7332
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 13.0794
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 14.1373
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 20.1961
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 20.7272
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 12.5454
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 24.6941
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 19.5371
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 19.5422
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 11.911
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.094826 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 14.1291
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.097487 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 17.5477
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.097487 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 17.5477
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.097394 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 21.9137
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.098595 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 12.3244
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.098595 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 12.3244
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 14.9846
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 15.0917
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 33.0732
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 15.3057
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 15.4128
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 33.1802
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11072 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 21.7005
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.11072 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 12.2896
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.10787 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 17.0145
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 17.3315
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 17.3315
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 43.7515
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 17.1202
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 17.0145
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 17.2258
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 43.2231
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.1071 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.1071 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 14.9292
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 13.1135
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 14.6266
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 40.2483
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 14.1979
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 14.2262
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 16.7134
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 14.3128
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 14.3884
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 16.7691
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.26261 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -152.5752
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 52.0438
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 52.0438
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.023675 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.7576
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.020826 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.99965
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.020826 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.958
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.28516
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 1.2119
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023763 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.40397
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.52279
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.59408
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.020826 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 2.1867
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.098431 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 8.2682
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.084468 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 6.7574
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.084378 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 12.6567
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.084378 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 12.6567
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -3.4062
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -3.2089
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -2.5498
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -7.3705
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -7.3849
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -7.3272
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -4.6186
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -11.7388
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.9244
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -4.828
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -4.4718
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -4.9436
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -4.9099
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.048135 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -1.5403
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.048135 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -1.4441
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -7.1349
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -7.1349
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -7.6491
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -7.0384
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 9.2705
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 9.3131
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.038173 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -5.1915
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.053499 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.7655
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.6007
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -1.6007
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.4483
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -1.4483
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.066941 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -4.7528
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.066941 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.66941
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -8.8983
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -8.8983
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -13.3748
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.7223
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -2.5129
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.7223
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -2.7223
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.03946 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -5.8795
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.03946 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -2.5688
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -3.8775
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -3.7326
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -3.7071
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -2.3222
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.51984
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.035074 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -26.06
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.036306 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -26.6849
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.9687
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.9687
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -5.9687
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -4.8196
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.037928 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -6.5615
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.037928 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -5.1203
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -5.5075
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -5.4602
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -5.3756
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -9.107
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -2.5203
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -2.4888
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -3.2527
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -2.8983
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -6.553
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -6.308
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -6.3241
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -6.304
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -10.8012
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.035139 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.17569
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.035139 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.73792
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 3.148
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 3.1847
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 3.1847
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 7.7577
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.033529 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -13.3445
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.8771
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.8771
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.8771
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -2.2443
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -2.2443
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -2.2035
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.074111 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 61.2898
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.074111 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 60.6969
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.054906 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -2.5312
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.6729
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -6.6729
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -9.2191
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.4973
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -6.4973
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -8.9557
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -7.0841
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -6.2419
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -6.1789
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.039849 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -1.3947
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.044471 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -20.4122
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -2.2835
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -2.3186
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -2.4592
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -2.2133
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -2.1781
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -3.6536
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -2.0727
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -4.346
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -4.2903
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -4.2903
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.027859 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -4.5132
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.034849 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -5.4713
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -2.7618
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -2.8007
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -1.517
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -1.1669
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.040526 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -3.161
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.040526 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -3.2421
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.039385 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.63804
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.039479 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -6.514
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.039505 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -6.6763
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.039393 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -8.3907
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.039368 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -8.9759
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.039523 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.47428
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.039523 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.71141
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.046071 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -2.3035
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -3.8237
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -3.8237
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9854
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.9486
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9854
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -2.0957
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9854
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.9854
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -2.1324
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -2.1324
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.035632 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.42758
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8483
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.9473
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8483
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8483
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.9473
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.8483
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.083453 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -5.5079
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -8.5478
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -8.8133
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -13.1668
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053092 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -28.9882
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053092 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -34.1382
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -35.5908
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -30.8344
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -32.8026
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.053092 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.6902
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.035108 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.4213
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -1.2242
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -1.2494
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -1.1774
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -1.6527
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.63732
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.73454
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.71654
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -1.2602
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.64813
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -3.075
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -5.329
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -4.3587
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -5.0196
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -3.1636
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.1005
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -6.046
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -6.1866
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -3.5151
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -1.2654
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -6.6084
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -4.9211
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -4.429
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -5.0617
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -4.5556
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -7.1005
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -6.8193
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -7.2411
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -5.343
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.6242
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -5.6242
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -12.0216
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -1.1603
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.080199 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 6.1352
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 6.7717
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 3.3858
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.085365 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 6.8292
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.084489 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 6.7591
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.080791 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 6.4633
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.07958 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 6.6847
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.085365 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 6.8292
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -18.1186
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 11.7109
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 22.7387
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 16.61
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -35.2836
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -29.244
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -35.6014
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -18.2775
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -15.8935
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.10082 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 6.0492
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.056233 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.060277 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.088016 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.42248
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 3.7171
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 10.6557
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 13.3816
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 11.7956
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 10.4079
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 7.9794
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.096448 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 14.4672
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 10.8138
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 14.3704
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 17.8789
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 20.6184
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.13334 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.10136 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.13949 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -3.4251
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -5.3334
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -9.052
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -12.5263
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -5.4636
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -5.0638
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -2.5319
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -12.5263
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -4.7973
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -5.7301
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -2.9317
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -4.9268
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.8949
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.8843
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.8949
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -4.9268
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -4.9268
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -19.7222
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -6.6629
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -7.3292
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -6.6629
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.13081 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -1.5698
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.12758 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.9137
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.12758 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -2.9343
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.12326 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -5.9165
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.1268 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -1.0144
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.13208 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -23.7742
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -23.7676
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13232 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -23.8171
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.13232 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -23.8171
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1395 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -13.9499
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1395 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -13.9499
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2826
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2826
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2826
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -2.1009
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2826
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2826
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -3.2826
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.9696
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1395 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1395 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -69.7495
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1395 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -69.7495
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.1395 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.13827 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.077419 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.1364 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.13526 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: 3414 TEMP_SS_ to 3429 SANDOW_ C: 3413 TEMP_SS_ to 3429 SANDOW_ | [7 empty] | 53.4232
Number of Bus | Name of Bus | ID | Max MW | L: 3414 TEMP_SS_ to 3429 SANDOW_ C: 3413 TEMP_SS_ to 3429 SANDOW_ | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.16343 | north | Y | 0.060992 | 0.32507 | 0.067288 | 0.20976 | 0.060992 | North | N | 0.060992 | 0
239 | BOSQUESW | 1 | 149 | 0.16343 | north | Y | 0.060992 | 0.32507 | 0.067288 | 0.20976 | 0.060992 | North | N | 0.060992 | 0
244 | WHITNYDM | 1 | 15 | 0.148 | north | N | 0.045554 | 0.30964 | 0.05185 | 0.19433 | 0.045554 | North | N | 0.045554 | 0
245 | WHITNYDM | 2 | 15 | 0.148 | north | N | 0.045554 | 0.30964 | 0.05185 | 0.19433 | 0.045554 | North | N | 0.045554 | 0
247 | BOSQUESW | 2 | 153 | 0.16343 | north | Y | 0.060992 | 0.32507 | 0.067288 | 0.20976 | 0.060992 | North | N | 0.060992 | 0
251 | BOSQUESW | 2 | 150 | 0.15589 | north | Y | 0.053451 | 0.31753 | 0.059747 | 0.20222 | 0.053451 | North | N | 0.053451 | 0
253 | BOSQUESW | 2 | 80 | 0.15589 | north | Y | 0.053451 | 0.31753 | 0.059747 | 0.20222 | 0.053451 | North | N | 0.053451 | 0
332 | RWMILLER | 1 | 73 | 0.11276 | north | Y | 0.010315 | 0.2744 | 0.016611 | 0.15909 | 0.010315 | North | N | 0.010315 | 0
333 | RWMILLER | 2 | 119 | 0.11276 | north | Y | 0.010315 | 0.2744 | 0.016611 | 0.15909 | 0.010315 | North | N | 0.010315 | 0
334 | RWMILLER | 3 | 205 | 0.11276 | north | Y | 0.010315 | 0.2744 | 0.016611 | 0.15909 | 0.010315 | North | N | 0.010315 | 0
335 | RWMILLER | 4 | 102 | 0.11276 | north | Y | 0.010315 | 0.2744 | 0.016611 | 0.15909 | 0.010315 | North | N | 0.010315 | 0
336 | RWMILLER | 5 | 96 | 0.11276 | north | Y | 0.010315 | 0.2744 | 0.016611 | 0.15909 | 0.010315 | North | N | 0.010315 | 0
344 | MRSSHPRD | 1 | 12 | 0.10918 | north | N | 0.0067339 | 0.27082 | 0.01303 | 0.15551 | 0.0067339 | North | N | 0.0067339 | 0
345 | MRSSHPRD | 2 | 12 | 0.10918 | north | N | 0.0067339 | 0.27082 | 0.01303 | 0.15551 | 0.0067339 | North | N | 0.0067339 | 0
366 | JNSNCNTY | 1 | 168 | 0.11771 | north | Y | 0.015271 | 0.27935 | 0.021567 | 0.16404 | 0.015271 | North | N | 0.015271 | 0
367 | JNSNCNTY | 2 | 90 | 0.11771 | north | Y | 0.015271 | 0.27935 | 0.021567 | 0.16404 | 0.015271 | North | N | 0.015271 | 0
503 | NTHTEXAS | 1 | 18 | 0.11144 | north | Y | 0.0089989 | 0.27308 | 0.015295 | 0.15777 | 0.0089989 | North | N | 0.0089989 | 0
504 | NTHTEXAS | 2 | 18 | 0.11144 | north | Y | 0.0089989 | 0.27308 | 0.015295 | 0.15777 | 0.0089989 | North | N | 0.0089989 | 0
505 | NTHTEXAS | 3 | 38 | 0.11144 | north | Y | 0.0089989 | 0.27308 | 0.015295 | 0.15777 | 0.0089989 | North | N | 0.0089989 | 0
580 | JCKCNTY8 | 1 | 288 | 0.11022 | north | Y | 0.0077739 | 0.27186 | 0.01407 | 0.15655 | 0.0077739 | North | N | 0.0077739 | 0
581 | JCKCNTY8 | 2 | 147 | 0.11022 | north | Y | 0.0077739 | 0.27186 | 0.01407 | 0.15655 | 0.0077739 | North | N | 0.0077739 | 0
582 | JCKCNTY8 | 3 | 147 | 0.11022 | north | Y | 0.0077739 | 0.27186 | 0.01407 | 0.15655 | 0.0077739 | North | N | 0.0077739 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.10892 | north | Y | 0.0064769 | 0.27056 | 0.012773 | 0.15525 | 0.0064769 | North | N | 0.0064769 | 0
837 | NEWMAN_G | 1 | 40 | 0.10684 | north | Y | 0.0044019 | 0.26848 | 0.010698 | 0.15317 | 0.0044019 | North | N | 0.0044019 | 0
842 | OLINGER_ | 1 | 79 | 0.10681 | north | Y | 0.0043649 | 0.26845 | 0.010661 | 0.15314 | 0.0043649 | North | N | 0.0043649 | 0
843 | OLINGER_ | 1 | 106 | 0.10681 | north | Y | 0.0043649 | 0.26845 | 0.010661 | 0.15314 | 0.0043649 | North | N | 0.0043649 | 0
844 | OLINGER_ | 1 | 146 | 0.10681 | north | Y | 0.0043649 | 0.26845 | 0.010661 | 0.15314 | 0.0043649 | North | N | 0.0043649 | 0
845 | OLINGER_ | 1 | 76 | 0.10681 | north | Y | 0.0043649 | 0.26845 | 0.010661 | 0.15314 | 0.0043649 | North | N | 0.0043649 | 0
923 | SPENCER_ | 1 | 60 | 0.10878 | north | Y | 0.0063409 | 0.27042 | 0.012637 | 0.15511 | 0.0063409 | North | N | 0.0063409 | 0
924 | SPENCER_ | 1 | 63 | 0.10878 | north | Y | 0.0063409 | 0.27042 | 0.012637 | 0.15511 | 0.0063409 | North | N | 0.0063409 | 0
948 | STEAM1 | 1 | 20 | 0.10664 | north | Y | 0.0041989 | 0.26828 | 0.010495 | 0.15297 | 0.0041989 | North | N | 0.0041989 | 0
949 | STEAM2 | 1 | 25 | 0.10664 | north | Y | 0.0041999 | 0.26828 | 0.010496 | 0.15297 | 0.0041999 | North | N | 0.0041999 | 0
950 | STEAM3 | 1 | 41 | 0.10664 | north | Y | 0.0041999 | 0.26828 | 0.010496 | 0.15297 | 0.0041999 | North | N | 0.0041999 | 0
990 | GIBN_CRE | 1 | 463 | 0.029588 | north | Y | -0.072854 | 0.19123 | -0.066558 | 0.075917 | 0.066558 | west | Y | 0.072854 | 2.915
1002 | PBCTAGE_ | A | 66 | 0.094434 | west | Y | -0.0080081 | 0.25607 | -0.0017122 | 0.14076 | 0.0017122 | west | N | 0.0017122 | 0
1003 | PBCTBGE_ | B | 65 | 0.094434 | west | Y | -0.0080081 | 0.25607 | -0.0017122 | 0.14076 | 0.0017122 | west | N | 0.0017122 | 0
1004 | PBCTCGE_ | C | 67 | 0.094434 | west | Y | -0.0080081 | 0.25607 | -0.0017122 | 0.14076 | 0.0017122 | west | N | 0.0017122 | 0
1005 | PBCTDGE_ | D | 67 | 0.094434 | west | Y | -0.0080081 | 0.25607 | -0.0017122 | 0.14076 | 0.0017122 | west | N | 0.0017122 | 0
1006 | PBCTEGE_ | E | 67 | 0.094434 | west | Y | -0.0080081 | 0.25607 | -0.0017122 | 0.14076 | 0.0017122 | west | N | 0.0017122 | 0
1007 | PB5GEN_6 | MB | 114 | 0.094434 | west | Y | -0.0080081 | 0.25607 | -0.0017122 | 0.14076 | 0.0017122 | west | N | 0.0017122 | 0
1008 | PB6GEN_7 | MB | 515 | 0.094434 | west | Y | -0.0080081 | 0.25607 | -0.0017122 | 0.14076 | 0.0017122 | west | N | 0.0017122 | 0
1039 | MRGNAG_1 | A | 66 | 0.097971 | west | Y | -0.0044711 | 0.25961 | 0.0018248 | 0.1443 | 0.0018248 | west | N | 0.0018248 | 0
1040 | MRGNBG_2 | B | 69 | 0.097971 | west | Y | -0.0044711 | 0.25961 | 0.0018248 | 0.1443 | 0.0018248 | west | N | 0.0018248 | 0
1041 | MRGNCG_3 | C | 69 | 0.097971 | west | Y | -0.0044711 | 0.25961 | 0.0018248 | 0.1443 | 0.0018248 | west | N | 0.0018248 | 0
1042 | MRGNDG_4 | D | 67 | 0.097971 | west | Y | -0.0044711 | 0.25961 | 0.0018248 | 0.1443 | 0.0018248 | west | N | 0.0018248 | 0
1043 | MRGNEG_5 | E | 67 | 0.097971 | west | Y | -0.0044711 | 0.25961 | 0.0018248 | 0.1443 | 0.0018248 | west | N | 0.0018248 | 0
1044 | MRGNFG_6 | F | 65 | 0.097971 | west | Y | -0.0044711 | 0.25961 | 0.0018248 | 0.1443 | 0.0018248 | west | N | 0.0018248 | 0
1045 | CALENG1G | 1 | 70 | 0.097431 | west | N | -0.0050111 | 0.25907 | 0.0012848 | 0.14376 | 0.0012848 | west | N | 0.0012848 | 0
1046 | CALENG2G | 2 | 73.4 | 0.097431 | west | N | -0.0050111 | 0.25907 | 0.0012848 | 0.14376 | 0.0012848 | west | N | 0.0012848 | 0
1047 | CALENG3G | 3 | 70.4 | 0.097431 | west | N | -0.0050111 | 0.25907 | 0.0012848 | 0.14376 | 0.0012848 | west | N | 0.0012848 | 0
1058 | LONGSHOR | 1 | 150 | 0.097711 | west | Y | -0.0047311 | 0.25935 | 0.0015648 | 0.14404 | 0.0015648 | west | N | 0.0015648 | 0
1058 | LONGSHOR | 2 | 220 | 0.097711 | west | Y | -0.0047311 | 0.25935 | 0.0015648 | 0.14404 | 0.0015648 | west | N | 0.0015648 | 0
1061 | CIELOGEN | 1 | 99 | 0.098178 | west | Y | -0.0042641 | 0.25982 | 0.0020318 | 0.14451 | 0.0020318 | west | N | 0.0020318 | 0
1062 | CIELOGEN | 1 | 61 | 0.098178 | west | Y | -0.0042641 | 0.25982 | 0.0020318 | 0.14451 | 0.0020318 | west | N | 0.0020318 | 0
1068 | SCURRYCW | 1 | 141 | 0.09815 | west | Y | -0.0042921 | 0.25979 | 0.0020038 | 0.14448 | 0.0020038 | west | N | 0.0020038 | 0
1069 | KINDERMG | 1 | 25 | 0.098178 | west | N | -0.0042641 | 0.25982 | 0.0020318 | 0.14451 | 0.0020318 | west | N | 0.0020318 | 0
1070 | KINDERMG | 1 | 45.7 | 0.098178 | west | N | -0.0042641 | 0.25982 | 0.0020318 | 0.14451 | 0.0020318 | west | N | 0.0020318 | 0
1071 | KINDERMG | 1 | 45.7 | 0.098178 | west | N | -0.0042641 | 0.25982 | 0.0020318 | 0.14451 | 0.0020318 | west | N | 0.0020318 | 0
1073 | SCURRYCW | 2 | 120 | 0.09815 | west | Y | -0.0042921 | 0.25979 | 0.0020038 | 0.14448 | 0.0020038 | west | N | 0.0020038 | 0
1320 | BSP 1 | 1 | 25.8 | 0.096671 | west | N | -0.0057711 | 0.25831 | 0.0005248 | 0.143 | 0.0005248 | west | N | 0.0005248 | 0
1326 | STANTONW | 1 | 100.5 | 0.0963 | west | Y | -0.0061421 | 0.25794 | 0.0001538 | 0.14263 | 0.0001538 | west | N | 0.0001538 | 0
1327 | WILDHRSE | 1 | 120 | 0.097188 | west | Y | -0.0052541 | 0.25883 | 0.0010418 | 0.14352 | 0.0010418 | west | N | 0.0010418 | 0
1328 | OCOTILLO | 1 | 58 | 0.096269 | west | Y | -0.0061731 | 0.25791 | 0.0001228 | 0.1426 | 0.0001228 | west | N | 0.0001228 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.096507 | west | Y | -0.0059351 | 0.25815 | 0.0003608 | 0.14284 | 0.0003608 | west | N | 0.0003608 | 0
1343 | TRENTIPP | 1 | 150 | 0.098858 | west | Y | -0.0035841 | 0.2605 | 0.0027118 | 0.14519 | 0.0027118 | west | N | 0.0027118 | 0
1349 | WESTXWIN | 1 | 6.6 | 0.095512 | west | Y | -0.0069301 | 0.25715 | -0.0006342 | 0.14184 | 0.0006342 | west | N | 0.0006342 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.095512 | west | Y | -0.0069301 | 0.25715 | -0.0006342 | 0.14184 | 0.0006342 | west | N | 0.0006342 | 0
1354 | AEPWIND_ | 1 | 101 | 0.098858 | west | Y | -0.0035841 | 0.2605 | 0.0027118 | 0.14519 | 0.0027118 | west | N | 0.0027118 | 0
1360 | GUNSIGHT | 1 | 120 | 0.09723 | west | Y | -0.0052121 | 0.25887 | 0.0010838 | 0.14356 | 0.0010838 | west | N | 0.0010838 | 0
1432 | GRHAMSES | 2 | 366 | 0.10622 | north | Y | 0.0037749 | 0.26786 | 0.010071 | 0.15255 | 0.0037749 | North | N | 0.0037749 | 0
1433 | GRHAMSES | 1 | 242 | 0.10657 | north | Y | 0.0041259 | 0.26821 | 0.010422 | 0.1529 | 0.0041259 | North | N | 0.0041259 | 0
1437 | MESQUITW | 1 | 400 | 0.10217 | west | Y | -0.00026914 | 0.26381 | 0.0060268 | 0.1485 | 0.00026914 | North | Y | 0.0060268 | 2.3031
1438 | MESQUITW | 1 | 236 | 0.10218 | west | Y | -0.00026414 | 0.26382 | 0.0060318 | 0.14851 | 0.00026414 | North | Y | 0.0060318 | 1.3612
1442 | COKFIELD | 1 | 165 | 0.10315 | west | Y | 0.00070486 | 0.26479 | 0.0070008 | 0.14948 | 0.00070486 | North | Y | 0.0070008 | 1.0388
1453 | WCPWRCO_ | 1 | 204 | 0.10839 | north | Y | 0.0059439 | 0.27003 | 0.01224 | 0.15472 | 0.0059439 | North | N | 0.0059439 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.10839 | north | Y | 0.0059439 | 0.27003 | 0.01224 | 0.15472 | 0.0059439 | North | N | 0.0059439 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.10839 | north | Y | 0.0059439 | 0.27003 | 0.01224 | 0.15472 | 0.0059439 | North | N | 0.0059439 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.10643 | west | Y | 0.0039849 | 0.26807 | 0.010281 | 0.15276 | 0.0039849 | North | Y | 0.010281 | 0.12592
1479 | WFCOGEN_ | 2 | 20 | 0.10643 | west | Y | 0.0039849 | 0.26807 | 0.010281 | 0.15276 | 0.0039849 | North | Y | 0.010281 | 0.12592
1482 | WFCOGEN_ | 1 | 20 | 0.10643 | west | Y | 0.0039849 | 0.26807 | 0.010281 | 0.15276 | 0.0039849 | North | Y | 0.010281 | 0.12592
1482 | WFCOGEN_ | 2 | 17 | 0.10643 | west | Y | 0.0039849 | 0.26807 | 0.010281 | 0.15276 | 0.0039849 | North | Y | 0.010281 | 0.10703
1600 | BARTNWND | 1 | 120 | 0.10917 | north | Y | 0.0067289 | 0.27081 | 0.013025 | 0.1555 | 0.0067289 | North | N | 0.0067289 | 0
1643 | SLSTR1PP | 1 | 60 | 0.11197 | north | Y | 0.0095309 | 0.27361 | 0.015827 | 0.1583 | 0.0095309 | North | N | 0.0095309 | 0
1675 | PEC_1G | 1 | 75 | 0.10686 | north | N | 0.0044149 | 0.2685 | 0.010711 | 0.15319 | 0.0044149 | North | N | 0.0044149 | 0
1676 | PEC_2G | 2 | 79.6 | 0.10686 | north | N | 0.0044149 | 0.2685 | 0.010711 | 0.15319 | 0.0044149 | North | N | 0.0044149 | 0
1677 | PEC_3G | 3 | 88.4 | 0.10686 | north | N | 0.0044149 | 0.2685 | 0.010711 | 0.15319 | 0.0044149 | North | N | 0.0044149 | 0
1678 | LAMARPWR | 1 | 160 | 0.10694 | north | Y | 0.0044989 | 0.26858 | 0.010795 | 0.15327 | 0.0044989 | North | N | 0.0044989 | 0
1679 | LAMARPWR | 2 | 156 | 0.10694 | north | Y | 0.0044989 | 0.26858 | 0.010795 | 0.15327 | 0.0044989 | North | N | 0.0044989 | 0
1680 | LAMARPWR | 3 | 196 | 0.10694 | north | Y | 0.0044989 | 0.26858 | 0.010795 | 0.15327 | 0.0044989 | North | N | 0.0044989 | 0
1681 | LAMARPWR | 4 | 156 | 0.10694 | north | Y | 0.0044989 | 0.26858 | 0.010795 | 0.15327 | 0.0044989 | North | N | 0.0044989 | 0
1682 | LAMARPWR | 5 | 157 | 0.10694 | north | Y | 0.0044989 | 0.26858 | 0.010795 | 0.15327 | 0.0044989 | North | N | 0.0044989 | 0
1683 | LAMARPWR | 6 | 198 | 0.10694 | north | Y | 0.0044989 | 0.26858 | 0.010795 | 0.15327 | 0.0044989 | North | N | 0.0044989 | 0
1687 | VALLEY_1 | 1 | 170 | 0.10719 | north | Y | 0.0047459 | 0.26883 | 0.011042 | 0.15352 | 0.0047459 | North | N | 0.0047459 | 0
1688 | VALLEY_2 | 2 | 520 | 0.10719 | north | Y | 0.0047459 | 0.26883 | 0.011042 | 0.15352 | 0.0047459 | North | N | 0.0047459 | 0
1689 | VALLEY_3 | 3 | 370 | 0.10703 | north | Y | 0.0045909 | 0.26867 | 0.010887 | 0.15336 | 0.0045909 | North | N | 0.0045909 | 0
1701 | MOSES_1G | 1 | 558 | 0.10679 | north | Y | 0.0043479 | 0.26843 | 0.010644 | 0.15312 | 0.0043479 | North | N | 0.0043479 | 0
1702 | MOSES_2G | 2 | 579 | 0.10679 | north | Y | 0.0043479 | 0.26843 | 0.010644 | 0.15312 | 0.0043479 | North | N | 0.0043479 | 0
1703 | MOSES_3G | 3 | 808 | 0.10679 | north | Y | 0.0043479 | 0.26843 | 0.010644 | 0.15312 | 0.0043479 | North | N | 0.0043479 | 0
1861 | EAGLEMNT | MB | 112 | 0.1105 | north | Y | 0.0080549 | 0.27214 | 0.014351 | 0.15683 | 0.0080549 | North | N | 0.0080549 | 0
1862 | EAGLEMNT | MB | 100 | 0.1105 | north | Y | 0.0080549 | 0.27214 | 0.014351 | 0.15683 | 0.0080549 | North | N | 0.0080549 | 0
1863 | EAGLEMNT | MB | 378 | 0.1105 | north | Y | 0.0080549 | 0.27214 | 0.014351 | 0.15683 | 0.0080549 | North | N | 0.0080549 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.11193 | north | Y | 0.0094879 | 0.27357 | 0.015784 | 0.15826 | 0.0094879 | North | N | 0.0094879 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.11193 | north | Y | 0.0094879 | 0.27357 | 0.015784 | 0.15826 | 0.0094879 | North | N | 0.0094879 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.11193 | north | Y | 0.0094879 | 0.27357 | 0.015784 | 0.15826 | 0.0094879 | North | N | 0.0094879 | 0
1889 | DECRDOVA | MB | 770 | 0.1122 | north | Y | 0.0097579 | 0.27384 | 0.016054 | 0.15853 | 0.0097579 | North | N | 0.0097579 | 0
1892 | DECRDOVA | A | 70 | 0.11419 | north | Y | 0.011748 | 0.27583 | 0.018044 | 0.16052 | 0.011748 | North | N | 0.011748 | 0
1893 | DECRDOVA | B | 69 | 0.11419 | north | Y | 0.011748 | 0.27583 | 0.018044 | 0.16052 | 0.011748 | North | N | 0.011748 | 0
1894 | DECRDOVA | C | 69 | 0.11419 | north | Y | 0.011748 | 0.27583 | 0.018044 | 0.16052 | 0.011748 | North | N | 0.011748 | 0
1895 | DECRDOVA | D | 68 | 0.11419 | north | Y | 0.011748 | 0.27583 | 0.018044 | 0.16052 | 0.011748 | North | N | 0.011748 | 0
1898 | COMCHEPK | 1 | 1157 | 0.11172 | north | N | 0.0092769 | 0.27336 | 0.015573 | 0.15805 | 0.0092769 | North | N | 0.0092769 | 0
1899 | COMCHEPK | 2 | 1158 | 0.11172 | north | N | 0.0092769 | 0.27336 | 0.015573 | 0.15805 | 0.0092769 | North | N | 0.0092769 | 0
1937 | MDLTHELP | 5 | 224 | 0.11675 | north | Y | 0.01431 | 0.27839 | 0.020606 | 0.16308 | 0.01431 | North | N | 0.01431 | 0
1938 | MDLTHELP | 6 | 226 | 0.11675 | north | Y | 0.01431 | 0.27839 | 0.020606 | 0.16308 | 0.01431 | North | N | 0.01431 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.11617 | north | Y | 0.013725 | 0.27781 | 0.020021 | 0.1625 | 0.013725 | North | N | 0.013725 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.11617 | north | Y | 0.013725 | 0.27781 | 0.020021 | 0.1625 | 0.013725 | North | N | 0.013725 | 0
1943 | MDLTHELP | 3 | 212 | 0.11675 | north | Y | 0.01431 | 0.27839 | 0.020606 | 0.16308 | 0.01431 | North | N | 0.01431 | 0
1944 | MDLTHELP | 4 | 211 | 0.11675 | north | Y | 0.01431 | 0.27839 | 0.020606 | 0.16308 | 0.01431 | North | N | 0.01431 | 0
1947 | HANDLEY_ | 3 | 395 | 0.11225 | north | Y | 0.0098039 | 0.27389 | 0.0161 | 0.15858 | 0.0098039 | North | N | 0.0098039 | 0
1948 | HANDLEY_ | 4 | 435 | 0.11202 | north | Y | 0.0095729 | 0.27365 | 0.015869 | 0.15834 | 0.0095729 | North | N | 0.0095729 | 0
1949 | HANDLEY_ | 5 | 435 | 0.11225 | north | Y | 0.0098039 | 0.27389 | 0.0161 | 0.15858 | 0.0098039 | North | N | 0.0098039 | 0
2371 | COLLIN_1 | MB | 138 | 0.1079 | north | Y | 0.0054599 | 0.26954 | 0.011756 | 0.15423 | 0.0054599 | North | N | 0.0054599 | 0
2413 | MTCK6_G | 6 | 118 | 0.10877 | north | Y | 0.0063319 | 0.27041 | 0.012628 | 0.1551 | 0.0063319 | North | N | 0.0063319 | 0
2414 | MTCK7_G | 7 | 115 | 0.10877 | north | Y | 0.0063319 | 0.27041 | 0.012628 | 0.1551 | 0.0063319 | North | N | 0.0063319 | 0
2417 | MTCK8_G | 8 | 556 | 0.10877 | north | Y | 0.0063319 | 0.27041 | 0.012628 | 0.1551 | 0.0063319 | North | N | 0.0063319 | 0
2451 | LKHB1_G | 1 | 388 | 0.10669 | north | Y | 0.0042479 | 0.26833 | 0.010544 | 0.15302 | 0.0042479 | North | N | 0.0042479 | 0
2452 | LKHB2_G | 2 | 515 | 0.10669 | north | Y | 0.0042479 | 0.26833 | 0.010544 | 0.15302 | 0.0042479 | North | N | 0.0042479 | 0
3097 | MARTLAKE | 1 | 785 | 0.10143 | north | Y | -0.0010071 | 0.26307 | 0.0052888 | 0.14776 | 0.0010071 | North | N | 0.0010071 | 0
3098 | MARTLAKE | 2 | 795 | 0.10143 | north | Y | -0.0010071 | 0.26307 | 0.0052888 | 0.14776 | 0.0010071 | North | N | 0.0010071 | 0
3099 | MARTLAKE | 3 | 780 | 0.10143 | north | Y | -0.0010071 | 0.26307 | 0.0052888 | 0.14776 | 0.0010071 | North | N | 0.0010071 | 0
3107 | STRYKER_ | 1 | 182 | 0.099735 | north | Y | -0.0027071 | 0.26137 | 0.0035888 | 0.14606 | 0.0027071 | North | N | 0.0027071 | 0
3108 | STRYKER_ | 2 | 484 | 0.099735 | north | Y | -0.0027071 | 0.26137 | 0.0035888 | 0.14606 | 0.0027071 | North | N | 0.0027071 | 0
3126 | TRINIDAD | 1 | 224 | 0.10627 | north | Y | 0.0038289 | 0.26791 | 0.010125 | 0.1526 | 0.0038289 | North | N | 0.0038289 | 0
3309 | ASPN_G | 1 | 50 | 0.10015 | north | Y | -0.0022871 | 0.26179 | 0.0040088 | 0.14648 | 0.0022871 | North | N | 0.0022871 | 0
3348 | CHAMPION | MB | 42 | 0.10021 | north | N | -0.0022361 | 0.26185 | 0.0040598 | 0.14654 | 0.0022361 | North | N | 0.0022361 | 0
3381 | BBRN_1G | 1 | 615 | 0.09279 | north | Y | -0.0096521 | 0.25443 | -0.0033562 | 0.13912 | 0.0033562 | west | Y | 0.0096521 | 3.872
3382 | BBRN_2G | 2 | 587 | 0.09279 | north | Y | -0.0096521 | 0.25443 | -0.0033562 | 0.13912 | 0.0033562 | west | Y | 0.0096521 | 3.6957
3403 | THOUSE_1 | MB | 537 | 0.17333 | north | Y | 0.070889 | 0.33497 | 0.077185 | 0.21966 | 0.070889 | North | N | 0.070889 | 0
3404 | THOUSE_2 | 2 | 787 | 0.17333 | north | Y | 0.070889 | 0.33497 | 0.077185 | 0.21966 | 0.070889 | North | N | 0.070889 | 0
3416 | LAKE_CRK | MB | 75 | 0.16854 | north | Y | 0.066101 | 0.33018 | 0.072397 | 0.21487 | 0.066101 | North | N | 0.066101 | 0
3417 | LAKE_CRK | MB | 222 | 0.16854 | north | Y | 0.066101 | 0.33018 | 0.072397 | 0.21487 | 0.066101 | North | N | 0.066101 | 0
3432 | SANDOW_4 | 4 | 569 | -0.26261 | south | Y | -0.36505 | -0.10097 | -0.35875 | -0.21628 | 0.10097 | south | N | 0.10097 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.15648 | south | Y | -0.25892 | 0.0051599 | -0.25263 | -0.11015 | 0.0051599 | south | N | 0.0051599 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.15648 | south | Y | -0.25892 | 0.0051599 | -0.25263 | -0.11015 | 0.0051599 | south | N | 0.0051599 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.15643 | south | Y | -0.25887 | 0.0052089 | -0.25258 | -0.1101 | 0.0052089 | south | N | 0.0052089 | 0
5031 | BRA_VHBC | 1 | 46 | -0.15648 | south | Y | -0.25892 | 0.0051599 | -0.25263 | -0.11015 | 0.0051599 | south | N | 0.0051599 | 0
5032 | BRA_VHBC | 2 | 47 | -0.15648 | south | Y | -0.25892 | 0.0051599 | -0.25263 | -0.11015 | 0.0051599 | south | N | 0.0051599 | 0
5033 | BRA_VHBC | 3 | 46 | -0.15648 | south | Y | -0.25892 | 0.0051599 | -0.25263 | -0.11015 | 0.0051599 | south | N | 0.0051599 | 0
5034 | BRA_VHBC | 4 | 46 | -0.15648 | south | Y | -0.25892 | 0.0051599 | -0.25263 | -0.11015 | 0.0051599 | south | N | 0.0051599 | 0
5111 | CALAVER_ | 1 | 424 | -0.15688 | south | Y | -0.25932 | 0.0047579 | -0.25303 | -0.11055 | 0.0047579 | south | N | 0.0047579 | 0
5112 | CALAVER_ | 2 | 425 | -0.15688 | south | Y | -0.25932 | 0.0047579 | -0.25303 | -0.11055 | 0.0047579 | south | N | 0.0047579 | 0
5264 | LEON_LCP | 3 | 58 | -0.15546 | south | Y | -0.2579 | 0.0061779 | -0.25161 | -0.10913 | 0.0061779 | south | N | 0.0061779 | 0
5265 | LEON_LCP | 4 | 89 | -0.15546 | south | Y | -0.2579 | 0.0061779 | -0.25161 | -0.10913 | 0.0061779 | south | N | 0.0061779 | 0
5266 | LEON_LCP | 1 | 44 | -0.15546 | south | Y | -0.2579 | 0.0061779 | -0.25161 | -0.10913 | 0.0061779 | south | N | 0.0061779 | 0
5267 | LEON_LCP | 2 | 44 | -0.15546 | south | Y | -0.2579 | 0.0061779 | -0.25161 | -0.10913 | 0.0061779 | south | N | 0.0061779 | 0
5268 | LEON_LCP | 3 | 43 | -0.15546 | south | Y | -0.2579 | 0.0061779 | -0.25161 | -0.10913 | 0.0061779 | south | N | 0.0061779 | 0
5269 | LEON_LCP | 4 | 45 | -0.15546 | south | Y | -0.2579 | 0.0061779 | -0.25161 | -0.10913 | 0.0061779 | south | N | 0.0061779 | 0
5396 | CALAVER_ | 1 | 412 | -0.15666 | south | Y | -0.2591 | 0.0049789 | -0.25281 | -0.11033 | 0.0049789 | south | N | 0.0049789 | 0
5397 | CALAVER_ | 2 | 400 | -0.15666 | south | Y | -0.2591 | 0.0049789 | -0.25281 | -0.11033 | 0.0049789 | south | N | 0.0049789 | 0
5401 | CALAVER_ | 1 | 546 | -0.15602 | south | Y | -0.25846 | 0.0056229 | -0.25216 | -0.10969 | 0.0056229 | south | N | 0.0056229 | 0
5402 | CALAVER_ | 2 | 750 | -0.15602 | south | Y | -0.25846 | 0.0056229 | -0.25216 | -0.10969 | 0.0056229 | south | N | 0.0056229 | 0
5436 | TUTTL_WB | MB | 61 | -0.15752 | south | Y | -0.25996 | 0.0041229 | -0.25366 | -0.11119 | 0.0041229 | south | N | 0.0041229 | 0
5438 | TUTTL_WB | MB | 95 | -0.15752 | south | Y | -0.25996 | 0.0041229 | -0.25366 | -0.11119 | 0.0041229 | south | N | 0.0041229 | 0
5439 | TUTTL_WB | MB | 151 | -0.15752 | south | Y | -0.25996 | 0.0041229 | -0.25366 | -0.11119 | 0.0041229 | south | N | 0.0041229 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.15643 | south | Y | -0.25888 | 0.0052049 | -0.25258 | -0.11011 | 0.0052049 | south | N | 0.0052049 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.15643 | south | Y | -0.25888 | 0.0052049 | -0.25258 | -0.11011 | 0.0052049 | south | N | 0.0052049 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.15643 | south | Y | -0.25888 | 0.0052049 | -0.25258 | -0.11011 | 0.0052049 | south | N | 0.0052049 | 0
5503 | RAYBURNG | 1 | 22 | -0.12867 | south | Y | -0.23111 | 0.032969 | -0.22482 | -0.082342 | 0.032969 | south | N | 0.032969 | 0
5505 | RAYBURNG | 1 | 11 | -0.12867 | south | Y | -0.23111 | 0.032969 | -0.22482 | -0.082342 | 0.032969 | south | N | 0.032969 | 0
5506 | RAYBURNG | 1 | 11 | -0.12867 | south | Y | -0.23111 | 0.032969 | -0.22482 | -0.082342 | 0.032969 | south | N | 0.032969 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.12966 | south | Y | -0.23211 | 0.031976 | -0.22581 | -0.083335 | 0.031976 | south | N | 0.031976 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.12966 | south | Y | -0.23211 | 0.031976 | -0.22581 | -0.083335 | 0.031976 | south | N | 0.031976 | 0
5511 | RAYBURNC | 1 | 46 | -0.12966 | south | Y | -0.23211 | 0.031976 | -0.22581 | -0.083335 | 0.031976 | south | N | 0.031976 | 0
5512 | RAYBURNC | 1 | 48 | -0.12966 | south | Y | -0.23211 | 0.031976 | -0.22581 | -0.083335 | 0.031976 | south | N | 0.031976 | 0
5728 | FALCONHY | 2 | 12 | -0.13512 | south | N | -0.23756 | 0.026524 | -0.23126 | -0.088787 | 0.026524 | south | N | 0.026524 | 0
5729 | FALCONHY | 3 | 11 | -0.13512 | south | N | -0.23756 | 0.026524 | -0.23126 | -0.088787 | 0.026524 | south | N | 0.026524 | 0
5890 | PEARSALL | 1 | 24 | -0.13972 | south | Y | -0.24217 | 0.021916 | -0.23587 | -0.093395 | 0.021916 | south | N | 0.021916 | 0
5891 | PEARSALL | 1 | 24 | -0.13972 | south | Y | -0.24217 | 0.021916 | -0.23587 | -0.093395 | 0.021916 | south | N | 0.021916 | 0
5892 | PEARSALL | 1 | 23 | -0.13972 | south | Y | -0.24217 | 0.021916 | -0.23587 | -0.093395 | 0.021916 | south | N | 0.021916 | 0
5903 | SANMIGUE | 1 | 396 | -0.14872 | south | Y | -0.25116 | 0.012918 | -0.24487 | -0.10239 | 0.012918 | south | N | 0.012918 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.088747 | houston | N | -0.19119 | 0.072893 | -0.18489 | -0.042418 | 0.042418 | houston | N | 0.042418 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.088747 | houston | N | -0.19119 | 0.072893 | -0.18489 | -0.042418 | 0.042418 | houston | N | 0.042418 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.10244 | 0
5932 | SI_RAY9 | 9 | 38 | -0.13333 | south | Y | -0.23578 | 0.028306 | -0.22948 | -0.087005 | 0.028306 | south | N | 0.028306 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.13333 | south | Y | -0.23578 | 0.028306 | -0.22948 | -0.087005 | 0.028306 | south | N | 0.028306 | 0
5934 | SI_RAY5 | 5 | 15 | -0.13333 | south | Y | -0.23578 | 0.028306 | -0.22948 | -0.087005 | 0.028306 | south | N | 0.028306 | 0
5935 | SI_RAY10 | 10 | 47 | -0.13333 | south | Y | -0.23578 | 0.028306 | -0.22948 | -0.087005 | 0.028306 | south | N | 0.028306 | 0
6016 | SWMESA | 1 | 75 | 0.084646 | west | Y | -0.017796 | 0.24629 | -0.0115 | 0.13098 | 0.0115 | west | N | 0.0115 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.096146 | 0
6144 | MCADOO1A | 1 | 150 | 0.099541 | west | Y | -0.0029011 | 0.26118 | 0.0033948 | 0.14587 | 0.0029011 | North | Y | 0.0033948 | 0.074049
6407 | TURKTRAK | 1 | 169.5 | 0.094962 | west | Y | -0.0074801 | 0.2566 | -0.0011842 | 0.14129 | 0.0011842 | west | N | 0.0011842 | 0
6476 | LANGFORD | 1 | 150 | 0.045049 | west | Y | -0.057393 | 0.20669 | -0.051097 | 0.091378 | 0.051097 | west | N | 0.051097 | 0
6637 | SNYDERW1 | 1 | 63 | 0.098078 | west | Y | -0.0043641 | 0.25972 | 0.0019318 | 0.14441 | 0.0019318 | west | N | 0.0019318 | 0
6752 | OKLA0A | 1 | 649.7 | 0.10394 | west | Y | 0.0015029 | 0.26558 | 0.0077988 | 0.15027 | 0.0015029 | North | Y | 0.0077988 | 4.0905
6948 | DENISNDM | 1 | 40 | 0.10732 | north | N | 0.0048799 | 0.26896 | 0.011176 | 0.15365 | 0.0048799 | North | N | 0.0048799 | 0
6948 | DENISNDM | 2 | 40 | 0.10732 | north | N | 0.0048799 | 0.26896 | 0.011176 | 0.15365 | 0.0048799 | North | N | 0.0048799 | 0
7000 | L_FERGUS | 1 | 422 | -0.10246 | south | Y | -0.20491 | 0.059176 | -0.19861 | -0.056135 | 0.056135 | houston | Y | 0.059176 | 1.2834
7004 | L_SIMGID | 1 | 132 | -0.16801 | south | Y | -0.27045 | -0.0063721 | -0.26416 | -0.12168 | 0.0063721 | south | N | 0.0063721 | 0
7005 | L_SIMGID | 2 | 134 | -0.16801 | south | Y | -0.27045 | -0.0063721 | -0.26416 | -0.12168 | 0.0063721 | south | N | 0.0063721 | 0
7006 | L_SIMGID | 3 | 323 | -0.16801 | south | Y | -0.27045 | -0.0063721 | -0.26416 | -0.12168 | 0.0063721 | south | N | 0.0063721 | 0
7007 | L_LOSTPI | 1 | 158 | -0.21699 | south | Y | -0.31944 | -0.055353 | -0.31314 | -0.17066 | 0.055353 | south | N | 0.055353 | 0
7008 | L_LOSTPI | 2 | 160 | -0.21699 | south | Y | -0.31944 | -0.055353 | -0.31314 | -0.17066 | 0.055353 | south | N | 0.055353 | 0
7009 | L_LOSTPI | 3 | 175 | -0.21699 | south | Y | -0.31944 | -0.055353 | -0.31314 | -0.17066 | 0.055353 | south | N | 0.055353 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.18647 | south | Y | -0.28891 | -0.024831 | -0.28262 | -0.14014 | 0.024831 | south | N | 0.024831 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.18647 | south | Y | -0.28891 | -0.024831 | -0.28262 | -0.14014 | 0.024831 | south | N | 0.024831 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.18624 | south | Y | -0.28868 | -0.024596 | -0.28238 | -0.13991 | 0.024596 | south | N | 0.024596 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.17516 | south | Y | -0.2776 | -0.013521 | -0.27131 | -0.12883 | 0.013521 | south | N | 0.013521 | 0
7015 | L_HAYSEN | 2 | 225 | -0.17516 | south | Y | -0.2776 | -0.013521 | -0.27131 | -0.12883 | 0.013521 | south | N | 0.013521 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.17516 | south | Y | -0.2776 | -0.013521 | -0.27131 | -0.12883 | 0.013521 | south | N | 0.013521 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.17516 | south | Y | -0.2776 | -0.013521 | -0.27131 | -0.12883 | 0.013521 | south | N | 0.013521 | 0
7020 | L_AUSTPL | 1 | 8 | -0.14741 | south | N | -0.24985 | 0.014233 | -0.24355 | -0.10108 | 0.014233 | south | N | 0.014233 | 0
7020 | L_AUSTPL | 2 | 8 | -0.14741 | south | N | -0.24985 | 0.014233 | -0.24355 | -0.10108 | 0.014233 | south | N | 0.014233 | 0
7022 | L_BUCHAN | 1 | 18 | -0.078044 | south | N | -0.18049 | 0.083596 | -0.17419 | -0.031715 | 0.031715 | houston | Y | 0.083596 | 0
7023 | L_BUCHAN | 2 | 18 | -0.078044 | south | N | -0.18049 | 0.083596 | -0.17419 | -0.031715 | 0.031715 | houston | Y | 0.083596 | 0
7024 | L_BUCHAN | 3 | 15 | -0.078044 | south | N | -0.18049 | 0.083596 | -0.17419 | -0.031715 | 0.031715 | houston | Y | 0.083596 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.083315 | south | N | -0.18576 | 0.078325 | -0.17946 | -0.036986 | 0.036986 | houston | Y | 0.078325 | 0
7028 | L_MARBFA | 1 | 18 | -0.11083 | south | N | -0.21328 | 0.050807 | -0.20698 | -0.064504 | 0.050807 | south | N | 0.050807 | 0
7029 | L_MARBFA | 2 | 18 | -0.11083 | south | N | -0.21328 | 0.050807 | -0.20698 | -0.064504 | 0.050807 | south | N | 0.050807 | 0
7031 | L_MARSFO | 1 | 35 | -0.12981 | south | N | -0.23226 | 0.031827 | -0.22596 | -0.083484 | 0.031827 | south | N | 0.031827 | 0
7032 | L_MARSFO | 2 | 34 | -0.12981 | south | N | -0.23226 | 0.031827 | -0.22596 | -0.083484 | 0.031827 | south | N | 0.031827 | 0
7033 | L_MARSFO | 3 | 35 | -0.12981 | south | N | -0.23226 | 0.031827 | -0.22596 | -0.083484 | 0.031827 | south | N | 0.031827 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.10224 | south | N | -0.20469 | 0.059396 | -0.19839 | -0.055915 | 0.055915 | houston | Y | 0.059396 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.10224 | south | N | -0.20469 | 0.059396 | -0.19839 | -0.055915 | 0.055915 | houston | Y | 0.059396 | 0
7038 | L_DELAWA | 1 | 35 | 0.094523 | west | Y | -0.0079191 | 0.25616 | -0.0016232 | 0.14085 | 0.0016232 | west | N | 0.0016232 | 0
7038 | L_DELAWA | 2 | 30 | 0.094523 | west | Y | -0.0079191 | 0.25616 | -0.0016232 | 0.14085 | 0.0016232 | west | N | 0.0016232 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.16803 | south | Y | -0.27047 | -0.0063871 | -0.26417 | -0.1217 | 0.0063871 | south | N | 0.0063871 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.16803 | south | Y | -0.27047 | -0.0063871 | -0.26417 | -0.1217 | 0.0063871 | south | N | 0.0063871 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.16803 | south | Y | -0.27047 | -0.0063871 | -0.26417 | -0.1217 | 0.0063871 | south | N | 0.0063871 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.16803 | south | Y | -0.27047 | -0.0063871 | -0.26417 | -0.1217 | 0.0063871 | south | N | 0.0063871 | 0
7487 | L_CANYHY | 1 | 6 | -0.16503 | south | N | -0.26747 | -0.0033861 | -0.26117 | -0.1187 | 0.0033861 | south | N | 0.0033861 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.1641 | south | N | -0.26654 | -0.0024561 | -0.26024 | -0.11777 | 0.0024561 | south | N | 0.0024561 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.1641 | south | N | -0.26654 | -0.0024561 | -0.26024 | -0.11777 | 0.0024561 | south | N | 0.0024561 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.1641 | south | N | -0.26654 | -0.0024561 | -0.26024 | -0.11777 | 0.0024561 | south | N | 0.0024561 | 0
7609 | L_SCHUMA | 1 | 4 | -0.16351 | south | N | -0.26595 | -0.0018671 | -0.25965 | -0.11718 | 0.0018671 | south | N | 0.0018671 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.15996 | south | N | -0.26241 | 0.0016749 | -0.25611 | -0.11364 | 0.0016749 | south | N | 0.0016749 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.15996 | south | N | -0.26241 | 0.0016749 | -0.25611 | -0.11364 | 0.0016749 | south | N | 0.0016749 | 0
7800 | L_GUADGE | 1 | 147 | -0.16231 | south | Y | -0.26475 | -0.00067206 | -0.25846 | -0.11598 | 0.00067206 | south | N | 0.00067206 | 0
7801 | L_GUADGE | 2 | 138 | -0.16231 | south | Y | -0.26475 | -0.00067206 | -0.25846 | -0.11598 | 0.00067206 | south | N | 0.00067206 | 0
7802 | L_GUADGE | 3 | 140 | -0.16231 | south | Y | -0.26475 | -0.00067206 | -0.25846 | -0.11598 | 0.00067206 | south | N | 0.00067206 | 0
7803 | L_GUADGE | 4 | 147 | -0.16231 | south | Y | -0.26475 | -0.00067206 | -0.25846 | -0.11598 | 0.00067206 | south | N | 0.00067206 | 0
7804 | L_GUADGE | 5 | 182 | -0.16231 | south | Y | -0.26475 | -0.00067206 | -0.25846 | -0.11598 | 0.00067206 | south | N | 0.00067206 | 0
7805 | L_GUADGE | 6 | 198 | -0.16231 | south | Y | -0.26475 | -0.00067206 | -0.25846 | -0.11598 | 0.00067206 | south | N | 0.00067206 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.21061 | south | Y | -0.31305 | -0.04897 | -0.30676 | -0.16428 | 0.04897 | south | N | 0.04897 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.21061 | south | Y | -0.31305 | -0.04897 | -0.30676 | -0.16428 | 0.04897 | south | N | 0.04897 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.21061 | south | Y | -0.31305 | -0.04897 | -0.30676 | -0.16428 | 0.04897 | south | N | 0.04897 | 0
7810 | L_RIONOG | 1 | 142 | -0.16843 | south | Y | -0.27087 | -0.0067901 | -0.26458 | -0.1221 | 0.0067901 | south | N | 0.0067901 | 0
7811 | L_RIONOG | 2 | 145 | -0.16843 | south | Y | -0.27087 | -0.0067901 | -0.26458 | -0.1221 | 0.0067901 | south | N | 0.0067901 | 0
7812 | L_RIONOG | 3 | 151 | -0.16843 | south | Y | -0.27087 | -0.0067901 | -0.26458 | -0.1221 | 0.0067901 | south | N | 0.0067901 | 0
7813 | L_RIONOG | 4 | 290 | -0.16843 | south | Y | -0.27087 | -0.0067901 | -0.26458 | -0.1221 | 0.0067901 | south | N | 0.0067901 | 0
8032 | AMISTADH | 1 | 33 | -0.077419 | south | N | -0.17986 | 0.084221 | -0.17357 | -0.03109 | 0.03109 | houston | Y | 0.084221 | 0
8033 | AMISTADH | 2 | 25 | -0.077419 | south | N | -0.17986 | 0.084221 | -0.17357 | -0.03109 | 0.03109 | houston | Y | 0.084221 | 0
8048 | FALCONHY | 1 | 12 | -0.13512 | south | N | -0.23756 | 0.026524 | -0.23126 | -0.088787 | 0.026524 | south | N | 0.026524 | 0
8066 | DUP1V#1 | 1 | 73 | -0.12975 | south | N | -0.2322 | 0.031887 | -0.2259 | -0.083424 | 0.031887 | south | N | 0.031887 | 0
8134 | FOR69CG0 | 1 | 79 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
8138 | FOR69CG0 | 2 | 81 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8147 | UCAR #2 | 10 | 28 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
8148 | UCAR #1 | 2 | 7 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
8153 | FOR69CG0 | 3 | 79 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
8154 | FOR69CG0 | 4 | 80 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
8156 | FOR69CG0 | 6 | 25 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
8157 | FOR69CG0 | 7 | 46 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
8161 | COLETOU1 | 1 | 629 | -0.13688 | south | Y | -0.23933 | 0.024756 | -0.23303 | -0.090555 | 0.024756 | south | N | 0.024756 | 0
8173 | VICEC51A | 5 | 144 | -0.13101 | south | Y | -0.23345 | 0.030629 | -0.22716 | -0.084682 | 0.030629 | south | N | 0.030629 | 0
8174 | VICEC61A | 6 | 188 | -0.13101 | south | Y | -0.23345 | 0.030629 | -0.22716 | -0.084682 | 0.030629 | south | N | 0.030629 | 0
8189 | CUERO 2 | 1 | 12 | -0.15173 | south | N | -0.25417 | 0.0099079 | -0.24788 | -0.1054 | 0.0099079 | south | N | 0.0099079 | 0
8262 | ELPS | 1 | 6 | -0.096846 | south | N | -0.19929 | 0.064794 | -0.19299 | -0.050517 | 0.050517 | houston | Y | 0.064794 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8442 | NBEC71A | 1 | 336 | -0.13204 | south | Y | -0.23448 | 0.029598 | -0.22819 | -0.085713 | 0.029598 | south | N | 0.029598 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.10244 | 0.16164 | -0.096146 | 0.046329 | 0.046329 | houston | Y | 0.16164 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.13232 | south | Y | -0.23476 | 0.029323 | -0.22846 | -0.085988 | 0.029323 | south | N | 0.029323 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.13232 | south | Y | -0.23476 | 0.029323 | -0.22846 | -0.085988 | 0.029323 | south | N | 0.029323 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.13246 | south | N | -0.23491 | 0.029175 | -0.22861 | -0.086136 | 0.029175 | south | N | 0.029175 | 0
8506 | VAL #1 | 1 | 25 | -0.13234 | south | N | -0.23479 | 0.029296 | -0.22849 | -0.086015 | 0.029296 | south | N | 0.029296 | 0
8507 | VAL #2 | 2 | 25 | -0.13234 | south | N | -0.23479 | 0.029296 | -0.22849 | -0.086015 | 0.029296 | south | N | 0.029296 | 0
8511 | OXY_CC0A | 1 | 38 | -0.13247 | south | N | -0.23491 | 0.029168 | -0.22862 | -0.086143 | 0.029168 | south | N | 0.029168 | 0
8517 | CELANEBI | 1 | 29 | -0.13306 | south | N | -0.2355 | 0.028578 | -0.22921 | -0.086733 | 0.028578 | south | N | 0.028578 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.13206 | south | N | -0.2345 | 0.029584 | -0.2282 | -0.085727 | 0.029584 | south | N | 0.029584 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.13206 | south | N | -0.2345 | 0.029584 | -0.2282 | -0.085727 | 0.029584 | south | N | 0.029584 | 0
8562 | CNOPST1 | 3 | 153 | -0.13206 | south | N | -0.2345 | 0.029584 | -0.2282 | -0.085727 | 0.029584 | south | N | 0.029584 | 0
8926 | LGE_GT10 | 1 | 158 | -0.13081 | south | N | -0.23326 | 0.030825 | -0.22696 | -0.084486 | 0.030825 | south | N | 0.030825 | 0
8927 | LGE_GT20 | 2 | 153 | -0.13081 | south | N | -0.23326 | 0.030825 | -0.22696 | -0.084486 | 0.030825 | south | N | 0.030825 | 0
8928 | LGE_STG0 | 3 | 100 | -0.13081 | south | N | -0.23326 | 0.030825 | -0.22696 | -0.084486 | 0.030825 | south | N | 0.030825 | 0
8930 | ICPGN10A | 1 | 145 | -0.13081 | south | N | -0.23326 | 0.030825 | -0.22696 | -0.084486 | 0.030825 | south | N | 0.030825 | 0
8931 | ICPGN20A | 2 | 147 | -0.13081 | south | N | -0.23326 | 0.030825 | -0.22696 | -0.084486 | 0.030825 | south | N | 0.030825 | 0
8932 | ICPGN30A | 3 | 127 | -0.13081 | south | N | -0.23326 | 0.030825 | -0.22696 | -0.084486 | 0.030825 | south | N | 0.030825 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.13377 | south | Y | -0.23621 | 0.027868 | -0.22992 | -0.087443 | 0.027868 | south | N | 0.027868 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.13377 | south | Y | -0.23621 | 0.027868 | -0.22992 | -0.087443 | 0.027868 | south | N | 0.027868 | 0
8935 | FGNTS201 | 3 | 173 | -0.13377 | south | Y | -0.23621 | 0.027868 | -0.22992 | -0.087443 | 0.027868 | south | N | 0.027868 | 0
8936 | MVGN#1 | 1 | 207 | -0.13356 | south | Y | -0.236 | 0.028083 | -0.2297 | -0.087228 | 0.028083 | south | N | 0.028083 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.13356 | south | Y | -0.236 | 0.028083 | -0.2297 | -0.087228 | 0.028083 | south | N | 0.028083 | 0
8938 | MVGN#3 | 3 | 242 | -0.13356 | south | Y | -0.236 | 0.028083 | -0.2297 | -0.087228 | 0.028083 | south | N | 0.028083 | 0
8981 | HECN1 | 1 | 144 | -0.13355 | south | Y | -0.236 | 0.028086 | -0.2297 | -0.087225 | 0.028086 | south | N | 0.028086 | 0
8982 | HECN2 | 2 | 144 | -0.13355 | south | Y | -0.236 | 0.028086 | -0.2297 | -0.087225 | 0.028086 | south | N | 0.028086 | 0
8983 | HECN3 | 3 | 171 | -0.13355 | south | Y | -0.236 | 0.028086 | -0.2297 | -0.087225 | 0.028086 | south | N | 0.028086 | 0
9000 | DECKR_G1 | 1 | 310 | -0.15464 | south | Y | -0.25708 | 0.0070009 | -0.25079 | -0.10831 | 0.0070009 | south | N | 0.0070009 | 0
9001 | DECKR_G2 | 2 | 413 | -0.15464 | south | Y | -0.25708 | 0.0070009 | -0.25079 | -0.10831 | 0.0070009 | south | N | 0.0070009 | 0
9002 | DECKR_G3 | 3 | 42 | -0.15753 | south | Y | -0.25997 | 0.0041079 | -0.25368 | -0.1112 | 0.0041079 | south | N | 0.0041079 | 0
9003 | DECKR_G4 | 4 | 44 | -0.15753 | south | Y | -0.25997 | 0.0041079 | -0.25368 | -0.1112 | 0.0041079 | south | N | 0.0041079 | 0
9004 | DECKR_G5 | 5 | 44 | -0.15753 | south | Y | -0.25997 | 0.0041079 | -0.25368 | -0.1112 | 0.0041079 | south | N | 0.0041079 | 0
9005 | DECKR_G6 | 6 | 47 | -0.15753 | south | Y | -0.25997 | 0.0041079 | -0.25368 | -0.1112 | 0.0041079 | south | N | 0.0041079 | 0
9016 | SANDH_G1 | 1 | 49 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
9017 | SANDH_G2 | 2 | 46 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
9018 | SANDH_G3 | 3 | 46 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
9019 | SANDH_G4 | 4 | 47 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
9020 | SANDHG5A | 5A | 154 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
9021 | SANDHG5C | 5C | 148 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
9022 | SANDH_G6 | 6 | 48 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
9023 | SANDH_G7 | 7 | 48 | -0.1598 | south | Y | -0.26224 | 0.0018379 | -0.25595 | -0.11347 | 0.0018379 | south | N | 0.0018379 | 0
11001 | NAV1CT | 1 | 70 | 0.096189 | west | Y | -0.0062531 | 0.25783 | 4.2802e-05 | 0.14252 | 4.2802e-05 | west | N | 4.2802e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.096189 | west | Y | -0.0062531 | 0.25783 | 4.2802e-05 | 0.14252 | 4.2802e-05 | west | N | 4.2802e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.096189 | west | Y | -0.0062531 | 0.25783 | 4.2802e-05 | 0.14252 | 4.2802e-05 | west | N | 4.2802e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.096189 | west | Y | -0.0062531 | 0.25783 | 4.2802e-05 | 0.14252 | 4.2802e-05 | west | N | 4.2802e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.096189 | west | Y | -0.0062531 | 0.25783 | 4.2802e-05 | 0.14252 | 4.2802e-05 | west | N | 4.2802e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.096189 | west | Y | -0.0062531 | 0.25783 | 4.2802e-05 | 0.14252 | 4.2802e-05 | west | N | 4.2802e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.096172 | west | Y | -0.0062701 | 0.25781 | 2.5802e-05 | 0.1425 | 2.5802e-05 | west | N | 2.5802e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.096172 | west | Y | -0.0062701 | 0.25781 | 2.5802e-05 | 0.1425 | 2.5802e-05 | west | N | 2.5802e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.096172 | west | Y | -0.0062701 | 0.25781 | 2.5802e-05 | 0.1425 | 2.5802e-05 | west | N | 2.5802e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.096172 | west | Y | -0.0062701 | 0.25781 | 2.5802e-05 | 0.1425 | 2.5802e-05 | west | N | 2.5802e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.096172 | west | Y | -0.0062701 | 0.25781 | 2.5802e-05 | 0.1425 | 2.5802e-05 | west | N | 2.5802e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.096172 | west | Y | -0.0062701 | 0.25781 | 2.5802e-05 | 0.1425 | 2.5802e-05 | west | N | 2.5802e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.099173 | west | Y | -0.0032691 | 0.26081 | 0.0030268 | 0.1455 | 0.0030268 | west | N | 0.0030268 | 0
11057 | CHAMPION | 1 | 126.5 | 0.099173 | west | Y | -0.0032691 | 0.26081 | 0.0030268 | 0.1455 | 0.0030268 | west | N | 0.0030268 | 0
11058 | PYRON_1G | 1 | 249 | 0.099173 | west | Y | -0.0032691 | 0.26081 | 0.0030268 | 0.1455 | 0.0030268 | west | N | 0.0030268 | 0
11059 | INADALE_ | 1 | 197 | 0.099173 | west | Y | -0.0032691 | 0.26081 | 0.0030268 | 0.1455 | 0.0030268 | west | N | 0.0030268 | 0
11061 | PNTHRCK1 | 1 | 200 | 0.097711 | west | Y | -0.0047311 | 0.25935 | 0.0015648 | 0.14404 | 0.0015648 | west | N | 0.0015648 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.097711 | west | Y | -0.0047311 | 0.25935 | 0.0015648 | 0.14404 | 0.0015648 | west | N | 0.0015648 | 0
11147 | NOTREES_ | 1 | 149 | 0.094826 | west | Y | -0.0076161 | 0.25647 | -0.0013202 | 0.14116 | 0.0013202 | west | N | 0.0013202 | 0
11309 | BULLCREK | 1 | 180 | 0.097487 | west | Y | -0.0049551 | 0.25913 | 0.0013408 | 0.14382 | 0.0013408 | west | N | 0.0013408 | 0
11310 | BULLCREK | 1 | 180 | 0.097487 | west | Y | -0.0049551 | 0.25913 | 0.0013408 | 0.14382 | 0.0013408 | west | N | 0.0013408 | 0
11320 | COYOTE_1 | 1 | 225 | 0.097394 | west | Y | -0.0050481 | 0.25903 | 0.0012478 | 0.14372 | 0.0012478 | west | N | 0.0012478 | 0
11415 | LORAINE_ | 1 | 125 | 0.098595 | west | Y | -0.0038471 | 0.26023 | 0.0024488 | 0.14492 | 0.0024488 | west | N | 0.0024488 | 0
11416 | LORAINE_ | 1 | 125 | 0.098595 | west | Y | -0.0038471 | 0.26023 | 0.0024488 | 0.14492 | 0.0024488 | west | N | 0.0024488 | 0
11691 | KMICHICT | 1 | 140 | 0.10703 | north | N | 0.0045909 | 0.26867 | 0.010887 | 0.15336 | 0.0045909 | North | N | 0.0045909 | 0
11692 | KMICHICT | 2 | 141 | 0.10703 | north | N | 0.0045909 | 0.26867 | 0.010887 | 0.15336 | 0.0045909 | North | N | 0.0045909 | 0
11693 | KMICHIST | 3 | 309 | 0.10703 | north | N | 0.0045909 | 0.26867 | 0.010887 | 0.15336 | 0.0045909 | North | N | 0.0045909 | 0
11694 | KMICHICT | 4 | 143 | 0.10703 | north | N | 0.0045909 | 0.26867 | 0.010887 | 0.15336 | 0.0045909 | North | N | 0.0045909 | 0
11695 | KMICHICT | 5 | 144 | 0.10703 | north | N | 0.0045909 | 0.26867 | 0.010887 | 0.15336 | 0.0045909 | North | N | 0.0045909 | 0
11696 | KMICHIST | 6 | 310 | 0.10703 | north | N | 0.0045909 | 0.26867 | 0.010887 | 0.15336 | 0.0045909 | North | N | 0.0045909 | 0
12322 | ENNSTRAC | 1 | 196 | 0.11072 | north | Y | 0.0082749 | 0.27236 | 0.014571 | 0.15705 | 0.0082749 | North | N | 0.0082749 | 0
12323 | ENNSTRAC | 2 | 111 | 0.11072 | north | Y | 0.0082749 | 0.27236 | 0.014571 | 0.15705 | 0.0082749 | North | N | 0.0082749 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.10787 | north | N | 0.0054239 | 0.26951 | 0.01172 | 0.1542 | 0.0054239 | North | N | 0.0054239 | 0
12411 | FPLEFR1A | 1 | 161 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12412 | FPLEFR1B | 2 | 164 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12413 | FPLEFR1C | 3 | 164 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12414 | FPLEFR1S | 4 | 414 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12421 | FPLEFR2A | 1 | 162 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12422 | FPLEFR2B | 2 | 161 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12423 | FPLEFR2C | 3 | 163 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12424 | FPLEFR2S | 4 | 409 | 0.10568 | north | Y | 0.0032379 | 0.26732 | 0.0095338 | 0.15201 | 0.0032379 | North | N | 0.0032379 | 0
12440 | PARKD_1S | 1 | 0 | 0.1071 | north | N | 0.0046569 | 0.26874 | 0.010953 | 0.15343 | 0.0046569 | North | N | 0.0046569 | 0
12449 | PARKD_2S | 1 | 0 | 0.1071 | north | N | 0.0046569 | 0.26874 | 0.010953 | 0.15343 | 0.0046569 | North | N | 0.0046569 | 0
13116 | TGATEWAY | 1 | 148 | 0.10087 | north | N | -0.0015691 | 0.26251 | 0.0047268 | 0.1472 | 0.0015691 | North | N | 0.0015691 | 0
13117 | TGATEWAY | 2 | 130 | 0.10087 | north | N | -0.0015691 | 0.26251 | 0.0047268 | 0.1472 | 0.0015691 | North | N | 0.0015691 | 0
13118 | TGATEWAY | 3 | 145 | 0.10087 | north | N | -0.0015691 | 0.26251 | 0.0047268 | 0.1472 | 0.0015691 | North | N | 0.0015691 | 0
13119 | TGATEWAY | 4 | 399 | 0.10087 | north | N | -0.0015691 | 0.26251 | 0.0047268 | 0.1472 | 0.0015691 | North | N | 0.0015691 | 0
13131 | CALFREST | 1 | 150.7 | 0.094213 | north | Y | -0.0082291 | 0.25585 | -0.0019332 | 0.14054 | 0.0019332 | west | Y | 0.0082291 | 0.9488
13132 | CALFREST | 2 | 151 | 0.094213 | north | Y | -0.0082291 | 0.25585 | -0.0019332 | 0.14054 | 0.0019332 | west | Y | 0.0082291 | 0.95069
13133 | CALFREST | 3 | 177.4 | 0.094213 | north | Y | -0.0082291 | 0.25585 | -0.0019332 | 0.14054 | 0.0019332 | west | Y | 0.0082291 | 1.1169
13134 | CALFREST | 4 | 151.5 | 0.094474 | north | Y | -0.0079681 | 0.25611 | -0.0016722 | 0.1408 | 0.0016722 | west | Y | 0.0079681 | 0.95384
13135 | CALFREST | 5 | 152.3 | 0.094474 | north | Y | -0.0079681 | 0.25611 | -0.0016722 | 0.1408 | 0.0016722 | west | Y | 0.0079681 | 0.95887
13136 | CALFREST | 6 | 177.5 | 0.094474 | north | Y | -0.0079681 | 0.25611 | -0.0016722 | 0.1408 | 0.0016722 | west | Y | 0.0079681 | 1.1175
13432 | SANDOW_5 | 5 | 581 | -0.26261 | south | Y | -0.36505 | -0.10097 | -0.35875 | -0.21628 | 0.10097 | south | N | 0.10097 | 0
13691 | OAKGROVE | 1 | 855 | 0.06087 | north | Y | -0.041572 | 0.22251 | -0.035276 | 0.1072 | 0.035276 | west | Y | 0.041572 | 5.383
13692 | OAKGROVE | 2 | 855 | 0.06087 | north | Y | -0.041572 | 0.22251 | -0.035276 | 0.1072 | 0.035276 | west | Y | 0.041572 | 5.383
32798 | BRYN_TAM | 1 | 32 | 0.023675 | north | N | -0.078767 | 0.18531 | -0.072471 | 0.070004 | 0.070004 | houston | Y | 0.078767 | 0
32883 | BRYN_DNS | 1 | 48 | 0.020826 | north | Y | -0.081616 | 0.18247 | -0.07532 | 0.067155 | 0.067155 | houston | Y | 0.081616 | 0.69412
32884 | BRYN_DNS | 1 | 46 | 0.020826 | north | Y | -0.081616 | 0.18247 | -0.07532 | 0.067155 | 0.067155 | houston | Y | 0.081616 | 0.6652
32886 | BRYN_ATK | MB | 12 | 0.023763 | north | Y | -0.078679 | 0.1854 | -0.072383 | 0.070092 | 0.070092 | houston | Y | 0.078679 | 0
32887 | BRYN_ATK | MB | 51 | 0.023763 | north | Y | -0.078679 | 0.1854 | -0.072383 | 0.070092 | 0.070092 | houston | Y | 0.078679 | 0
32888 | BRYN_ATK | 1 | 17 | 0.023763 | north | Y | -0.078679 | 0.1854 | -0.072383 | 0.070092 | 0.070092 | houston | Y | 0.078679 | 0.14598
32890 | BRYN_ATK | MB | 22 | 0.023763 | north | Y | -0.078679 | 0.1854 | -0.072383 | 0.070092 | 0.070092 | houston | Y | 0.078679 | 0
32891 | BRYN_ATK | MB | 25 | 0.023763 | north | Y | -0.078679 | 0.1854 | -0.072383 | 0.070092 | 0.070092 | houston | Y | 0.078679 | 0
32892 | BRYN_DNS | 1 | 105 | 0.020826 | north | Y | -0.081616 | 0.18247 | -0.07532 | 0.067155 | 0.067155 | houston | Y | 0.081616 | 1.5184
36998 | RDCNYNG1 | 1 | 84 | 0.098431 | west | Y | -0.0040111 | 0.26007 | 0.0022848 | 0.14476 | 0.0022848 | west | N | 0.0022848 | 0
38332 | WDWRDU2 | 1 | 80 | 0.084468 | west | Y | -0.017974 | 0.24611 | -0.011678 | 0.1308 | 0.011678 | west | N | 0.011678 | 0
38437 | TNSRBNMS | 1 | 150 | 0.084378 | west | Y | -0.018064 | 0.24602 | -0.011768 | 0.13071 | 0.011768 | west | N | 0.011768 | 0
38438 | TNSRBNMS | 1 | 150 | 0.084378 | west | Y | -0.018064 | 0.24602 | -0.011768 | 0.13071 | 0.011768 | west | N | 0.011768 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38600 | TNBP_CGN | 5 | 53 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38614 | TNBPAMCG | 4 | 96 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38615 | TNBPAMCG | 1 | 244 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38690 | TNBP_CGN | 3 | 40 | -0.04811 | houston | N | -0.15055 | 0.11353 | -0.14426 | -0.0017807 | 0.0017807 | houston | N | 0.0017807 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.048136 | houston | N | -0.15058 | 0.1135 | -0.14428 | -0.0018067 | 0.0018067 | houston | N | 0.0018067 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.048136 | houston | N | -0.15058 | 0.1135 | -0.14428 | -0.0018067 | 0.0018067 | houston | N | 0.0018067 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.048136 | houston | N | -0.15058 | 0.1135 | -0.14428 | -0.0018067 | 0.0018067 | houston | N | 0.0018067 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.048136 | houston | N | -0.15058 | 0.1135 | -0.14428 | -0.0018067 | 0.0018067 | houston | N | 0.0018067 | 0
39470 | TNDOWCGN | 1 | 32 | -0.048135 | houston | N | -0.15058 | 0.1135 | -0.14428 | -0.0018057 | 0.0018057 | houston | N | 0.0018057 | 0
39480 | TNDOWCGN | 1 | 30 | -0.048135 | houston | N | -0.15058 | 0.1135 | -0.14428 | -0.0018057 | 0.0018057 | houston | N | 0.0018057 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.064278 | houston | N | -0.16672 | 0.097362 | -0.16042 | -0.017949 | 0.017949 | houston | N | 0.017949 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.064278 | houston | N | -0.16672 | 0.097362 | -0.16042 | -0.017949 | 0.017949 | houston | N | 0.017949 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.064278 | houston | N | -0.16672 | 0.097362 | -0.16042 | -0.017949 | 0.017949 | houston | N | 0.017949 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.064278 | houston | N | -0.16672 | 0.097362 | -0.16042 | -0.017949 | 0.017949 | houston | N | 0.017949 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.06087 | north | Y | -0.041572 | 0.22251 | -0.035276 | 0.1072 | 0.035276 | west | Y | 0.041572 | 0.95887
39970 | TNTNPONE | 1 | 153 | 0.06087 | north | Y | -0.041572 | 0.22251 | -0.035276 | 0.1072 | 0.035276 | west | Y | 0.041572 | 0.96328
48500 | APD_GT1_ | 1 | 136 | -0.038173 | houston | N | -0.14062 | 0.12347 | -0.13432 | 0.0081563 | 0.0081563 | houston | N | 0.0081563 | 0
48510 | AK_GT1__ | 1 | 33 | -0.053499 | houston | N | -0.15594 | 0.10814 | -0.14965 | -0.0071697 | 0.0071697 | houston | N | 0.0071697 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.038112 | houston | Y | -0.14055 | 0.12353 | -0.13426 | 0.0082173 | 0.0082173 | houston | N | 0.0082173 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.038112 | houston | Y | -0.14055 | 0.12353 | -0.13426 | 0.0082173 | 0.0082173 | houston | N | 0.0082173 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.038112 | houston | Y | -0.14055 | 0.12353 | -0.13426 | 0.0082173 | 0.0082173 | houston | N | 0.0082173 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.038112 | houston | Y | -0.14055 | 0.12353 | -0.13426 | 0.0082173 | 0.0082173 | houston | N | 0.0082173 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.066941 | houston | N | -0.16938 | 0.094699 | -0.16309 | -0.020612 | 0.020612 | houston | N | 0.020612 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.066941 | houston | N | -0.16938 | 0.094699 | -0.16309 | -0.020612 | 0.020612 | houston | N | 0.020612 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.054591 | houston | N | -0.15703 | 0.10705 | -0.15074 | -0.0082617 | 0.0082617 | houston | N | 0.0082617 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.054591 | houston | N | -0.15703 | 0.10705 | -0.15074 | -0.0082617 | 0.0082617 | houston | N | 0.0082617 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.054591 | houston | N | -0.15703 | 0.10705 | -0.15074 | -0.0082617 | 0.0082617 | houston | N | 0.0082617 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.041881 | houston | N | -0.14432 | 0.11976 | -0.13803 | 0.0044483 | 0.0044483 | houston | N | 0.0044483 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.041881 | houston | N | -0.14432 | 0.11976 | -0.13803 | 0.0044483 | 0.0044483 | houston | N | 0.0044483 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.041881 | houston | N | -0.14432 | 0.11976 | -0.13803 | 0.0044483 | 0.0044483 | houston | N | 0.0044483 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.041881 | houston | N | -0.14432 | 0.11976 | -0.13803 | 0.0044483 | 0.0044483 | houston | N | 0.0044483 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.03946 | houston | N | -0.1419 | 0.12218 | -0.13561 | 0.0068693 | 0.0068693 | houston | N | 0.0068693 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.03946 | houston | N | -0.1419 | 0.12218 | -0.13561 | 0.0068693 | 0.0068693 | houston | N | 0.0068693 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.04261 | houston | N | -0.14505 | 0.11903 | -0.13876 | 0.0037193 | 0.0037193 | houston | N | 0.0037193 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.04261 | houston | N | -0.14505 | 0.11903 | -0.13876 | 0.0037193 | 0.0037193 | houston | N | 0.0037193 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.04261 | houston | N | -0.14505 | 0.11903 | -0.13876 | 0.0037193 | 0.0037193 | houston | N | 0.0037193 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.04261 | houston | N | -0.14505 | 0.11903 | -0.13876 | 0.0037193 | 0.0037193 | houston | N | 0.0037193 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.04261 | houston | N | -0.14505 | 0.11903 | -0.13876 | 0.0037193 | 0.0037193 | houston | N | 0.0037193 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.035074 | houston | Y | -0.13752 | 0.12657 | -0.13122 | 0.011255 | 0.011255 | houston | N | 0.011255 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.036306 | houston | Y | -0.13875 | 0.12533 | -0.13245 | 0.010023 | 0.010023 | houston | N | 0.010023 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.034702 | houston | Y | -0.13714 | 0.12694 | -0.13085 | 0.011627 | 0.011627 | houston | N | 0.011627 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.034702 | houston | Y | -0.13714 | 0.12694 | -0.13085 | 0.011627 | 0.011627 | houston | N | 0.011627 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.034702 | houston | Y | -0.13714 | 0.12694 | -0.13085 | 0.011627 | 0.011627 | houston | N | 0.011627 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.027859 | houston | N | -0.1303 | 0.13378 | -0.12401 | 0.01847 | 0.01847 | houston | N | 0.01847 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.037928 | houston | N | -0.14037 | 0.12371 | -0.13407 | 0.0084013 | 0.0084013 | houston | N | 0.0084013 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.037928 | houston | N | -0.14037 | 0.12371 | -0.13407 | 0.0084013 | 0.0084013 | houston | N | 0.0084013 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.03383 | houston | N | -0.13627 | 0.12781 | -0.12998 | 0.012499 | 0.012499 | houston | N | 0.012499 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.03383 | houston | N | -0.13627 | 0.12781 | -0.12998 | 0.012499 | 0.012499 | houston | N | 0.012499 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.03383 | houston | N | -0.13627 | 0.12781 | -0.12998 | 0.012499 | 0.012499 | houston | N | 0.012499 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.03383 | houston | N | -0.13627 | 0.12781 | -0.12998 | 0.012499 | 0.012499 | houston | N | 0.012499 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.039379 | houston | N | -0.14182 | 0.12226 | -0.13553 | 0.0069503 | 0.0069503 | houston | N | 0.0069503 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.039379 | houston | N | -0.14182 | 0.12226 | -0.13553 | 0.0069503 | 0.0069503 | houston | N | 0.0069503 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.039379 | houston | N | -0.14182 | 0.12226 | -0.13553 | 0.0069503 | 0.0069503 | houston | N | 0.0069503 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.039379 | houston | N | -0.14182 | 0.12226 | -0.13553 | 0.0069503 | 0.0069503 | houston | N | 0.0069503 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.040153 | houston | N | -0.1426 | 0.12149 | -0.1363 | 0.0061763 | 0.0061763 | houston | N | 0.0061763 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.040153 | houston | N | -0.1426 | 0.12149 | -0.1363 | 0.0061763 | 0.0061763 | houston | N | 0.0061763 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.040153 | houston | N | -0.1426 | 0.12149 | -0.1363 | 0.0061763 | 0.0061763 | houston | N | 0.0061763 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.040153 | houston | N | -0.1426 | 0.12149 | -0.1363 | 0.0061763 | 0.0061763 | houston | N | 0.0061763 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.040153 | houston | N | -0.1426 | 0.12149 | -0.1363 | 0.0061763 | 0.0061763 | houston | N | 0.0061763 | 0
48651 | EP_1_2 | 1 | 5 | -0.035139 | houston | N | -0.13758 | 0.1265 | -0.13129 | 0.01119 | 0.01119 | houston | N | 0.01119 | 0
48651 | EP_1_2 | 2 | 21 | -0.035139 | houston | N | -0.13758 | 0.1265 | -0.13129 | 0.01119 | 0.01119 | houston | N | 0.01119 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.020415 | north | N | -0.082027 | 0.18205 | -0.075731 | 0.066744 | 0.066744 | houston | Y | 0.082027 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.020415 | north | N | -0.082027 | 0.18205 | -0.075731 | 0.066744 | 0.066744 | houston | Y | 0.082027 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.020415 | north | N | -0.082027 | 0.18205 | -0.075731 | 0.066744 | 0.066744 | houston | Y | 0.082027 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.020415 | north | N | -0.082027 | 0.18205 | -0.075731 | 0.066744 | 0.066744 | houston | Y | 0.082027 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.033529 | houston | Y | -0.13597 | 0.12811 | -0.12968 | 0.0128 | 0.0128 | houston | N | 0.0128 | 0
48691 | GBY_7374 | A | 46 | -0.040806 | houston | Y | -0.14325 | 0.12083 | -0.13695 | 0.0055233 | 0.0055233 | houston | N | 0.0055233 | 0
48691 | GBY_7374 | B | 46 | -0.040806 | houston | Y | -0.14325 | 0.12083 | -0.13695 | 0.0055233 | 0.0055233 | houston | N | 0.0055233 | 0
48692 | GBY_8182 | C | 46 | -0.040806 | houston | Y | -0.14325 | 0.12083 | -0.13695 | 0.0055233 | 0.0055233 | houston | N | 0.0055233 | 0
48692 | GBY_8182 | D | 55 | -0.040806 | houston | Y | -0.14325 | 0.12083 | -0.13695 | 0.0055233 | 0.0055233 | houston | N | 0.0055233 | 0
48693 | GBY_8384 | E | 55 | -0.040806 | houston | Y | -0.14325 | 0.12083 | -0.13695 | 0.0055233 | 0.0055233 | houston | N | 0.0055233 | 0
48693 | GBY_8384 | F | 54 | -0.040806 | houston | Y | -0.14325 | 0.12083 | -0.13695 | 0.0055233 | 0.0055233 | houston | N | 0.0055233 | 0
48721 | LEG_1___ | 1 | 827 | 0.074111 | north | Y | -0.028331 | 0.23575 | -0.022035 | 0.12044 | 0.022035 | west | Y | 0.028331 | 5.2067
48722 | LEG_2___ | 2 | 819 | 0.074111 | north | Y | -0.028331 | 0.23575 | -0.022035 | 0.12044 | 0.022035 | west | Y | 0.028331 | 5.1564
48730 | MNS_GT | 1 | 46.1 | -0.054906 | houston | N | -0.15735 | 0.10673 | -0.15105 | -0.0085767 | 0.0085767 | houston | N | 0.0085767 | 0
48731 | CBE_GT1 | 1 | 76 | -0.087801 | houston | Y | -0.19024 | 0.073839 | -0.18395 | -0.041472 | 0.041472 | houston | N | 0.041472 | 0
48732 | CBE_GT2 | 1 | 76 | -0.087801 | houston | Y | -0.19024 | 0.073839 | -0.18395 | -0.041472 | 0.041472 | houston | N | 0.041472 | 0
48733 | CBE_ST12 | 1 | 105 | -0.087801 | houston | Y | -0.19024 | 0.073839 | -0.18395 | -0.041472 | 0.041472 | houston | N | 0.041472 | 0
48734 | CBE_GT3 | 1 | 74 | -0.087801 | houston | Y | -0.19024 | 0.073839 | -0.18395 | -0.041472 | 0.041472 | houston | N | 0.041472 | 0
48735 | CBE_GT4 | 1 | 74 | -0.087801 | houston | Y | -0.19024 | 0.073839 | -0.18395 | -0.041472 | 0.041472 | houston | N | 0.041472 | 0
48736 | CBE_ST34 | 1 | 102 | -0.087801 | houston | Y | -0.19024 | 0.073839 | -0.18395 | -0.041472 | 0.041472 | houston | N | 0.041472 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.039356 | houston | N | -0.1418 | 0.12228 | -0.1355 | 0.0069733 | 0.0069733 | houston | N | 0.0069733 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.039356 | houston | N | -0.1418 | 0.12228 | -0.1355 | 0.0069733 | 0.0069733 | houston | N | 0.0069733 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.039356 | houston | N | -0.1418 | 0.12228 | -0.1355 | 0.0069733 | 0.0069733 | houston | N | 0.0069733 | 0
48761 | PR_GT1__ | 1 | 35 | -0.039849 | houston | N | -0.14229 | 0.12179 | -0.136 | 0.0064803 | 0.0064803 | houston | N | 0.0064803 | 0
48772 | PHR_GN2_ | MB | 459 | -0.044471 | houston | Y | -0.14691 | 0.11717 | -0.14062 | 0.0018583 | 0.0018583 | houston | N | 0.0018583 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.035131 | houston | N | -0.13757 | 0.12651 | -0.13128 | 0.011198 | 0.011198 | houston | N | 0.011198 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.035131 | houston | N | -0.13757 | 0.12651 | -0.13128 | 0.011198 | 0.011198 | houston | N | 0.011198 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.035131 | houston | N | -0.13757 | 0.12651 | -0.13128 | 0.011198 | 0.011198 | houston | N | 0.011198 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.035131 | houston | N | -0.13757 | 0.12651 | -0.13128 | 0.011198 | 0.011198 | houston | N | 0.011198 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.035131 | houston | N | -0.13757 | 0.12651 | -0.13128 | 0.011198 | 0.011198 | houston | N | 0.011198 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.035131 | houston | N | -0.13757 | 0.12651 | -0.13128 | 0.011198 | 0.011198 | houston | N | 0.011198 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.035131 | houston | N | -0.13757 | 0.12651 | -0.13128 | 0.011198 | 0.011198 | houston | N | 0.011198 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.027859 | houston | N | -0.1303 | 0.13378 | -0.12401 | 0.01847 | 0.01847 | houston | N | 0.01847 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.027859 | houston | N | -0.1303 | 0.13378 | -0.12401 | 0.01847 | 0.01847 | houston | N | 0.01847 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.027859 | houston | N | -0.1303 | 0.13378 | -0.12401 | 0.01847 | 0.01847 | houston | N | 0.01847 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.027859 | houston | N | -0.1303 | 0.13378 | -0.12401 | 0.01847 | 0.01847 | houston | N | 0.01847 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.034849 | houston | N | -0.13729 | 0.12679 | -0.131 | 0.01148 | 0.01148 | houston | N | 0.01148 | 0
48820 | SHELLG1_ | 1 | 71 | -0.038898 | houston | N | -0.14134 | 0.12274 | -0.13504 | 0.0074313 | 0.0074313 | houston | N | 0.0074313 | 0
48821 | SHELLG2 | 2 | 72 | -0.038898 | houston | N | -0.14134 | 0.12274 | -0.13504 | 0.0074313 | 0.0074313 | houston | N | 0.0074313 | 0
48822 | SHELLG3_ | 1 | 39 | -0.038898 | houston | N | -0.14134 | 0.12274 | -0.13504 | 0.0074313 | 0.0074313 | houston | N | 0.0074313 | 0
48822 | SHELLG3_ | 2 | 30 | -0.038898 | houston | N | -0.14134 | 0.12274 | -0.13504 | 0.0074313 | 0.0074313 | houston | N | 0.0074313 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.040526 | houston | N | -0.14297 | 0.12111 | -0.13667 | 0.0058033 | 0.0058033 | houston | N | 0.0058033 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.040526 | houston | N | -0.14297 | 0.12111 | -0.13667 | 0.0058033 | 0.0058033 | houston | N | 0.0058033 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.039385 | houston | N | -0.14183 | 0.12225 | -0.13553 | 0.0069443 | 0.0069443 | houston | N | 0.0069443 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.039479 | houston | Y | -0.14192 | 0.12216 | -0.13563 | 0.0068503 | 0.0068503 | houston | N | 0.0068503 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.039505 | houston | Y | -0.14195 | 0.12213 | -0.13565 | 0.0068243 | 0.0068243 | houston | N | 0.0068243 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.039393 | houston | Y | -0.14184 | 0.12225 | -0.13554 | 0.0069363 | 0.0069363 | houston | N | 0.0069363 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.039368 | houston | Y | -0.14181 | 0.12227 | -0.13551 | 0.0069613 | 0.0069613 | houston | N | 0.0069613 | 0
48855 | SRB_GT21 | B2 | 12 | -0.039523 | houston | Y | -0.14197 | 0.12212 | -0.13567 | 0.0068063 | 0.0068063 | houston | N | 0.0068063 | 0
48855 | SRB_GT21 | MB | 18 | -0.039523 | houston | Y | -0.14197 | 0.12212 | -0.13567 | 0.0068063 | 0.0068063 | houston | N | 0.0068063 | 0
48865 | TECO_GT1 | 1 | 50 | -0.046071 | houston | Y | -0.14851 | 0.11557 | -0.14222 | 0.00025826 | 0.00025826 | houston | N | 0.00025826 | 0
48873 | THW_ST3_ | 3 | 104 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48874 | THW_ST4_ | 4 | 104 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48875 | THW_3132 | A | 54 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48875 | THW_3132 | B | 53 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48877 | THW_3334 | C | 54 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48877 | THW_3334 | D | 57 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48879 | THW_4142 | E | 54 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48879 | THW_4142 | F | 54 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48881 | THW_4344 | G | 58 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48881 | THW_4344 | H | 58 | -0.036766 | houston | Y | -0.13921 | 0.12487 | -0.13291 | 0.0095633 | 0.0095633 | houston | N | 0.0095633 | 0
48883 | THW_GT1_ | B2 | 12 | -0.035632 | houston | Y | -0.13807 | 0.12601 | -0.13178 | 0.010697 | 0.010697 | houston | N | 0.010697 | 0
48885 | THW_5152 | A | 56 | -0.033005 | houston | Y | -0.13545 | 0.12863 | -0.12915 | 0.013324 | 0.013324 | houston | N | 0.013324 | 0
48885 | THW_5152 | B | 59 | -0.033005 | houston | Y | -0.13545 | 0.12863 | -0.12915 | 0.013324 | 0.013324 | houston | N | 0.013324 | 0
48886 | THW_5354 | C | 56 | -0.033005 | houston | Y | -0.13545 | 0.12863 | -0.12915 | 0.013324 | 0.013324 | houston | N | 0.013324 | 0
48886 | THW_5354 | D | 56 | -0.033005 | houston | Y | -0.13545 | 0.12863 | -0.12915 | 0.013324 | 0.013324 | houston | N | 0.013324 | 0
48887 | THW_5556 | E | 59 | -0.033005 | houston | Y | -0.13545 | 0.12863 | -0.12915 | 0.013324 | 0.013324 | houston | N | 0.013324 | 0
48887 | THW_5556 | F | 56 | -0.033005 | houston | Y | -0.13545 | 0.12863 | -0.12915 | 0.013324 | 0.013324 | houston | N | 0.013324 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.083453 | houston | Y | -0.1859 | 0.078187 | -0.1796 | -0.037124 | 0.037124 | houston | N | 0.037124 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.053092 | houston | Y | -0.15553 | 0.10855 | -0.14924 | -0.0067627 | 0.0067627 | houston | N | 0.0067627 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.053092 | houston | Y | -0.15553 | 0.10855 | -0.14924 | -0.0067627 | 0.0067627 | houston | N | 0.0067627 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.053092 | houston | Y | -0.15553 | 0.10855 | -0.14924 | -0.0067627 | 0.0067627 | houston | N | 0.0067627 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.053092 | houston | Y | -0.15553 | 0.10855 | -0.14924 | -0.0067627 | 0.0067627 | houston | N | 0.0067627 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.053092 | houston | N | -0.15553 | 0.10855 | -0.14924 | -0.0067627 | 0.0067627 | houston | N | 0.0067627 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.054671 | houston | Y | -0.15711 | 0.10697 | -0.15082 | -0.0083417 | 0.0083417 | houston | N | 0.0083417 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.054671 | houston | Y | -0.15711 | 0.10697 | -0.15082 | -0.0083417 | 0.0083417 | houston | N | 0.0083417 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.054671 | houston | Y | -0.15711 | 0.10697 | -0.15082 | -0.0083417 | 0.0083417 | houston | N | 0.0083417 | 0
48929 | WAPGT21_ | B1 | 13 | -0.053092 | houston | Y | -0.15553 | 0.10855 | -0.14924 | -0.0067627 | 0.0067627 | houston | N | 0.0067627 | 0
48940 | WARVUE_G | G1 | 12 | -0.035108 | houston | Y | -0.13755 | 0.12653 | -0.13125 | 0.011221 | 0.011221 | houston | N | 0.011221 | 0
49803 | EXN_15GT | 1 | 34 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49826 | EXN938GT | 5 | 45.9 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49828 | EXN941GT | 10 | 17.7 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49829 | EXN942GT | 11 | 20.4 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49830 | EXN943GT | 12 | 19.9 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49831 | EXN944GT | 13 | 35 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49832 | EXN945GT | 9 | 18 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49837 | EXN_GT | 4 | 85.4 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49838 | EXN_14GT | 14 | 148 | -0.036007 | houston | N | -0.13845 | 0.12563 | -0.13215 | 0.010322 | 0.010322 | houston | N | 0.010322 | 0
49851 | DOW17000 | 37 | 62 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49858 | DOW38100 | 31 | 71.4 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49859 | DOW38200 | 33 | 45 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49860 | DOW38300 | 32 | 101 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49862 | DOW39100 | 36 | 86 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49863 | DOW39200 | 35 | 88 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49865 | DOW41000 | 41 | 50 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49866 | DOW42000 | 42 | 18 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49869 | DOW49000 | 45 | 94 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49870 | DOW61000 | 61 | 70 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49871 | DOW62000 | 62 | 63 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49872 | DOW63000 | 63 | 72 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49873 | DOW64000 | 64 | 64.8 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49876 | DOW65000 | 65 | 101 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49877 | DOW66000 | 66 | 97 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49878 | DOW67000 | 67 | 103 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49882 | DOW81000 | 81 | 76 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49884 | DOW82000 | 82 | 80 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49885 | DOW83000 | 83 | 80 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
49886 | DOW84000 | 84 | 171 | -0.070302 | houston | N | -0.17274 | 0.091338 | -0.16645 | -0.023973 | 0.023973 | houston | N | 0.023973 | 0
58909 | PEARSALL | 1 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58909 | PEARSALL | 2 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58909 | PEARSALL | 3 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58909 | PEARSALL | 4 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58909 | PEARSALL | 5 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58909 | PEARSALL | 6 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58919 | PEARSALL | 1 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58919 | PEARSALL | 2 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58919 | PEARSALL | 3 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58919 | PEARSALL | 4 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58919 | PEARSALL | 5 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58919 | PEARSALL | 6 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58929 | PEARSALL | 1 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58929 | PEARSALL | 2 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58929 | PEARSALL | 3 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58929 | PEARSALL | 4 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58929 | PEARSALL | 5 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58929 | PEARSALL | 6 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58949 | PEARSALL | 1 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58949 | PEARSALL | 2 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58949 | PEARSALL | 3 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58949 | PEARSALL | 4 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58949 | PEARSALL | 5 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
58949 | PEARSALL | 6 | 8.4 | -0.13813 | south | Y | -0.24058 | 0.023507 | -0.23428 | -0.091804 | 0.023507 | south | N | 0.023507 | 0
60000 | DSKY2 | 1 | 76.5 | 0.080199 | west | Y | -0.022243 | 0.24184 | -0.015947 | 0.12653 | 0.015947 | west | N | 0.015947 | 0
60003 | KING_NE1 | 1 | 80 | 0.084646 | west | Y | -0.017796 | 0.24629 | -0.0115 | 0.13098 | 0.0115 | west | N | 0.0115 | 0
60005 | KING_SE1 | 1 | 40 | 0.084646 | west | Y | -0.017796 | 0.24629 | -0.0115 | 0.13098 | 0.0115 | west | N | 0.0115 | 0
60007 | KING_SW1 | 1 | 80 | 0.085365 | west | Y | -0.017077 | 0.247 | -0.010781 | 0.13169 | 0.010781 | west | N | 0.010781 | 0
60016 | WOODWRD1 | 1 | 80 | 0.084489 | west | Y | -0.017953 | 0.24613 | -0.011657 | 0.13082 | 0.011657 | west | N | 0.011657 | 0
60017 | ORNNWP1 | 1 | 80 | 0.080791 | west | Y | -0.021651 | 0.24243 | -0.015355 | 0.12712 | 0.015355 | west | N | 0.015355 | 0
60018 | DSKY1 | 1 | 84 | 0.07958 | west | Y | -0.022862 | 0.24122 | -0.016566 | 0.12591 | 0.016566 | west | N | 0.016566 | 0
60019 | KING_NW1 | 1 | 80 | 0.085365 | west | Y | -0.017077 | 0.247 | -0.010781 | 0.13169 | 0.010781 | west | N | 0.010781 | 0
60057 | CALLAHAN | 1 | 114 | -0.15893 | south | Y | -0.26138 | 0.0027049 | -0.25508 | -0.11261 | 0.0027049 | south | N | 0.0027049 | 0
60058 | BUFF_GAP | 1 | 120 | 0.097591 | west | Y | -0.0048511 | 0.25923 | 0.0014448 | 0.14392 | 0.0014448 | west | N | 0.0014448 | 0
60060 | CIRELLO | 1 | 233 | 0.097591 | west | Y | -0.0048511 | 0.25923 | 0.0014448 | 0.14392 | 0.0014448 | west | N | 0.0014448 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.097591 | west | Y | -0.0048511 | 0.25923 | 0.0014448 | 0.14392 | 0.0014448 | west | N | 0.0014448 | 0
60066 | H_HOLLOW | 1 | 222 | -0.15893 | south | Y | -0.26138 | 0.0027049 | -0.25508 | -0.11261 | 0.0027049 | south | N | 0.0027049 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.15893 | south | Y | -0.26138 | 0.0027049 | -0.25508 | -0.11261 | 0.0027049 | south | N | 0.0027049 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.15893 | south | Y | -0.26138 | 0.0027049 | -0.25508 | -0.11261 | 0.0027049 | south | N | 0.0027049 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.15893 | south | Y | -0.26138 | 0.0027049 | -0.25508 | -0.11261 | 0.0027049 | south | N | 0.0027049 | 0
60074 | HORSH5 | 1 | 100 | -0.15893 | south | Y | -0.26138 | 0.0027049 | -0.25508 | -0.11261 | 0.0027049 | south | N | 0.0027049 | 0
60081 | WHRLWIND | 1 | 60 | 0.10082 | west | Y | -0.0016221 | 0.26246 | 0.0046738 | 0.14715 | 0.0016221 | North | Y | 0.0046738 | 0.1831
60201 | RIO DRCS | F | 0 | -0.056233 | south | N | -0.15868 | 0.10541 | -0.15238 | -0.0099037 | 0.0099037 | houston | Y | 0.10541 | 0
60202 | FRIEND_R | F | 0 | 0.060277 | west | N | -0.042165 | 0.22192 | -0.035869 | 0.10661 | 0.035869 | west | N | 0.035869 | 0
60203 | PRES0A | BT | 4.8 | 0.088016 | west | N | -0.014426 | 0.24966 | -0.0081302 | 0.13435 | 0.0081302 | west | N | 0.0081302 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.099123 | west | Y | -0.0033191 | 0.26076 | 0.0029768 | 0.14545 | 0.0029768 | west | N | 0.0029768 | 0
71054 | L_SWEETW | W1 | 107.5 | 0.099123 | west | Y | -0.0033191 | 0.26076 | 0.0029768 | 0.14545 | 0.0029768 | west | N | 0.0029768 | 0
71057 | L_SWEETW | W1 | 135 | 0.099123 | west | Y | -0.0033191 | 0.26076 | 0.0029768 | 0.14545 | 0.0029768 | west | N | 0.0029768 | 0
71059 | L_SWEETW | W1 | 119 | 0.099123 | west | Y | -0.0033191 | 0.26076 | 0.0029768 | 0.14545 | 0.0029768 | west | N | 0.0029768 | 0
71060 | L_SWEETW | W1 | 105 | 0.099123 | west | Y | -0.0033191 | 0.26076 | 0.0029768 | 0.14545 | 0.0029768 | west | N | 0.0029768 | 0
71061 | L_SWEETW | W1 | 80.5 | 0.099123 | west | Y | -0.0033191 | 0.26076 | 0.0029768 | 0.14545 | 0.0029768 | west | N | 0.0029768 | 0
76031 | L_GASCCR | W1 | 150 | 0.096448 | west | Y | -0.0059941 | 0.25809 | 0.0003018 | 0.14278 | 0.0003018 | west | N | 0.0003018 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.096123 | west | Y | -0.0063191 | 0.25776 | -2.3198e-05 | 0.14245 | 2.3198e-05 | west | N | 2.3198e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.096123 | west | Y | -0.0063191 | 0.25776 | -2.3198e-05 | 0.14245 | 2.3198e-05 | west | N | 2.3198e-05 | 0
76096 | L_CAPRSI | W1 | 186 | 0.096123 | west | Y | -0.0063191 | 0.25776 | -2.3198e-05 | 0.14245 | 2.3198e-05 | west | N | 2.3198e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.096123 | west | Y | -0.0063191 | 0.25776 | -2.3198e-05 | 0.14245 | 2.3198e-05 | west | N | 2.3198e-05 | 0
80003 | MILHWYS | F | 0 | -0.13334 | south | N | -0.23578 | 0.028305 | -0.22948 | -0.087006 | 0.028305 | south | N | 0.028305 | 0
80010 | EPLVT1 | F | 0 | -0.10136 | south | N | -0.20381 | 0.060276 | -0.19751 | -0.055035 | 0.055035 | houston | Y | 0.060276 | 0
80012 | LAR | F | 0 | -0.13949 | south | N | -0.24193 | 0.022153 | -0.23563 | -0.093158 | 0.022153 | south | N | 0.022153 | 0
80051 | FORPVCM0 | 8 | 28 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
80053 | FOR69CG0 | 10 | 74 | -0.12233 | south | N | -0.22477 | 0.039315 | -0.21847 | -0.075996 | 0.039315 | south | N | 0.039315 | 0
80080 | GWINDT11 | 1 | 94 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80080 | GWINDT11 | 2 | 41 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80080 | GWINDT11 | 3 | 38 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80080 | GWINDT11 | 4 | 19 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80081 | GWINDT21 | 1 | 94 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80081 | GWINDT21 | 2 | 36 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80081 | GWINDT21 | 3 | 43 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80081 | GWINDT21 | 4 | 22 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80137 | CSDR89 | 8 | 39 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
80137 | CSDR89 | 9 | 15 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
80138 | CSDR7 | 7 | 7 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
80139 | CSDR56 | 5 | 15 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
80139 | CSDR56 | 6 | 39 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
80140 | CSDR11 | 11 | 39 | -0.12633 | south | N | -0.22877 | 0.035311 | -0.22248 | -0.08 | 0.035311 | south | N | 0.035311 | 0
80180 | PNSCALT1 | 1 | 148 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80180 | PNSCALT1 | 2 | 50 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80181 | PNSCALT2 | 1 | 55 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80181 | PNSCALT2 | 2 | 50 | -0.13326 | south | Y | -0.2357 | 0.028382 | -0.2294 | -0.086929 | 0.028382 | south | N | 0.028382 | 0
80223 | REYSHR G | 1 | 12 | -0.13081 | south | N | -0.23326 | 0.030825 | -0.22696 | -0.084486 | 0.030825 | south | N | 0.030825 | 0
80224 | VISTRONG | 1 | 15 | -0.12758 | south | N | -0.23002 | 0.034061 | -0.22373 | -0.08125 | 0.034061 | south | N | 0.034061 | 0
80225 | VISTRONG | 2 | 23 | -0.12758 | south | N | -0.23002 | 0.034061 | -0.22373 | -0.08125 | 0.034061 | south | N | 0.034061 | 0
80226 | ALCOA G | 1 | 48 | -0.12326 | south | N | -0.2257 | 0.038379 | -0.21941 | -0.076932 | 0.038379 | south | N | 0.038379 | 0
80227 | AIRCO G | 1 | 8 | -0.1268 | south | N | -0.22924 | 0.034844 | -0.22294 | -0.080467 | 0.034844 | south | N | 0.034844 | 0
80261 | NBEC81A | 1 | 180 | -0.13208 | south | Y | -0.23452 | 0.029561 | -0.22823 | -0.08575 | 0.029561 | south | N | 0.029561 | 0
80262 | NBEC91A | 1 | 180 | -0.13204 | south | Y | -0.23448 | 0.029598 | -0.22819 | -0.085713 | 0.029598 | south | N | 0.029598 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.13232 | south | Y | -0.23476 | 0.029323 | -0.22846 | -0.085988 | 0.029323 | south | N | 0.029323 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.13232 | south | Y | -0.23476 | 0.029323 | -0.22846 | -0.085988 | 0.029323 | south | N | 0.029323 | 0
80265 | LARECU40 | 4 | 100 | -0.1395 | south | Y | -0.24194 | 0.022141 | -0.23565 | -0.09317 | 0.022141 | south | N | 0.022141 | 0
80266 | LARECU50 | 5 | 100 | -0.1395 | south | Y | -0.24194 | 0.022141 | -0.23565 | -0.09317 | 0.022141 | south | N | 0.022141 | 0
80291 | PAPALOTE | 1 | 25 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
80291 | PAPALOTE | 2 | 25 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
80291 | PAPALOTE | 3 | 25 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
80291 | PAPALOTE | 4 | 16 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
80294 | PAPALOTE | 5 | 25 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
80294 | PAPALOTE | 6 | 25 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
80294 | PAPALOTE | 7 | 25 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
80294 | PAPALOTE | 8 | 15 | -0.13131 | south | Y | -0.23375 | 0.030335 | -0.22745 | -0.084976 | 0.030335 | south | N | 0.030335 | 0
86104 | CID-138 | EQ | 0 | -0.1395 | south | N | -0.24194 | 0.022141 | -0.23565 | -0.09317 | 0.022141 | south | N | 0.022141 | 0
86105 | CID-230 | EQ | 500 | -0.1395 | south | N | -0.24194 | 0.022141 | -0.23565 | -0.09317 | 0.022141 | south | N | 0.022141 | 0
86106 | CUF-230 | EQ | 500 | -0.1395 | south | N | -0.24194 | 0.022141 | -0.23565 | -0.09317 | 0.022141 | south | N | 0.022141 | 0
86107 | CUF-138 | EQ | 0 | -0.1395 | south | N | -0.24194 | 0.022141 | -0.23565 | -0.09317 | 0.022141 | south | N | 0.022141 | 0
88198 | BEEVILLE | F | 0 | -0.13827 | south | N | -0.24071 | 0.023373 | -0.23441 | -0.091938 | 0.023373 | south | N | 0.023373 | 0
88253 | HAMILTON | F | 0 | -0.077419 | south | N | -0.17986 | 0.084221 | -0.17357 | -0.03109 | 0.03109 | houston | Y | 0.084221 | 0
88299 | ZAPATA | F | 0 | -0.1364 | south | N | -0.23884 | 0.025238 | -0.23255 | -0.090073 | 0.025238 | south | N | 0.025238 | 0
88508 | FALFURRI | F | 0 | -0.13526 | south | N | -0.2377 | 0.026382 | -0.2314 | -0.088929 | 0.026382 | south | N | 0.026382 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: 3414 TEMP_SS_ to 3429 SANDOW_ C: 3413 TEMP_SS_ to 3429 SANDOW_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.17333 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32778 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.17333 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 136.4115 | 787 | 0.32778 | 257.9654 | 787 | 257.9654
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.16854 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.323 | 0 | 787 | 257.9654
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.16854 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.323 | 0 | 787 | 257.9654 | Weighted Shift Factors
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.16343 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.6757 | 255 | 0.31789 | 81.061 | 1042 | 339.0264 | North | 0.10244
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.16343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.3517 | 149 | 0.31789 | 47.365 | 1191 | 386.3914 | South | -0.15445
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.16343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 25.0054 | 153 | 0.31789 | 48.6366 | 1344 | 435.028 |  | 0.25689
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.15589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3839 | 150 | 0.31035 | 46.5518 | 1494 | 481.5798
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.15589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.4714 | 80 | 0.31035 | 24.8276 | 1574 | 506.4074 | Line Rating | 1072
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.148 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.2199 | 0 | 0.30245 | 0 | 1574 | 506.4074 | Conc Gen | 2056
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.148 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.2199 | 0 | 0.30245 | 0 | 1574 | 506.4074 | Weighted Imp. | 637.3758
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11771 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7758 | 168 | 0.27217 | 45.7238 | 1742 | 552.1312 | PTDF | 0.31001
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11771 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.5942 | 90 | 0.27217 | 24.4949 | 1832 | 576.626
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.1524 | 224 | 0.2712 | 60.7497 | 2056 | 637.3758 | Concentration | 1.2068
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.386 | 226 | 0.2712 | 61.2922
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.7514 | 212 | 0.2712 | 57.4953
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.6347 | 211 | 0.2712 | 57.2241
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.11617 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.1385 | 216.4 | 0.27062 | 58.562
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.11617 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.1037 | 216.1 | 0.27062 | 58.4808
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.9933 | 70 | 0.26864 | 18.805
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8791 | 69 | 0.26864 | 18.5363
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8791 | 69 | 0.26864 | 18.5363
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7649 | 68 | 0.26864 | 18.2677
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11276 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.2313 | 73 | 0.26721 | 19.5063
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11276 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.4181 | 119 | 0.26721 | 31.7979
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11276 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.1152 | 205 | 0.26721 | 54.7779
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11276 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.5012 | 102 | 0.26721 | 27.2553
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11276 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.8247 | 96 | 0.26721 | 25.6521
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11225 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 44.3372 | 395 | 0.2667 | 105.3458
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11225 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.827 | 435 | 0.2667 | 116.0137
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.1122 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26665 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11202 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.7265 | 435 | 0.26647 | 115.9132
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.11197 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.7184 | 60 | 0.26643 | 15.9855
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3224 | 217.3 | 0.26638 | 57.8849
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9457 | 205 | 0.26638 | 54.6084
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.4897 | 272.4 | 0.26638 | 72.5625
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11172 | north | 3 | N | N | Nnorth | Nnorth | 1 | 129.2589 | 0 | 0.26617 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11172 | north | 3 | N | N | Nnorth | Nnorth | 1 | 129.3706 | 0 | 0.26617 | 0
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0059 | 18 | 0.26589 | 4.7861
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0059 | 18 | 0.26589 | 4.7861
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.2348 | 38 | 0.26589 | 10.1039
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7005 | 196 | 0.26517 | 51.9732
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2896 | 111 | 0.26517 | 29.4338
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.1105 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26495 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.1105 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26495 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.1105 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26495 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.7422 | 288 | 0.26467 | 76.2244
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2018 | 147 | 0.26467 | 38.9062
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2018 | 147 | 0.26467 | 38.9062
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.10918 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3101 | 0 | 0.26363 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.10918 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3101 | 0 | 0.26363 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.10917 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.1005 | 120 | 0.26362 | 31.6348
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.10892 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 12.2534 | 112.5 | 0.26337 | 29.6293
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.10878 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.527 | 60 | 0.26324 | 15.7941
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.10878 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.8533 | 63 | 0.26324 | 16.5838
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.10877 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.8353 | 118 | 0.26323 | 31.0607
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.10877 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.509 | 115 | 0.26323 | 30.271
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.10877 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.4783 | 556 | 0.26323 | 146.3538
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1107 | 204 | 0.26284 | 53.619
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7856 | 201 | 0.26284 | 52.8305
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.2294 | 242 | 0.26284 | 63.6068
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.1079 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26235 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.10787 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26232 | 0
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.10732 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2929 | 0 | 0.26177 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.10732 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2929 | 0 | 0.26177 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.10719 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 18.222 | 170 | 0.26164 | 44.4788
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.10719 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 55.7378 | 520 | 0.26164 | 136.0529
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.1071 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26155 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.1071 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26155 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.10703 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 39.6022 | 370 | 0.26149 | 96.7495
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.9846 | 0 | 0.26149 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.0917 | 0 | 0.26149 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 33.0732 | 0 | 0.26149 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.3057 | 0 | 0.26149 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.4128 | 0 | 0.26149 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 33.1802 | 0 | 0.26149 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1106 | 160 | 0.26139 | 41.8229
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6828 | 156 | 0.26139 | 40.7773
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9604 | 196 | 0.26139 | 51.2331
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6828 | 156 | 0.26139 | 40.7773
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7897 | 157 | 0.26139 | 41.0387
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.1743 | 198 | 0.26139 | 51.7559
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | 1 | 8.0143 | 0 | 0.26131 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | 1 | 8.5058 | 0 | 0.26131 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.4462 | 0 | 0.26131 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.10684 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.2738 | 40 | 0.2613 | 10.4518
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4378 | 79 | 0.26126 | 20.6395
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.3215 | 106 | 0.26126 | 27.6935
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.5938 | 146 | 0.26126 | 38.1438
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.10681 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.1173 | 76 | 0.26126 | 19.8557
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 59.5888 | 558 | 0.26124 | 145.7732
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.8314 | 579 | 0.26124 | 151.2592
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 86.2863 | 808 | 0.26124 | 211.0837
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.10669 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 41.3957 | 388 | 0.26114 | 101.3232
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.10669 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.9453 | 515 | 0.26114 | 134.4882
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.666 | 25 | 0.26109 | 6.5274
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3723 | 41 | 0.26109 | 10.7049
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1328 | 20 | 0.26109 | 5.2219
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.10657 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.7895 | 242 | 0.26102 | 63.1669
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1285 | 20 | 0.26088 | 5.2176
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1285 | 20 | 0.26088 | 5.2176
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1285 | 20 | 0.26088 | 5.2176
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.8093 | 17 | 0.26088 | 4.4349
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.10627 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.8047 | 224 | 0.26072 | 58.402
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.10622 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 38.8754 | 366 | 0.26067 | 95.4049
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0145 | 161 | 0.26013 | 41.8813
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.3315 | 164 | 0.26013 | 42.6617
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.3315 | 164 | 0.26013 | 42.6617
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.7515 | 414 | 0.26013 | 107.6947
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1202 | 162 | 0.26013 | 42.1414
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0145 | 161 | 0.26013 | 41.8813
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.2258 | 163 | 0.26013 | 42.4016
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.2231 | 409 | 0.26013 | 106.3941
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.10394 | west | 4 | Y | N | Ywest | Nwest | 1 | 67.5331 | 649.7 | 0.2584 | 167.8807
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.10315 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.0193 | 165 | 0.2576 | 42.5039
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.10218 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.114 | 236 | 0.25663 | 60.5647
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10217 | west | 6 | Y | N | Ywest | Nwest | 1 | 40.8692 | 400 | 0.25663 | 102.6501
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.6265 | 785 | 0.25589 | 200.8715
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.6408 | 795 | 0.25589 | 203.4303
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.1193 | 780 | 0.25589 | 199.592
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.9292 | 0 | 0.25533 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.1135 | 0 | 0.25533 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.6266 | 0 | 0.25533 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 40.2483 | 0 | 0.25533 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10082 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0492 | 60 | 0.25527 | 15.3163
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.10021 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.25466 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.10015 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 5.0077 | 50 | 0.25461 | 12.7304
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.099735 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.1518 | 182 | 0.25419 | 46.2621
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.099735 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.2717 | 484 | 0.25419 | 123.0266
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.099541 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.9312 | 150 | 0.25399 | 38.099
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.7272 | 209 | 0.25363 | 53.0077
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5454 | 126.5 | 0.25363 | 32.0836
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6941 | 249 | 0.25363 | 63.1527
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.5371 | 197 | 0.25363 | 49.9642
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7171 | 37.5 | 0.25358 | 9.5091
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6557 | 107.5 | 0.25358 | 27.2593
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3816 | 135 | 0.25358 | 34.2327
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7956 | 119 | 0.25358 | 30.1755
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.4079 | 105 | 0.25358 | 26.6254
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9794 | 80.5 | 0.25358 | 20.4128
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.098858 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8287 | 150 | 0.25331 | 37.9965
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.098858 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9847 | 101 | 0.25331 | 25.5843
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098595 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3244 | 125 | 0.25305 | 31.6309
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098595 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3244 | 125 | 0.25305 | 31.6309
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.098431 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2682 | 84 | 0.25288 | 21.2422
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.098178 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.7196 | 99 | 0.25263 | 25.0104
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.098178 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9889 | 61 | 0.25263 | 15.4104
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4545 | 0 | 0.25263 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4867 | 0 | 0.25263 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4867 | 0 | 0.25263 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.09815 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8392 | 141 | 0.2526 | 35.6169
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.09815 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.778 | 120 | 0.2526 | 30.3123
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.098078 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1789 | 63 | 0.25253 | 15.9094
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.4661 | 66 | 0.25242 | 16.6599
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.76 | 69 | 0.25242 | 17.4172
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.76 | 69 | 0.25242 | 17.4172
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5641 | 67 | 0.25242 | 16.9124
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5641 | 67 | 0.25242 | 16.9124
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3681 | 65 | 0.25242 | 16.4075
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6567 | 150 | 0.25216 | 37.8245
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.4964 | 220 | 0.25216 | 55.4759
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.5422 | 200 | 0.25216 | 50.4326
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.911 | 121.9 | 0.25216 | 30.7387
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7109 | 120 | 0.25204 | 30.2452
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7387 | 233 | 0.25204 | 58.7261
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.61 | 170.2 | 0.25204 | 42.8978
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097487 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5477 | 180 | 0.25194 | 45.3491
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097487 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5477 | 180 | 0.25194 | 45.3491
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 1 | 6.8202 | 0 | 0.25188 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 1 | 7.1514 | 0 | 0.25188 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 1 | 6.8591 | 0 | 0.25188 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.097394 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.9137 | 225 | 0.25185 | 56.6654
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.09723 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6676 | 120 | 0.25168 | 30.2019
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.097188 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6626 | 120 | 0.25164 | 30.1968
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.096671 | west | 8 | N | N | Nwest | Nwest | 1 | 2.4941 | 0 | 0.25112 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.096507 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6718 | 214.2 | 0.25096 | 53.7555
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.096448 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.4672 | 150 | 0.2509 | 37.635
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.0963 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6782 | 100.5 | 0.25075 | 25.2006
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.096269 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5836 | 58 | 0.25072 | 14.5418
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7332 | 70 | 0.25064 | 17.5449
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7332 | 70 | 0.25064 | 17.5449
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.9263 | 92.8 | 0.25064 | 23.2595
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.6951 | 80 | 0.25064 | 20.0513
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.6951 | 80 | 0.25064 | 20.0513
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0617 | 115 | 0.25064 | 28.8237
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.023 | 208.2 | 0.25062 | 52.18
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.666 | 142.1 | 0.25062 | 35.6137
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.7332 | 132.4 | 0.25062 | 33.1826
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.0794 | 136 | 0.25062 | 34.0849
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.1373 | 147 | 0.25062 | 36.8418
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.1961 | 210 | 0.25062 | 52.6311
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8138 | 112.5 | 0.25058 | 28.1897
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3704 | 149.5 | 0.25058 | 37.461
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8789 | 186 | 0.25058 | 46.607
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6184 | 214.5 | 0.25058 | 53.7484
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.095512 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.63038 | 6.6 | 0.24996 | 1.6498
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.095512 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2761 | 34.3 | 0.24996 | 8.5738
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.094962 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0961 | 169.5 | 0.24941 | 42.2757
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.094826 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1291 | 149 | 0.24928 | 37.1425
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.094523 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3083 | 35 | 0.24898 | 8.7141
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.094523 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8357 | 30 | 0.24898 | 7.4693
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3128 | 151.5 | 0.24893 | 37.7123
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3884 | 152.3 | 0.24893 | 37.9115
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7691 | 177.5 | 0.24893 | 44.1844
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.2326 | 66 | 0.24889 | 16.4265
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.1382 | 65 | 0.24889 | 16.1776
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3271 | 67 | 0.24889 | 16.6754
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3271 | 67 | 0.24889 | 16.6754
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3271 | 67 | 0.24889 | 16.6754
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.094434 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.24889 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.094434 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.24889 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1979 | 150.7 | 0.24867 | 37.4738
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.2262 | 151 | 0.24867 | 37.5484
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7134 | 177.4 | 0.24867 | 44.1132
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.09279 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.0658 | 615 | 0.24724 | 152.054
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.09279 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 54.4677 | 587 | 0.24724 | 145.1312
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.088016 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.42248 | 0 | 0.24247 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085365 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8292 | 80 | 0.23982 | 19.1854
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085365 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8292 | 80 | 0.23982 | 19.1854
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3484 | 75 | 0.2391 | 17.9324
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7717 | 80 | 0.2391 | 19.1279
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3858 | 40 | 0.2391 | 9.5639
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084489 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7591 | 80 | 0.23894 | 19.1153
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.084468 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7574 | 80 | 0.23892 | 19.1136
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.084378 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6567 | 150 | 0.23883 | 35.8245
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.084378 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6567 | 150 | 0.23883 | 35.8245
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.080791 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4633 | 80 | 0.23524 | 18.8195
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.080199 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1352 | 76.5 | 0.23465 | 17.9508
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.07958 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6847 | 84 | 0.23403 | 19.6587
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.074111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.2898 | 827 | 0.22856 | 189.0218
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.074111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 60.6969 | 819 | 0.22856 | 187.1933
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 52.0438 | 855 | 0.21532 | 184.1005
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 52.0438 | 855 | 0.21532 | 184.1005
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.2705 | 152.3 | 0.21532 | 32.7936
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.3131 | 153 | 0.21532 | 32.9443
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.060277 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.21473 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.045049 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7573 | 150 | 0.1995 | 29.9252
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.029588 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.6992 | 463 | 0.18404 | 85.2106
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.023763 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.40397 | 17 | 0.17822 | 3.0297
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.023675 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.7576 | 0 | 0.17813 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.020826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.99965 | 48 | 0.17528 | 8.4134
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.020826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.958 | 46 | 0.17528 | 8.0628
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.020826 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1867 | 105 | 0.17528 | 18.4042
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.148 | 0 | 0.17487 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1847 | 0 | 0.17487 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1847 | 0 | 0.17487 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.7577 | 0 | 0.17487 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.15445 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.15445 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.056233 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.098219 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -15.8935 | 100 | -0.0044828 | -0.44828
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10244 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10244 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8196 | 0 | -0.1303 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.346 | 0 | -0.1303 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2903 | 0 | -0.1303 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2903 | 0 | -0.1303 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.027859 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5132 | 0 | -0.1303 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9473 | 59 | -0.13545 | -7.9914
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9473 | 59 | -0.13545 | -7.9914
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.033529 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.3445 | 398 | -0.13597 | -54.1165
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5075 | 0 | -0.13627 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4602 | 0 | -0.13627 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3756 | 0 | -0.13627 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.107 | 0 | -0.13627 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9687 | 172 | -0.13714 | -23.5888
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9687 | 172 | -0.13714 | -23.5888
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9687 | 172 | -0.13714 | -23.5888
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.034849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.4713 | 0 | -0.13729 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.035074 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.06 | 743 | -0.13752 | -102.1745
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.035108 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.4213 | 12 | -0.13755 | -1.6506
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2835 | 0 | -0.13757 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3186 | 0 | -0.13757 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4592 | 0 | -0.13757 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2133 | 0 | -0.13757 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1781 | 0 | -0.13757 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6536 | 0 | -0.13757 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0727 | 0 | -0.13757 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.035139 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17569 | 0 | -0.13758 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.035139 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73792 | 0 | -0.13758 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.035632 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42758 | 12 | -0.13807 | -1.6569
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2242 | 0 | -0.13845 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2494 | 0 | -0.13845 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1774 | 0 | -0.13845 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6527 | 0 | -0.13845 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63732 | 0 | -0.13845 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73454 | 0 | -0.13845 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71654 | 0 | -0.13845 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2602 | 0 | -0.13845 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64813 | 0 | -0.13845 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.075 | 0 | -0.13845 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.329 | 0 | -0.13845 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.036306 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.6849 | 735 | -0.13875 | -101.9799
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.8237 | 104 | -0.13921 | -14.4776
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.8237 | 104 | -0.13921 | -14.4776
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9486 | 53 | -0.13921 | -7.378
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0957 | 57 | -0.13921 | -7.9349
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1324 | 58 | -0.13921 | -8.0741
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1324 | 58 | -0.13921 | -8.0741
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.037928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5615 | 0 | -0.14037 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.037928 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1203 | 0 | -0.14037 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6007 | 42 | -0.14055 | -5.9033
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6007 | 42 | -0.14055 | -5.9033
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4483 | 38 | -0.14055 | -5.3411
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4483 | 38 | -0.14055 | -5.3411
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.038173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1915 | 0 | -0.14062 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7618 | 0 | -0.14134 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8007 | 0 | -0.14134 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.517 | 0 | -0.14134 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1669 | 0 | -0.14134 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0841 | 0 | -0.1418 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2419 | 0 | -0.1418 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1789 | 0 | -0.1418 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039368 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.9759 | 228 | -0.14181 | -32.3327
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5203 | 0 | -0.14182 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4888 | 0 | -0.14182 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2527 | 0 | -0.14182 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8983 | 0 | -0.14182 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039385 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63804 | 0 | -0.14183 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039393 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.3907 | 213 | -0.14184 | -30.2109
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.03946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8795 | 0 | -0.1419 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.03946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5688 | 0 | -0.1419 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039479 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.514 | 165 | -0.14192 | -23.417
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039505 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.6763 | 169 | -0.14195 | -23.9891
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039523 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47428 | 12 | -0.14197 | -1.7036
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039523 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14197 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3947 | 0 | -0.14229 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.553 | 0 | -0.1426 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.308 | 0 | -0.1426 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3241 | 0 | -0.1426 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.304 | 0 | -0.1426 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8012 | 0 | -0.1426 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.040526 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.161 | 0 | -0.14297 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.040526 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2421 | 0 | -0.14297 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8771 | 46 | -0.14325 | -6.5894
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8771 | 46 | -0.14325 | -6.5894
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8771 | 46 | -0.14325 | -6.5894
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2443 | 55 | -0.14325 | -7.8786
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2443 | 55 | -0.14325 | -7.8786
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2035 | 54 | -0.14325 | -7.7354
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7223 | 0 | -0.14432 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5129 | 0 | -0.14432 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7223 | 0 | -0.14432 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7223 | 0 | -0.14432 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8775 | 0 | -0.14505 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7326 | 0 | -0.14505 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7071 | 0 | -0.14505 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3222 | 0 | -0.14505 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51984 | 0 | -0.14505 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.044471 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14691 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.046071 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.3035 | 50 | -0.14851 | -7.4257
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4062 | 0 | -0.15055 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2089 | 0 | -0.15055 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5498 | 0 | -0.15055 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3705 | 0 | -0.15055 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3849 | 0 | -0.15055 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3272 | 0 | -0.15055 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.6186 | 0 | -0.15055 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.7388 | 0 | -0.15055 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9244 | 0 | -0.15055 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.048135 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5403 | 0 | -0.15058 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.048135 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4441 | 0 | -0.15058 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.828 | 0 | -0.15058 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.4718 | 0 | -0.15058 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9436 | 0 | -0.15058 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9099 | 0 | -0.15058 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.5478 | 161 | -0.15553 | -25.041
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.8133 | 166 | -0.15553 | -25.8187
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.1668 | 248 | -0.15553 | -38.5725
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.053092 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -28.9882 | 546 | -0.15553 | -84.9216
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.053092 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -34.1382 | 0 | -0.15553 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.053092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6902 | 13 | -0.15553 | -2.0219
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.053499 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7655 | 0 | -0.15594 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8983 | 0 | -0.15703 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8983 | 0 | -0.15703 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.3748 | 0 | -0.15703 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -35.5908 | 651 | -0.15711 | -102.2807
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -30.8344 | 564 | -0.15711 | -88.6118
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.8026 | 600 | -0.15711 | -94.2679
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.054906 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5312 | 0 | -0.15735 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.1349 | 0 | -0.16672 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.1349 | 0 | -0.16672 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.6491 | 0 | -0.16672 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0384 | 0 | -0.16672 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.066941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7528 | 0 | -0.16938 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.066941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66941 | 0 | -0.16938 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3587 | 0 | -0.17274 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0196 | 0 | -0.17274 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1636 | 0 | -0.17274 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1005 | 0 | -0.17274 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.046 | 0 | -0.17274 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1866 | 0 | -0.17274 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5151 | 0 | -0.17274 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2654 | 0 | -0.17274 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6084 | 0 | -0.17274 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9211 | 0 | -0.17274 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.429 | 0 | -0.17274 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0617 | 0 | -0.17274 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5556 | 0 | -0.17274 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1005 | 0 | -0.17274 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8193 | 0 | -0.17274 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2411 | 0 | -0.17274 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.343 | 0 | -0.17274 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6242 | 0 | -0.17274 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6242 | 0 | -0.17274 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.0216 | 0 | -0.17274 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.077419 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5548 | 0 | -0.17986 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.077419 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9355 | 0 | -0.17986 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.077419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17986 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4048 | 0 | -0.18049 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4048 | 0 | -0.18049 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1707 | 0 | -0.18049 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.083315 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1414 | 0 | -0.18576 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.083453 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5079 | 66 | -0.1859 | -12.2691
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6729 | 76 | -0.19024 | -14.4585
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6729 | 76 | -0.19024 | -14.4585
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2191 | 105 | -0.19024 | -19.9755
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4973 | 74 | -0.19024 | -14.078
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4973 | 74 | -0.19024 | -14.078
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.9557 | 102 | -0.19024 | -19.4048
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.088747 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.2998 | 0 | -0.19119 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.088747 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -117.856 | 0 | -0.19119 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.096846 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.58108 | 0 | -0.19929 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.10136 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20381 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.10224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8628 | 0 | -0.20469 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.10224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9651 | 0 | -0.20469 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.10246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -43.2398 | 422 | -0.20491 | -86.4704
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.11083 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.995 | 0 | -0.21328 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.11083 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.995 | 0 | -0.21328 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6637 | 0 | -0.22477 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.9083 | 0 | -0.22477 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6637 | 0 | -0.22477 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.786 | 0 | -0.22477 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.5903 | 0 | -0.22477 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0581 | 0 | -0.22477 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6269 | 0 | -0.22477 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4251 | 0 | -0.22477 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3334 | 0 | -0.22477 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.052 | 0 | -0.22477 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.12326 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9165 | 0 | -0.2257 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5372 | 0 | -0.22877 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8843 | 0 | -0.22877 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9268 | 0 | -0.22877 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8949 | 0 | -0.22877 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8843 | 0 | -0.22877 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8949 | 0 | -0.22877 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9268 | 0 | -0.22877 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9268 | 0 | -0.22877 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.1268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0144 | 0 | -0.22924 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.12758 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9137 | 0 | -0.23002 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.12758 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9343 | 0 | -0.23002 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.12867 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8308 | 22 | -0.23111 | -5.0845
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.12867 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4154 | 11 | -0.23111 | -2.5422
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.12867 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4154 | 11 | -0.23111 | -2.5422
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.185 | 47.7 | -0.23211 | -11.0715
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8365 | 37.3 | -0.23211 | -8.6576
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9645 | 46 | -0.23211 | -10.6769
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2239 | 48 | -0.23211 | -11.1411
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.12975 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.472 | 0 | -0.2322 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5435 | 0 | -0.23226 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.4136 | 0 | -0.23226 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5435 | 0 | -0.23226 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.6688 | 0 | -0.23326 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.0147 | 0 | -0.23326 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -13.0815 | 0 | -0.23326 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.9682 | 0 | -0.23326 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.2298 | 0 | -0.23326 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -16.6135 | 0 | -0.23326 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.13081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5698 | 0 | -0.23326 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.13101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -18.8656 | 144 | -0.23345 | -33.6173
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.13101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6301 | 188 | -0.23345 | -43.8892
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 25 | -0.23375 | -5.8437
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 25 | -0.23375 | -5.8437
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 25 | -0.23375 | -5.8437
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.1009 | 16 | -0.23375 | -3.74
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 25 | -0.23375 | -5.8437
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 25 | -0.23375 | -5.8437
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 25 | -0.23375 | -5.8437
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9696 | 15 | -0.23375 | -3.5062
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.3661 | 336 | -0.23448 | -78.7867
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7676 | 180 | -0.23448 | -42.2071
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.5839 | 0 | -0.2345 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.6235 | 0 | -0.2345 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.2046 | 0 | -0.2345 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13208 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7742 | 180 | -0.23452 | -42.2138
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.13232 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.1939 | 334 | -0.23476 | -78.4096
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.13232 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.9878 | 340 | -0.23476 | -79.8181
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.13232 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8171 | 180 | -0.23476 | -42.2566
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.13232 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8171 | 180 | -0.23476 | -42.2566
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.13234 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3086 | 0 | -0.23479 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.13234 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3086 | 0 | -0.23479 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.13246 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0337 | 0 | -0.23491 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.13247 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0339 | 0 | -0.23491 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.13306 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8588 | 0 | -0.2355 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5263 | 94 | -0.2357 | -22.1558
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4636 | 41 | -0.2357 | -9.6637
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.0638 | 38 | -0.2357 | -8.9566
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.5319 | 19 | -0.2357 | -4.4783
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5263 | 94 | -0.2357 | -22.1558
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7973 | 36 | -0.2357 | -8.4852
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7301 | 43 | -0.2357 | -10.1351
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9317 | 22 | -0.2357 | -5.1854
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.7222 | 148 | -0.2357 | -34.8836
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.6629 | 50 | -0.2357 | -11.785
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.3292 | 55 | -0.2357 | -12.9635
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.6629 | 50 | -0.2357 | -11.785
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0667 | 38 | -0.23578 | -8.9595
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.5733 | 19.3 | -0.23578 | -4.5505
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2 | 15 | -0.23578 | -3.5366
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.13333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.2667 | 47 | -0.23578 | -11.0815
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.13334 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.23578 | 0
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.2318 | 144 | -0.236 | -33.9834
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.2318 | 144 | -0.236 | -33.9834
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.8377 | 171 | -0.236 | -40.3553
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6463 | 207 | -0.236 | -48.8518
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.9418 | 216.7 | -0.236 | -51.141
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.3208 | 242 | -0.236 | -57.1118
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.5976 | 146.5 | -0.23621 | -34.6054
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.7849 | 147.9 | -0.23621 | -34.9361
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.1426 | 173 | -0.23621 | -40.865
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6214 | 0 | -0.23756 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4863 | 0 | -0.23756 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6214 | 0 | -0.23756 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.13526 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2377 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.1364 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.23884 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.13688 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -86.1 | 629 | -0.23933 | -150.5361
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.13827 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24071 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.13949 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24193 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.1395 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9499 | 100 | -0.24194 | -24.1941
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.1395 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9499 | 100 | -0.24194 | -24.1941
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3534 | 24 | -0.24217 | -5.812
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13972 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.3534 | 24 | -0.24217 | -5.812
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.13972 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.2137 | 23 | -0.24217 | -5.5698
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.14741 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1793 | 0 | -0.24985 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.14741 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1793 | 0 | -0.24985 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.14872 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -58.8939 | 396 | -0.25116 | -99.461
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15173 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8208 | 0 | -0.25417 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.15464 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.9381 | 310 | -0.25708 | -79.6952
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.15464 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.8659 | 413 | -0.25708 | -106.1745
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.15546 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.0168 | 58 | -0.2579 | -14.9584
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.15546 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.8361 | 89 | -0.2579 | -22.9535
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8403 | 44 | -0.2579 | -11.3478
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8403 | 44 | -0.2579 | -11.3478
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6849 | 43 | -0.2579 | -11.0899
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9958 | 45 | -0.2579 | -11.6057
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.15602 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.1853 | 546 | -0.25846 | -141.1187
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.15602 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -117.0127 | 750 | -0.25846 | -193.8444
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.15643 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.6674 | 407 | -0.25887 | -105.3614
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2474 | 155 | -0.25888 | -40.126
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.5939 | 170 | -0.25888 | -44.0091
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2474 | 155 | -0.25888 | -40.126
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.15648 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -32.7043 | 209 | -0.25892 | -54.1147
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.15648 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -33.7997 | 216 | -0.25892 | -55.9272
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1981 | 46 | -0.25892 | -11.9104
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3546 | 47 | -0.25892 | -12.1693
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1981 | 46 | -0.25892 | -11.9104
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1981 | 46 | -0.25892 | -11.9104
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.15666 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -64.5443 | 412 | -0.2591 | -106.7505
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.15666 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -62.6644 | 400 | -0.2591 | -103.6413
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.15688 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.518 | 424 | -0.25932 | -109.9534
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.15688 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.6749 | 425 | -0.25932 | -110.2128
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25996 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25996 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25996 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6163 | 42 | -0.25997 | -10.9189
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9314 | 44 | -0.25997 | -11.4389
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9314 | 44 | -0.25997 | -11.4389
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.404 | 47 | -0.25997 | -12.2188
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.1186 | 114 | -0.26138 | -29.797
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.2836 | 222 | -0.26138 | -58.0257
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -29.244 | 184 | -0.26138 | -48.0934
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.6014 | 224 | -0.26138 | -58.5485
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.2775 | 115 | -0.26138 | -30.0584
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8303 | 49 | -0.26224 | -12.85
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3509 | 46 | -0.26224 | -12.0632
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3509 | 46 | -0.26224 | -12.0632
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.5107 | 47 | -0.26224 | -12.3255
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.1598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6095 | 154 | -0.26224 | -40.3856
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.1598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.6507 | 148 | -0.26224 | -38.8121
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6705 | 48 | -0.26224 | -12.5877
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6705 | 48 | -0.26224 | -12.5877
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.15996 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38392 | 0 | -0.26241 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.15996 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38392 | 0 | -0.26241 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8599 | 147 | -0.26475 | -38.9189
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3991 | 138 | -0.26475 | -36.5361
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.7237 | 140 | -0.26475 | -37.0656
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8599 | 147 | -0.26475 | -38.9189
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.5408 | 182 | -0.26475 | -48.1853
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.1378 | 198 | -0.26475 | -52.4213
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.16351 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65403 | 0 | -0.26595 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39383 | 0 | -0.26654 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39383 | 0 | -0.26654 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45947 | 0 | -0.26654 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.16503 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.99016 | 0 | -0.26747 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.1776 | 132 | -0.27045 | -35.6999
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.5136 | 134 | -0.27045 | -36.2409
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -54.2679 | 323 | -0.27045 | -87.3567
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.9171 | 142 | -0.27087 | -38.4638
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.4224 | 145 | -0.27087 | -39.2765
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.4329 | 151 | -0.27087 | -40.9017
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.8447 | 290 | -0.27087 | -78.5529
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.2185 | 223.9 | -0.2776 | -62.1553
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.4112 | 225 | -0.2776 | -62.4607
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.3412 | 224.6 | -0.2776 | -62.3497
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.709 | 226.7 | -0.2776 | -62.9326
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.18624 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -80.6402 | 433 | -0.28868 | -124.9976
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.18647 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -108.8991 | 584 | -0.28891 | -168.7253
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.18647 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -110.9502 | 595 | -0.28891 | -171.9033
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.118 | 152.5 | -0.31305 | -47.7405
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.4862 | 149.5 | -0.31305 | -46.8013
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.9879 | 232.6 | -0.31305 | -72.8159
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.2849 | 158 | -0.31944 | -50.4708
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.7189 | 160 | -0.31944 | -51.1096
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.9738 | 175 | -0.31944 | -55.9011
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.26261 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -149.424 | 569 | -0.36505 | -207.7135
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.26261 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -152.5752 | 581 | -0.36505 | -212.0941

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: 3414 TEMP_SS_ to 3429 SANDOW_ C: 3413 TEMP_SS_ to 3429 SANDOW_ | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.26261 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -149.424 | 0 | -0.36505 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.26261 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -152.5752 | 0 | -0.36505 | 0 | 0 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.2849 | 158 | -0.31944 | -50.4708 | 158 | 50.4708
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -34.7189 | 160 | -0.31944 | -51.1096 | 318 | 101.5804 | Weighted Shift Factors
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.21699 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -37.9738 | 175 | -0.31944 | -55.9011 | 493 | 157.4815 | North | 0.10244
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.118 | 152.5 | -0.31305 | -47.7405 | 645.5 | 205.222 | South | -0.15445
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -31.4862 | 149.5 | -0.31305 | -46.8013 | 795 | 252.0233 |  | 0.25689
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.21061 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.9879 | 232.6 | -0.31305 | -72.8159 | 1027.6 | 324.8392
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.18647 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -108.8991 | 0 | -0.28891 | 0 | 1027.6 | 324.8392 | Line Rating | 1072
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.18647 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -110.9502 | 0 | -0.28891 | 0 | 1027.6 | 324.8392 | Conc Gen | 2069.8
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.18624 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -80.6402 | 0 | -0.28868 | 0 | 1027.6 | 324.8392 | Weighted Imp. | 613.2014
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.2185 | 223.9 | -0.2776 | -62.1553 | 1251.5 | 386.9945 | PTDF | 0.29626
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.4112 | 225 | -0.2776 | -62.4607 | 1476.5 | 449.4552
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.3412 | 224.6 | -0.2776 | -62.3497 | 1701.1 | 511.8049 | Concentration | 1.1532
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.17516 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -39.709 | 226.7 | -0.2776 | -62.9326 | 1927.8 | 574.7375
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.9171 | 142 | -0.27087 | -38.4638 | 2069.8 | 613.2014
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.4224 | 145 | -0.27087 | -39.2765
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -25.4329 | 151 | -0.27087 | -40.9017
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.16843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -48.8447 | 290 | -0.27087 | -78.5529
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.16803 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -8.4014 | 50 | -0.27047 | -13.5235
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.1776 | 132 | -0.27045 | -35.6999
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -22.5136 | 134 | -0.27045 | -36.2409
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.16801 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -54.2679 | 323 | -0.27045 | -87.3567
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.16503 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.99016 | 0 | -0.26747 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39383 | 0 | -0.26654 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.39383 | 0 | -0.26654 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.1641 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.45947 | 0 | -0.26654 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.16351 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.65403 | 0 | -0.26595 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8599 | 147 | -0.26475 | -38.9189
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.3991 | 138 | -0.26475 | -36.5361
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.7237 | 140 | -0.26475 | -37.0656
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8599 | 147 | -0.26475 | -38.9189
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -29.5408 | 182 | -0.26475 | -48.1853
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.16231 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.1378 | 198 | -0.26475 | -52.4213
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.15996 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38392 | 0 | -0.26241 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.15996 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.38392 | 0 | -0.26241 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.8303 | 49 | -0.26224 | -12.85
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3509 | 46 | -0.26224 | -12.0632
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3509 | 46 | -0.26224 | -12.0632
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.5107 | 47 | -0.26224 | -12.3255
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.1598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6095 | 154 | -0.26224 | -40.3856
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.1598 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.6507 | 148 | -0.26224 | -38.8121
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6705 | 48 | -0.26224 | -12.5877
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.1598 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.6705 | 48 | -0.26224 | -12.5877
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.1186 | 0 | -0.26138 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.2836 | 0 | -0.26138 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -29.244 | 0 | -0.26138 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -35.6014 | 0 | -0.26138 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -18.2775 | 0 | -0.26138 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6163 | 42 | -0.25997 | -10.9189
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9314 | 44 | -0.25997 | -11.4389
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9314 | 44 | -0.25997 | -11.4389
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.15753 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.404 | 47 | -0.25997 | -12.2188
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25996 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25996 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.15752 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.25996 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.15688 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.518 | 0 | -0.25932 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.15688 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -66.6749 | 0 | -0.25932 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.15666 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -64.5443 | 412 | -0.2591 | -106.7505
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.15666 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -62.6644 | 400 | -0.2591 | -103.6413
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.15648 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -32.7043 | 209 | -0.25892 | -54.1147
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.15648 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -33.7997 | 216 | -0.25892 | -55.9272
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1981 | 46 | -0.25892 | -11.9104
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.3546 | 47 | -0.25892 | -12.1693
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1981 | 46 | -0.25892 | -11.9104
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.15648 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.1981 | 46 | -0.25892 | -11.9104
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2474 | 155 | -0.25888 | -40.126
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -26.5939 | 170 | -0.25888 | -44.0091
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.15643 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.2474 | 155 | -0.25888 | -40.126
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.15643 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.6674 | 407 | -0.25887 | -105.3614
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.15602 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.1853 | 0 | -0.25846 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.15602 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -117.0127 | 0 | -0.25846 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.15546 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -9.0168 | 58 | -0.2579 | -14.9584
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.15546 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -13.8361 | 89 | -0.2579 | -22.9535
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8403 | 44 | -0.2579 | -11.3478
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.8403 | 44 | -0.2579 | -11.3478
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.6849 | 43 | -0.2579 | -11.0899
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.15546 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.9958 | 45 | -0.2579 | -11.6057
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.15464 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -47.9381 | 310 | -0.25708 | -79.6952
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.15464 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -63.8659 | 413 | -0.25708 | -106.1745
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.15173 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.8208 | 0 | -0.25417 | 0
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.14872 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -58.8939 | 0 | -0.25116 | 0
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.14741 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1793 | 0 | -0.24985 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.14741 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1793 | 0 | -0.24985 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13972 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -3.3534 | 24 | -0.24217 | -5.812
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.13972 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.3534 | 24 | -0.24217 | -5.812
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.13972 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -3.2137 | 23 | -0.24217 | -5.5698
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.1395 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9499 | 100 | -0.24194 | -24.1941
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.1395 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -13.9499 | 100 | -0.24194 | -24.1941
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.1395 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24194 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.13949 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24193 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.13827 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.24071 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.13813 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -1.1603 | 8.4 | -0.24058 | -2.0208
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.13688 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -86.1 | 0 | -0.23933 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.1364 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.23884 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.13526 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.2377 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6214 | 0 | -0.23756 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4863 | 0 | -0.23756 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.13512 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.6214 | 0 | -0.23756 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.5976 | 146.5 | -0.23621 | -34.6054
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.7849 | 147.9 | -0.23621 | -34.9361
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.13377 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.1426 | 173 | -0.23621 | -40.865
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.6463 | 207 | -0.236 | -48.8518
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -28.9418 | 216.7 | -0.236 | -51.141
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.13356 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -32.3208 | 242 | -0.236 | -57.1118
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.2318 | 144 | -0.236 | -33.9834
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.2318 | 144 | -0.236 | -33.9834
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.13355 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.8377 | 171 | -0.236 | -40.3553
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.13334 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.23578 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0667 | 38 | -0.23578 | -8.9595
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.5733 | 19.3 | -0.23578 | -4.5505
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.13333 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2 | 15 | -0.23578 | -3.5366
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.13333 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -6.2667 | 47 | -0.23578 | -11.0815
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5263 | 0 | -0.2357 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.4636 | 0 | -0.2357 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.0638 | 0 | -0.2357 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.5319 | 0 | -0.2357 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -12.5263 | 0 | -0.2357 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.7973 | 0 | -0.2357 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -5.7301 | 0 | -0.2357 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.9317 | 0 | -0.2357 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.7222 | 0 | -0.2357 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.6629 | 0 | -0.2357 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -7.3292 | 0 | -0.2357 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.13326 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.6629 | 0 | -0.2357 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.13306 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.8588 | 0 | -0.2355 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.13247 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0339 | 0 | -0.23491 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.13246 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0337 | 0 | -0.23491 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.13234 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3086 | 0 | -0.23479 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.13234 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.3086 | 0 | -0.23479 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.13232 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.1939 | 334 | -0.23476 | -78.4096
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.13232 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -44.9878 | 340 | -0.23476 | -79.8181
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.13232 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8171 | 180 | -0.23476 | -42.2566
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.13232 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.8171 | 180 | -0.23476 | -42.2566
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13208 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7742 | 180 | -0.23452 | -42.2138
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.5839 | 0 | -0.2345 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.6235 | 0 | -0.2345 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.13206 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.2046 | 0 | -0.2345 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -44.3661 | 336 | -0.23448 | -78.7867
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.13204 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -23.7676 | 180 | -0.23448 | -42.2071
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 0 | -0.23375 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 0 | -0.23375 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 0 | -0.23375 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.1009 | 0 | -0.23375 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 0 | -0.23375 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 0 | -0.23375 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.2826 | 0 | -0.23375 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.13131 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.9696 | 0 | -0.23375 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.13101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -18.8656 | 144 | -0.23345 | -33.6173
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.13101 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.6301 | 188 | -0.23345 | -43.8892
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.6688 | 0 | -0.23326 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -20.0147 | 0 | -0.23326 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -13.0815 | 0 | -0.23326 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -18.9682 | 0 | -0.23326 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -19.2298 | 0 | -0.23326 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.13081 | south | 8 | N | N | Nsouth | Nsouth | -1 | -16.6135 | 0 | -0.23326 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.13081 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.5698 | 0 | -0.23326 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5435 | 0 | -0.23226 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.4136 | 0 | -0.23226 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.12981 | south | 5 | N | N | Nsouth | Nsouth | -1 | -4.5435 | 0 | -0.23226 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.12975 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.472 | 0 | -0.2322 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.185 | 47.7 | -0.23211 | -11.0715
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -4.8365 | 37.3 | -0.23211 | -8.6576
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -5.9645 | 46 | -0.23211 | -10.6769
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.12966 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -6.2239 | 48 | -0.23211 | -11.1411
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.12867 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.8308 | 22 | -0.23111 | -5.0845
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.12867 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4154 | 11 | -0.23111 | -2.5422
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.12867 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -1.4154 | 11 | -0.23111 | -2.5422
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.12758 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.9137 | 0 | -0.23002 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.12758 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9343 | 0 | -0.23002 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.1268 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0144 | 0 | -0.22924 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.5372 | 0 | -0.22877 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8843 | 0 | -0.22877 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9268 | 0 | -0.22877 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8949 | 0 | -0.22877 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.8843 | 0 | -0.22877 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8949 | 0 | -0.22877 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9268 | 0 | -0.22877 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.12633 | south | 7 | N | N | Nsouth | Nsouth | -1 | -4.9268 | 0 | -0.22877 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.12326 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.9165 | 0 | -0.2257 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6637 | 0 | -0.22477 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.9083 | 0 | -0.22477 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.6637 | 0 | -0.22477 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.786 | 0 | -0.22477 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.5903 | 0 | -0.22477 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.0581 | 0 | -0.22477 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.6269 | 0 | -0.22477 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.4251 | 0 | -0.22477 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3334 | 0 | -0.22477 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.12233 | south | 7 | N | N | Nsouth | Nsouth | -1 | -9.052 | 0 | -0.22477 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.11083 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.995 | 0 | -0.21328 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.11083 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.995 | 0 | -0.21328 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.10246 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -43.2398 | 422 | -0.20491 | -86.4704
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.10224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.8628 | 0 | -0.20469 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.10224 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.9651 | 0 | -0.20469 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.10136 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.20381 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.096846 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.58108 | 0 | -0.19929 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.088747 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -118.2998 | 0 | -0.19119 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.088747 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -117.856 | 0 | -0.19119 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6729 | 76 | -0.19024 | -14.4585
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.6729 | 76 | -0.19024 | -14.4585
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -9.2191 | 105 | -0.19024 | -19.9755
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4973 | 74 | -0.19024 | -14.078
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -6.4973 | 74 | -0.19024 | -14.078
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.087801 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -8.9557 | 102 | -0.19024 | -19.4048
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.083453 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -5.5079 | 66 | -0.1859 | -12.2691
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.083315 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1414 | 0 | -0.18576 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4048 | 0 | -0.18049 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4048 | 0 | -0.18049 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.078044 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.1707 | 0 | -0.18049 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.077419 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.5548 | 0 | -0.17986 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.077419 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.9355 | 0 | -0.17986 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.077419 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.17986 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.3587 | 0 | -0.17274 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0196 | 0 | -0.17274 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1636 | 0 | -0.17274 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1005 | 0 | -0.17274 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.046 | 0 | -0.17274 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.1866 | 0 | -0.17274 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5151 | 0 | -0.17274 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2654 | 0 | -0.17274 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.6084 | 0 | -0.17274 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.9211 | 0 | -0.17274 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.429 | 0 | -0.17274 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.0617 | 0 | -0.17274 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5556 | 0 | -0.17274 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.1005 | 0 | -0.17274 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8193 | 0 | -0.17274 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -7.2411 | 0 | -0.17274 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.343 | 0 | -0.17274 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6242 | 0 | -0.17274 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.6242 | 0 | -0.17274 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.070302 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -12.0216 | 0 | -0.17274 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.066941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.7528 | 0 | -0.16938 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.066941 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.66941 | 0 | -0.16938 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.1349 | 0 | -0.16672 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.1349 | 0 | -0.16672 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.6491 | 0 | -0.16672 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.064278 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0384 | 0 | -0.16672 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.054906 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5312 | 0 | -0.15735 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -35.5908 | 0 | -0.15711 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -30.8344 | 0 | -0.15711 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.054671 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -32.8026 | 0 | -0.15711 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8983 | 0 | -0.15703 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -8.8983 | 0 | -0.15703 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.054591 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -13.3748 | 0 | -0.15703 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.053499 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7655 | 0 | -0.15594 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.5478 | 161 | -0.15553 | -25.041
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.8133 | 166 | -0.15553 | -25.8187
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.053092 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.1668 | 248 | -0.15553 | -38.5725
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.053092 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -28.9882 | 546 | -0.15553 | -84.9216
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.053092 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -34.1382 | 0 | -0.15553 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.053092 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.6902 | 13 | -0.15553 | -2.0219
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.828 | 0 | -0.15058 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.4718 | 0 | -0.15058 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9436 | 0 | -0.15058 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.048136 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.9099 | 0 | -0.15058 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.048135 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5403 | 0 | -0.15058 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.048135 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4441 | 0 | -0.15058 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4062 | 0 | -0.15055 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2089 | 0 | -0.15055 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5498 | 0 | -0.15055 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3705 | 0 | -0.15055 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3849 | 0 | -0.15055 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.3272 | 0 | -0.15055 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.6186 | 0 | -0.15055 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.04811 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -11.7388 | 0 | -0.15055 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.04811 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9244 | 0 | -0.15055 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.046071 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.3035 | 50 | -0.14851 | -7.4257
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.044471 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14691 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8775 | 0 | -0.14505 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7326 | 0 | -0.14505 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7071 | 0 | -0.14505 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3222 | 0 | -0.14505 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.04261 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.51984 | 0 | -0.14505 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7223 | 0 | -0.14432 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5129 | 0 | -0.14432 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7223 | 0 | -0.14432 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.041881 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.7223 | 0 | -0.14432 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8771 | 46 | -0.14325 | -6.5894
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8771 | 46 | -0.14325 | -6.5894
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8771 | 46 | -0.14325 | -6.5894
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2443 | 55 | -0.14325 | -7.8786
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2443 | 55 | -0.14325 | -7.8786
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.040806 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -2.2035 | 54 | -0.14325 | -7.7354
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.040526 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.161 | 0 | -0.14297 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.040526 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2421 | 0 | -0.14297 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.553 | 0 | -0.1426 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.308 | 0 | -0.1426 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3241 | 0 | -0.1426 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.304 | 0 | -0.1426 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.040153 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -10.8012 | 0 | -0.1426 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039849 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3947 | 0 | -0.14229 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039523 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.47428 | 12 | -0.14197 | -1.7036
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039523 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14197 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039505 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.6763 | 169 | -0.14195 | -23.9891
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039479 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -6.514 | 165 | -0.14192 | -23.417
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.03946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.8795 | 0 | -0.1419 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.03946 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5688 | 0 | -0.1419 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039393 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.3907 | 213 | -0.14184 | -30.2109
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039385 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63804 | 0 | -0.14183 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5203 | 0 | -0.14182 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4888 | 0 | -0.14182 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2527 | 0 | -0.14182 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.039379 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8983 | 0 | -0.14182 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039368 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -8.9759 | 228 | -0.14181 | -32.3327
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.0841 | 0 | -0.1418 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.2419 | 0 | -0.1418 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039356 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.1789 | 0 | -0.1418 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7618 | 0 | -0.14134 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8007 | 0 | -0.14134 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.517 | 0 | -0.14134 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.038898 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1669 | 0 | -0.14134 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.038173 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1915 | 0 | -0.14062 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6007 | 42 | -0.14055 | -5.9033
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.6007 | 42 | -0.14055 | -5.9033
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4483 | 38 | -0.14055 | -5.3411
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.038112 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.4483 | 38 | -0.14055 | -5.3411
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.037928 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.5615 | 0 | -0.14037 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.037928 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1203 | 0 | -0.14037 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.8237 | 104 | -0.13921 | -14.4776
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.8237 | 104 | -0.13921 | -14.4776
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9486 | 53 | -0.13921 | -7.378
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.0957 | 57 | -0.13921 | -7.9349
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.9854 | 54 | -0.13921 | -7.5172
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1324 | 58 | -0.13921 | -8.0741
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.036766 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.1324 | 58 | -0.13921 | -8.0741
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.036306 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.6849 | 735 | -0.13875 | -101.9799
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2242 | 0 | -0.13845 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2494 | 0 | -0.13845 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1774 | 0 | -0.13845 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6527 | 0 | -0.13845 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.63732 | 0 | -0.13845 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73454 | 0 | -0.13845 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.71654 | 0 | -0.13845 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2602 | 0 | -0.13845 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.64813 | 0 | -0.13845 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.075 | 0 | -0.13845 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.036007 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.329 | 0 | -0.13845 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.035632 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.42758 | 12 | -0.13807 | -1.6569
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.035139 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.17569 | 0 | -0.13758 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.035139 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73792 | 0 | -0.13758 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2835 | 0 | -0.13757 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.3186 | 0 | -0.13757 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4592 | 0 | -0.13757 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2133 | 0 | -0.13757 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1781 | 0 | -0.13757 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.6536 | 0 | -0.13757 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.035131 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0727 | 0 | -0.13757 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.035108 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.4213 | 0 | -0.13755 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.035074 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -26.06 | 743 | -0.13752 | -102.1745
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.034849 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.4713 | 0 | -0.13729 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9687 | 172 | -0.13714 | -23.5888
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9687 | 172 | -0.13714 | -23.5888
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.034702 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.9687 | 172 | -0.13714 | -23.5888
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.5075 | 0 | -0.13627 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4602 | 0 | -0.13627 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.3756 | 0 | -0.13627 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.03383 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -9.107 | 0 | -0.13627 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.033529 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -13.3445 | 398 | -0.13597 | -54.1165
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9473 | 59 | -0.13545 | -7.9914
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.9473 | 59 | -0.13545 | -7.9914
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.033005 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.8483 | 56 | -0.13545 | -7.585
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.8196 | 0 | -0.1303 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.346 | 0 | -0.1303 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2903 | 0 | -0.1303 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.027859 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2903 | 0 | -0.1303 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.027859 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.5132 | 0 | -0.1303 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.10244 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10244 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.10244 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.15893 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -15.8935 | 0 | -0.0044828 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.056233 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.098219 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.15445 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.15445 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.148 | 0 | 0.17487 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1847 | 0 | 0.17487 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.1847 | 0 | 0.17487 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.020415 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.7577 | 0 | 0.17487 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.020826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.99965 | 48 | 0.17528 | 8.4134
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.020826 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.958 | 46 | 0.17528 | 8.0628
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.020826 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1867 | 105 | 0.17528 | 18.4042
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.023675 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.7576 | 0 | 0.17813 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.023763 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.40397 | 17 | 0.17822 | 3.0297
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.023763 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17822 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.029588 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 13.6992 | 0 | 0.18404 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.045049 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7573 | 0 | 0.1995 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.060277 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.21473 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 52.0438 | 0 | 0.21532 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 52.0438 | 0 | 0.21532 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.2705 | 0 | 0.21532 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.06087 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 9.3131 | 0 | 0.21532 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.074111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.2898 | 0 | 0.22856 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.074111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 60.6969 | 0 | 0.22856 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.07958 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.6847 | 0 | 0.23403 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.080199 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1352 | 0 | 0.23465 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.080791 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4633 | 0 | 0.23524 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.084378 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6567 | 0 | 0.23883 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.084378 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.6567 | 0 | 0.23883 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.084468 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7574 | 0 | 0.23892 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084489 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7591 | 0 | 0.23894 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.3484 | 0 | 0.2391 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7717 | 0 | 0.2391 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.084646 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3858 | 0 | 0.2391 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085365 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8292 | 0 | 0.23982 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.085365 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.8292 | 0 | 0.23982 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.088016 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.42248 | 0 | 0.24247 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.09279 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 57.0658 | 0 | 0.24724 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.09279 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 54.4677 | 0 | 0.24724 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.1979 | 150.7 | 0.24867 | 37.4738
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.2262 | 151 | 0.24867 | 37.5484
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.094213 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7134 | 177.4 | 0.24867 | 44.1132
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.2326 | 66 | 0.24889 | 16.4265
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.1382 | 65 | 0.24889 | 16.1776
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3271 | 67 | 0.24889 | 16.6754
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3271 | 67 | 0.24889 | 16.6754
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.094434 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3271 | 67 | 0.24889 | 16.6754
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.094434 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.24889 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.094434 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.24889 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3128 | 151.5 | 0.24893 | 37.7123
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3884 | 152.3 | 0.24893 | 37.9115
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.094474 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7691 | 177.5 | 0.24893 | 44.1844
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.094523 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3083 | 0 | 0.24898 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.094523 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.8357 | 0 | 0.24898 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.094826 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.1291 | 0 | 0.24928 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.094962 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.0961 | 0 | 0.24941 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.095512 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.63038 | 0 | 0.24996 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.095512 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.2761 | 0 | 0.24996 | 0
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.8138 | 0 | 0.25058 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.3704 | 0 | 0.25058 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.8789 | 0 | 0.25058 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.096123 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6184 | 0 | 0.25058 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.023 | 208.2 | 0.25062 | 52.18
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.666 | 142.1 | 0.25062 | 35.6137
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 12.7332 | 132.4 | 0.25062 | 33.1826
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 13.0794 | 136 | 0.25062 | 34.0849
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 14.1373 | 147 | 0.25062 | 36.8418
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.096172 | west | 9 | Y | Y | Ywest | Ywest | 1 | 20.1961 | 210 | 0.25062 | 52.6311
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7332 | 70 | 0.25064 | 17.5449
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.7332 | 70 | 0.25064 | 17.5449
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 8.9263 | 92.8 | 0.25064 | 23.2595
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.6951 | 80 | 0.25064 | 20.0513
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.6951 | 80 | 0.25064 | 20.0513
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.096189 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0617 | 115 | 0.25064 | 28.8237
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.096269 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5836 | 0 | 0.25072 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.0963 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6782 | 0 | 0.25075 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.096448 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.4672 | 0 | 0.2509 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.096507 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.6718 | 0 | 0.25096 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.096671 | west | 8 | N | N | Nwest | Nwest | 1 | 2.4941 | 0 | 0.25112 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.097188 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6626 | 0 | 0.25164 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.09723 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.6676 | 0 | 0.25168 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.097394 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.9137 | 0 | 0.25185 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 1 | 6.8202 | 0 | 0.25188 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 1 | 7.1514 | 0 | 0.25188 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.097431 | west | 8 | N | N | Nwest | Nwest | 1 | 6.8591 | 0 | 0.25188 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097487 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5477 | 0 | 0.25194 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.097487 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.5477 | 0 | 0.25194 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7109 | 0 | 0.25204 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.7387 | 0 | 0.25204 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.097591 | west | 6 | Y | N | Ywest | Nwest | 1 | 16.61 | 0 | 0.25204 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.6567 | 0 | 0.25216 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 21.4964 | 0 | 0.25216 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.5422 | 0 | 0.25216 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.097711 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.911 | 0 | 0.25216 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.4661 | 66 | 0.25242 | 16.6599
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.76 | 69 | 0.25242 | 17.4172
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.76 | 69 | 0.25242 | 17.4172
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5641 | 67 | 0.25242 | 16.9124
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.5641 | 67 | 0.25242 | 16.9124
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.097971 | west | 13 | Y | Y | Ywest | Ywest | 1 | 6.3681 | 65 | 0.25242 | 16.4075
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.098078 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.1789 | 0 | 0.25253 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.09815 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.8392 | 0 | 0.2526 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.09815 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.778 | 0 | 0.2526 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.098178 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.7196 | 0 | 0.25263 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.098178 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9889 | 0 | 0.25263 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4545 | 0 | 0.25263 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4867 | 0 | 0.25263 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.098178 | west | 7 | N | N | Nwest | Nwest | 1 | 4.4867 | 0 | 0.25263 | 0
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.098431 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2682 | 0 | 0.25288 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098595 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3244 | 0 | 0.25305 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.098595 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.3244 | 0 | 0.25305 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.098858 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.8287 | 0 | 0.25331 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.098858 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.9847 | 0 | 0.25331 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7171 | 0 | 0.25358 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.6557 | 0 | 0.25358 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.3816 | 0 | 0.25358 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.7956 | 0 | 0.25358 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.4079 | 0 | 0.25358 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.099123 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9794 | 0 | 0.25358 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 20.7272 | 0 | 0.25363 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5454 | 0 | 0.25363 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.6941 | 0 | 0.25363 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.099173 | west | 6 | Y | N | Ywest | Nwest | 1 | 19.5371 | 0 | 0.25363 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.099541 | west | 6 | Y | N | Ywest | Nwest | 1 | 14.9312 | 0 | 0.25399 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.099735 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 18.1518 | 182 | 0.25419 | 46.2621
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.099735 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 48.2717 | 484 | 0.25419 | 123.0266
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.10015 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 5.0077 | 0 | 0.25461 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.10021 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.25466 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.10082 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.0492 | 0 | 0.25527 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.9292 | 0 | 0.25533 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 13.1135 | 0 | 0.25533 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.6266 | 0 | 0.25533 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.10087 | north | 1 | N | N | Nnorth | Nnorth | 1 | 40.2483 | 0 | 0.25533 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.6265 | 0 | 0.25589 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 80.6408 | 0 | 0.25589 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.10143 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 79.1193 | 0 | 0.25589 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.10217 | west | 6 | Y | N | Ywest | Nwest | 1 | 40.8692 | 0 | 0.25663 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.10218 | west | 6 | Y | N | Ywest | Nwest | 1 | 24.114 | 0 | 0.25663 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.10315 | west | 6 | Y | N | Ywest | Nwest | 1 | 17.0193 | 0 | 0.2576 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.10394 | west | 4 | Y | N | Ywest | Nwest | 1 | 67.5331 | 0 | 0.2584 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0145 | 161 | 0.26013 | 41.8813
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.3315 | 164 | 0.26013 | 42.6617
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.3315 | 164 | 0.26013 | 42.6617
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.7515 | 414 | 0.26013 | 107.6947
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1202 | 162 | 0.26013 | 42.1414
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.0145 | 161 | 0.26013 | 41.8813
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.2258 | 163 | 0.26013 | 42.4016
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.10568 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 43.2231 | 409 | 0.26013 | 106.3941
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.10622 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 38.8754 | 366 | 0.26067 | 95.4049
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.10627 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.8047 | 224 | 0.26072 | 58.402
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1285 | 20 | 0.26088 | 5.2176
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1285 | 20 | 0.26088 | 5.2176
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 2.1285 | 20 | 0.26088 | 5.2176
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.10643 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.8093 | 17 | 0.26088 | 4.4349
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.10657 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 25.7895 | 242 | 0.26102 | 63.1669
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.1328 | 20 | 0.26109 | 5.2219
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.666 | 25 | 0.26109 | 6.5274
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.10664 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.3723 | 41 | 0.26109 | 10.7049
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.10669 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 41.3957 | 388 | 0.26114 | 101.3232
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.10669 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 54.9453 | 515 | 0.26114 | 134.4882
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 59.5888 | 0 | 0.26124 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 61.8314 | 0 | 0.26124 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.10679 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 86.2863 | 0 | 0.26124 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.4378 | 79 | 0.26126 | 20.6395
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 11.3215 | 106 | 0.26126 | 27.6935
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.10681 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 15.5938 | 146 | 0.26126 | 38.1438
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.10681 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 8.1173 | 76 | 0.26126 | 19.8557
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.10684 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.2738 | 40 | 0.2613 | 10.4518
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | 1 | 8.0143 | 0 | 0.26131 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | 1 | 8.5058 | 0 | 0.26131 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.10686 | north | 8 | N | N | Nnorth | Nnorth | 1 | 9.4462 | 0 | 0.26131 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.1106 | 160 | 0.26139 | 41.8229
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6828 | 156 | 0.26139 | 40.7773
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 20.9604 | 196 | 0.26139 | 51.2331
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.6828 | 156 | 0.26139 | 40.7773
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7897 | 157 | 0.26139 | 41.0387
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.10694 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.1743 | 198 | 0.26139 | 51.7559
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.10703 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 39.6022 | 370 | 0.26149 | 96.7495
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 14.9846 | 0 | 0.26149 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.0917 | 0 | 0.26149 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 33.0732 | 0 | 0.26149 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.3057 | 0 | 0.26149 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 15.4128 | 0 | 0.26149 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.10703 | north | 1 | N | N | Nnorth | Nnorth | 1 | 33.1802 | 0 | 0.26149 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.1071 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26155 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.1071 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26155 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.10719 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 18.222 | 170 | 0.26164 | 44.4788
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.10719 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 55.7378 | 520 | 0.26164 | 136.0529
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.10732 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2929 | 0 | 0.26177 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.10732 | north | 5 | N | N | Nnorth | Nnorth | 1 | 4.2929 | 0 | 0.26177 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.10787 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.26232 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.1079 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26235 | 0
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.1107 | 204 | 0.26284 | 53.619
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7856 | 201 | 0.26284 | 52.8305
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.10839 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.2294 | 242 | 0.26284 | 63.6068
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.10877 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.8353 | 118 | 0.26323 | 31.0607
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.10877 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 12.509 | 115 | 0.26323 | 30.271
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.10877 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 60.4783 | 556 | 0.26323 | 146.3538
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.10878 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.527 | 60 | 0.26324 | 15.7941
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.10878 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.8533 | 63 | 0.26324 | 16.5838
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.10892 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 12.2534 | 0 | 0.26337 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.10917 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 13.1005 | 0 | 0.26362 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.10918 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3101 | 0 | 0.26363 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.10918 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.3101 | 0 | 0.26363 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 31.7422 | 288 | 0.26467 | 76.2244
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2018 | 147 | 0.26467 | 38.9062
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.11022 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.2018 | 147 | 0.26467 | 38.9062
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.1105 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26495 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.1105 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26495 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.1105 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26495 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.11072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 21.7005 | 196 | 0.26517 | 51.9732
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.11072 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.2896 | 111 | 0.26517 | 29.4338
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0059 | 18 | 0.26589 | 4.7861
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.0059 | 18 | 0.26589 | 4.7861
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.11144 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.2348 | 38 | 0.26589 | 10.1039
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.11172 | north | 3 | N | N | Nnorth | Nnorth | 1 | 129.2589 | 0 | 0.26617 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.11172 | north | 3 | N | N | Nnorth | Nnorth | 1 | 129.3706 | 0 | 0.26617 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.3224 | 217.3 | 0.26638 | 57.8849
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 22.9457 | 205 | 0.26638 | 54.6084
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.11193 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 30.4897 | 272.4 | 0.26638 | 72.5625
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.11197 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.7184 | 0 | 0.26643 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.11202 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.7265 | 435 | 0.26647 | 115.9132
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.1122 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.26665 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.11225 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 44.3372 | 395 | 0.2667 | 105.3458
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.11225 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 48.827 | 435 | 0.2667 | 116.0137
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.11276 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 8.2313 | 73 | 0.26721 | 19.5063
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.11276 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.4181 | 119 | 0.26721 | 31.7979
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.11276 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 23.1152 | 205 | 0.26721 | 54.7779
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.11276 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 11.5012 | 102 | 0.26721 | 27.2553
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.11276 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 10.8247 | 96 | 0.26721 | 25.6521
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.9933 | 70 | 0.26864 | 18.805
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8791 | 69 | 0.26864 | 18.5363
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.8791 | 69 | 0.26864 | 18.5363
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.11419 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 7.7649 | 68 | 0.26864 | 18.2677
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.11617 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.1385 | 216.4 | 0.27062 | 58.562
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.11617 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 25.1037 | 216.1 | 0.27062 | 58.4808
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.1524 | 224 | 0.2712 | 60.7497
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 26.386 | 226 | 0.2712 | 61.2922
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.7514 | 212 | 0.2712 | 57.4953
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.11675 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 24.6347 | 211 | 0.2712 | 57.2241
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.11771 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 19.7758 | 168 | 0.27217 | 45.7238
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.11771 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.5942 | 90 | 0.27217 | 24.4949
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.148 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.2199 | 0 | 0.30245 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.148 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.2199 | 0 | 0.30245 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.15589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.3839 | 150 | 0.31035 | 46.5518
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.15589 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.4714 | 80 | 0.31035 | 24.8276
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.16343 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 41.6757 | 255 | 0.31789 | 81.061
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.16343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 24.3517 | 149 | 0.31789 | 47.365
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.16343 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 25.0054 | 153 | 0.31789 | 48.6366
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.16854 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.323 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.16854 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.323 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.17333 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.32778 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.17333 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 136.4115 | 787 | 0.32778 | 257.9654

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown