## test results
CRE test for: |  | TEMP_SS_ to SANDOW_ 345kV [3414 - 3429] | [5 empty] | FAIL
Line Rating: |  | 1072
Direction |  | North | → | South |  | N-S
Average Weighted Shift Factors
Number | 433 | Y
| Source | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TEMP_SS_ to SANDOW_ 345kV [3414 - 3429]
| 26455.4 | North | -0.057993 | -0.17324 | 0.17324 | 0.16585 | 0.057993 | 0.055887
| 21167.8 | South | -0.018994 | 0.23296 | -0.23296 | -0.059574 | 0.018994 | -0.089716
| 11246.4 | West | 0.75392 | -0.15588 | 0.15588 | 0.13936 | -0.75392 | 0.053044
| 8229 | Houston | -0.038687 | 0.049426 | -0.049426 | -0.18587 | 0.038687 | -0.026957
Total | 67098.6
| 308 | Y
| Sink | Zone | W-N weighted GSF | S-N weighted GSF | N-S weighted GSF | N-H weighted GSF | N-W weighted GSF | TEMP_SS_ to SANDOW_ 345kV [3414 - 3429]
| 16481.6 | North | -0.058813 | -0.18775 | 0.18775 | 0.15488 | 0.058813 | 0.061825
| 13405.8 | South | -0.017866 | 0.22869 | -0.22869 | -0.062504 | 0.017866 | -0.085447
| 2295.5 | West | 0.75677 | -0.15662 | 0.15662 | 0.13972 | -0.75677 | 0.053282
| 6402 | Houston | -0.039018 | 0.045916 | -0.045916 | -0.17811 | 0.039018 | -0.02567
Total | 38584.9
7.2.3.1.1 | Power Transfer Distribution Factors (PTDFs)
PTDF calculation |  |  | W-N | S-N | N-S | N-H | N-W | TEMP_SS_ to SANDOW_ 345kV [3414 - 3429]
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.14133
North | → | West | -0.81477 | -0.016614 | 0.016614 | 0.026133 | 0.81477 | 0.0026045
North | → | Houston | -0.018975 | -0.21915 | 0.21915 | 0.34396 | 0.018975 | 0.081557
South | → | West | -0.77577 | 0.38958 | -0.38958 | -0.19929 | 0.77577 | -0.143
South | → | Houston | 0.020024 | 0.18705 | -0.18705 | 0.11854 | -0.020024 | -0.062759
West | → | Houston | 0.79294 | -0.20179 | 0.20179 | 0.31747 | -0.79294 | 0.078714
PTDF tests
North | → | South | -0.040127 | -0.40193 | 0.40193 | 0.22835 | 0.040127 | 0.14133 | FAIL
7.2.3.1.2 | Generation Concentration
Generation Concentration |  | = {[Abs(Generator's PTDF designated zone)] - [Abs(Generators PTDF alternate zone)]} * Maximum Capacity
Threshold: |  | Generation weighted average PTDF <= 2 x zonal average PTDF on the CRE of the designated zone
[6 empty] | Zonal Average PTDF |  | 0.14133 | 0.14133
Decremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.1722
[6 empty] | Concentration |  | 1.2184 | PASS
Incremental Side
| Weighted average of movable generation equal to 2x CRE's rating | [6 empty] | 0.16414
[6 empty] | Concentration |  | 1.1613 | PASS
7.2.3.1.3 | Boundary Generation Resources
Impact Error of Boundary Generation Resources = |  | = {[Sum(Generator's PTDF designated zone)] / Sum(Generators's capacity designated zone)]
Threshold: |  | Sum of Boundary Generation Resources Impact Errors should be <= 30%
| Boundary Generation Resources Impact Errors sum => | [5 empty] | 30.7451
| Percent of line rating => | [6 empty] | 2.868% | PASS
7.2.3.1.4 | CRE Correlation to CSC test
[7 empty] | A | 2.8438
[7 empty] | B1(N-S) | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B2 (N-W) | 0.0092071 | 0.016614 | 0.0074067 | 0.0092071
Scaling Factor "A" |  | A = CSC PTDF div by CRE PTDF |  |  |  |  | B3 (N-H) | -0.012781 | 0.21915 | 0.23193 | -0.012781
[7 empty] | B4 (S-W) | 0.017077 | -0.38958 | -0.40666 | 0.017077
Deployment Error "Bp" |  | Bp = CSC PTDF - (CRE PTDF x A) |  |  |  |  | B5 (S-H) | -0.0085704 | -0.18705 | -0.17848 | -0.0085704
|  | where p = one pair of congestion zones |  |  |  |  | B6 (W-H) | -0.022054 | 0.20179 | 0.22385 | -0.022054
[7 empty] | test | 0 | 0.40193 | 0.40193 | 0
[7 empty] | B1 | 0%
Deployment Error Percent | [6 empty] | B2 | 2.291%
|  | Error% = Bp div CSC PTDF |  |  |  |  | B3 | -3.18%
[7 empty] | B4 | 4.249%
[7 empty] | B5 | -2.132%
[7 empty] | B6 | -5.487%
[7 empty] | Max Abs Error | 5.487% | PASS

## Generation_sensitivity
Generator Sensitivities | [12 empty] | N-S
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | W-N | S-N | N-S | N-H | N-W | L: TEMP_SS_ to SANDOW_ 345kV [3414 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | W-N GSF | S-N GSF | N-S GSF | N-H GSF | N-W GSF | L: TEMP_SS_ to SANDOW_ 345kV [3414 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414]
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.091815 | north | 9 | Y | Y | Ynorth | Ynorth | -12.4603 | -62.3595 | 62.3595 | 30.1012 | 12.4603 | 23.4128
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.091815 | north | 13 | Y | Y | Ynorth | Ynorth | -7.2807 | -36.4375 | 36.4375 | 17.5886 | 7.2807 | 13.6804
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.083659 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.2549
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | -0.046395 | -0.20035 | 0.20035 | 0.12608 | 0.046395 | 0.083659 | north | 5 | N | N | Nnorth | Nnorth | -0.69593 | -3.0053 | 3.0053 | 1.8911 | 0.69593 | 1.2549
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | -0.048864 | -0.24455 | 0.24455 | 0.11804 | 0.048864 | 0.091815 | north | 13 | Y | Y | Ynorth | Ynorth | -7.4762 | -37.4157 | 37.4157 | 18.0607 | 7.4762 | 14.0477
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.08846 | north | 9 | Y | Y | Ynorth | Ynorth | -7.0694 | -30.7583 | 30.7583 | 18.0738 | 7.0694 | 13.269
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | -0.047129 | -0.20505 | 0.20505 | 0.12049 | 0.047129 | 0.08846 | north | 9 | Y | Y | Ynorth | Ynorth | -3.7703 | -16.4044 | 16.4044 | 9.6394 | 3.7703 | 7.0768
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.062373 | north | 12 | Y | Y | Ynorth | Ynorth | 0.57743 | -13.0644 | 13.0644 | 10.7422 | -0.57743 | 4.5532
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.062373 | north | 10 | Y | Y | Ynorth | Ynorth | 0.94129 | -21.2968 | 21.2968 | 17.5113 | -0.94129 | 7.4224
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.062373 | north | 10 | Y | Y | Ynorth | Ynorth | 1.6216 | -36.6878 | 36.6878 | 30.1666 | -1.6216 | 12.7865
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.062373 | north | 13 | Y | Y | Ynorth | Ynorth | 0.80682 | -18.2544 | 18.2544 | 15.0097 | -0.80682 | 6.362
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.00791 | -0.17897 | 0.17897 | 0.14715 | -0.00791 | 0.062373 | north | 13 | Y | Y | Ynorth | Ynorth | 0.75936 | -17.1806 | 17.1806 | 14.1268 | -0.75936 | 5.9878
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.060176 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.72211
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.13156 | -0.17742 | 0.17742 | 0.14883 | -0.13156 | 0.060176 | north | 5 | N | N | Nnorth | Nnorth | 1.5787 | -2.1291 | 2.1291 | 1.786 | -1.5787 | 0.72211
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.065029 | north | 9 | Y | Y | Ynorth | Ynorth | -10.0753 | -31.836 | 31.836 | 24.8978 | 10.0753 | 10.9249
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | -0.059972 | -0.1895 | 0.1895 | 0.1482 | 0.059972 | 0.065029 | north | 9 | Y | Y | Ynorth | Ynorth | -5.3975 | -17.055 | 17.055 | 13.3381 | 5.3975 | 5.8526
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.1055
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 0.078012 | -3.2605 | 3.2605 | 2.704 | -0.078012 | 1.1055
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.004334 | -0.18114 | 0.18114 | 0.15022 | -0.004334 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 0.16469 | -6.8833 | 6.8833 | 5.7085 | -0.16469 | 2.3339
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 10.0673 | -52.2418 | 52.2418 | 43.8143 | -10.0673 | 17.4563
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 8.91
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.034956 | -0.1814 | 0.1814 | 0.15213 | -0.034956 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 5.1385 | -26.6651 | 26.6651 | 22.3636 | -5.1385 | 8.91
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.038686 | -0.18115 | 0.18115 | 0.15441 | -0.038686 | 0.05977 | north | 6 | Y | N | Ynorth | Nnorth | 4.3522 | -20.3794 | 20.3794 | 17.3708 | -4.3522 | 6.7241
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | -0.067641 | -0.18015 | 0.18015 | 0.16061 | 0.067641 | 0.058384 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7056 | -7.2061 | 7.2061 | 6.4245 | 2.7056 | 2.3354
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | -5.3494 | -14.2318 | 14.2318 | 12.688 | 5.3494 | 4.6106
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | -7.1777 | -19.0959 | 19.0959 | 17.0243 | 7.1777 | 6.1864
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | -9.8862 | -26.3019 | 26.3019 | 23.4486 | 9.8862 | 8.5209
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | -0.067714 | -0.18015 | 0.18015 | 0.16061 | 0.067714 | 0.058362 | north | 13 | Y | Y | Ynorth | Ynorth | -5.1463 | -13.6914 | 13.6914 | 12.2061 | 5.1463 | 4.4355
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.059614 | north | 11 | Y | Y | Ynorth | Ynorth | -3.9203 | -10.9323 | 10.9323 | 9.3672 | 3.9203 | 3.5768
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | -0.065339 | -0.18221 | 0.18221 | 0.15612 | 0.065339 | 0.059614 | north | 11 | Y | Y | Ynorth | Ynorth | -4.1164 | -11.4789 | 11.4789 | 9.8356 | 4.1164 | 3.7557
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.058263 | north | 11 | Y | Y | Ynorth | Ynorth | -1.3517 | -3.5982 | 3.5982 | 3.2165 | 1.3517 | 1.1653
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.058264 | north | 11 | Y | Y | Ynorth | Ynorth | -1.6896 | -4.4977 | 4.4977 | 4.0206 | 1.6896 | 1.4566
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | -0.067584 | -0.17991 | 0.17991 | 0.16082 | 0.067584 | 0.058264 | north | 11 | Y | Y | Ynorth | Ynorth | -2.7709 | -7.3762 | 7.3762 | 6.5938 | 2.7709 | 2.3888
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | -0.049519 | -0.065144 | 0.065144 | 0.24366 | 0.049519 | 0.014683 | north | 4 | Y | N | Ynorth | Nnorth | -22.9273 | -30.1617 | 30.1617 | 112.8137 | 22.9273 | 6.7982
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 49.8165 | -10.1036 | 10.1036 | 9.0979 | -49.8165 | 3.4389
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 49.0617 | -9.9505 | 9.9505 | 8.9601 | -49.0617 | 3.3868
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.491
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.491
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 50.5713 | -10.2567 | 10.2567 | 9.2357 | -50.5713 | 3.491
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.052105 | west | 11 | Y | Y | mothballed | mothballed | 86.0466 | -17.4517 | 17.4517 | 15.7146 | -86.0466 | 5.94
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.75479 | -0.15308 | 0.15308 | 0.13785 | -0.75479 | 0.052105 | west | 10 | Y | Y | mothballed | mothballed | 388.7194 | -78.8388 | 78.8388 | 70.9912 | -388.7194 | 26.8341
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 50.0619 | -10.4745 | 10.4745 | 9.2959 | -50.0619 | 3.5674
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.7295
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 52.3375 | -10.9506 | 10.9506 | 9.7184 | -52.3375 | 3.7295
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.6214
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 50.8204 | -10.6332 | 10.6332 | 9.4367 | -50.8204 | 3.6214
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.75851 | -0.1587 | 0.1587 | 0.14085 | -0.75851 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 49.3034 | -10.3158 | 10.3158 | 9.1551 | -49.3034 | 3.5133
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 53.7727 | -11.0538 | 11.0538 | 9.8298 | -53.7727 | 3.7626
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 56.3846 | -11.5907 | 11.5907 | 10.3073 | -56.3846 | 3.9453
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.76818 | -0.15791 | 0.15791 | 0.14043 | -0.76818 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 54.08 | -11.1169 | 11.1169 | 9.886 | -54.08 | 3.7841
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 115.4565 | -23.7551 | 23.7551 | 21.1003 | -115.4565 | 8.0858
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 169.3362 | -34.8407 | 34.8407 | 30.9472 | -169.3362 | 11.8591
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.054166 | west | 6 | Y | N | Ywest | Nwest | 73.1876 | -15.7425 | 15.7425 | 13.9579 | -73.1876 | 5.3624
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.054166 | west | 6 | Y | N | Ywest | Nwest | 45.0954 | -9.6999 | 9.6999 | 8.6003 | -45.0954 | 3.3041
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.054151 | west | 6 | Y | N | Ywest | Nwest | 104.3032 | -22.4148 | 22.4148 | 19.8761 | -104.3032 | 7.6353
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 18.4817 | -3.9754 | 3.9754 | 3.5247 | -18.4817 | 1.3541
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.4754
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.73927 | -0.15901 | 0.15901 | 0.14099 | -0.73927 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 33.7846 | -7.267 | 7.267 | 6.4432 | -33.7846 | 2.4754
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.73974 | -0.15897 | 0.15897 | 0.14097 | -0.73974 | 0.054151 | west | 6 | Y | N | Ywest | Nwest | 88.7687 | -19.0764 | 19.0764 | 16.9158 | -88.7687 | 6.4981
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.74844 | -0.15636 | 0.15636 | 0.13969 | -0.74844 | 0.05335 | west | 8 | N | N | Nwest | Nwest | 19.3098 | -4.034 | 4.034 | 3.604 | -19.3098 | 1.3764
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.75623 | -0.156 | 0.156 | 0.13942 | -0.75623 | 0.053134 | west | 6 | Y | N | Ywest | Nwest | 76.0006 | -15.6779 | 15.6779 | 14.0122 | -76.0006 | 5.34
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.75105 | -0.15736 | 0.15736 | 0.14016 | -0.75105 | 0.053626 | west | 6 | Y | N | Ywest | Nwest | 90.1262 | -18.8827 | 18.8827 | 16.819 | -90.1262 | 6.4351
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.7561 | -0.15597 | 0.15597 | 0.1394 | -0.7561 | 0.053116 | west | 6 | Y | N | Ywest | Nwest | 43.8536 | -9.0465 | 9.0465 | 8.0851 | -43.8536 | 3.0807
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.75643 | -0.15636 | 0.15636 | 0.1396 | -0.75643 | 0.053247 | west | 6 | Y | N | Ywest | Nwest | 162.0282 | -33.4915 | 33.4915 | 29.9027 | -162.0282 | 11.4055
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.054569 | west | 6 | Y | N | Ywest | Nwest | 106.7662 | -23.9263 | 23.9263 | 21.1923 | -106.7662 | 8.1853
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.052737 | west | 6 | Y | N | Ywest | Nwest | 4.8775 | -1.0165 | 1.0165 | 0.91495 | -4.8775 | 0.34806
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.73902 | -0.15401 | 0.15401 | 0.13863 | -0.73902 | 0.052737 | west | 6 | Y | N | Ywest | Nwest | 25.3485 | -5.2826 | 5.2826 | 4.755 | -25.3485 | 1.8089
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.71178 | -0.15951 | 0.15951 | 0.14128 | -0.71178 | 0.054569 | west | 6 | Y | N | Ywest | Nwest | 71.8893 | -16.1104 | 16.1104 | 14.2695 | -71.8893 | 5.5115
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.74961 | -0.15742 | 0.15742 | 0.14019 | -0.74961 | 0.053649 | west | 6 | Y | N | Ywest | Nwest | 89.9534 | -18.8908 | 18.8908 | 16.8229 | -89.9534 | 6.4379
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | -0.13089 | -0.17498 | 0.17498 | 0.14876 | 0.13089 | 0.058432 | north | 10 | Y | Y | Ynorth | Ynorth | -47.9068 | -64.043 | 64.043 | 54.4469 | 47.9068 | 21.3861
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.1555 | -0.17396 | 0.17396 | 0.14783 | -0.1555 | 0.058705 | north | 10 | Y | Y | Ynorth | Ynorth | 37.6305 | -42.0974 | 42.0974 | 35.7749 | -37.6305 | 14.2066
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.80747 | -0.16675 | 0.16675 | 0.14481 | -0.80747 | 0.056296 | west | 6 | Y | N | Ywest | Nwest | 322.9896 | -66.698 | 66.698 | 57.9256 | -322.9896 | 22.5184
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.80761 | -0.16676 | 0.16676 | 0.14482 | -0.80761 | 0.056298 | west | 6 | Y | N | Ywest | Nwest | 190.5955 | -39.3544 | 39.3544 | 34.1773 | -190.5955 | 13.2863
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.82237 | -0.16873 | 0.16873 | 0.14577 | -0.82237 | 0.05681 | west | 6 | Y | N | Ywest | Nwest | 135.6906 | -27.8405 | 27.8405 | 24.0514 | -135.6906 | 9.3736
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | -24.8782 | -36.6598 | 36.6598 | 30.8464 | 24.8782 | 12.1502
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | -24.5124 | -36.1207 | 36.1207 | 30.3928 | 24.5124 | 11.9716
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | -0.12195 | -0.17971 | 0.17971 | 0.15121 | 0.12195 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | -29.5124 | -43.4886 | 43.4886 | 36.5923 | 29.5124 | 14.4135
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.1711
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.1711
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 12.8584 | -3.5014 | 3.5014 | 2.9787 | -12.8584 | 1.1711
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.64292 | -0.17507 | 0.17507 | 0.14894 | -0.64292 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 10.9296 | -2.9762 | 2.9762 | 2.5319 | -10.9296 | 0.99543
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.085093 | -0.17722 | 0.17722 | 0.14862 | -0.085093 | 0.060184 | north | 6 | Y | N | Ynorth | Nnorth | 10.2112 | -21.2669 | 21.2669 | 17.8345 | -10.2112 | 7.2221
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.091969 | -0.17107 | 0.17107 | 0.14208 | -0.091969 | 0.062279 | north | 6 | Y | N | Ynorth | Nnorth | 5.5181 | -10.2643 | 10.2643 | 8.5246 | -5.5181 | 3.7367
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | -5.0249 | -13.5155 | 13.5155 | 12.0215 | 5.0249 | 4.38
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | -5.3331 | -14.3445 | 14.3445 | 12.7588 | 5.3331 | 4.6486
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | -0.066999 | -0.18021 | 0.18021 | 0.16029 | 0.066999 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | -5.9227 | -15.9303 | 15.9303 | 14.1694 | 5.9227 | 5.1626
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7683 | -28.8555 | 28.8555 | 25.6298 | 10.7683 | 9.3518
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 9.118
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | -13.1912 | -35.348 | 35.348 | 31.3965 | 13.1912 | 11.456
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | -10.4991 | -28.1341 | 28.1341 | 24.989 | 10.4991 | 9.118
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | -10.5664 | -28.3145 | 28.3145 | 25.1492 | 10.5664 | 9.1765
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | -0.067302 | -0.18035 | 0.18035 | 0.16019 | 0.067302 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | -13.3258 | -35.7087 | 35.7087 | 31.7168 | 13.3258 | 11.5729
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.058602 | north | 11 | Y | Y | Ynorth | Ynorth | -11.0845 | -30.7059 | 30.7059 | 27.1541 | 11.0845 | 9.9623
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | -0.065203 | -0.18062 | 0.18062 | 0.15973 | 0.065203 | 0.058602 | north | 10 | Y | Y | Ynorth | Ynorth | -33.9056 | -93.924 | 93.924 | 83.0596 | 33.9056 | 30.473
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058505 | north | 12 | Y | Y | Ynorth | Ynorth | -24.8806 | -66.7769 | 66.7769 | 59.2178 | 24.8806 | 21.6469
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | -37.7766 | -100.5243 | 100.5243 | 89.5188 | 37.7766 | 32.5632
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | -39.1983 | -104.3074 | 104.3074 | 92.8878 | 39.1983 | 33.7887
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | -0.0677 | -0.18015 | 0.18015 | 0.16043 | 0.0677 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | -54.7016 | -145.562 | 145.562 | 129.6258 | 54.7016 | 47.1525
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.060651 | north | 12 | Y | Y | mothballed | mothballed | -7.485 | -20.6453 | 20.6453 | 17.2255 | 7.485 | 6.7929
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.060651 | north | 10 | Y | Y | mothballed | mothballed | -6.683 | -18.4333 | 18.4333 | 15.3799 | 6.683 | 6.0651
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | -0.06683 | -0.18433 | 0.18433 | 0.1538 | 0.06683 | 0.060651 | north | 12 | Y | Y | mothballed | mothballed | -25.2617 | -69.6779 | 69.6779 | 58.136 | 25.2617 | 22.9261
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | -16.6845 | -40.2513 | 40.2513 | 32.8319 | 16.6845 | 13.3789
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | -15.7401 | -37.973 | 37.973 | 30.9734 | 15.7401 | 12.6216
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | -0.076781 | -0.18523 | 0.18523 | 0.15109 | 0.076781 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | -20.9151 | -50.4577 | 50.4577 | 41.1569 | 20.9151 | 16.7714
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | -0.075199 | -0.18579 | 0.18579 | 0.15146 | 0.075199 | 0.061706 | north | 10 | Y | Y | mothballed | mothballed | -57.9032 | -143.0622 | 143.0622 | 116.6211 | 57.9032 | 47.5136
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8971 | -12.9521 | 12.9521 | 10.4488 | 3.8971 | 4.4097
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 4.3467
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | -3.8414 | -12.7671 | 12.7671 | 10.2996 | 3.8414 | 4.3467
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | -0.055673 | -0.18503 | 0.18503 | 0.14927 | 0.055673 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | -3.7858 | -12.582 | 12.582 | 10.1503 | 3.7858 | 4.2837
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.061476 | north | 3 | N | N | Nnorth | Nnorth | -89.6536 | -213.382 | 213.382 | 174.3379 | 89.6536 | 71.1277
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | -0.077488 | -0.18443 | 0.18443 | 0.15068 | 0.077488 | 0.061476 | north | 3 | N | N | Nnorth | Nnorth | -89.7311 | -213.5665 | 213.5665 | 174.4886 | 89.7311 | 71.1892
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | -15.2743 | -44.1589 | 44.1589 | 34.0946 | 15.2743 | 14.3615
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | -15.4107 | -44.5532 | 44.5532 | 34.399 | 15.4107 | 14.4898
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.063705 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5492 | -42.7648 | 42.7648 | 33.299 | 14.5492 | 13.7858
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | -0.067233 | -0.19762 | 0.19762 | 0.15388 | 0.067233 | 0.063705 | north | 9 | Y | Y | Ynorth | Ynorth | -14.5291 | -42.7055 | 42.7055 | 33.2528 | 14.5291 | 13.7667
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | -14.4561 | -41.7933 | 41.7933 | 32.2681 | 14.4561 | 13.5922
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | -0.068189 | -0.19714 | 0.19714 | 0.15221 | 0.068189 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | -14.3879 | -41.5961 | 41.5961 | 32.1159 | 14.3879 | 13.5281
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.061589 | north | 10 | Y | Y | Ynorth | Ynorth | -28.1449 | -74.3651 | 74.3651 | 60.8944 | 28.1449 | 24.3277
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | -0.070755 | -0.18787 | 0.18787 | 0.15451 | 0.070755 | 0.061452 | north | 12 | Y | Y | Ynorth | Ynorth | -30.7784 | -81.7239 | 81.7239 | 67.2127 | 30.7784 | 26.7316
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | -0.071253 | -0.18827 | 0.18827 | 0.15416 | 0.071253 | 0.061589 | north | 12 | Y | Y | Ynorth | Ynorth | -30.9951 | -81.8957 | 81.8957 | 67.0609 | 30.9951 | 26.7912
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | -0.0679 | -0.18166 | 0.18166 | 0.15871 | 0.0679 | 0.059032 | north | 11 | Y | Y | mothballed | mothballed | -9.3702 | -25.0692 | 25.0692 | 21.9027 | 9.3702 | 8.1464
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.059497 | north | 10 | Y | Y | Ynorth | Ynorth | -8.0157 | -21.6622 | 21.6622 | 18.777 | 8.0157 | 7.0206
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.059497 | north | 11 | Y | Y | Ynorth | Ynorth | -7.812 | -21.1115 | 21.1115 | 18.2996 | 7.812 | 6.8422
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | -0.06793 | -0.18358 | 0.18358 | 0.15913 | 0.06793 | 0.059497 | north | 10 | Y | Y | Ynorth | Ynorth | -37.7691 | -102.0694 | 102.0694 | 88.4746 | 37.7691 | 33.0803
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.058281 | north | 12 | Y | Y | Ynorth | Ynorth | -26.1621 | -69.9215 | 69.9215 | 62.4796 | 26.1621 | 22.613
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | -0.067428 | -0.18021 | 0.18021 | 0.16103 | 0.067428 | 0.058281 | north | 10 | Y | Y | Ynorth | Ynorth | -34.7254 | -92.8081 | 92.8081 | 82.9304 | 34.7254 | 30.0147
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | -50.9387 | -135.4078 | 135.4078 | 131.124 | 50.9387 | 43.3006
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | -51.5876 | -137.1327 | 137.1327 | 132.7944 | 51.5876 | 43.8522
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | -0.06489 | -0.17249 | 0.17249 | 0.16704 | 0.06489 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | -50.6142 | -134.5453 | 134.5453 | 130.2889 | 50.6142 | 43.0248
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.054175 | north | 10 | Y | Y | Ynorth | Ynorth | -11.6793 | -30.8819 | 30.8819 | 30.677 | 11.6793 | 9.8598
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | -0.064172 | -0.16968 | 0.16968 | 0.16856 | 0.064172 | 0.054175 | north | 10 | Y | Y | Ynorth | Ynorth | -31.0592 | -82.1256 | 82.1256 | 81.5806 | 31.0592 | 26.2207
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | -0.063087 | -0.17456 | 0.17456 | 0.16234 | 0.063087 | 0.058092 | north | 10 | Y | Y | Ynorth | Ynorth | -14.1315 | -39.1021 | 39.1021 | 36.3635 | 14.1315 | 13.0126
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | -0.064313 | -0.17063 | 0.17063 | 0.16846 | 0.064313 | 0.054401 | north | 6 | Y | N | Ynorth | Nnorth | -3.2157 | -8.5317 | 8.5317 | 8.4229 | 3.2157 | 2.7201
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | -0.064335 | -0.17069 | 0.17069 | 0.16838 | 0.064335 | 0.054433 | north | 7 | N | N | mothballed | mothballed | -2.7021 | -7.1689 | 7.1689 | 7.0721 | 2.7021 | 2.2862
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.04995 | north | 4 | Y | N | Ynorth | Nnorth | -37.4892 | -99.0882 | 99.0882 | 109.3648 | 37.4892 | 30.7192
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | -0.060958 | -0.16112 | 0.16112 | 0.17783 | 0.060958 | 0.04995 | north | 4 | Y | N | Ynorth | Nnorth | -35.7823 | -94.5769 | 94.5769 | 104.3856 | 35.7823 | 29.3207
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.096231 | north | 10 | Y | Y | mothballed | mothballed | -27.4751 | -163.9987 | 163.9987 | 61.8796 | 27.4751 | 51.676
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | -0.051164 | -0.3054 | 0.3054 | 0.11523 | 0.051164 | 0.096231 | north | 10 | Y | Y | Ynorth | Ynorth | -40.2661 | -240.3482 | 240.3482 | 90.6876 | 40.2661 | 75.7338
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.09236 | north | 11 | Y | Y | mothballed | mothballed | -3.6914 | -15.0405 | 15.0405 | 8.501 | 3.6914 | 6.927
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | -0.049219 | -0.20054 | 0.20054 | 0.11335 | 0.049219 | 0.09236 | north | 11 | Y | Y | mothballed | mothballed | -10.9266 | -44.5199 | 44.5199 | 25.163 | 10.9266 | 20.5039
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.14701 | south | 4 | Y | N | Ysouth | Nsouth | -19.655 | 197.7867 | -197.7867 | 16.6535 | 19.655 | -83.6504
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087025 | south | 10 | Y | Y | Ysouth | Ysouth | -3.0439 | 46.4266 | -46.4266 | -13.8174 | 3.0439 | -18.1882
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087025 | south | 10 | Y | Y | Ysouth | Ysouth | -3.1458 | 47.9816 | -47.9816 | -14.2802 | 3.1458 | -18.7974
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.014108 | 0.22204 | -0.22204 | -0.065865 | 0.014108 | -0.086999 | south | 10 | Y | Y | Ysouth | Ysouth | -5.742 | 90.3687 | -90.3687 | -26.8071 | 5.742 | -35.4086
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -4.0031
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -0.68451 | 10.4404 | -10.4404 | -3.1073 | 0.68451 | -4.0902
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -4.0031
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.014564 | 0.22214 | -0.22214 | -0.066112 | 0.014564 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -0.66994 | 10.2183 | -10.2183 | -3.0412 | 0.66994 | -4.0031
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.087255 | south | 4 | Y | N | Ysouth | Nsouth | -6.2837 | 94.3629 | -94.3629 | -27.9683 | 6.2837 | -36.9961
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.01482 | 0.22255 | -0.22255 | -0.065963 | 0.01482 | -0.087255 | south | 4 | Y | N | Ysouth | Nsouth | -6.2985 | 94.5854 | -94.5854 | -28.0343 | 6.2985 | -37.0834
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.086454 | south | 10 | Y | Y | Ysouth | Ysouth | -0.73863 | 12.8056 | -12.8056 | -3.8223 | 0.73863 | -5.0143
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.086454 | south | 10 | Y | Y | Ysouth | Ysouth | -1.1334 | 19.65 | -19.65 | -5.8652 | 1.1334 | -7.6944
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -3.804
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -0.56034 | 9.7146 | -9.7146 | -2.8996 | 0.56034 | -3.804
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -0.54761 | 9.4938 | -9.4938 | -2.8337 | 0.54761 | -3.7175
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.012735 | 0.22079 | -0.22079 | -0.065901 | 0.012735 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -0.57308 | 9.9354 | -9.9354 | -2.9655 | 0.57308 | -3.8904
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.087125 | south | 10 | Y | Y | Ysouth | Ysouth | -6.0061 | 91.6247 | -91.6247 | -27.1599 | 6.0061 | -35.8955
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.014578 | 0.22239 | -0.22239 | -0.065922 | 0.014578 | -0.087125 | south | 10 | Y | Y | Ysouth | Ysouth | -5.8312 | 88.956 | -88.956 | -26.3688 | 5.8312 | -34.85
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.086822 | south | 4 | Y | N | Ysouth | Nsouth | -9.0188 | 120.3772 | -120.3772 | -37.567 | 9.0188 | -47.4048
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.016518 | 0.22047 | -0.22047 | -0.068804 | 0.016518 | -0.086822 | south | 4 | Y | N | Ysouth | Nsouth | -12.3885 | 165.3533 | -165.3533 | -51.603 | 12.3885 | -65.1165
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -0.96459 | 13.615 | -13.615 | -4.0375 | 0.96459 | -5.3449
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -1.5022 | 21.2036 | -21.2036 | -6.2879 | 1.5022 | -8.324
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.015813 | 0.2232 | -0.2232 | -0.066188 | 0.015813 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -2.3878 | 33.7026 | -33.7026 | -9.9944 | 2.3878 | -13.2308
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -13.489
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7373 | 37.672 | -37.672 | -11.4847 | 2.7373 | -14.7944
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.016102 | 0.2216 | -0.2216 | -0.067557 | 0.016102 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -2.4958 | 34.348 | -34.348 | -10.4713 | 2.4958 | -13.489
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.071885 | south | 10 | Y | Y | Ysouth | Ysouth | -0.43655 | 3.9161 | -3.9161 | -2.2765 | 0.43655 | -1.5815
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.071885 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.79073
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.019843 | 0.178 | -0.178 | -0.10347 | 0.019843 | -0.071885 | south | 13 | Y | Y | Ysouth | Ysouth | -0.21827 | 1.958 | -1.958 | -1.1382 | 0.21827 | -0.79073
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97384 | 8.5698 | -8.5698 | -4.8928 | 0.97384 | -3.4546
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -0.76152 | 6.7013 | -6.7013 | -3.826 | 0.76152 | -2.7014
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -0.93914 | 8.2644 | -8.2644 | -4.7184 | 0.93914 | -3.3315
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.020416 | 0.17966 | -0.17966 | -0.10257 | 0.020416 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -0.97997 | 8.6237 | -8.6237 | -4.9236 | 0.97997 | -3.4763
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.90476
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -0.10498 | 2.0665 | -2.0665 | -0.98749 | 0.10498 | -0.82937
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077807 | south | 10 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.8674
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077807 | south | 11 | Y | Y | Ysouth | Ysouth | 0.33816 | 4.7131 | -4.7131 | -1.6207 | -0.33816 | -1.8674
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | 0.01409 | 0.19638 | -0.19638 | -0.067529 | -0.01409 | -0.077807 | south | 11 | Y | Y | Ysouth | Ysouth | 0.32407 | 4.5167 | -4.5167 | -1.5532 | -0.32407 | -1.7896
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.014111 | 0.20841 | -0.20841 | -0.076799 | 0.014111 | -0.082867 | south | 4 | Y | N | Ysouth | Nsouth | -5.588 | 82.5312 | -82.5312 | -30.4124 | 5.588 | -32.8153
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.0502 | houston | 3 | N | N | Nhouston | Nhouston | -42.6133 | 151.6301 | -151.6301 | -217.7735 | 42.6133 | -66.9166
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.031968 | 0.11375 | -0.11375 | -0.16337 | 0.031968 | -0.0502 | houston | 3 | N | N | Nhouston | Nhouston | -42.4535 | 151.0613 | -151.0613 | -216.9567 | 42.4535 | -66.6656
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | 0 | 0 | 0 | 0 | 0 | north | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -0.64847 | 7.0246 | -7.0246 | -3.6873 | 0.64847 | -2.829
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -0.32935 | 3.5677 | -3.5677 | -1.8728 | 0.32935 | -1.4368
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -0.25598 | 2.7729 | -2.7729 | -1.4555 | 0.25598 | -1.1167
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.017065 | 0.18486 | -0.18486 | -0.097034 | 0.017065 | -0.074448 | south | 13 | Y | Y | Ysouth | Ysouth | -0.80205 | 8.6883 | -8.6883 | -4.5606 | 0.80205 | -3.4991
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 54.1048 | -10.3076 | 10.3076 | 9.7097 | -54.1048 | 3.5044
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | 0 | 0 | 0 | 0 | 0 | west | 1 | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.68306 | -0.16121 | 0.16121 | 0.14206 | -0.68306 | 0.054915 | west | 6 | Y | N | Ywest | Nwest | 102.459 | -24.1812 | 24.1812 | 21.3093 | -102.459 | 8.2372
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.74044 | -0.15229 | 0.15229 | 0.13806 | -0.74044 | 0.052476 | west | 6 | Y | N | Ywest | Nwest | 125.5044 | -25.8138 | 25.8138 | 23.4017 | -125.5044 | 8.8947
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.58096 | -0.070376 | 0.070376 | 0.096938 | -0.58096 | 0.025139 | west | 6 | Y | N | Ywest | Nwest | 87.1434 | -10.5564 | 10.5564 | 14.5407 | -87.1434 | 3.7708
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.74313 | -0.15884 | 0.15884 | 0.1409 | -0.74313 | 0.054112 | west | 6 | Y | N | Ywest | Nwest | 46.8175 | -10.0067 | 10.0067 | 8.877 | -46.8175 | 3.4091
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.75077 | -0.17021 | 0.17021 | 0.14657 | -0.75077 | 0.057237 | west | 4 | Y | N | Ywest | Nwest | 487.774 | -110.5828 | 110.5828 | 95.2291 | -487.774 | 37.1869
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.058686 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 2.3474
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | -0.063906 | -0.18077 | 0.18077 | 0.15948 | 0.063906 | 0.058686 | north | 5 | N | N | Nnorth | Nnorth | -2.5562 | -7.2308 | 7.2308 | 6.3791 | 2.5562 | 2.3474
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | 0.001511 | 0.24948 | -0.24948 | -0.008371 | -0.001511 | -0.051993 | south | 10 | Y | Y | Ysouth | Ysouth | 0.63764 | 105.2822 | -105.2822 | -3.5326 | -0.63764 | -21.941
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -3.5256 | 36.8906 | -36.8906 | -3.6839 | 3.5256 | -12.067
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -3.579 | 37.4495 | -37.4495 | -3.7397 | 3.579 | -12.2499
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.026709 | 0.27947 | -0.27947 | -0.027908 | 0.026709 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -8.627 | 90.2701 | -90.2701 | -9.0143 | 8.627 | -29.5277
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -4.396 | 44.6235 | -44.6235 | -4.9129 | 4.396 | -19.2398
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -4.4517 | 45.1883 | -45.1883 | -4.975 | 4.4517 | -19.4834
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.027823 | 0.28243 | -0.28243 | -0.031094 | 0.027823 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -4.869 | 49.4247 | -49.4247 | -5.4414 | 4.869 | -21.3099
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.1043 | south | 4 | Y | N | Ysouth | Nsouth | -16.2107 | 146.7166 | -146.7166 | -30.7645 | 16.2107 | -60.9094
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.027758 | 0.25123 | -0.25123 | -0.052679 | 0.027758 | -0.1043 | south | 4 | Y | N | Ysouth | Nsouth | -16.516 | 149.4801 | -149.4801 | -31.344 | 16.516 | -62.0567
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.02775 | 0.25097 | -0.25097 | -0.052883 | 0.02775 | -0.10416 | south | 4 | Y | N | Ysouth | Nsouth | -12.0158 | 108.6717 | -108.6717 | -22.8983 | 12.0158 | -45.1021
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5727 | 54.9728 | -54.9728 | -11.7619 | 4.5727 | -21.8347
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -4.5952 | 55.2429 | -55.2429 | -11.8197 | 4.5952 | -21.942
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -4.587 | 55.1447 | -55.1447 | -11.7987 | 4.587 | -21.903
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.020423 | 0.24552 | -0.24552 | -0.052532 | 0.020423 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -4.6299 | 55.6603 | -55.6603 | -11.909 | 4.6299 | -22.1078
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.078023 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.62418
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.024621 | 0.29087 | -0.29087 | -0.016951 | 0.024621 | -0.078023 | south | 5 | N | N | Nsouth | Nsouth | -0.19697 | 2.3269 | -2.3269 | -0.13561 | 0.19697 | -0.62418
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.6637
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -0.050796 | 4.4546 | -4.4546 | 0.053334 | 0.050796 | -0.6637
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.002822 | 0.24748 | -0.24748 | 0.002963 | 0.002822 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -0.04233 | 3.7122 | -3.7122 | 0.044445 | 0.04233 | -0.55308
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | 0.00919 | 0.24394 | -0.24394 | 0.000948 | -0.00919 | -0.040318 | south | 5 | N | N | Nsouth | Nsouth | 0.1259 | 3.342 | -3.342 | 0.012988 | -0.1259 | -0.55236
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.056749 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.0215
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.004672 | 0.25913 | -0.25913 | -0.010073 | 0.004672 | -0.056749 | south | 5 | N | N | Nsouth | Nsouth | -0.084096 | 4.6644 | -4.6644 | -0.18131 | 0.084096 | -1.0215
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -2.3637
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -0.63556 | 9.5543 | -9.5543 | -0.47369 | 0.63556 | -2.2962
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.018693 | 0.28101 | -0.28101 | -0.013932 | 0.018693 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -0.65426 | 9.8353 | -9.8353 | -0.48762 | 0.65426 | -2.3637
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.051766 | south | 5 | N | N | Nsouth | Nsouth | -0.019068 | 7.0384 | -7.0384 | -0.22072 | 0.019068 | -1.4494
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.000681 | 0.25137 | -0.25137 | -0.007883 | 0.000681 | -0.051766 | south | 5 | N | N | Nsouth | Nsouth | -0.019749 | 7.2897 | -7.2897 | -0.22861 | 0.019749 | -1.5012
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.052155 | west | 6 | Y | N | Ywest | Nwest | 26.4032 | -5.3629 | 5.3629 | 4.8273 | -26.4032 | 1.8254
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.75438 | -0.15323 | 0.15323 | 0.13792 | -0.75438 | 0.052155 | west | 6 | Y | N | Ywest | Nwest | 22.6313 | -4.5968 | 4.5968 | 4.1377 | -22.6313 | 1.5647
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.6338
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.6338
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.6338
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.027316 | 0.25402 | -0.25402 | -0.047007 | 0.027316 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1.3658 | 12.7009 | -12.7009 | -2.3504 | 1.3658 | -4.6338
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.01911 | 0.25171 | -0.25171 | -0.044951 | 0.01911 | -0.090903 | south | 5 | N | N | Nsouth | Nsouth | -0.11466 | 1.5102 | -1.5102 | -0.26971 | 0.11466 | -0.54542
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.21844
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -0.047174 | 0.57024 | -0.57024 | -0.13747 | 0.047174 | -0.21844
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.019656 | 0.2376 | -0.2376 | -0.057279 | 0.019656 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -0.055037 | 0.66528 | -0.66528 | -0.16038 | 0.055037 | -0.25485
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.018373 | 0.23413 | -0.23413 | -0.059392 | 0.018373 | -0.090819 | south | 5 | N | N | Nsouth | Nsouth | -0.073492 | 0.93652 | -0.93652 | -0.23757 | 0.073492 | -0.36328
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.088608 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.21266
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.020848 | 0.23434 | -0.23434 | -0.060147 | 0.020848 | -0.088608 | south | 5 | N | N | Nsouth | Nsouth | -0.050035 | 0.56242 | -0.56242 | -0.14435 | 0.050035 | -0.21266
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -13.2838
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -2.5817 | 31.4919 | -31.4919 | -8.9129 | 2.5817 | -12.4705
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6191 | 31.9483 | -31.9483 | -9.042 | 2.6191 | -12.6512
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7501 | 33.5457 | -33.5457 | -9.4941 | 2.7501 | -13.2838
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4049 | 41.5328 | -41.5328 | -11.7547 | 3.4049 | -16.4466
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.018708 | 0.2282 | -0.2282 | -0.064586 | 0.018708 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -3.7042 | 45.184 | -45.184 | -12.788 | 3.7042 | -17.8925
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -4.047 | 43.3797 | -43.3797 | -4.3186 | 4.047 | -17.9483
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9674 | 42.5263 | -42.5263 | -4.2337 | 3.9674 | -17.5953
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.026538 | 0.28446 | -0.28446 | -0.028319 | 0.026538 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -6.1727 | 66.1647 | -66.1647 | -6.587 | 6.1727 | -27.3756
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -2.7797 | 33.6027 | -33.6027 | -8.3394 | 2.7797 | -13.3143
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8384 | 34.3127 | -34.3127 | -8.5156 | 2.8384 | -13.5956
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9558 | 35.7325 | -35.7325 | -8.8679 | 2.9558 | -14.1582
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.019575 | 0.23664 | -0.23664 | -0.058728 | 0.019575 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -5.6768 | 68.6253 | -68.6253 | -17.0311 | 5.6768 | -27.1913
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.043138 | south | 5 | N | N | Nsouth | Nsouth | 6.8307 | 3.4819 | -3.4819 | -0.40969 | -6.8307 | -1.4236
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.043138 | south | 5 | N | N | Nsouth | Nsouth | 5.1748 | 2.6378 | -2.6378 | -0.31038 | -5.1748 | -1.0784
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.009544 | 0.18786 | -0.18786 | -0.089772 | 0.009544 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -0.11453 | 2.2543 | -2.2543 | -1.0773 | 0.11453 | -0.90476
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.020961 | 0.18005 | -0.18005 | -0.10261 | 0.020961 | -0.07246 | south | 7 | N | N | Nsouth | Nsouth | -1.5302 | 13.1437 | -13.1437 | -7.4902 | 1.5302 | -5.2896
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.4059
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1.8514 | 13.6104 | -13.6104 | -9.1677 | 1.8514 | -5.5427
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.60421 | 4.8833 | -4.8833 | -3.008 | 0.60421 | -1.977
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.49424
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1.8057 | 13.2744 | -13.2744 | -8.9414 | 1.8057 | -5.4059
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1.8286 | 13.4424 | -13.4424 | -9.0546 | 1.8286 | -5.4743
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1.792 | 13.1736 | -13.1736 | -8.8735 | 1.792 | -5.3648
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -0.57142 | 4.2008 | -4.2008 | -2.8295 | 0.57142 | -1.7107
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1.0514 | 7.7294 | -7.7294 | -5.2064 | 1.0514 | -3.1477
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.018284 | 0.1909 | -0.1909 | -0.092759 | 0.018284 | -0.076364 | south | 4 | Y | N | Ysouth | Nsouth | -11.5006 | 120.073 | -120.073 | -58.3454 | 11.5006 | -48.033
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.073142 | south | 9 | Y | Y | Ysouth | Ysouth | -2.9798 | 26.2238 | -26.2238 | -14.5179 | 2.9798 | -10.5324
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.020693 | 0.18211 | -0.18211 | -0.10082 | 0.020693 | -0.073142 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8903 | 34.2367 | -34.2367 | -18.954 | 3.8903 | -13.7507
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.020653 | 0.21995 | -0.21995 | -0.071066 | 0.020653 | -0.084188 | south | 5 | N | N | Nsouth | Nsouth | -0.24784 | 2.6394 | -2.6394 | -0.85279 | 0.24784 | -1.0103
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | 0.14569 | 0.13377 | -0.13377 | -0.030419 | -0.14569 | -0.053953 | south | 5 | N | N | Nsouth | Nsouth | 0.87415 | 0.80263 | -0.80263 | -0.18251 | -0.87415 | -0.32372
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | 0 | 0 | 0 | 0 | 0 | south | 10 | Y | Y | mothballed | mothballed | 0 | 0 | 0 | 0 | 0 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.073743 | south | 9 | Y | Y | Ysouth | Ysouth | -6.0887 | 61.4403 | -61.4403 | -33.349 | 6.0887 | -24.7776
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | 0 | 0 | 0 | 0 | 0 | south | 7 | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073893 | south | 10 | Y | Y | Ysouth | Ysouth | -6.016 | 61.2169 | -61.2169 | -33.0172 | 6.016 | -24.6803
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073893 | south | 10 | Y | Y | Ysouth | Ysouth | -6.1241 | 62.3166 | -62.3166 | -33.6104 | 6.1241 | -25.1236
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.01787 | 0.18355 | -0.18355 | -0.098538 | 0.01787 | -0.073972 | south | 7 | N | N | Nsouth | Nsouth | -0.67906 | 6.9748 | -6.9748 | -3.7444 | 0.67906 | -2.8109
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.073907 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8477
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.017943 | 0.18335 | -0.18335 | -0.098743 | 0.017943 | -0.073907 | south | 7 | N | N | Nsouth | Nsouth | -0.44858 | 4.5838 | -4.5838 | -2.4686 | 0.44858 | -1.8477
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.017938 | 0.18354 | -0.18354 | -0.098604 | 0.017938 | -0.073977 | south | 7 | N | N | Nsouth | Nsouth | -0.68164 | 6.9743 | -6.9743 | -3.747 | 0.68164 | -2.8111
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.01758 | 0.18443 | -0.18443 | -0.097688 | 0.01758 | -0.0743 | south | 7 | N | N | Nsouth | Nsouth | -0.50982 | 5.3486 | -5.3486 | -2.833 | 0.50982 | -2.1547
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -2.6865 | 27.1211 | -27.1211 | -14.7161 | 2.6865 | -10.9373
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -2.6919 | 27.176 | -27.176 | -14.7459 | 2.6919 | -10.9594
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.018115 | 0.18288 | -0.18288 | -0.099232 | 0.018115 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -2.7716 | 27.9806 | -27.9806 | -15.1825 | 2.7716 | -11.2839
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -2.9516 | 28.5884 | -28.5884 | -15.9743 | 2.9516 | -11.5457
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -2.8582 | 27.6837 | -27.6837 | -15.4688 | 2.8582 | -11.1803
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1.8681 | 18.0939 | -18.0939 | -10.1103 | 1.8681 | -7.3074
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -2.7087 | 26.2362 | -26.2362 | -14.6599 | 2.7087 | -10.5957
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -2.7461 | 26.598 | -26.598 | -14.8621 | 2.7461 | -10.7419
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -2.3725 | 22.9793 | -22.9793 | -12.8401 | 2.3725 | -9.2804
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2683 | 27.1881 | -27.1881 | -13.9809 | 2.2683 | -10.9409
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -2.2899 | 27.4479 | -27.4479 | -14.1145 | 2.2899 | -11.0455
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.015483 | 0.18558 | -0.18558 | -0.095433 | 0.015483 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -2.6786 | 32.106 | -32.106 | -16.5099 | 2.6786 | -12.92
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -3.4097 | 38.3403 | -38.3403 | -19.9473 | 3.4097 | -15.4356
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -3.5695 | 40.137 | -40.137 | -20.8821 | 3.5695 | -16.1589
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.016472 | 0.18522 | -0.18522 | -0.096364 | 0.016472 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -3.9862 | 44.823 | -44.823 | -23.3201 | 3.9862 | -18.0455
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.7375
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -2.3723 | 26.6707 | -26.6707 | -13.8774 | 2.3723 | -10.7375
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.016474 | 0.18521 | -0.18521 | -0.096371 | 0.016474 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -2.8171 | 31.6714 | -31.6714 | -16.4794 | 2.8171 | -12.7508
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.082468 | south | 10 | Y | Y | Ysouth | Ysouth | -7.812 | 90.5445 | -90.5445 | -5.3097 | 7.812 | -25.5651
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.0252 | 0.29208 | -0.29208 | -0.017128 | 0.0252 | -0.082468 | south | 10 | Y | Y | Ysouth | Ysouth | -10.4076 | 120.6286 | -120.6286 | -7.0739 | 10.4076 | -34.0593
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1.082 | 12.3985 | -12.3985 | -0.6476 | 1.082 | -3.5329
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -3.7011
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1336 | 12.9889 | -12.9889 | -0.67844 | 1.1336 | -3.7011
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.025763 | 0.2952 | -0.2952 | -0.015419 | 0.025763 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2109 | 13.8745 | -13.8745 | -0.72469 | 1.2109 | -3.9535
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.2226 | 14.1506 | -14.1506 | -0.96824 | 1.2226 | -4.2063
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -3.9488
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1477 | 13.2842 | -13.2842 | -0.90896 | 1.1477 | -3.9488
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1727 | 13.573 | -13.573 | -0.92872 | 1.1727 | -4.0346
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 9 | Y | Y | Ysouth | Ysouth | -3.8425 | 44.4734 | -44.4734 | -3.043 | 3.8425 | -13.2198
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 9 | Y | Y | Ysouth | Ysouth | -3.6927 | 42.7406 | -42.7406 | -2.9245 | 3.6927 | -12.7048
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -4.1205
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.024951 | 0.28879 | -0.28879 | -0.01976 | 0.024951 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1.1976 | 13.8618 | -13.8618 | -0.94848 | 1.1976 | -4.1205
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.7149
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 53.3893 | -10.9136 | 10.9136 | 9.7551 | -53.3893 | 3.7149
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 70.7789 | -14.4684 | 14.4684 | 12.9324 | -70.7789 | 4.9249
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 4.2456
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 61.0163 | -12.4727 | 12.4727 | 11.1486 | -61.0163 | 4.2456
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.7627 | -0.15591 | 0.15591 | 0.13936 | -0.7627 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 87.711 | -17.9295 | 17.9295 | 16.0262 | -87.711 | 6.103
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 158.7789 | -32.4546 | 32.4546 | 29.0112 | -158.7789 | 11.0471
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 108.3693 | -22.1508 | 22.1508 | 19.8006 | -108.3693 | 7.5398
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 100.9718 | -20.6388 | 20.6388 | 18.449 | -100.9718 | 7.0251
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 103.7173 | -21.2 | 21.2 | 18.9506 | -103.7173 | 7.2162
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 112.1062 | -22.9147 | 22.9147 | 20.4834 | -112.1062 | 7.7998
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.76263 | -0.15588 | 0.15588 | 0.13934 | -0.76263 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 160.1517 | -32.7352 | 32.7352 | 29.262 | -160.1517 | 11.1426
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 163.9137 | -33.6705 | 33.6705 | 29.6839 | -163.9137 | 11.43
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 99.2109 | -20.3795 | 20.3795 | 17.9665 | -99.2109 | 6.9182
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 195.2847 | -40.1146 | 40.1146 | 35.365 | -195.2847 | 13.6176
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.78428 | -0.1611 | 0.1611 | 0.14203 | -0.78428 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 154.5024 | -31.7373 | 31.7373 | 27.9795 | -154.5024 | 10.7737
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 153.942 | -31.6734 | 31.6734 | 28.1338 | -153.942 | 10.781
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.76971 | -0.15837 | 0.15837 | 0.14067 | -0.76971 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 93.8276 | -19.3049 | 19.3049 | 17.1476 | -93.8276 | 6.571
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.75382 | -0.1537 | 0.1537 | 0.13818 | -0.75382 | 0.052322 | west | 6 | Y | N | Ywest | Nwest | 112.3186 | -22.9016 | 22.9016 | 20.5884 | -112.3186 | 7.796
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.053787 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 9.6817
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.7458 | -0.1579 | 0.1579 | 0.14041 | -0.7458 | 0.053787 | west | 6 | Y | N | Ywest | Nwest | 134.244 | -28.4225 | 28.4225 | 25.2742 | -134.244 | 9.6817
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.74615 | -0.15776 | 0.15776 | 0.14033 | -0.74615 | 0.053736 | west | 6 | Y | N | Ywest | Nwest | 167.8828 | -35.4949 | 35.4949 | 31.5752 | -167.8828 | 12.0906
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.054383 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.7979
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.77581 | -0.15993 | 0.15993 | 0.14147 | -0.77581 | 0.054383 | west | 6 | Y | N | Ywest | Nwest | 96.9765 | -19.9916 | 19.9916 | 17.6833 | -96.9765 | 6.7979
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | -9.4143 | -25.2669 | 25.2669 | 22.4067 | 9.4143 | 8.1907
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | -9.4815 | -25.4474 | 25.4474 | 22.5668 | 9.4815 | 8.2492
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | -20.7787 | -55.7677 | 55.7677 | 49.4548 | 20.7787 | 18.078
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | -9.616 | -25.8084 | 25.8084 | 22.8869 | 9.616 | 8.3662
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | -9.6833 | -25.9888 | 25.9888 | 23.0469 | 9.6833 | 8.4247
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | -0.067245 | -0.18048 | 0.18048 | 0.16005 | 0.067245 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | -20.8459 | -55.9482 | 55.9482 | 49.6149 | 20.8459 | 18.1365
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.060703 | north | 9 | Y | Y | Ynorth | Ynorth | -12.729 | -35.7757 | 35.7757 | 30.9165 | 12.729 | 11.8978
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | -0.064944 | -0.18253 | 0.18253 | 0.15774 | 0.064944 | 0.060703 | north | 9 | Y | Y | Ynorth | Ynorth | -7.2088 | -20.2607 | 20.2607 | 17.5088 | 7.2088 | 6.738
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | -0.068725 | -0.18176 | 0.18176 | 0.15908 | 0.068725 | 0.058998 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 9.2873
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 9.4603
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9906 | -29.3055 | 29.3055 | 26.5862 | 10.9906 | 9.4603
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -27.7446 | -73.9785 | 73.9785 | 67.114 | 27.7446 | 23.8816
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -10.8566 | -28.9481 | 28.9481 | 26.262 | 10.8566 | 9.345
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -10.7896 | -28.7694 | 28.7694 | 26.0999 | 10.7896 | 9.2873
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9236 | -29.1268 | 29.1268 | 26.4241 | 10.9236 | 9.4027
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | -0.067016 | -0.17869 | 0.17869 | 0.16211 | 0.067016 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | -27.4095 | -73.085 | 73.085 | 66.3034 | 27.4095 | 23.5932
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.058518 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | -0.067531 | -0.18094 | 0.18094 | 0.1607 | 0.067531 | 0.058518 | north | #N/A | N | N | Nnorth | Nnorth | 0 | 0 | 0 | 0 | 0 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | -9.5608 | -25.4156 | 25.4156 | 24.8276 | 9.5608 | 8.1137
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | -8.398 | -22.3245 | 22.3245 | 21.808 | 8.398 | 7.1269
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | -9.367 | -24.9004 | 24.9004 | 24.3243 | 9.367 | 7.9492
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | -0.0646 | -0.17173 | 0.17173 | 0.16775 | 0.0646 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | -25.7754 | -68.5191 | 68.5191 | 66.9338 | 25.7754 | 21.874
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | -9.2822 | -24.5757 | 24.5757 | 26.5422 | 9.2822 | 7.6562
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3007 | -24.6246 | 24.6246 | 26.595 | 9.3007 | 7.6714
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | -0.061594 | -0.16308 | 0.16308 | 0.17613 | 0.061594 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9268 | -28.9299 | 28.9299 | 31.2448 | 10.9268 | 9.0126
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3401 | -24.7436 | 24.7436 | 26.6346 | 9.3401 | 7.7207
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | -9.3894 | -24.8742 | 24.8742 | 26.7753 | 9.3894 | 7.7615
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | -0.061651 | -0.16332 | 0.16332 | 0.17581 | 0.061651 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | -10.9431 | -28.99 | 28.99 | 31.2056 | 10.9431 | 9.0458
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.034543 | 0.3476 | -0.3476 | 0.029268 | 0.034543 | -0.14701 | south | 4 | Y | N | Ysouth | Nsouth | -20.0695 | 201.9579 | -201.9579 | 17.0047 | 20.0695 | -85.4146
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 27.2506
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | -46.1862 | -96.4662 | 96.4662 | 180.1075 | 46.1862 | 27.2506
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | -0.049561 | -0.053677 | 0.053677 | 0.22603 | 0.049561 | 0.011556 | north | 7 | N | N | Nnorth | Nnorth | -1.586 | -1.7177 | 1.7177 | 7.233 | 1.586 | 0.36979
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.010031 | north | 13 | Y | Y | Ynorth | Ynorth | -2.3761 | -2.3301 | 2.3301 | 10.562 | 2.3761 | 0.48149
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.010031 | north | 13 | Y | Y | Ynorth | Ynorth | -2.2771 | -2.233 | 2.233 | 10.1219 | 2.2771 | 0.46143
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | -0.59509 | -0.64532 | 0.64532 | 2.7061 | 0.59509 | 0.13928
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | -2.5291 | -2.7426 | 2.7426 | 11.5008 | 2.5291 | 0.59196
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011607 | north | 13 | Y | Y | Ynorth | Ynorth | -0.84305 | -0.91421 | 0.91421 | 3.8336 | 0.84305 | 0.19732
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | -1.091 | -1.1831 | 1.1831 | 4.9611 | 1.091 | 0.25535
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | -0.049591 | -0.053777 | 0.053777 | 0.22551 | 0.049591 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | -1.2398 | -1.3444 | 1.3444 | 5.6376 | 1.2398 | 0.29018
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | -0.049503 | -0.048543 | 0.048543 | 0.22004 | 0.049503 | 0.010031 | north | 11 | Y | Y | Ynorth | Ynorth | -5.1978 | -5.097 | 5.097 | 23.1044 | 5.1978 | 1.0533
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.72883 | -0.15942 | 0.15942 | 0.14119 | -0.72883 | 0.054305 | west | 6 | Y | N | Ywest | Nwest | 61.222 | -13.3914 | 13.3914 | 11.8598 | -61.222 | 4.5616
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.72081 | -0.13715 | 0.13715 | 0.12931 | -0.72081 | 0.046628 | west | 6 | Y | N | Ywest | Nwest | 57.6648 | -10.9724 | 10.9724 | 10.3449 | -57.6648 | 3.7302
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.046578 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 6.9867
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.7205 | -0.13701 | 0.13701 | 0.12923 | -0.7205 | 0.046578 | west | 6 | Y | N | Ywest | Nwest | 108.075 | -20.5515 | 20.5515 | 19.3849 | -108.075 | 6.9867
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -2.7187 | 3.6863 | -3.6863 | -13.0783 | 2.7187 | -1.9779
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -2.5613 | 3.4729 | -3.4729 | -12.321 | 2.5613 | -1.8633
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -2.0352 | 2.7596 | -2.7596 | -9.7903 | 2.0352 | -1.4806
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -5.8829 | 7.9767 | -7.9767 | -28.2994 | 5.8829 | -4.2798
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -5.8944 | 7.9923 | -7.9923 | -28.3548 | 5.8944 | -4.2882
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -5.8483 | 7.9298 | -7.9298 | -28.1332 | 5.8483 | -4.2547
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -3.6864 | 4.9984 | -4.9984 | -17.7333 | 3.6864 | -2.6819
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -9.3696 | 12.7043 | -12.7043 | -45.0722 | 9.3696 | -6.8164
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.0384 | 0.052067 | -0.052067 | -0.18472 | 0.0384 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1.536 | 2.0827 | -2.0827 | -7.3889 | 1.536 | -1.1174
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -3.8511 | 5.2263 | -5.2263 | -18.5312 | 3.8511 | -2.8034
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -3.567 | 4.8407 | -4.8407 | -17.164 | 3.567 | -2.5966
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -3.9433 | 5.3514 | -5.3514 | -18.9746 | 3.9433 | -2.8705
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.038396 | 0.052107 | -0.052107 | -0.18476 | 0.038396 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -3.9164 | 5.3149 | -5.3149 | -18.8453 | 3.9164 | -2.8509
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.02795 | houston | 7 | N | N | Nhouston | Nhouston | -1.2287 | 1.6674 | -1.6674 | -5.9122 | 1.2287 | -0.8944
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.038396 | 0.052105 | -0.052105 | -0.18476 | 0.038396 | -0.02795 | houston | 7 | N | N | Nhouston | Nhouston | -1.1519 | 1.5632 | -1.5632 | -5.5427 | 1.1519 | -0.8385
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -4.0832
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -3.9865 | 8.5216 | -8.5216 | -20.5601 | 3.9865 | -4.0832
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -4.2738 | 9.1357 | -9.1357 | -22.0419 | 4.2738 | -4.3775
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.035914 | 0.076771 | -0.076771 | -0.18523 | 0.035914 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -3.9326 | 8.4064 | -8.4064 | -20.2822 | 3.9326 | -4.0281
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | -8.2271 | -17.1834 | 17.1834 | 32.0823 | 8.2271 | 4.8541
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | -0.054019 | -0.11283 | 0.11283 | 0.21065 | 0.054019 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | -8.2649 | -17.2624 | 17.2624 | 32.2298 | 8.2649 | 4.8764
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.03988 | 0.037034 | -0.037034 | -0.16969 | 0.03988 | -0.022488 | houston | 8 | N | N | Nhouston | Nhouston | -5.4237 | 5.0366 | -5.0366 | -23.0778 | 5.4237 | -3.0584
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.037573 | 0.060296 | -0.060296 | -0.18455 | 0.037573 | -0.030886 | houston | 7 | N | N | Nhouston | Nhouston | -1.2399 | 1.9898 | -1.9898 | -6.0901 | 1.2399 | -1.0192
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.94311
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.6747 | 1.5517 | -1.5517 | -6.9206 | 1.6747 | -0.94311
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.85329
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.039874 | 0.036946 | -0.036946 | -0.16478 | 0.039874 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.5152 | 1.4039 | -1.4039 | -6.2615 | 1.5152 | -0.85329
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.038249 | houston | 7 | N | N | Nhouston | Nhouston | -2.5177 | 5.7319 | -5.7319 | -13.0572 | 2.5177 | -2.7157
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.035461 | 0.080731 | -0.080731 | -0.1839 | 0.035461 | -0.038249 | houston | 7 | N | N | Nhouston | Nhouston | -0.35461 | 0.80731 | -0.80731 | -1.839 | 0.35461 | -0.38249
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -5.1332
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -6.1158 | 10.0731 | -10.0731 | -34.7829 | 6.1158 | -5.1332
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.03752 | 0.061798 | -0.061798 | -0.21339 | 0.03752 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -9.1924 | 15.1405 | -15.1405 | -52.281 | 9.1924 | -7.7155
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.5939
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -2.3592 | 2.5588 | -2.5588 | -10.3269 | 2.3592 | -1.4713
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.5939
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.03932 | 0.042647 | -0.042647 | -0.17211 | 0.03932 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -2.5558 | 2.7721 | -2.7721 | -11.1875 | 2.5558 | -1.5939
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.023194 | houston | 7 | N | N | Nhouston | Nhouston | -5.9122 | 5.8089 | -5.8089 | -24.9764 | 5.9122 | -3.4559
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.039679 | 0.038986 | -0.038986 | -0.16763 | 0.039679 | -0.023194 | houston | 7 | N | N | Nhouston | Nhouston | -2.5831 | 2.538 | -2.538 | -10.9125 | 2.5831 | -1.5099
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -3.5685 | 3.9813 | -3.9813 | -15.8327 | 3.5685 | -2.2677
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -3.4351 | 3.8325 | -3.8325 | -15.2412 | 3.4351 | -2.183
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -3.4116 | 3.8062 | -3.8062 | -15.1368 | 3.4116 | -2.168
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -2.1372 | 2.3844 | -2.3844 | -9.4822 | 2.1372 | -1.3581
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.039214 | 0.04375 | -0.04375 | -0.17399 | 0.039214 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -0.47841 | 0.53375 | -0.53375 | -2.1226 | 0.47841 | -0.30402
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.040313 | 0.032352 | -0.032352 | -0.15833 | 0.040313 | -0.020789 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.9526 | 24.0375 | -24.0375 | -117.6414 | 29.9526 | -15.4462
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.040135 | 0.034216 | -0.034216 | -0.16085 | 0.040135 | -0.021465 | houston | 10 | Y | Y | Yhouston | Yhouston | -29.4992 | 25.1488 | -25.1488 | -118.2255 | 29.4992 | -15.7768
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -3.5406
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -3.5406
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.040365 | 0.03179 | -0.03179 | -0.15775 | 0.040365 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -6.9428 | 5.4679 | -5.4679 | -27.1335 | 6.9428 | -3.5406
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -7.1553 | 3.7102 | -3.7102 | -22.2035 | 7.1553 | -2.9123
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.022354 | houston | 7 | N | N | Nhouston | Nhouston | -6.9053 | 6.3429 | -6.3429 | -29.1642 | 6.9053 | -3.8672
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.039915 | 0.036664 | -0.036664 | -0.16858 | 0.039915 | -0.022354 | houston | 8 | N | N | Nhouston | Nhouston | -5.3885 | 4.9496 | -4.9496 | -22.7582 | 5.3885 | -3.0178
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -6.5919 | 4.9608 | -4.9608 | -25.0785 | 6.5919 | -3.2736
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -6.5352 | 4.9182 | -4.9182 | -24.8629 | 6.5352 | -3.2454
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -6.434 | 4.842 | -4.842 | -24.4778 | 6.434 | -3.1952
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.040491 | 0.030472 | -0.030472 | -0.15404 | 0.040491 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -10.9002 | 8.2031 | -8.2031 | -41.4689 | 10.9002 | -5.4131
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -2.5402 | 2.4872 | -2.4872 | -10.7062 | 2.5402 | -1.4815
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -2.5084 | 2.4561 | -2.4561 | -10.5724 | 2.5084 | -1.463
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -3.2784 | 3.2101 | -3.2101 | -13.8177 | 3.2784 | -1.9121
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.03969 | 0.038863 | -0.038863 | -0.16728 | 0.03969 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -2.9212 | 2.8603 | -2.8603 | -12.3122 | 2.9212 | -1.7038
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -6.4567 | 6.5332 | -6.5332 | -27.4262 | 6.4567 | -3.8471
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -6.2153 | 6.289 | -6.289 | -26.4011 | 6.2153 | -3.7033
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -6.2312 | 6.305 | -6.305 | -26.4683 | 6.2312 | -3.7127
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -6.2114 | 6.285 | -6.285 | -26.3843 | 6.2114 | -3.701
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.039563 | 0.040032 | -0.040032 | -0.16805 | 0.039563 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -10.6424 | 10.7686 | -10.7686 | -45.2063 | 10.6424 | -6.3411
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.020825 | houston | 7 | N | N | Nhouston | Nhouston | -0.20154 | 0.16225 | -0.16225 | -0.79155 | 0.20154 | -0.10412
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.040308 | 0.03245 | -0.03245 | -0.15831 | 0.040308 | -0.020825 | houston | 7 | N | N | Nhouston | Nhouston | -0.84647 | 0.68145 | -0.68145 | -3.3245 | 0.84647 | -0.43733
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | -7.4224 | -7.9398 | 7.9398 | 34.4191 | 7.4224 | 1.4856
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.5029
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | -7.5091 | -8.0324 | 8.0324 | 34.8209 | 7.5091 | 1.5029
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | -0.048135 | -0.05149 | 0.05149 | 0.22321 | 0.048135 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | -18.2913 | -19.5662 | 19.5662 | 84.8202 | 18.2913 | 3.6609
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.040549 | 0.030015 | -0.030015 | -0.15207 | 0.040549 | -0.019943 | houston | 12 | Y | Y | Yhouston | Yhouston | -16.1385 | 11.946 | -11.946 | -60.5219 | 16.1385 | -7.9373
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.1009
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.1009
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1.8176 | 1.8863 | -1.8863 | -8.8256 | 1.8176 | -1.1009
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.3163
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1732 | 2.2554 | -2.2554 | -10.5523 | 2.1732 | -1.3163
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.039513 | 0.041007 | -0.041007 | -0.19186 | 0.039513 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1337 | 2.2144 | -2.2144 | -10.3604 | 2.1337 | -1.2923
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.039111 | north | 4 | Y | N | Ynorth | Nnorth | -46.1574 | -110.278 | 110.278 | 163.5219 | 46.1574 | 32.3448
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | -0.055813 | -0.13335 | 0.13335 | 0.19773 | 0.055813 | 0.039111 | north | 4 | Y | N | Ynorth | Nnorth | -45.7108 | -109.2112 | 109.2112 | 161.9401 | 45.7108 | 32.0319
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.037357 | 0.062437 | -0.062437 | -0.18499 | 0.037357 | -0.031657 | houston | 7 | N | N | Nhouston | Nhouston | -1.7222 | 2.8783 | -2.8783 | -8.5279 | 1.7222 | -1.4594
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -3.7734
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.4623 | 8.5873 | -8.5873 | -11.9939 | 2.4623 | -3.7734
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.4019 | 11.8641 | -11.8641 | -16.5706 | 3.4019 | -5.2133
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -3.6741
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3975 | 8.3613 | -8.3613 | -11.6783 | 2.3975 | -3.6741
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.032399 | 0.11299 | -0.11299 | -0.15782 | 0.032399 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -3.3047 | 11.5251 | -11.5251 | -16.0971 | 3.3047 | -5.0643
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -7.1453 | 6.9892 | -6.9892 | -30.1621 | 7.1453 | -4.1647
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -6.2958 | 6.1583 | -6.1583 | -26.5761 | 6.2958 | -3.6695
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.039696 | 0.038829 | -0.038829 | -0.16757 | 0.039696 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -6.2323 | 6.0962 | -6.0962 | -26.308 | 6.2323 | -3.6325
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.039625 | 0.039574 | -0.039574 | -0.16914 | 0.039625 | -0.023407 | houston | 7 | N | N | Nhouston | Nhouston | -1.3869 | 1.3851 | -1.3851 | -5.9199 | 1.3869 | -0.81925
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.038936 | 0.046563 | -0.046563 | -0.17713 | 0.038936 | -0.025941 | houston | 10 | Y | Y | mothballed | mothballed | -17.8716 | 21.3724 | -21.3724 | -81.3027 | 17.8716 | -11.9069
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -2.6203 | 2.1085 | -2.1085 | -10.1467 | 2.6203 | -1.3534
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -2.6607 | 2.1409 | -2.1409 | -10.3028 | 2.6607 | -1.3742
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -2.8219 | 2.2707 | -2.2707 | -10.9272 | 2.8219 | -1.4575
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -2.5397 | 2.0436 | -2.0436 | -9.8345 | 2.5397 | -1.3117
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -2.4994 | 2.0112 | -2.0112 | -9.6784 | 2.4994 | -1.2909
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -4.1926 | 3.3736 | -3.3736 | -16.2347 | 4.1926 | -2.1654
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.040313 | 0.032438 | -0.032438 | -0.1561 | 0.040313 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -2.3785 | 1.9138 | -1.9138 | -9.2101 | 2.3785 | -1.2284
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -6.4522 | 3.3456 | -3.3456 | -20.0217 | 6.4522 | -2.6261
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5924
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -6.3694 | 3.3027 | -3.3027 | -19.765 | 6.3694 | -2.5924
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.04136 | 0.021446 | -0.021446 | -0.12834 | 0.04136 | -0.016834 | houston | 7 | N | N | Nhouston | Nhouston | -6.7003 | 3.4743 | -3.4743 | -20.7917 | 6.7003 | -2.7271
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.040355 | 0.032012 | -0.032012 | -0.15539 | 0.040355 | -0.020666 | houston | 8 | N | N | Nhouston | Nhouston | -6.3357 | 5.0259 | -5.0259 | -24.3967 | 6.3357 | -3.2446
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -2.823 | 2.7076 | -2.7076 | -11.8204 | 2.823 | -1.6248
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -2.8628 | 2.7457 | -2.7457 | -11.9869 | 2.8628 | -1.6477
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1.5507 | 1.4873 | -1.4873 | -6.4929 | 1.5507 | -0.89251
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.039761 | 0.038135 | -0.038135 | -0.16648 | 0.039761 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1.1928 | 1.1441 | -1.1441 | -4.9946 | 1.1928 | -0.68655
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.023778 | houston | 8 | N | N | Nhouston | Nhouston | -3.0826 | 3.1666 | -3.1666 | -13.2 | 3.0826 | -1.8547
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.03952 | 0.040598 | -0.040598 | -0.16923 | 0.03952 | -0.023778 | houston | 8 | N | N | Nhouston | Nhouston | -3.1616 | 3.2478 | -3.2478 | -13.5385 | 3.1616 | -1.9022
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.039689 | 0.038872 | -0.038872 | -0.16726 | 0.039689 | -0.023153 | houston | 7 | N | N | Nhouston | Nhouston | -0.64296 | 0.62973 | -0.62973 | -2.7096 | 0.64296 | -0.37508
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.039675 | 0.039015 | -0.039015 | -0.16754 | 0.039675 | -0.023204 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.5464 | 6.4375 | -6.4375 | -27.6444 | 6.5464 | -3.8287
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.039672 | 0.039055 | -0.039055 | -0.16761 | 0.039672 | -0.023219 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.7046 | 6.6003 | -6.6003 | -28.3261 | 6.7046 | -3.924
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.039687 | 0.038885 | -0.038885 | -0.16723 | 0.039687 | -0.023157 | houston | 12 | Y | Y | Yhouston | Yhouston | -8.4533 | 8.2825 | -8.2825 | -35.6198 | 8.4533 | -4.9324
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.039692 | 0.038846 | -0.038846 | -0.16733 | 0.039692 | -0.023143 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.0498 | 8.8569 | -8.8569 | -38.1515 | 9.0498 | -5.2766
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.023228 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.47603 | 0.46898 | -0.46898 | -2.0121 | 0.47603 | -0.27874
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.039669 | 0.039082 | -0.039082 | -0.16767 | 0.039669 | -0.023228 | houston | 13 | Y | Y | mothballed | mothballed | -0.71404 | 0.70348 | -0.70348 | -3.0181 | 0.71404 | -0.4181
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.038751 | 0.048975 | -0.048975 | -0.19272 | 0.038751 | -0.026818 | houston | 9 | Y | Y | Yhouston | Yhouston | -1.9376 | 2.4487 | -2.4487 | -9.6362 | 1.9376 | -1.3409
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.2587
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -4.1711 | 3.6292 | -3.6292 | -22.2361 | 4.1711 | -2.2587
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1728
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1257 | 1.8495 | -1.8495 | -11.3319 | 2.1257 | -1.1511
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1728
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.2861 | 1.9891 | -1.9891 | -12.1871 | 2.2861 | -1.2379
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1728
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.1658 | 1.8844 | -1.8844 | -11.5457 | 2.1658 | -1.1728
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.2596
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.040107 | 0.034896 | -0.034896 | -0.21381 | 0.040107 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -2.3262 | 2.024 | -2.024 | -12.4009 | 2.3262 | -1.2596
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.040265 | 0.033184 | -0.033184 | -0.20015 | 0.040265 | -0.021096 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.48318 | 0.39821 | -0.39821 | -2.4018 | 0.48318 | -0.25315
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.1007
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.1597
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.1007
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.1007
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.3972 | 1.7235 | -1.7235 | -13.6968 | 2.3972 | -1.1597
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.040631 | 0.029212 | -0.029212 | -0.23215 | 0.040631 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.2753 | 1.6359 | -1.6359 | -13.0004 | 2.2753 | -1.1007
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.032706 | 0.10643 | -0.10643 | -0.16289 | 0.032706 | -0.047265 | houston | 13 | Y | Y | Yhouston | Yhouston | -2.1586 | 7.0242 | -7.0242 | -10.7505 | 2.1586 | -3.1195
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.0852 | 9.6037 | -9.6037 | -31.9788 | 6.0852 | -4.9369
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -6.2741 | 9.9019 | -9.9019 | -32.9719 | 6.2741 | -5.0902
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -9.3734 | 14.7932 | -14.7932 | -49.2592 | 9.3734 | -7.6047
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030664 | houston | 10 | Y | Y | Yhouston | Yhouston | -20.6366 | 32.5689 | -32.5689 | -108.4498 | 20.6366 | -16.7425
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030664 | houston | 1 | N | N | Nhouston | Nhouston | -24.3028 | 38.355 | -38.355 | -127.7165 | 24.3028 | -19.717
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -24.4177 | 40.3093 | -40.3093 | -138.9358 | 24.4177 | -20.5299
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -21.1545 | 34.9223 | -34.9223 | -120.3683 | 21.1545 | -17.7863
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.037508 | 0.061919 | -0.061919 | -0.21342 | 0.037508 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -22.5048 | 37.1514 | -37.1514 | -128.0514 | 22.5048 | -18.9216
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.037796 | 0.05965 | -0.05965 | -0.19863 | 0.037796 | -0.030664 | houston | 13 | Y | Y | Yhouston | Yhouston | -0.49135 | 0.77545 | -0.77545 | -2.5821 | 0.49135 | -0.39863
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.04031 | 0.032403 | -0.032403 | -0.15832 | 0.04031 | -0.020808 | houston | 6 | Y | N | Yhouston | Nhouston | -0.48372 | 0.38884 | -0.38884 | -1.8998 | 0.48372 | -0.2497
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1.3661 | 1.1479 | -1.1479 | -5.4357 | 1.3661 | -0.72423
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1.3942 | 1.1716 | -1.1716 | -5.5476 | 1.3942 | -0.73914
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1.3139 | 1.1041 | -1.1041 | -5.2279 | 1.3139 | -0.69654
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1.8443 | 1.5497 | -1.5497 | -7.3382 | 1.8443 | -0.97772
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -0.71119 | 0.59761 | -0.59761 | -2.8298 | 0.71119 | -0.37703
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -0.81967 | 0.68877 | -0.68877 | -3.2614 | 0.81967 | -0.43454
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -0.79958 | 0.67188 | -0.67188 | -3.1815 | 0.79958 | -0.42389
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1.4063 | 1.1817 | -1.1817 | -5.5956 | 1.4063 | -0.74553
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -0.72324 | 0.60773 | -0.60773 | -2.8777 | 0.72324 | -0.38342
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -3.4314 | 2.8834 | -2.8834 | -13.6532 | 3.4314 | -1.8191
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.04018 | 0.033763 | -0.033763 | -0.15987 | 0.04018 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -5.9466 | 4.9969 | -4.9969 | -23.6614 | 5.9466 | -3.1525
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.1656 | 5.316 | -5.316 | -11.3281 | 2.1656 | -2.4859
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.4939 | 6.122 | -6.122 | -13.0456 | 2.4939 | -2.8628
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1.5718 | 3.8584 | -3.8584 | -8.222 | 1.5718 | -1.8043
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -4.0496
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -3.0039 | 7.3738 | -7.3738 | -15.7132 | 3.0039 | -3.4482
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -3.0738 | 7.5453 | -7.5453 | -16.0787 | 3.0738 | -3.5284
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1.7465 | 4.2871 | -4.2871 | -9.1356 | 1.7465 | -2.0048
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -0.62872 | 1.5434 | -1.5434 | -3.2888 | 0.62872 | -0.72171
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -3.2833 | 8.0597 | -8.0597 | -17.1749 | 3.2833 | -3.7689
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.445 | 6.0019 | -6.0019 | -12.7898 | 2.445 | -2.8066
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.2005 | 5.4017 | -5.4017 | -11.5109 | 2.2005 | -2.526
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.5149 | 6.1734 | -6.1734 | -13.1553 | 2.5149 | -2.8868
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.2634 | 5.5561 | -5.5561 | -11.8397 | 2.2634 | -2.5982
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -3.5278 | 8.6599 | -8.6599 | -18.4539 | 3.5278 | -4.0496
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -3.3881 | 8.317 | -8.317 | -17.7231 | 3.3881 | -3.8892
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -3.5977 | 8.8314 | -8.8314 | -18.8193 | 3.5977 | -4.1298
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.6546 | 6.5164 | -6.5164 | -13.8861 | 2.6546 | -3.0472
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -3.2076
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -2.7943 | 6.8594 | -6.8594 | -14.617 | 2.7943 | -3.2076
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.034929 | 0.085742 | -0.085742 | -0.18271 | 0.034929 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -5.9729 | 14.6619 | -14.6619 | -31.2438 | 5.9729 | -6.8562
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | 0.019922 | 0.19412 | -0.19412 | -0.065489 | -0.019922 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | 0.16734 | 1.6306 | -1.6306 | -0.55011 | -0.16734 | -0.6461
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.70628 | -0.13032 | 0.13032 | 0.12565 | -0.70628 | 0.044282 | west | 6 | Y | N | Ywest | Nwest | 54.0302 | -9.9693 | 9.9693 | 9.6125 | -54.0302 | 3.3876
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 57.7118 | -10.9948 | 10.9948 | 10.357 | -57.7118 | 3.7381
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.7214 | -0.13744 | 0.13744 | 0.12946 | -0.7214 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 28.8559 | -5.4974 | 5.4974 | 5.1785 | -28.8559 | 1.869
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.047121 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.7697
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.72088 | -0.13719 | 0.13719 | 0.12933 | -0.72088 | 0.046639 | west | 6 | Y | N | Ywest | Nwest | 57.6704 | -10.975 | 10.975 | 10.3463 | -57.6704 | 3.7311
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.70844 | -0.13131 | 0.13131 | 0.12617 | -0.70844 | 0.044604 | west | 6 | Y | N | Ywest | Nwest | 56.6748 | -10.505 | 10.505 | 10.0933 | -56.6748 | 3.5683
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.70436 | -0.12939 | 0.12939 | 0.12513 | -0.70436 | 0.043938 | west | 6 | Y | N | Ywest | Nwest | 59.1666 | -10.8688 | 10.8688 | 10.511 | -59.1666 | 3.6908
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.7238 | -0.13857 | 0.13857 | 0.13008 | -0.7238 | 0.047121 | west | 6 | Y | N | Ywest | Nwest | 57.904 | -11.0859 | 11.0859 | 10.4062 | -57.904 | 3.7697
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1.3951 | 26.5402 | -26.5402 | -6.2466 | 1.3951 | -10.0347
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 89.9489 | -18.862 | 18.862 | 16.8367 | -89.9489 | 6.4666
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 174.6507 | -36.6236 | 36.6236 | 32.6913 | -174.6507 | 12.5559
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.74957 | -0.15718 | 0.15718 | 0.14031 | -0.74957 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 127.5775 | -26.7525 | 26.7525 | 23.8801 | -127.5775 | 9.1717
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -2.7168 | 51.6836 | -51.6836 | -12.1645 | 2.7168 | -19.5413
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -2.2518 | 42.8369 | -42.8369 | -10.0823 | 2.2518 | -16.1964
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -2.7413 | 52.1492 | -52.1492 | -12.2741 | 2.7413 | -19.7174
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1.4074 | 26.773 | -26.773 | -6.3014 | 1.4074 | -10.1228
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.012238 | 0.23281 | -0.23281 | -0.054795 | 0.012238 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1.2238 | 23.2809 | -23.2809 | -5.4795 | 1.2238 | -8.8024
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.65661 | -0.1635 | 0.1635 | 0.14319 | -0.65661 | 0.055605 | west | 6 | Y | N | Ywest | Nwest | 39.3969 | -9.8098 | 9.8098 | 8.5912 | -39.3969 | 3.3363
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | 0.22353 | 0.12205 | -0.12205 | 0.023633 | -0.22353 | -0.02909 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.63938 | -0.098751 | 0.098751 | 0.10863 | -0.63938 | 0.033317 | west | #N/A | N | N | Nwest | Nwest | 0 | 0 | 0 | 0 | 0 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.73291 | -0.14283 | 0.14283 | 0.13235 | -0.73291 | 0.048578 | west | #N/A | N | N | Nwest | Nwest | 3.518 | -0.68556 | 0.68556 | 0.63528 | -3.518 | 0.23317
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 28.9077 | -6.0278 | 6.0278 | 5.3213 | -28.9077 | 2.0503
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 82.8688 | -17.2797 | 17.2797 | 15.2543 | -82.8688 | 5.8776
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 104.0679 | -21.7 | 21.7 | 19.1565 | -104.0679 | 7.3811
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 91.7339 | -19.1282 | 19.1282 | 16.8861 | -91.7339 | 6.5063
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 80.9417 | -16.8778 | 16.8778 | 14.8995 | -80.9417 | 5.7409
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.77087 | -0.16074 | 0.16074 | 0.1419 | -0.77087 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 62.0553 | -12.9397 | 12.9397 | 11.423 | -62.0553 | 4.4013
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.76654 | -0.15544 | 0.15544 | 0.13938 | -0.76654 | 0.053256 | west | 6 | Y | N | Ywest | Nwest | 114.9804 | -23.3166 | 23.3166 | 20.9076 | -114.9804 | 7.9884
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 86.1244 | -17.4088 | 17.4088 | 15.6448 | -86.1244 | 5.9721
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 114.4497 | -23.1344 | 23.1344 | 20.7902 | -114.4497 | 7.9362
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 142.3923 | -28.7826 | 28.7826 | 25.8661 | -142.3923 | 9.8738
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.76555 | -0.15474 | 0.15474 | 0.13906 | -0.76555 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 164.2105 | -33.1928 | 33.1928 | 29.8294 | -164.2105 | 11.3867
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.017064 | 0.18486 | -0.18486 | -0.097034 | 0.017064 | -0.074448 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | 0.13143 | 0.14034 | -0.14034 | -0.034607 | -0.13143 | -0.056469 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | 0.002631 | 0.19499 | -0.19499 | -0.076253 | -0.002631 | -0.077747 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -0.64 | 4.7048 | -4.7048 | -3.1691 | 0.64 | -1.916
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -0.99657 | 7.3261 | -7.3261 | -4.9347 | 0.99657 | -2.9835
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.022857 | 0.16803 | -0.16803 | -0.11318 | 0.022857 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1.6914 | 12.4342 | -12.4342 | -8.3755 | 1.6914 | -5.0637
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.9942
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.70926 | 7.574 | -7.574 | -3.9887 | 0.70926 | -3.0506
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.65736 | 7.0198 | -7.0198 | -3.6969 | 0.65736 | -2.8274
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.32868 | 3.5099 | -3.5099 | -1.8484 | 0.32868 | -1.4137
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1.6261 | 17.3647 | -17.3647 | -9.1449 | 1.6261 | -6.9942
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.62276 | 6.6503 | -6.6503 | -3.5023 | 0.62276 | -2.6786
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.74386 | 7.9434 | -7.9434 | -4.1833 | 0.74386 | -3.1995
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.38058 | 4.0641 | -4.0641 | -2.1403 | 0.38058 | -1.6369
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7536
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0591
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.15105 | 1.2208 | -1.2208 | -0.752 | 0.15105 | -0.49424
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.32369 | 2.6161 | -2.6161 | -1.6114 | 0.32369 | -1.0591
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7536
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.021579 | 0.1744 | -0.1744 | -0.10743 | 0.021579 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -0.84158 | 6.8018 | -6.8018 | -4.1897 | 0.84158 | -2.7536
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -2.5603 | 27.3402 | -27.3402 | -14.3983 | 2.5603 | -11.0121
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.7203
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.95144 | 10.1602 | -10.1602 | -5.3507 | 0.95144 | -4.0923
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.017299 | 0.18473 | -0.18473 | -0.097286 | 0.017299 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -0.86495 | 9.2365 | -9.2365 | -4.8643 | 0.86495 | -3.7203
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.018681 | 0.18094 | -0.18094 | -0.1011 | 0.018681 | -0.073074 | south | 7 | N | N | Nsouth | Nsouth | -0.22417 | 2.1713 | -2.1713 | -1.2132 | 0.22417 | -0.87689
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.071284 | south | 7 | N | N | Nsouth | Nsouth | -0.31965 | 2.6467 | -2.6467 | -1.5852 | 0.31965 | -1.0693
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.02131 | 0.17645 | -0.17645 | -0.10568 | 0.02131 | -0.071284 | south | 7 | N | N | Nsouth | Nsouth | -0.49013 | 4.0583 | -4.0583 | -2.4307 | 0.49013 | -1.6395
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.022587 | 0.16953 | -0.16953 | -0.11185 | 0.022587 | -0.068937 | south | 7 | N | N | Nsouth | Nsouth | -1.0842 | 8.1375 | -8.1375 | -5.3687 | 1.0842 | -3.309
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.021381 | 0.17513 | -0.17513 | -0.10679 | 0.021381 | -0.070862 | south | 7 | N | N | Nsouth | Nsouth | -0.17105 | 1.401 | -1.401 | -0.85434 | 0.17105 | -0.5669
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018104 | 0.18292 | -0.18292 | -0.099196 | 0.018104 | -0.073763 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2587 | 32.9249 | -32.9249 | -17.8553 | 3.2587 | -13.2773
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.018121 | 0.18286 | -0.18286 | -0.099253 | 0.018121 | -0.073743 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2618 | 32.9144 | -32.9144 | -17.8655 | 3.2618 | -13.2737
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073893 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.3007
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.018012 | 0.18328 | -0.18328 | -0.098854 | 0.018012 | -0.073893 | south | 9 | Y | Y | Ysouth | Ysouth | -3.2422 | 32.9911 | -32.9911 | -17.7937 | 3.2422 | -13.3007
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077754 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -7.7754
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077754 | south | 13 | Y | Y | Ysouth | Ysouth | 0.2619 | 19.5004 | -19.5004 | -7.6248 | -0.2619 | -7.7754
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8336
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8336
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8336
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.29509 | 2.9071 | -2.9071 | -1.606 | 0.29509 | -1.1735
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8336
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8336
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.46108 | 4.5424 | -4.5424 | -2.5093 | 0.46108 | -1.8336
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.018443 | 0.1817 | -0.1817 | -0.10037 | 0.018443 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -0.27664 | 2.7254 | -2.7254 | -1.5056 | 0.27664 | -1.1001
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077754 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077754 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -38.877
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077754 | south | #N/A | N | N | dc-tie | dc-tie | 1.3095 | 97.502 | -97.502 | -38.124 | -1.3095 | -38.877
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | 0.002619 | 0.195 | -0.195 | -0.076248 | -0.002619 | -0.077754 | south | #N/A | N | N | dc-tie | dc-tie | 0 | 0 | 0 | 0 | 0 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.014884 | 0.19345 | -0.19345 | -0.088657 | 0.014884 | -0.077094 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | 0.20699 | 0.10551 | -0.10551 | -0.012415 | -0.20699 | -0.043138 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.003862 | 0.19004 | -0.19004 | -0.084355 | 0.003862 | -0.076081 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.01426 | 0.18791 | -0.18791 | -0.092806 | 0.01426 | -0.07549 | south | #N/A | N | N | Nsouth | Nsouth | 0 | 0 | 0 | 0 | 0 | 0

## BoundaryGens
Boundary Generation Resources test (Protocols Section 7.2.3.1.3) | [6 empty] | L: TEMP_SS_ to SANDOW_ 345kV [3414 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | [7 empty] | 30.7451
Number of Bus | Name of Bus | ID | Max MW | L: TEMP_SS_ to SANDOW_ 345kV [3414 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | CMZ | North | South | West | Houston | Minimum PTDF Absolute Value | Minimum PTDF Zone | Boundary Generator? Y/N | CRE Designated Zone | Boundary Gen Impact Error
238 | BOSQUESW | 1 | 255 | 0.091815 | north | Y | 0.035928 | 0.18153 | 0.038771 | 0.11877 | 0.035928 | North | N | 0.035928 | 0
239 | BOSQUESW | 1 | 149 | 0.091815 | north | Y | 0.035928 | 0.18153 | 0.038771 | 0.11877 | 0.035928 | North | N | 0.035928 | 0
244 | WHITNYDM | 1 | 15 | 0.083659 | north | N | 0.027772 | 0.17338 | 0.030615 | 0.11062 | 0.027772 | North | N | 0.027772 | 0
245 | WHITNYDM | 2 | 15 | 0.083659 | north | N | 0.027772 | 0.17338 | 0.030615 | 0.11062 | 0.027772 | North | N | 0.027772 | 0
247 | BOSQUESW | 2 | 153 | 0.091815 | north | Y | 0.035928 | 0.18153 | 0.038771 | 0.11877 | 0.035928 | North | N | 0.035928 | 0
251 | BOSQUESW | 2 | 150 | 0.08846 | north | Y | 0.032573 | 0.17818 | 0.035416 | 0.11542 | 0.032573 | North | N | 0.032573 | 0
253 | BOSQUESW | 2 | 80 | 0.08846 | north | Y | 0.032573 | 0.17818 | 0.035416 | 0.11542 | 0.032573 | North | N | 0.032573 | 0
332 | RWMILLER | 1 | 73 | 0.062373 | north | Y | 0.0064861 | 0.15209 | 0.0093293 | 0.08933 | 0.0064861 | North | N | 0.0064861 | 0
333 | RWMILLER | 2 | 119 | 0.062373 | north | Y | 0.0064861 | 0.15209 | 0.0093293 | 0.08933 | 0.0064861 | North | N | 0.0064861 | 0
334 | RWMILLER | 3 | 205 | 0.062373 | north | Y | 0.0064861 | 0.15209 | 0.0093293 | 0.08933 | 0.0064861 | North | N | 0.0064861 | 0
335 | RWMILLER | 4 | 102 | 0.062373 | north | Y | 0.0064861 | 0.15209 | 0.0093293 | 0.08933 | 0.0064861 | North | N | 0.0064861 | 0
336 | RWMILLER | 5 | 96 | 0.062373 | north | Y | 0.0064861 | 0.15209 | 0.0093293 | 0.08933 | 0.0064861 | North | N | 0.0064861 | 0
344 | MRSSHPRD | 1 | 12 | 0.060176 | north | N | 0.0042891 | 0.14989 | 0.0071323 | 0.087133 | 0.0042891 | North | N | 0.0042891 | 0
345 | MRSSHPRD | 2 | 12 | 0.060176 | north | N | 0.0042891 | 0.14989 | 0.0071323 | 0.087133 | 0.0042891 | North | N | 0.0042891 | 0
366 | JNSNCNTY | 1 | 168 | 0.065029 | north | Y | 0.0091421 | 0.15475 | 0.011985 | 0.091986 | 0.0091421 | North | N | 0.0091421 | 0
367 | JNSNCNTY | 2 | 90 | 0.065029 | north | Y | 0.0091421 | 0.15475 | 0.011985 | 0.091986 | 0.0091421 | North | N | 0.0091421 | 0
503 | NTHTEXAS | 1 | 18 | 0.061418 | north | Y | 0.0055311 | 0.15113 | 0.0083743 | 0.088375 | 0.0055311 | North | N | 0.0055311 | 0
504 | NTHTEXAS | 2 | 18 | 0.061418 | north | Y | 0.0055311 | 0.15113 | 0.0083743 | 0.088375 | 0.0055311 | North | N | 0.0055311 | 0
505 | NTHTEXAS | 3 | 38 | 0.061418 | north | Y | 0.0055311 | 0.15113 | 0.0083743 | 0.088375 | 0.0055311 | North | N | 0.0055311 | 0
580 | JCKCNTY8 | 1 | 288 | 0.060612 | north | Y | 0.0047251 | 0.15033 | 0.0075683 | 0.087569 | 0.0047251 | North | N | 0.0047251 | 0
581 | JCKCNTY8 | 2 | 147 | 0.060612 | north | Y | 0.0047251 | 0.15033 | 0.0075683 | 0.087569 | 0.0047251 | North | N | 0.0047251 | 0
582 | JCKCNTY8 | 3 | 147 | 0.060612 | north | Y | 0.0047251 | 0.15033 | 0.0075683 | 0.087569 | 0.0047251 | North | N | 0.0047251 | 0
728 | WOLFRIDG | 1 | 112.5 | 0.05977 | north | Y | 0.0038831 | 0.14949 | 0.0067263 | 0.086727 | 0.0038831 | North | N | 0.0038831 | 0
837 | NEWMAN_G | 1 | 40 | 0.058384 | north | Y | 0.0024971 | 0.1481 | 0.0053403 | 0.085341 | 0.0024971 | North | N | 0.0024971 | 0
842 | OLINGER_ | 1 | 79 | 0.058362 | north | Y | 0.0024751 | 0.14808 | 0.0053183 | 0.085319 | 0.0024751 | North | N | 0.0024751 | 0
843 | OLINGER_ | 1 | 106 | 0.058362 | north | Y | 0.0024751 | 0.14808 | 0.0053183 | 0.085319 | 0.0024751 | North | N | 0.0024751 | 0
844 | OLINGER_ | 1 | 146 | 0.058362 | north | Y | 0.0024751 | 0.14808 | 0.0053183 | 0.085319 | 0.0024751 | North | N | 0.0024751 | 0
845 | OLINGER_ | 1 | 76 | 0.058362 | north | Y | 0.0024751 | 0.14808 | 0.0053183 | 0.085319 | 0.0024751 | North | N | 0.0024751 | 0
923 | SPENCER_ | 1 | 60 | 0.059614 | north | Y | 0.0037271 | 0.14933 | 0.0065703 | 0.086571 | 0.0037271 | North | N | 0.0037271 | 0
924 | SPENCER_ | 1 | 63 | 0.059614 | north | Y | 0.0037271 | 0.14933 | 0.0065703 | 0.086571 | 0.0037271 | North | N | 0.0037271 | 0
948 | STEAM1 | 1 | 20 | 0.058263 | north | Y | 0.0023761 | 0.14798 | 0.0052193 | 0.08522 | 0.0023761 | North | N | 0.0023761 | 0
949 | STEAM2 | 1 | 25 | 0.058264 | north | Y | 0.0023771 | 0.14798 | 0.0052203 | 0.085221 | 0.0023771 | North | N | 0.0023771 | 0
950 | STEAM3 | 1 | 41 | 0.058264 | north | Y | 0.0023771 | 0.14798 | 0.0052203 | 0.085221 | 0.0023771 | North | N | 0.0023771 | 0
990 | GIBN_CRE | 1 | 463 | 0.014683 | north | Y | -0.041204 | 0.1044 | -0.038361 | 0.04164 | 0.038361 | west | Y | 0.041204 | 1.3164
1002 | PBCTAGE_ | A | 66 | 0.052105 | west | Y | -0.0037819 | 0.14182 | -0.00093873 | 0.079062 | 0.00093873 | west | N | 0.00093873 | 0
1003 | PBCTBGE_ | B | 65 | 0.052105 | west | Y | -0.0037819 | 0.14182 | -0.00093873 | 0.079062 | 0.00093873 | west | N | 0.00093873 | 0
1004 | PBCTCGE_ | C | 67 | 0.052105 | west | Y | -0.0037819 | 0.14182 | -0.00093873 | 0.079062 | 0.00093873 | west | N | 0.00093873 | 0
1005 | PBCTDGE_ | D | 67 | 0.052105 | west | Y | -0.0037819 | 0.14182 | -0.00093873 | 0.079062 | 0.00093873 | west | N | 0.00093873 | 0
1006 | PBCTEGE_ | E | 67 | 0.052105 | west | Y | -0.0037819 | 0.14182 | -0.00093873 | 0.079062 | 0.00093873 | west | N | 0.00093873 | 0
1007 | PB5GEN_6 | MB | 114 | 0.052105 | west | Y | -0.0037819 | 0.14182 | -0.00093873 | 0.079062 | 0.00093873 | west | N | 0.00093873 | 0
1008 | PB6GEN_7 | MB | 515 | 0.052105 | west | Y | -0.0037819 | 0.14182 | -0.00093873 | 0.079062 | 0.00093873 | west | N | 0.00093873 | 0
1039 | MRGNAG_1 | A | 66 | 0.054051 | west | Y | -0.0018359 | 0.14377 | 0.0010073 | 0.081008 | 0.0010073 | west | N | 0.0010073 | 0
1040 | MRGNBG_2 | B | 69 | 0.054051 | west | Y | -0.0018359 | 0.14377 | 0.0010073 | 0.081008 | 0.0010073 | west | N | 0.0010073 | 0
1041 | MRGNCG_3 | C | 69 | 0.054051 | west | Y | -0.0018359 | 0.14377 | 0.0010073 | 0.081008 | 0.0010073 | west | N | 0.0010073 | 0
1042 | MRGNDG_4 | D | 67 | 0.054051 | west | Y | -0.0018359 | 0.14377 | 0.0010073 | 0.081008 | 0.0010073 | west | N | 0.0010073 | 0
1043 | MRGNEG_5 | E | 67 | 0.054051 | west | Y | -0.0018359 | 0.14377 | 0.0010073 | 0.081008 | 0.0010073 | west | N | 0.0010073 | 0
1044 | MRGNFG_6 | F | 65 | 0.054051 | west | Y | -0.0018359 | 0.14377 | 0.0010073 | 0.081008 | 0.0010073 | west | N | 0.0010073 | 0
1045 | CALENG1G | 1 | 70 | 0.053751 | west | N | -0.0021359 | 0.14347 | 0.00070727 | 0.080708 | 0.00070727 | west | N | 0.00070727 | 0
1046 | CALENG2G | 2 | 73.4 | 0.053751 | west | N | -0.0021359 | 0.14347 | 0.00070727 | 0.080708 | 0.00070727 | west | N | 0.00070727 | 0
1047 | CALENG3G | 3 | 70.4 | 0.053751 | west | N | -0.0021359 | 0.14347 | 0.00070727 | 0.080708 | 0.00070727 | west | N | 0.00070727 | 0
1058 | LONGSHOR | 1 | 150 | 0.053905 | west | Y | -0.0019819 | 0.14362 | 0.00086127 | 0.080862 | 0.00086127 | west | N | 0.00086127 | 0
1058 | LONGSHOR | 2 | 220 | 0.053905 | west | Y | -0.0019819 | 0.14362 | 0.00086127 | 0.080862 | 0.00086127 | west | N | 0.00086127 | 0
1061 | CIELOGEN | 1 | 99 | 0.054166 | west | Y | -0.0017209 | 0.14388 | 0.0011223 | 0.081123 | 0.0011223 | west | N | 0.0011223 | 0
1062 | CIELOGEN | 1 | 61 | 0.054166 | west | Y | -0.0017209 | 0.14388 | 0.0011223 | 0.081123 | 0.0011223 | west | N | 0.0011223 | 0
1068 | SCURRYCW | 1 | 141 | 0.054151 | west | Y | -0.0017359 | 0.14387 | 0.0011073 | 0.081108 | 0.0011073 | west | N | 0.0011073 | 0
1069 | KINDERMG | 1 | 25 | 0.054166 | west | N | -0.0017209 | 0.14388 | 0.0011223 | 0.081123 | 0.0011223 | west | N | 0.0011223 | 0
1070 | KINDERMG | 1 | 45.7 | 0.054166 | west | N | -0.0017209 | 0.14388 | 0.0011223 | 0.081123 | 0.0011223 | west | N | 0.0011223 | 0
1071 | KINDERMG | 1 | 45.7 | 0.054166 | west | N | -0.0017209 | 0.14388 | 0.0011223 | 0.081123 | 0.0011223 | west | N | 0.0011223 | 0
1073 | SCURRYCW | 2 | 120 | 0.054151 | west | Y | -0.0017359 | 0.14387 | 0.0011073 | 0.081108 | 0.0011073 | west | N | 0.0011073 | 0
1320 | BSP 1 | 1 | 25.8 | 0.05335 | west | N | -0.0025369 | 0.14307 | 0.00030627 | 0.080307 | 0.00030627 | west | N | 0.00030627 | 0
1326 | STANTONW | 1 | 100.5 | 0.053134 | west | Y | -0.0027529 | 0.14285 | 9.0265e-05 | 0.080091 | 9.0265e-05 | west | N | 9.0265e-05 | 0
1327 | WILDHRSE | 1 | 120 | 0.053626 | west | Y | -0.0022609 | 0.14334 | 0.00058227 | 0.080583 | 0.00058227 | west | N | 0.00058227 | 0
1328 | OCOTILLO | 1 | 58 | 0.053116 | west | Y | -0.0027709 | 0.14283 | 7.2265e-05 | 0.080073 | 7.2265e-05 | west | N | 7.2265e-05 | 0
1333 | MCDDONAL | 1 | 214.2 | 0.053247 | west | Y | -0.0026399 | 0.14296 | 0.00020327 | 0.080204 | 0.00020327 | west | N | 0.00020327 | 0
1343 | TRENTIPP | 1 | 150 | 0.054569 | west | Y | -0.0013179 | 0.14429 | 0.0015253 | 0.081526 | 0.0013179 | North | Y | 0.0015253 | 0.031104
1349 | WESTXWIN | 1 | 6.6 | 0.052737 | west | Y | -0.0031499 | 0.14245 | -0.00030673 | 0.079694 | 0.00030673 | west | N | 0.00030673 | 0
1350 | NWPWRG1_ | 1 | 34.3 | 0.052737 | west | Y | -0.0031499 | 0.14245 | -0.00030673 | 0.079694 | 0.00030673 | west | N | 0.00030673 | 0
1354 | AEPWIND_ | 1 | 101 | 0.054569 | west | Y | -0.0013179 | 0.14429 | 0.0015253 | 0.081526 | 0.0013179 | North | Y | 0.0015253 | 0.020943
1360 | GUNSIGHT | 1 | 120 | 0.053649 | west | Y | -0.0022379 | 0.14337 | 0.00060527 | 0.080606 | 0.00060527 | west | N | 0.00060527 | 0
1432 | GRHAMSES | 2 | 366 | 0.058432 | north | Y | 0.0025451 | 0.14815 | 0.0053883 | 0.085389 | 0.0025451 | North | N | 0.0025451 | 0
1433 | GRHAMSES | 1 | 242 | 0.058705 | north | Y | 0.0028181 | 0.14842 | 0.0056613 | 0.085662 | 0.0028181 | North | N | 0.0028181 | 0
1437 | MESQUITW | 1 | 400 | 0.056296 | west | Y | 0.00040909 | 0.14601 | 0.0032523 | 0.083253 | 0.00040909 | North | Y | 0.0032523 | 1.1373
1438 | MESQUITW | 1 | 236 | 0.056298 | west | Y | 0.00041109 | 0.14601 | 0.0032543 | 0.083255 | 0.00041109 | North | Y | 0.0032543 | 0.67099
1442 | COKFIELD | 1 | 165 | 0.05681 | west | Y | 0.00092309 | 0.14653 | 0.0037663 | 0.083767 | 0.00092309 | North | Y | 0.0037663 | 0.46912
1453 | WCPWRCO_ | 1 | 204 | 0.05956 | north | Y | 0.0036731 | 0.14928 | 0.0065163 | 0.086517 | 0.0036731 | North | N | 0.0036731 | 0
1454 | WCPWRCO_ | 2 | 201 | 0.05956 | north | Y | 0.0036731 | 0.14928 | 0.0065163 | 0.086517 | 0.0036731 | North | N | 0.0036731 | 0
1455 | WCPWRCO_ | 3 | 242 | 0.05956 | north | Y | 0.0036731 | 0.14928 | 0.0065163 | 0.086517 | 0.0036731 | North | N | 0.0036731 | 0
1479 | WFCOGEN_ | 1 | 20 | 0.058555 | west | Y | 0.0026681 | 0.14827 | 0.0055113 | 0.085512 | 0.0026681 | North | Y | 0.0055113 | 0.056863
1479 | WFCOGEN_ | 2 | 20 | 0.058555 | west | Y | 0.0026681 | 0.14827 | 0.0055113 | 0.085512 | 0.0026681 | North | Y | 0.0055113 | 0.056863
1482 | WFCOGEN_ | 1 | 20 | 0.058555 | west | Y | 0.0026681 | 0.14827 | 0.0055113 | 0.085512 | 0.0026681 | North | Y | 0.0055113 | 0.056863
1482 | WFCOGEN_ | 2 | 17 | 0.058555 | west | Y | 0.0026681 | 0.14827 | 0.0055113 | 0.085512 | 0.0026681 | North | Y | 0.0055113 | 0.048334
1600 | BARTNWND | 1 | 120 | 0.060184 | north | Y | 0.0042971 | 0.1499 | 0.0071403 | 0.087141 | 0.0042971 | North | N | 0.0042971 | 0
1643 | SLSTR1PP | 1 | 60 | 0.062279 | north | Y | 0.0063921 | 0.152 | 0.0092353 | 0.089236 | 0.0063921 | North | N | 0.0063921 | 0
1675 | PEC_1G | 1 | 75 | 0.0584 | north | N | 0.0025131 | 0.14812 | 0.0053563 | 0.085357 | 0.0025131 | North | N | 0.0025131 | 0
1676 | PEC_2G | 2 | 79.6 | 0.0584 | north | N | 0.0025131 | 0.14812 | 0.0053563 | 0.085357 | 0.0025131 | North | N | 0.0025131 | 0
1677 | PEC_3G | 3 | 88.4 | 0.0584 | north | N | 0.0025131 | 0.14812 | 0.0053563 | 0.085357 | 0.0025131 | North | N | 0.0025131 | 0
1678 | LAMARPWR | 1 | 160 | 0.058449 | north | Y | 0.0025621 | 0.14817 | 0.0054053 | 0.085406 | 0.0025621 | North | N | 0.0025621 | 0
1679 | LAMARPWR | 2 | 156 | 0.058449 | north | Y | 0.0025621 | 0.14817 | 0.0054053 | 0.085406 | 0.0025621 | North | N | 0.0025621 | 0
1680 | LAMARPWR | 3 | 196 | 0.058449 | north | Y | 0.0025621 | 0.14817 | 0.0054053 | 0.085406 | 0.0025621 | North | N | 0.0025621 | 0
1681 | LAMARPWR | 4 | 156 | 0.058449 | north | Y | 0.0025621 | 0.14817 | 0.0054053 | 0.085406 | 0.0025621 | North | N | 0.0025621 | 0
1682 | LAMARPWR | 5 | 157 | 0.058449 | north | Y | 0.0025621 | 0.14817 | 0.0054053 | 0.085406 | 0.0025621 | North | N | 0.0025621 | 0
1683 | LAMARPWR | 6 | 198 | 0.058449 | north | Y | 0.0025621 | 0.14817 | 0.0054053 | 0.085406 | 0.0025621 | North | N | 0.0025621 | 0
1687 | VALLEY_1 | 1 | 170 | 0.058602 | north | Y | 0.0027151 | 0.14832 | 0.0055583 | 0.085559 | 0.0027151 | North | N | 0.0027151 | 0
1688 | VALLEY_2 | 2 | 520 | 0.058602 | north | Y | 0.0027151 | 0.14832 | 0.0055583 | 0.085559 | 0.0027151 | North | N | 0.0027151 | 0
1689 | VALLEY_3 | 3 | 370 | 0.058505 | north | Y | 0.0026181 | 0.14822 | 0.0054613 | 0.085462 | 0.0026181 | North | N | 0.0026181 | 0
1701 | MOSES_1G | 1 | 558 | 0.058357 | north | Y | 0.0024701 | 0.14807 | 0.0053133 | 0.085314 | 0.0024701 | North | N | 0.0024701 | 0
1702 | MOSES_2G | 2 | 579 | 0.058357 | north | Y | 0.0024701 | 0.14807 | 0.0053133 | 0.085314 | 0.0024701 | North | N | 0.0024701 | 0
1703 | MOSES_3G | 3 | 808 | 0.058357 | north | Y | 0.0024701 | 0.14807 | 0.0053133 | 0.085314 | 0.0024701 | North | N | 0.0024701 | 0
1861 | EAGLEMNT | MB | 112 | 0.060651 | north | Y | 0.0047641 | 0.15037 | 0.0076073 | 0.087608 | 0.0047641 | North | N | 0.0047641 | 0
1862 | EAGLEMNT | MB | 100 | 0.060651 | north | Y | 0.0047641 | 0.15037 | 0.0076073 | 0.087608 | 0.0047641 | North | N | 0.0047641 | 0
1863 | EAGLEMNT | MB | 378 | 0.060651 | north | Y | 0.0047641 | 0.15037 | 0.0076073 | 0.087608 | 0.0047641 | North | N | 0.0047641 | 0
1877 | WLFHOLW_ | 1 | 217.3 | 0.061569 | north | Y | 0.0056821 | 0.15129 | 0.0085253 | 0.088526 | 0.0056821 | North | N | 0.0056821 | 0
1878 | WLFHOLW_ | 2 | 205 | 0.061569 | north | Y | 0.0056821 | 0.15129 | 0.0085253 | 0.088526 | 0.0056821 | North | N | 0.0056821 | 0
1879 | WLFHOLW_ | 3 | 272.4 | 0.061569 | north | Y | 0.0056821 | 0.15129 | 0.0085253 | 0.088526 | 0.0056821 | North | N | 0.0056821 | 0
1889 | DECRDOVA | MB | 770 | 0.061706 | north | Y | 0.0058191 | 0.15142 | 0.0086623 | 0.088663 | 0.0058191 | North | N | 0.0058191 | 0
1892 | DECRDOVA | A | 70 | 0.062996 | north | Y | 0.0071091 | 0.15271 | 0.0099523 | 0.089953 | 0.0071091 | North | N | 0.0071091 | 0
1893 | DECRDOVA | B | 69 | 0.062996 | north | Y | 0.0071091 | 0.15271 | 0.0099523 | 0.089953 | 0.0071091 | North | N | 0.0071091 | 0
1894 | DECRDOVA | C | 69 | 0.062996 | north | Y | 0.0071091 | 0.15271 | 0.0099523 | 0.089953 | 0.0071091 | North | N | 0.0071091 | 0
1895 | DECRDOVA | D | 68 | 0.062996 | north | Y | 0.0071091 | 0.15271 | 0.0099523 | 0.089953 | 0.0071091 | North | N | 0.0071091 | 0
1898 | COMCHEPK | 1 | 1157 | 0.061476 | north | N | 0.0055891 | 0.15119 | 0.0084323 | 0.088433 | 0.0055891 | North | N | 0.0055891 | 0
1899 | COMCHEPK | 2 | 1158 | 0.061476 | north | N | 0.0055891 | 0.15119 | 0.0084323 | 0.088433 | 0.0055891 | North | N | 0.0055891 | 0
1937 | MDLTHELP | 5 | 224 | 0.064114 | north | Y | 0.0082271 | 0.15383 | 0.01107 | 0.091071 | 0.0082271 | North | N | 0.0082271 | 0
1938 | MDLTHELP | 6 | 226 | 0.064114 | north | Y | 0.0082271 | 0.15383 | 0.01107 | 0.091071 | 0.0082271 | North | N | 0.0082271 | 0
1941 | MDLTHELP | 1 | 216.4 | 0.063705 | north | Y | 0.0078181 | 0.15342 | 0.010661 | 0.090662 | 0.0078181 | North | N | 0.0078181 | 0
1942 | MDLTHELP | 2 | 216.1 | 0.063705 | north | Y | 0.0078181 | 0.15342 | 0.010661 | 0.090662 | 0.0078181 | North | N | 0.0078181 | 0
1943 | MDLTHELP | 3 | 212 | 0.064114 | north | Y | 0.0082271 | 0.15383 | 0.01107 | 0.091071 | 0.0082271 | North | N | 0.0082271 | 0
1944 | MDLTHELP | 4 | 211 | 0.064114 | north | Y | 0.0082271 | 0.15383 | 0.01107 | 0.091071 | 0.0082271 | North | N | 0.0082271 | 0
1947 | HANDLEY_ | 3 | 395 | 0.061589 | north | Y | 0.0057021 | 0.15131 | 0.0085453 | 0.088546 | 0.0057021 | North | N | 0.0057021 | 0
1948 | HANDLEY_ | 4 | 435 | 0.061452 | north | Y | 0.0055651 | 0.15117 | 0.0084083 | 0.088409 | 0.0055651 | North | N | 0.0055651 | 0
1949 | HANDLEY_ | 5 | 435 | 0.061589 | north | Y | 0.0057021 | 0.15131 | 0.0085453 | 0.088546 | 0.0057021 | North | N | 0.0057021 | 0
2371 | COLLIN_1 | MB | 138 | 0.059032 | north | Y | 0.0031451 | 0.14875 | 0.0059883 | 0.085989 | 0.0031451 | North | N | 0.0031451 | 0
2413 | MTCK6_G | 6 | 118 | 0.059497 | north | Y | 0.0036101 | 0.14921 | 0.0064533 | 0.086454 | 0.0036101 | North | N | 0.0036101 | 0
2414 | MTCK7_G | 7 | 115 | 0.059497 | north | Y | 0.0036101 | 0.14921 | 0.0064533 | 0.086454 | 0.0036101 | North | N | 0.0036101 | 0
2417 | MTCK8_G | 8 | 556 | 0.059497 | north | Y | 0.0036101 | 0.14921 | 0.0064533 | 0.086454 | 0.0036101 | North | N | 0.0036101 | 0
2451 | LKHB1_G | 1 | 388 | 0.058281 | north | Y | 0.0023941 | 0.148 | 0.0052373 | 0.085238 | 0.0023941 | North | N | 0.0023941 | 0
2452 | LKHB2_G | 2 | 515 | 0.058281 | north | Y | 0.0023941 | 0.148 | 0.0052373 | 0.085238 | 0.0023941 | North | N | 0.0023941 | 0
3097 | MARTLAKE | 1 | 785 | 0.05516 | north | Y | -0.00072691 | 0.14488 | 0.0021163 | 0.082117 | 0.00072691 | North | N | 0.00072691 | 0
3098 | MARTLAKE | 2 | 795 | 0.05516 | north | Y | -0.00072691 | 0.14488 | 0.0021163 | 0.082117 | 0.00072691 | North | N | 0.00072691 | 0
3099 | MARTLAKE | 3 | 780 | 0.05516 | north | Y | -0.00072691 | 0.14488 | 0.0021163 | 0.082117 | 0.00072691 | North | N | 0.00072691 | 0
3107 | STRYKER_ | 1 | 182 | 0.054175 | north | Y | -0.0017119 | 0.14389 | 0.0011313 | 0.081132 | 0.0011313 | west | Y | 0.0017119 | 0.10568
3108 | STRYKER_ | 2 | 484 | 0.054175 | north | Y | -0.0017119 | 0.14389 | 0.0011313 | 0.081132 | 0.0011313 | west | Y | 0.0017119 | 0.28103
3126 | TRINIDAD | 1 | 224 | 0.058092 | north | Y | 0.0022051 | 0.14781 | 0.0050483 | 0.085049 | 0.0022051 | North | N | 0.0022051 | 0
3309 | ASPN_G | 1 | 50 | 0.054401 | north | Y | -0.0014859 | 0.14412 | 0.0013573 | 0.081358 | 0.0013573 | west | Y | 0.0014859 | 0.0064321
3348 | CHAMPION | MB | 42 | 0.054433 | north | N | -0.0014539 | 0.14415 | 0.0013893 | 0.08139 | 0.0013893 | west | Y | 0.0014539 | 0
3381 | BBRN_1G | 1 | 615 | 0.04995 | north | Y | -0.0059369 | 0.13967 | -0.0030937 | 0.076907 | 0.0030937 | west | Y | 0.0059369 | 1.7486
3382 | BBRN_2G | 2 | 587 | 0.04995 | north | Y | -0.0059369 | 0.13967 | -0.0030937 | 0.076907 | 0.0030937 | west | Y | 0.0059369 | 1.6689
3403 | THOUSE_1 | MB | 537 | 0.096231 | north | Y | 0.040344 | 0.18595 | 0.043187 | 0.12319 | 0.040344 | North | N | 0.040344 | 0
3404 | THOUSE_2 | 2 | 787 | 0.096231 | north | Y | 0.040344 | 0.18595 | 0.043187 | 0.12319 | 0.040344 | North | N | 0.040344 | 0
3416 | LAKE_CRK | MB | 75 | 0.09236 | north | Y | 0.036473 | 0.18208 | 0.039316 | 0.11932 | 0.036473 | North | N | 0.036473 | 0
3417 | LAKE_CRK | MB | 222 | 0.09236 | north | Y | 0.036473 | 0.18208 | 0.039316 | 0.11932 | 0.036473 | North | N | 0.036473 | 0
3432 | SANDOW_4 | 4 | 569 | -0.14701 | south | Y | -0.2029 | -0.057297 | -0.20006 | -0.12006 | 0.057297 | south | N | 0.057297 | 0
5026 | BRAUNIG_ | 1 | 209 | -0.087025 | south | Y | -0.14291 | 0.0026911 | -0.14007 | -0.060068 | 0.0026911 | south | N | 0.0026911 | 0
5027 | BRAUNIG_ | 2 | 216 | -0.087025 | south | Y | -0.14291 | 0.0026911 | -0.14007 | -0.060068 | 0.0026911 | south | N | 0.0026911 | 0
5028 | BRAUNIG_ | 3 | 407 | -0.086999 | south | Y | -0.14289 | 0.0027171 | -0.14004 | -0.060042 | 0.0027171 | south | N | 0.0027171 | 0
5031 | BRA_VHBC | 1 | 46 | -0.087025 | south | Y | -0.14291 | 0.0026911 | -0.14007 | -0.060068 | 0.0026911 | south | N | 0.0026911 | 0
5032 | BRA_VHBC | 2 | 47 | -0.087025 | south | Y | -0.14291 | 0.0026911 | -0.14007 | -0.060068 | 0.0026911 | south | N | 0.0026911 | 0
5033 | BRA_VHBC | 3 | 46 | -0.087025 | south | Y | -0.14291 | 0.0026911 | -0.14007 | -0.060068 | 0.0026911 | south | N | 0.0026911 | 0
5034 | BRA_VHBC | 4 | 46 | -0.087025 | south | Y | -0.14291 | 0.0026911 | -0.14007 | -0.060068 | 0.0026911 | south | N | 0.0026911 | 0
5111 | CALAVER_ | 1 | 424 | -0.087255 | south | Y | -0.14314 | 0.0024611 | -0.1403 | -0.060298 | 0.0024611 | south | N | 0.0024611 | 0
5112 | CALAVER_ | 2 | 425 | -0.087255 | south | Y | -0.14314 | 0.0024611 | -0.1403 | -0.060298 | 0.0024611 | south | N | 0.0024611 | 0
5264 | LEON_LCP | 3 | 58 | -0.086454 | south | Y | -0.14234 | 0.0032621 | -0.1395 | -0.059497 | 0.0032621 | south | N | 0.0032621 | 0
5265 | LEON_LCP | 4 | 89 | -0.086454 | south | Y | -0.14234 | 0.0032621 | -0.1395 | -0.059497 | 0.0032621 | south | N | 0.0032621 | 0
5266 | LEON_LCP | 1 | 44 | -0.086454 | south | Y | -0.14234 | 0.0032621 | -0.1395 | -0.059497 | 0.0032621 | south | N | 0.0032621 | 0
5267 | LEON_LCP | 2 | 44 | -0.086454 | south | Y | -0.14234 | 0.0032621 | -0.1395 | -0.059497 | 0.0032621 | south | N | 0.0032621 | 0
5268 | LEON_LCP | 3 | 43 | -0.086454 | south | Y | -0.14234 | 0.0032621 | -0.1395 | -0.059497 | 0.0032621 | south | N | 0.0032621 | 0
5269 | LEON_LCP | 4 | 45 | -0.086454 | south | Y | -0.14234 | 0.0032621 | -0.1395 | -0.059497 | 0.0032621 | south | N | 0.0032621 | 0
5396 | CALAVER_ | 1 | 412 | -0.087125 | south | Y | -0.14301 | 0.0025911 | -0.14017 | -0.060168 | 0.0025911 | south | N | 0.0025911 | 0
5397 | CALAVER_ | 2 | 400 | -0.087125 | south | Y | -0.14301 | 0.0025911 | -0.14017 | -0.060168 | 0.0025911 | south | N | 0.0025911 | 0
5401 | CALAVER_ | 1 | 546 | -0.086822 | south | Y | -0.14271 | 0.0028941 | -0.13987 | -0.059865 | 0.0028941 | south | N | 0.0028941 | 0
5402 | CALAVER_ | 2 | 750 | -0.086822 | south | Y | -0.14271 | 0.0028941 | -0.13987 | -0.059865 | 0.0028941 | south | N | 0.0028941 | 0
5436 | TUTTL_WB | MB | 61 | -0.087621 | south | Y | -0.14351 | 0.0020951 | -0.14066 | -0.060664 | 0.0020951 | south | N | 0.0020951 | 0
5438 | TUTTL_WB | MB | 95 | -0.087621 | south | Y | -0.14351 | 0.0020951 | -0.14066 | -0.060664 | 0.0020951 | south | N | 0.0020951 | 0
5439 | TUTTL_WB | MB | 151 | -0.087621 | south | Y | -0.14351 | 0.0020951 | -0.14066 | -0.060664 | 0.0020951 | south | N | 0.0020951 | 0
5476 | BRA_AVR1 | 1 | 155 | -0.087026 | south | Y | -0.14291 | 0.0026901 | -0.14007 | -0.060069 | 0.0026901 | south | N | 0.0026901 | 0
5477 | BRA_AVR1 | 1 | 170 | -0.087026 | south | Y | -0.14291 | 0.0026901 | -0.14007 | -0.060069 | 0.0026901 | south | N | 0.0026901 | 0
5478 | BRA_AVR1 | 1 | 155 | -0.087026 | south | Y | -0.14291 | 0.0026901 | -0.14007 | -0.060069 | 0.0026901 | south | N | 0.0026901 | 0
5503 | RAYBURNG | 1 | 22 | -0.071885 | south | Y | -0.12777 | 0.017831 | -0.12493 | -0.044928 | 0.017831 | south | N | 0.017831 | 0
5505 | RAYBURNG | 1 | 11 | -0.071885 | south | Y | -0.12777 | 0.017831 | -0.12493 | -0.044928 | 0.017831 | south | N | 0.017831 | 0
5506 | RAYBURNG | 1 | 11 | -0.071885 | south | Y | -0.12777 | 0.017831 | -0.12493 | -0.044928 | 0.017831 | south | N | 0.017831 | 0
5508 | RAYBURNC | 1 | 47.7 | -0.072423 | south | Y | -0.12831 | 0.017293 | -0.12547 | -0.045466 | 0.017293 | south | N | 0.017293 | 0
5509 | RAYBURNC | 1 | 37.3 | -0.072423 | south | Y | -0.12831 | 0.017293 | -0.12547 | -0.045466 | 0.017293 | south | N | 0.017293 | 0
5511 | RAYBURNC | 1 | 46 | -0.072423 | south | Y | -0.12831 | 0.017293 | -0.12547 | -0.045466 | 0.017293 | south | N | 0.017293 | 0
5512 | RAYBURNC | 1 | 48 | -0.072423 | south | Y | -0.12831 | 0.017293 | -0.12547 | -0.045466 | 0.017293 | south | N | 0.017293 | 0
5728 | FALCONHY | 2 | 12 | -0.075397 | south | N | -0.13128 | 0.014319 | -0.12844 | -0.04844 | 0.014319 | south | N | 0.014319 | 0
5729 | FALCONHY | 3 | 11 | -0.075397 | south | N | -0.13128 | 0.014319 | -0.12844 | -0.04844 | 0.014319 | south | N | 0.014319 | 0
5890 | PEARSALL | 1 | 24 | -0.077807 | south | Y | -0.13369 | 0.011909 | -0.13085 | -0.05085 | 0.011909 | south | N | 0.011909 | 0
5891 | PEARSALL | 1 | 24 | -0.077807 | south | Y | -0.13369 | 0.011909 | -0.13085 | -0.05085 | 0.011909 | south | N | 0.011909 | 0
5892 | PEARSALL | 1 | 23 | -0.077807 | south | Y | -0.13369 | 0.011909 | -0.13085 | -0.05085 | 0.011909 | south | N | 0.011909 | 0
5903 | SANMIGUE | 1 | 396 | -0.082867 | south | Y | -0.13875 | 0.0068491 | -0.13591 | -0.05591 | 0.0068491 | south | N | 0.0068491 | 0
5911 | STP_GN1_ | 1 | 1333 | -0.0502 | houston | N | -0.10609 | 0.039516 | -0.10324 | -0.023243 | 0.023243 | houston | N | 0.023243 | 0
5912 | STP_GN2_ | 2 | 1328 | -0.0502 | houston | N | -0.10609 | 0.039516 | -0.10324 | -0.023243 | 0.023243 | houston | N | 0.023243 | 0
5920 | WELSHDC1 | EQ | 600 | 0 | north | N | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.055887 | 0
5932 | SI_RAY9 | 9 | 38 | -0.074448 | south | Y | -0.13033 | 0.015268 | -0.12749 | -0.047491 | 0.015268 | south | N | 0.015268 | 0
5933 | SI_RAY6 | 6 | 19.3 | -0.074448 | south | Y | -0.13033 | 0.015268 | -0.12749 | -0.047491 | 0.015268 | south | N | 0.015268 | 0
5934 | SI_RAY5 | 5 | 15 | -0.074448 | south | Y | -0.13033 | 0.015268 | -0.12749 | -0.047491 | 0.015268 | south | N | 0.015268 | 0
5935 | SI_RAY10 | 10 | 47 | -0.074448 | south | Y | -0.13033 | 0.015268 | -0.12749 | -0.047491 | 0.015268 | south | N | 0.015268 | 0
6016 | SWMESA | 1 | 75 | 0.046726 | west | Y | -0.0091609 | 0.13644 | -0.0063177 | 0.073683 | 0.0063177 | west | N | 0.0063177 | 0
6096 | NORTHDC7 | EQ | 220 | 0 | west | N | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.053044 | 0
6144 | MCADOO1A | 1 | 150 | 0.054915 | west | Y | -0.00097191 | 0.14463 | 0.0018713 | 0.081872 | 0.00097191 | North | Y | 0.0018713 | 0.1349
6407 | TURKTRAK | 1 | 169.5 | 0.052476 | west | Y | -0.0034109 | 0.14219 | -0.00056773 | 0.079433 | 0.00056773 | west | N | 0.00056773 | 0
6476 | LANGFORD | 1 | 150 | 0.025139 | west | Y | -0.030748 | 0.11486 | -0.027905 | 0.052096 | 0.027905 | west | N | 0.027905 | 0
6637 | SNYDERW1 | 1 | 63 | 0.054112 | west | Y | -0.0017749 | 0.14383 | 0.0010683 | 0.081069 | 0.0010683 | west | N | 0.0010683 | 0
6752 | OKLA0A | 1 | 649.7 | 0.057237 | west | Y | 0.0013501 | 0.14695 | 0.0041933 | 0.084194 | 0.0013501 | North | Y | 0.0041933 | 1.8472
6948 | DENISNDM | 1 | 40 | 0.058686 | north | N | 0.0027991 | 0.1484 | 0.0056423 | 0.085643 | 0.0027991 | North | N | 0.0027991 | 0
6948 | DENISNDM | 2 | 40 | 0.058686 | north | N | 0.0027991 | 0.1484 | 0.0056423 | 0.085643 | 0.0027991 | North | N | 0.0027991 | 0
7000 | L_FERGUS | 1 | 422 | -0.051993 | south | Y | -0.10788 | 0.037723 | -0.10504 | -0.025036 | 0.025036 | houston | Y | 0.037723 | 5.3539
7004 | L_SIMGID | 1 | 132 | -0.091417 | south | Y | -0.1473 | -0.0017009 | -0.14446 | -0.06446 | 0.0017009 | south | N | 0.0017009 | 0
7005 | L_SIMGID | 2 | 134 | -0.091417 | south | Y | -0.1473 | -0.0017009 | -0.14446 | -0.06446 | 0.0017009 | south | N | 0.0017009 | 0
7006 | L_SIMGID | 3 | 323 | -0.091417 | south | Y | -0.1473 | -0.0017009 | -0.14446 | -0.06446 | 0.0017009 | south | N | 0.0017009 | 0
7007 | L_LOSTPI | 1 | 158 | -0.12177 | south | Y | -0.17766 | -0.032055 | -0.17481 | -0.094814 | 0.032055 | south | N | 0.032055 | 0
7008 | L_LOSTPI | 2 | 160 | -0.12177 | south | Y | -0.17766 | -0.032055 | -0.17481 | -0.094814 | 0.032055 | south | N | 0.032055 | 0
7009 | L_LOSTPI | 3 | 175 | -0.12177 | south | Y | -0.17766 | -0.032055 | -0.17481 | -0.094814 | 0.032055 | south | N | 0.032055 | 0
7010 | L_FPPYD1 | 1 | 584 | -0.1043 | south | Y | -0.16018 | -0.014581 | -0.15734 | -0.07734 | 0.014581 | south | N | 0.014581 | 0
7011 | L_FPPYD1 | 2 | 595 | -0.1043 | south | Y | -0.16018 | -0.014581 | -0.15734 | -0.07734 | 0.014581 | south | N | 0.014581 | 0
7012 | L_FPPYD2 | 3 | 433 | -0.10416 | south | Y | -0.16005 | -0.014446 | -0.15721 | -0.077205 | 0.014446 | south | N | 0.014446 | 0
7014 | L_HAYSEN | 1 | 223.9 | -0.09752 | south | Y | -0.15341 | -0.0078039 | -0.15056 | -0.070563 | 0.0078039 | south | N | 0.0078039 | 0
7015 | L_HAYSEN | 2 | 225 | -0.09752 | south | Y | -0.15341 | -0.0078039 | -0.15056 | -0.070563 | 0.0078039 | south | N | 0.0078039 | 0
7016 | L_HAYSEN | 3 | 224.6 | -0.09752 | south | Y | -0.15341 | -0.0078039 | -0.15056 | -0.070563 | 0.0078039 | south | N | 0.0078039 | 0
7017 | L_HAYSEN | 4 | 226.7 | -0.09752 | south | Y | -0.15341 | -0.0078039 | -0.15056 | -0.070563 | 0.0078039 | south | N | 0.0078039 | 0
7020 | L_AUSTPL | 1 | 8 | -0.078023 | south | N | -0.13391 | 0.011693 | -0.13107 | -0.051066 | 0.011693 | south | N | 0.011693 | 0
7020 | L_AUSTPL | 2 | 8 | -0.078023 | south | N | -0.13391 | 0.011693 | -0.13107 | -0.051066 | 0.011693 | south | N | 0.011693 | 0
7022 | L_BUCHAN | 1 | 18 | -0.036872 | south | N | -0.092759 | 0.052844 | -0.089916 | -0.0099151 | 0.0099151 | houston | Y | 0.052844 | 0
7023 | L_BUCHAN | 2 | 18 | -0.036872 | south | N | -0.092759 | 0.052844 | -0.089916 | -0.0099151 | 0.0099151 | houston | Y | 0.052844 | 0
7024 | L_BUCHAN | 3 | 15 | -0.036872 | south | N | -0.092759 | 0.052844 | -0.089916 | -0.0099151 | 0.0099151 | houston | Y | 0.052844 | 0
7026 | L_INKSDA | 1 | 13.7 | -0.040318 | south | N | -0.096205 | 0.049398 | -0.093362 | -0.013361 | 0.013361 | houston | Y | 0.049398 | 0
7028 | L_MARBFA | 1 | 18 | -0.056749 | south | N | -0.11264 | 0.032967 | -0.10979 | -0.029792 | 0.029792 | houston | Y | 0.032967 | 0
7029 | L_MARBFA | 2 | 18 | -0.056749 | south | N | -0.11264 | 0.032967 | -0.10979 | -0.029792 | 0.029792 | houston | Y | 0.032967 | 0
7031 | L_MARSFO | 1 | 35 | -0.067534 | south | N | -0.12342 | 0.022182 | -0.12058 | -0.040577 | 0.022182 | south | N | 0.022182 | 0
7032 | L_MARSFO | 2 | 34 | -0.067534 | south | N | -0.12342 | 0.022182 | -0.12058 | -0.040577 | 0.022182 | south | N | 0.022182 | 0
7033 | L_MARSFO | 3 | 35 | -0.067534 | south | N | -0.12342 | 0.022182 | -0.12058 | -0.040577 | 0.022182 | south | N | 0.022182 | 0
7035 | L_WIRTZ_ | 1 | 28 | -0.051766 | south | N | -0.10765 | 0.03795 | -0.10481 | -0.024809 | 0.024809 | houston | Y | 0.03795 | 0
7036 | L_WIRTZ_ | 2 | 29 | -0.051766 | south | N | -0.10765 | 0.03795 | -0.10481 | -0.024809 | 0.024809 | houston | Y | 0.03795 | 0
7038 | L_DELAWA | 1 | 35 | 0.052155 | west | Y | -0.0037319 | 0.14187 | -0.00088873 | 0.079112 | 0.00088873 | west | N | 0.00088873 | 0
7038 | L_DELAWA | 2 | 30 | 0.052155 | west | Y | -0.0037319 | 0.14187 | -0.00088873 | 0.079112 | 0.00088873 | west | N | 0.00088873 | 0
7303 | L_WPPGS1 | 1 | 50 | -0.092675 | south | Y | -0.14856 | -0.0029589 | -0.14572 | -0.065718 | 0.0029589 | south | N | 0.0029589 | 0
7303 | L_WPPGS1 | 2 | 50 | -0.092675 | south | Y | -0.14856 | -0.0029589 | -0.14572 | -0.065718 | 0.0029589 | south | N | 0.0029589 | 0
7305 | L_WPPGS3 | 3 | 50 | -0.092675 | south | Y | -0.14856 | -0.0029589 | -0.14572 | -0.065718 | 0.0029589 | south | N | 0.0029589 | 0
7305 | L_WPPGS3 | 4 | 50 | -0.092675 | south | Y | -0.14856 | -0.0029589 | -0.14572 | -0.065718 | 0.0029589 | south | N | 0.0029589 | 0
7487 | L_CANYHY | 1 | 6 | -0.090903 | south | N | -0.14679 | -0.0011869 | -0.14395 | -0.063946 | 0.0011869 | south | N | 0.0011869 | 0
7605 | L_MCQUEE | 1 | 2.4 | -0.091018 | south | N | -0.1469 | -0.0013019 | -0.14406 | -0.064061 | 0.0013019 | south | N | 0.0013019 | 0
7605 | L_MCQUEE | 2 | 2.4 | -0.091018 | south | N | -0.1469 | -0.0013019 | -0.14406 | -0.064061 | 0.0013019 | south | N | 0.0013019 | 0
7605 | L_MCQUEE | 3 | 2.8 | -0.091018 | south | N | -0.1469 | -0.0013019 | -0.14406 | -0.064061 | 0.0013019 | south | N | 0.0013019 | 0
7609 | L_SCHUMA | 1 | 4 | -0.090819 | south | N | -0.14671 | -0.0011029 | -0.14386 | -0.063862 | 0.0011029 | south | N | 0.0011029 | 0
7624 | L_LAKEWO | 1 | 2.4 | -0.088608 | south | N | -0.14449 | 0.0011081 | -0.14165 | -0.061651 | 0.0011081 | south | N | 0.0011081 | 0
7624 | L_LAKEWO | 2 | 2.4 | -0.088608 | south | N | -0.14449 | 0.0011081 | -0.14165 | -0.061651 | 0.0011081 | south | N | 0.0011081 | 0
7800 | L_GUADGE | 1 | 147 | -0.090366 | south | Y | -0.14625 | -0.00064985 | -0.14341 | -0.063409 | 0.00064985 | south | N | 0.00064985 | 0
7801 | L_GUADGE | 2 | 138 | -0.090366 | south | Y | -0.14625 | -0.00064985 | -0.14341 | -0.063409 | 0.00064985 | south | N | 0.00064985 | 0
7802 | L_GUADGE | 3 | 140 | -0.090366 | south | Y | -0.14625 | -0.00064985 | -0.14341 | -0.063409 | 0.00064985 | south | N | 0.00064985 | 0
7803 | L_GUADGE | 4 | 147 | -0.090366 | south | Y | -0.14625 | -0.00064985 | -0.14341 | -0.063409 | 0.00064985 | south | N | 0.00064985 | 0
7804 | L_GUADGE | 5 | 182 | -0.090366 | south | Y | -0.14625 | -0.00064985 | -0.14341 | -0.063409 | 0.00064985 | south | N | 0.00064985 | 0
7805 | L_GUADGE | 6 | 198 | -0.090366 | south | Y | -0.14625 | -0.00064985 | -0.14341 | -0.063409 | 0.00064985 | south | N | 0.00064985 | 0
7807 | L_BASTEN | 1 | 152.5 | -0.11769 | south | Y | -0.17358 | -0.027978 | -0.17074 | -0.090737 | 0.027978 | south | N | 0.027978 | 0
7808 | L_BASTEN | 1 | 149.5 | -0.11769 | south | Y | -0.17358 | -0.027978 | -0.17074 | -0.090737 | 0.027978 | south | N | 0.027978 | 0
7809 | L_BASTEN | 1 | 232.6 | -0.11769 | south | Y | -0.17358 | -0.027978 | -0.17074 | -0.090737 | 0.027978 | south | N | 0.027978 | 0
7810 | L_RIONOG | 1 | 142 | -0.093763 | south | Y | -0.14965 | -0.0040469 | -0.14681 | -0.066806 | 0.0040469 | south | N | 0.0040469 | 0
7811 | L_RIONOG | 2 | 145 | -0.093763 | south | Y | -0.14965 | -0.0040469 | -0.14681 | -0.066806 | 0.0040469 | south | N | 0.0040469 | 0
7812 | L_RIONOG | 3 | 151 | -0.093763 | south | Y | -0.14965 | -0.0040469 | -0.14681 | -0.066806 | 0.0040469 | south | N | 0.0040469 | 0
7813 | L_RIONOG | 4 | 290 | -0.093763 | south | Y | -0.14965 | -0.0040469 | -0.14681 | -0.066806 | 0.0040469 | south | N | 0.0040469 | 0
8032 | AMISTADH | 1 | 33 | -0.043138 | south | N | -0.099025 | 0.046578 | -0.096182 | -0.016181 | 0.016181 | houston | Y | 0.046578 | 0
8033 | AMISTADH | 2 | 25 | -0.043138 | south | N | -0.099025 | 0.046578 | -0.096182 | -0.016181 | 0.016181 | houston | Y | 0.046578 | 0
8048 | FALCONHY | 1 | 12 | -0.075397 | south | N | -0.13128 | 0.014319 | -0.12844 | -0.04844 | 0.014319 | south | N | 0.014319 | 0
8066 | DUP1V#1 | 1 | 73 | -0.07246 | south | N | -0.12835 | 0.017256 | -0.1255 | -0.045503 | 0.017256 | south | N | 0.017256 | 0
8134 | FOR69CG0 | 1 | 79 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
8138 | FOR69CG0 | 2 | 81 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
8139 | JOS #1 | MB | 255 | 0 | south | Y | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8147 | UCAR #2 | 10 | 28 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
8148 | UCAR #1 | 2 | 7 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
8153 | FOR69CG0 | 3 | 79 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
8154 | FOR69CG0 | 4 | 80 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
8155 | FOR69CG0 | 5 | 78.4 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
8156 | FOR69CG0 | 6 | 25 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
8157 | FOR69CG0 | 7 | 46 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
8161 | COLETOU1 | 1 | 629 | -0.076364 | south | Y | -0.13225 | 0.013352 | -0.12941 | -0.049407 | 0.013352 | south | N | 0.013352 | 0
8173 | VICEC51A | 5 | 144 | -0.073142 | south | Y | -0.12903 | 0.016574 | -0.12619 | -0.046185 | 0.016574 | south | N | 0.016574 | 0
8174 | VICEC61A | 6 | 188 | -0.073142 | south | Y | -0.12903 | 0.016574 | -0.12619 | -0.046185 | 0.016574 | south | N | 0.016574 | 0
8189 | CUERO 2 | 1 | 12 | -0.084188 | south | N | -0.14007 | 0.0055281 | -0.13723 | -0.057231 | 0.0055281 | south | N | 0.0055281 | 0
8262 | ELPS | 1 | 6 | -0.053953 | south | N | -0.10984 | 0.035763 | -0.107 | -0.026996 | 0.026996 | houston | Y | 0.035763 | 0
8285 | LAR #1 | MB | 32 | 0 | south | Y | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8287 | LAR #2 | MB | 32 | 0 | south | Y | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8288 | LAR #3 | MB | 105 | 0 | south | Y | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8388 | BATES0A | MB | 70 | 0 | south | Y | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8393 | BATES0B | MB | 110 | 0 | south | Y | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8442 | NBEC71A | 1 | 336 | -0.073743 | south | Y | -0.12963 | 0.015973 | -0.12679 | -0.046786 | 0.015973 | south | N | 0.015973 | 0
8456 | COSW#1 | 1 | 20 | 0 | south | N | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8457 | COSW#2 | 2 | 14 | 0 | south | N | -0.055887 | 0.089716 | -0.053044 | 0.026957 | 0.026957 | houston | Y | 0.089716 | 0
8459 | B_DAVIS1 | 1 | 334 | -0.073893 | south | Y | -0.12978 | 0.015823 | -0.12694 | -0.046936 | 0.015823 | south | N | 0.015823 | 0
8460 | B_DAVIS2 | 2 | 340 | -0.073893 | south | Y | -0.12978 | 0.015823 | -0.12694 | -0.046936 | 0.015823 | south | N | 0.015823 | 0
8461 | KOCH_UP0 | 1 | 38 | -0.073972 | south | N | -0.12986 | 0.015744 | -0.12702 | -0.047015 | 0.015744 | south | N | 0.015744 | 0
8506 | VAL #1 | 1 | 25 | -0.073907 | south | N | -0.12979 | 0.015809 | -0.12695 | -0.04695 | 0.015809 | south | N | 0.015809 | 0
8507 | VAL #2 | 2 | 25 | -0.073907 | south | N | -0.12979 | 0.015809 | -0.12695 | -0.04695 | 0.015809 | south | N | 0.015809 | 0
8511 | OXY_CC0A | 1 | 38 | -0.073977 | south | N | -0.12986 | 0.015739 | -0.12702 | -0.04702 | 0.015739 | south | N | 0.015739 | 0
8517 | CELANEBI | 1 | 29 | -0.0743 | south | N | -0.13019 | 0.015416 | -0.12734 | -0.047343 | 0.015416 | south | N | 0.015416 | 0
8560 | CNOPGT1 | 1 | 148.3 | -0.073751 | south | N | -0.12964 | 0.015965 | -0.12679 | -0.046794 | 0.015965 | south | N | 0.015965 | 0
8561 | CNOPGT2 | 2 | 148.6 | -0.073751 | south | N | -0.12964 | 0.015965 | -0.12679 | -0.046794 | 0.015965 | south | N | 0.015965 | 0
8562 | CNOPST1 | 3 | 153 | -0.073751 | south | N | -0.12964 | 0.015965 | -0.12679 | -0.046794 | 0.015965 | south | N | 0.015965 | 0
8926 | LGE_GT10 | 1 | 158 | -0.073074 | south | N | -0.12896 | 0.016642 | -0.12612 | -0.046117 | 0.016642 | south | N | 0.016642 | 0
8927 | LGE_GT20 | 2 | 153 | -0.073074 | south | N | -0.12896 | 0.016642 | -0.12612 | -0.046117 | 0.016642 | south | N | 0.016642 | 0
8928 | LGE_STG0 | 3 | 100 | -0.073074 | south | N | -0.12896 | 0.016642 | -0.12612 | -0.046117 | 0.016642 | south | N | 0.016642 | 0
8930 | ICPGN10A | 1 | 145 | -0.073074 | south | N | -0.12896 | 0.016642 | -0.12612 | -0.046117 | 0.016642 | south | N | 0.016642 | 0
8931 | ICPGN20A | 2 | 147 | -0.073074 | south | N | -0.12896 | 0.016642 | -0.12612 | -0.046117 | 0.016642 | south | N | 0.016642 | 0
8932 | ICPGN30A | 3 | 127 | -0.073074 | south | N | -0.12896 | 0.016642 | -0.12612 | -0.046117 | 0.016642 | south | N | 0.016642 | 0
8933 | FGNTS001 | 1 | 146.5 | -0.074682 | south | Y | -0.13057 | 0.015034 | -0.12773 | -0.047725 | 0.015034 | south | N | 0.015034 | 0
8934 | FGNTS101 | 2 | 147.9 | -0.074682 | south | Y | -0.13057 | 0.015034 | -0.12773 | -0.047725 | 0.015034 | south | N | 0.015034 | 0
8935 | FGNTS201 | 3 | 173 | -0.074682 | south | Y | -0.13057 | 0.015034 | -0.12773 | -0.047725 | 0.015034 | south | N | 0.015034 | 0
8936 | MVGN#1 | 1 | 207 | -0.074568 | south | Y | -0.13045 | 0.015148 | -0.12761 | -0.047611 | 0.015148 | south | N | 0.015148 | 0
8937 | MVGN#2 | 2 | 216.7 | -0.074568 | south | Y | -0.13045 | 0.015148 | -0.12761 | -0.047611 | 0.015148 | south | N | 0.015148 | 0
8938 | MVGN#3 | 3 | 242 | -0.074568 | south | Y | -0.13045 | 0.015148 | -0.12761 | -0.047611 | 0.015148 | south | N | 0.015148 | 0
8981 | HECN1 | 1 | 144 | -0.074566 | south | Y | -0.13045 | 0.01515 | -0.12761 | -0.047609 | 0.01515 | south | N | 0.01515 | 0
8982 | HECN2 | 2 | 144 | -0.074566 | south | Y | -0.13045 | 0.01515 | -0.12761 | -0.047609 | 0.01515 | south | N | 0.01515 | 0
8983 | HECN3 | 3 | 171 | -0.074566 | south | Y | -0.13045 | 0.01515 | -0.12761 | -0.047609 | 0.01515 | south | N | 0.01515 | 0
9000 | DECKR_G1 | 1 | 310 | -0.082468 | south | Y | -0.13835 | 0.0072481 | -0.13551 | -0.055511 | 0.0072481 | south | N | 0.0072481 | 0
9001 | DECKR_G2 | 2 | 413 | -0.082468 | south | Y | -0.13835 | 0.0072481 | -0.13551 | -0.055511 | 0.0072481 | south | N | 0.0072481 | 0
9002 | DECKR_G3 | 3 | 42 | -0.084117 | south | Y | -0.14 | 0.0055991 | -0.13716 | -0.05716 | 0.0055991 | south | N | 0.0055991 | 0
9003 | DECKR_G4 | 4 | 44 | -0.084117 | south | Y | -0.14 | 0.0055991 | -0.13716 | -0.05716 | 0.0055991 | south | N | 0.0055991 | 0
9004 | DECKR_G5 | 5 | 44 | -0.084117 | south | Y | -0.14 | 0.0055991 | -0.13716 | -0.05716 | 0.0055991 | south | N | 0.0055991 | 0
9005 | DECKR_G6 | 6 | 47 | -0.084117 | south | Y | -0.14 | 0.0055991 | -0.13716 | -0.05716 | 0.0055991 | south | N | 0.0055991 | 0
9016 | SANDH_G1 | 1 | 49 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
9017 | SANDH_G2 | 2 | 46 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
9018 | SANDH_G3 | 3 | 46 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
9019 | SANDH_G4 | 4 | 47 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
9020 | SANDHG5A | 5A | 154 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
9021 | SANDHG5C | 5C | 148 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
9022 | SANDH_G6 | 6 | 48 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
9023 | SANDH_G7 | 7 | 48 | -0.085843 | south | Y | -0.14173 | 0.0038731 | -0.13889 | -0.058886 | 0.0038731 | south | N | 0.0038731 | 0
11001 | NAV1CT | 1 | 70 | 0.05307 | west | Y | -0.0028169 | 0.14279 | 2.6265e-05 | 0.080027 | 2.6265e-05 | west | N | 2.6265e-05 | 0
11009 | NAV2CT | 1 | 70 | 0.05307 | west | Y | -0.0028169 | 0.14279 | 2.6265e-05 | 0.080027 | 2.6265e-05 | west | N | 2.6265e-05 | 0
11011 | NAV3ST | 1 | 92.8 | 0.05307 | west | Y | -0.0028169 | 0.14279 | 2.6265e-05 | 0.080027 | 2.6265e-05 | west | N | 2.6265e-05 | 0
11012 | NAV4CT | 1 | 80 | 0.05307 | west | Y | -0.0028169 | 0.14279 | 2.6265e-05 | 0.080027 | 2.6265e-05 | west | N | 2.6265e-05 | 0
11013 | NAV5CT | 1 | 80 | 0.05307 | west | Y | -0.0028169 | 0.14279 | 2.6265e-05 | 0.080027 | 2.6265e-05 | west | N | 2.6265e-05 | 0
11014 | NAV6ST | 1 | 115 | 0.05307 | west | Y | -0.0028169 | 0.14279 | 2.6265e-05 | 0.080027 | 2.6265e-05 | west | N | 2.6265e-05 | 0
11020 | TIEHVSG_ | 1 | 208.2 | 0.05306 | west | Y | -0.0028269 | 0.14278 | 1.6265e-05 | 0.080017 | 1.6265e-05 | west | N | 1.6265e-05 | 0
11021 | TIEHVCG_ | 1 | 142.1 | 0.05306 | west | Y | -0.0028269 | 0.14278 | 1.6265e-05 | 0.080017 | 1.6265e-05 | west | N | 1.6265e-05 | 0
11022 | TIEHVCG_ | 1 | 132.4 | 0.05306 | west | Y | -0.0028269 | 0.14278 | 1.6265e-05 | 0.080017 | 1.6265e-05 | west | N | 1.6265e-05 | 0
11023 | TIEHVCG_ | 1 | 136 | 0.05306 | west | Y | -0.0028269 | 0.14278 | 1.6265e-05 | 0.080017 | 1.6265e-05 | west | N | 1.6265e-05 | 0
11024 | TIEHVCG_ | 1 | 147 | 0.05306 | west | Y | -0.0028269 | 0.14278 | 1.6265e-05 | 0.080017 | 1.6265e-05 | west | N | 1.6265e-05 | 0
11025 | TIEHVSG_ | 1 | 210 | 0.05306 | west | Y | -0.0028269 | 0.14278 | 1.6265e-05 | 0.080017 | 1.6265e-05 | west | N | 1.6265e-05 | 0
11056 | ROSCOE_1 | 1 | 209 | 0.054689 | west | Y | -0.0011979 | 0.14441 | 0.0016453 | 0.081646 | 0.0011979 | North | Y | 0.0016453 | 0.093498
11057 | CHAMPION | 1 | 126.5 | 0.054689 | west | Y | -0.0011979 | 0.14441 | 0.0016453 | 0.081646 | 0.0011979 | North | Y | 0.0016453 | 0.056591
11058 | PYRON_1G | 1 | 249 | 0.054689 | west | Y | -0.0011979 | 0.14441 | 0.0016453 | 0.081646 | 0.0011979 | North | Y | 0.0016453 | 0.11139
11059 | INADALE_ | 1 | 197 | 0.054689 | west | Y | -0.0011979 | 0.14441 | 0.0016453 | 0.081646 | 0.0011979 | North | Y | 0.0016453 | 0.088129
11061 | PNTHRCK1 | 1 | 200 | 0.053905 | west | Y | -0.0019819 | 0.14362 | 0.00086127 | 0.080862 | 0.00086127 | west | N | 0.00086127 | 0
11065 | ELBOWCK_ | 1 | 121.9 | 0.053905 | west | Y | -0.0019819 | 0.14362 | 0.00086127 | 0.080862 | 0.00086127 | west | N | 0.00086127 | 0
11147 | NOTREES_ | 1 | 149 | 0.052322 | west | Y | -0.0035649 | 0.14204 | -0.00072173 | 0.079279 | 0.00072173 | west | N | 0.00072173 | 0
11309 | BULLCREK | 1 | 180 | 0.053787 | west | Y | -0.0020999 | 0.1435 | 0.00074327 | 0.080744 | 0.00074327 | west | N | 0.00074327 | 0
11310 | BULLCREK | 1 | 180 | 0.053787 | west | Y | -0.0020999 | 0.1435 | 0.00074327 | 0.080744 | 0.00074327 | west | N | 0.00074327 | 0
11320 | COYOTE_1 | 1 | 225 | 0.053736 | west | Y | -0.0021509 | 0.14345 | 0.00069227 | 0.080693 | 0.00069227 | west | N | 0.00069227 | 0
11415 | LORAINE_ | 1 | 125 | 0.054383 | west | Y | -0.0015039 | 0.1441 | 0.0013393 | 0.08134 | 0.0013393 | west | N | 0.0013393 | 0
11416 | LORAINE_ | 1 | 125 | 0.054383 | west | Y | -0.0015039 | 0.1441 | 0.0013393 | 0.08134 | 0.0013393 | west | N | 0.0013393 | 0
11691 | KMICHICT | 1 | 140 | 0.058505 | north | N | 0.0026181 | 0.14822 | 0.0054613 | 0.085462 | 0.0026181 | North | N | 0.0026181 | 0
11692 | KMICHICT | 2 | 141 | 0.058505 | north | N | 0.0026181 | 0.14822 | 0.0054613 | 0.085462 | 0.0026181 | North | N | 0.0026181 | 0
11693 | KMICHIST | 3 | 309 | 0.058505 | north | N | 0.0026181 | 0.14822 | 0.0054613 | 0.085462 | 0.0026181 | North | N | 0.0026181 | 0
11694 | KMICHICT | 4 | 143 | 0.058505 | north | N | 0.0026181 | 0.14822 | 0.0054613 | 0.085462 | 0.0026181 | North | N | 0.0026181 | 0
11695 | KMICHICT | 5 | 144 | 0.058505 | north | N | 0.0026181 | 0.14822 | 0.0054613 | 0.085462 | 0.0026181 | North | N | 0.0026181 | 0
11696 | KMICHIST | 6 | 310 | 0.058505 | north | N | 0.0026181 | 0.14822 | 0.0054613 | 0.085462 | 0.0026181 | North | N | 0.0026181 | 0
12322 | ENNSTRAC | 1 | 196 | 0.060703 | north | Y | 0.0048161 | 0.15042 | 0.0076593 | 0.08766 | 0.0048161 | North | N | 0.0048161 | 0
12323 | ENNSTRAC | 2 | 111 | 0.060703 | north | Y | 0.0048161 | 0.15042 | 0.0076593 | 0.08766 | 0.0048161 | North | N | 0.0048161 | 0
12357 | RNRTPL_1 | 1 | 0 | 0.058998 | north | N | 0.0031111 | 0.14871 | 0.0059543 | 0.085955 | 0.0031111 | North | N | 0.0031111 | 0
12411 | FPLEFR1A | 1 | 161 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12412 | FPLEFR1B | 2 | 164 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12413 | FPLEFR1C | 3 | 164 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12414 | FPLEFR1S | 4 | 414 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12421 | FPLEFR2A | 1 | 162 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12422 | FPLEFR2B | 2 | 161 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12423 | FPLEFR2C | 3 | 163 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12424 | FPLEFR2S | 4 | 409 | 0.057685 | north | Y | 0.0017981 | 0.1474 | 0.0046413 | 0.084642 | 0.0017981 | North | N | 0.0017981 | 0
12440 | PARKD_1S | 1 | 0 | 0.058518 | north | N | 0.0026311 | 0.14823 | 0.0054743 | 0.085475 | 0.0026311 | North | N | 0.0026311 | 0
12449 | PARKD_2S | 1 | 0 | 0.058518 | north | N | 0.0026311 | 0.14823 | 0.0054743 | 0.085475 | 0.0026311 | North | N | 0.0026311 | 0
13116 | TGATEWAY | 1 | 148 | 0.054822 | north | N | -0.0010649 | 0.14454 | 0.0017783 | 0.081779 | 0.0010649 | North | N | 0.0010649 | 0
13117 | TGATEWAY | 2 | 130 | 0.054822 | north | N | -0.0010649 | 0.14454 | 0.0017783 | 0.081779 | 0.0010649 | North | N | 0.0010649 | 0
13118 | TGATEWAY | 3 | 145 | 0.054822 | north | N | -0.0010649 | 0.14454 | 0.0017783 | 0.081779 | 0.0010649 | North | N | 0.0010649 | 0
13119 | TGATEWAY | 4 | 399 | 0.054822 | north | N | -0.0010649 | 0.14454 | 0.0017783 | 0.081779 | 0.0010649 | North | N | 0.0010649 | 0
13131 | CALFREST | 1 | 150.7 | 0.050804 | north | Y | -0.0050829 | 0.14052 | -0.0022397 | 0.077761 | 0.0022397 | west | Y | 0.0050829 | 0.42847
13132 | CALFREST | 2 | 151 | 0.050804 | north | Y | -0.0050829 | 0.14052 | -0.0022397 | 0.077761 | 0.0022397 | west | Y | 0.0050829 | 0.42932
13133 | CALFREST | 3 | 177.4 | 0.050804 | north | Y | -0.0050829 | 0.14052 | -0.0022397 | 0.077761 | 0.0022397 | west | Y | 0.0050829 | 0.50438
13134 | CALFREST | 4 | 151.5 | 0.050962 | north | Y | -0.0049249 | 0.14068 | -0.0020817 | 0.077919 | 0.0020817 | west | Y | 0.0049249 | 0.43074
13135 | CALFREST | 5 | 152.3 | 0.050962 | north | Y | -0.0049249 | 0.14068 | -0.0020817 | 0.077919 | 0.0020817 | west | Y | 0.0049249 | 0.43302
13136 | CALFREST | 6 | 177.5 | 0.050962 | north | Y | -0.0049249 | 0.14068 | -0.0020817 | 0.077919 | 0.0020817 | west | Y | 0.0049249 | 0.50466
13432 | SANDOW_5 | 5 | 581 | -0.14701 | south | Y | -0.2029 | -0.057297 | -0.20006 | -0.12006 | 0.057297 | south | N | 0.057297 | 0
13691 | OAKGROVE | 1 | 855 | 0.031872 | north | Y | -0.024015 | 0.12159 | -0.021172 | 0.058829 | 0.021172 | west | Y | 0.024015 | 2.4309
13692 | OAKGROVE | 2 | 855 | 0.031872 | north | Y | -0.024015 | 0.12159 | -0.021172 | 0.058829 | 0.021172 | west | Y | 0.024015 | 2.4309
32798 | BRYN_TAM | 1 | 32 | 0.011556 | north | N | -0.044331 | 0.10127 | -0.041488 | 0.038513 | 0.038513 | houston | Y | 0.044331 | 0
32883 | BRYN_DNS | 1 | 48 | 0.010031 | north | Y | -0.045856 | 0.099747 | -0.043013 | 0.036988 | 0.036988 | houston | Y | 0.045856 | 0.42566
32884 | BRYN_DNS | 1 | 46 | 0.010031 | north | Y | -0.045856 | 0.099747 | -0.043013 | 0.036988 | 0.036988 | houston | Y | 0.045856 | 0.40793
32886 | BRYN_ATK | MB | 12 | 0.011607 | north | Y | -0.04428 | 0.10132 | -0.041437 | 0.038564 | 0.038564 | houston | Y | 0.04428 | 0
32887 | BRYN_ATK | MB | 51 | 0.011607 | north | Y | -0.04428 | 0.10132 | -0.041437 | 0.038564 | 0.038564 | houston | Y | 0.04428 | 0
32888 | BRYN_ATK | 1 | 17 | 0.011607 | north | Y | -0.04428 | 0.10132 | -0.041437 | 0.038564 | 0.038564 | houston | Y | 0.04428 | 0.097172
32890 | BRYN_ATK | MB | 22 | 0.011607 | north | Y | -0.04428 | 0.10132 | -0.041437 | 0.038564 | 0.038564 | houston | Y | 0.04428 | 0
32891 | BRYN_ATK | MB | 25 | 0.011607 | north | Y | -0.04428 | 0.10132 | -0.041437 | 0.038564 | 0.038564 | houston | Y | 0.04428 | 0
32892 | BRYN_DNS | 1 | 105 | 0.010031 | north | Y | -0.045856 | 0.099747 | -0.043013 | 0.036988 | 0.036988 | houston | Y | 0.045856 | 0.93114
36998 | RDCNYNG1 | 1 | 84 | 0.054305 | west | Y | -0.0015819 | 0.14402 | 0.0012613 | 0.081262 | 0.0012613 | west | N | 0.0012613 | 0
38332 | WDWRDU2 | 1 | 80 | 0.046628 | west | Y | -0.0092589 | 0.13634 | -0.0064157 | 0.073585 | 0.0064157 | west | N | 0.0064157 | 0
38437 | TNSRBNMS | 1 | 150 | 0.046578 | west | Y | -0.0093089 | 0.13629 | -0.0064657 | 0.073535 | 0.0064657 | west | N | 0.0064657 | 0
38438 | TNSRBNMS | 1 | 150 | 0.046578 | west | Y | -0.0093089 | 0.13629 | -0.0064657 | 0.073535 | 0.0064657 | west | N | 0.0064657 | 0
38580 | TNBP_CGN | 1 | 70.8 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38590 | TNBP_CGN | 2 | 66.7 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38600 | TNBP_CGN | 5 | 53 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38611 | TNBPAMCG | 1 | 153.2 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38612 | TNBPAMCG | 2 | 153.5 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38613 | TNBPAMCG | 3 | 152.3 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38614 | TNBPAMCG | 4 | 96 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38615 | TNBPAMCG | 1 | 244 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38690 | TNBP_CGN | 3 | 40 | -0.027936 | houston | N | -0.083823 | 0.06178 | -0.08098 | -0.00097907 | 0.00097907 | houston | N | 0.00097907 | 0
38711 | TNTXCTY1 | 1 | 100.3 | -0.02795 | houston | N | -0.083837 | 0.061766 | -0.080994 | -0.00099307 | 0.00099307 | houston | N | 0.00099307 | 0
38712 | TNTXCTY2 | 1 | 92.9 | -0.02795 | houston | N | -0.083837 | 0.061766 | -0.080994 | -0.00099307 | 0.00099307 | houston | N | 0.00099307 | 0
38713 | TNTXCTY3 | 1 | 102.7 | -0.02795 | houston | N | -0.083837 | 0.061766 | -0.080994 | -0.00099307 | 0.00099307 | houston | N | 0.00099307 | 0
38714 | TNTXCTY4 | 1 | 102 | -0.02795 | houston | N | -0.083837 | 0.061766 | -0.080994 | -0.00099307 | 0.00099307 | houston | N | 0.00099307 | 0
39470 | TNDOWCGN | 1 | 32 | -0.02795 | houston | N | -0.083837 | 0.061766 | -0.080994 | -0.00099307 | 0.00099307 | houston | N | 0.00099307 | 0
39480 | TNDOWCGN | 1 | 30 | -0.02795 | houston | N | -0.083837 | 0.061766 | -0.080994 | -0.00099307 | 0.00099307 | houston | N | 0.00099307 | 0
39760 | TNSCLP1_ | 1 | 111 | -0.036786 | houston | N | -0.092673 | 0.05293 | -0.08983 | -0.0098291 | 0.0098291 | houston | N | 0.0098291 | 0
39770 | TNSCLP2_ | 1 | 111 | -0.036786 | houston | N | -0.092673 | 0.05293 | -0.08983 | -0.0098291 | 0.0098291 | houston | N | 0.0098291 | 0
39775 | TNSCLP4_ | 1 | 119 | -0.036786 | houston | N | -0.092673 | 0.05293 | -0.08983 | -0.0098291 | 0.0098291 | houston | N | 0.0098291 | 0
39790 | TNSCLP3_ | 1 | 109.5 | -0.036786 | houston | N | -0.092673 | 0.05293 | -0.08983 | -0.0098291 | 0.0098291 | houston | N | 0.0098291 | 0
39960 | TNTNPONE | 1 | 152.3 | 0.031872 | north | Y | -0.024015 | 0.12159 | -0.021172 | 0.058829 | 0.021172 | west | Y | 0.024015 | 0.43302
39970 | TNTNPONE | 1 | 153 | 0.031872 | north | Y | -0.024015 | 0.12159 | -0.021172 | 0.058829 | 0.021172 | west | Y | 0.024015 | 0.43501
48500 | APD_GT1_ | 1 | 136 | -0.022488 | houston | N | -0.078375 | 0.067228 | -0.075532 | 0.0044689 | 0.0044689 | houston | N | 0.0044689 | 0
48510 | AK_GT1__ | 1 | 33 | -0.030886 | houston | N | -0.086773 | 0.05883 | -0.08393 | -0.0039291 | 0.0039291 | houston | N | 0.0039291 | 0
48511 | LPE_GT1_ | 1 | 42 | -0.022455 | houston | Y | -0.078342 | 0.067261 | -0.075499 | 0.0045019 | 0.0045019 | houston | N | 0.0045019 | 0
48512 | LPE_GT2_ | 2 | 42 | -0.022455 | houston | Y | -0.078342 | 0.067261 | -0.075499 | 0.0045019 | 0.0045019 | houston | N | 0.0045019 | 0
48513 | LPE_GT3_ | 3 | 38 | -0.022455 | houston | Y | -0.078342 | 0.067261 | -0.075499 | 0.0045019 | 0.0045019 | houston | N | 0.0045019 | 0
48514 | LPE_GT4_ | 4 | 38 | -0.022455 | houston | Y | -0.078342 | 0.067261 | -0.075499 | 0.0045019 | 0.0045019 | houston | N | 0.0045019 | 0
48520 | BSF_GT1_ | 1 | 71 | -0.038249 | houston | N | -0.094136 | 0.051467 | -0.091293 | -0.011292 | 0.011292 | houston | N | 0.011292 | 0
48520 | BSF_GT1_ | 2 | 10 | -0.038249 | houston | N | -0.094136 | 0.051467 | -0.091293 | -0.011292 | 0.011292 | houston | N | 0.011292 | 0
48521 | BVE_GT1_ | 1 | 163 | -0.031492 | houston | N | -0.087379 | 0.058224 | -0.084536 | -0.0045351 | 0.0045351 | houston | N | 0.0045351 | 0
48522 | BVE_GT2_ | 2 | 163 | -0.031492 | houston | N | -0.087379 | 0.058224 | -0.084536 | -0.0045351 | 0.0045351 | houston | N | 0.0045351 | 0
48523 | BVE_ST1_ | 3 | 245 | -0.031492 | houston | N | -0.087379 | 0.058224 | -0.084536 | -0.0045351 | 0.0045351 | houston | N | 0.0045351 | 0
48531 | BYU_GT1_ | 1 | 65 | -0.024521 | houston | N | -0.080408 | 0.065195 | -0.077565 | 0.0024359 | 0.0024359 | houston | N | 0.0024359 | 0
48532 | BYU_GT2_ | 2 | 60 | -0.024521 | houston | N | -0.080408 | 0.065195 | -0.077565 | 0.0024359 | 0.0024359 | houston | N | 0.0024359 | 0
48533 | BYU_GT3_ | 3 | 65 | -0.024521 | houston | N | -0.080408 | 0.065195 | -0.077565 | 0.0024359 | 0.0024359 | houston | N | 0.0024359 | 0
48534 | BYU_GT4_ | 4 | 65 | -0.024521 | houston | N | -0.080408 | 0.065195 | -0.077565 | 0.0024359 | 0.0024359 | houston | N | 0.0024359 | 0
48551 | CAL_GT1_ | 1 | 149 | -0.023194 | houston | N | -0.079081 | 0.066522 | -0.076238 | 0.0037629 | 0.0037629 | houston | N | 0.0037629 | 0
48552 | CAL_ST1_ | 2 | 65.1 | -0.023194 | houston | N | -0.079081 | 0.066522 | -0.076238 | 0.0037629 | 0.0037629 | houston | N | 0.0037629 | 0
48561 | CTL_GT2_ | 1 | 91 | -0.02492 | houston | N | -0.080807 | 0.064796 | -0.077964 | 0.0020369 | 0.0020369 | houston | N | 0.0020369 | 0
48562 | CTL_GT3_ | 2 | 87.6 | -0.02492 | houston | N | -0.080807 | 0.064796 | -0.077964 | 0.0020369 | 0.0020369 | houston | N | 0.0020369 | 0
48563 | CTL_GT4_ | 3 | 87 | -0.02492 | houston | N | -0.080807 | 0.064796 | -0.077964 | 0.0020369 | 0.0020369 | houston | N | 0.0020369 | 0
48564 | CTL_GN1_ | 4 | 54.5 | -0.02492 | houston | N | -0.080807 | 0.064796 | -0.077964 | 0.0020369 | 0.0020369 | houston | N | 0.0020369 | 0
48565 | CTL_GN2_ | 5 | 12.2 | -0.02492 | houston | N | -0.080807 | 0.064796 | -0.077964 | 0.0020369 | 0.0020369 | houston | N | 0.0020369 | 0
48581 | CBY_GN1_ | 1 | 743 | -0.020789 | houston | Y | -0.076676 | 0.068927 | -0.073833 | 0.0061679 | 0.0061679 | houston | N | 0.0061679 | 0
48582 | CBY_GN2_ | 2 | 735 | -0.021465 | houston | Y | -0.077352 | 0.068251 | -0.074509 | 0.0054919 | 0.0054919 | houston | N | 0.0054919 | 0
48583 | CBY_GT4_ | 1 | 172 | -0.020585 | houston | Y | -0.076472 | 0.069131 | -0.073629 | 0.0063719 | 0.0063719 | houston | N | 0.0063719 | 0
48584 | CBY_GT4_ | 2 | 172 | -0.020585 | houston | Y | -0.076472 | 0.069131 | -0.073629 | 0.0063719 | 0.0063719 | houston | N | 0.0063719 | 0
48585 | CBY_ST4_ | 3 | 172 | -0.020585 | houston | Y | -0.076472 | 0.069131 | -0.073629 | 0.0063719 | 0.0063719 | houston | N | 0.0063719 | 0
48591 | CHE_GT2_ | 2 | 173 | -0.016834 | houston | N | -0.072721 | 0.072882 | -0.069878 | 0.010123 | 0.010123 | houston | N | 0.010123 | 0
48593 | CHE_GT1_ | 1 | 173 | -0.022354 | houston | N | -0.078241 | 0.067362 | -0.075398 | 0.0046029 | 0.0046029 | houston | N | 0.0046029 | 0
48594 | CHE_GN4_ | 4 | 135 | -0.022354 | houston | N | -0.078241 | 0.067362 | -0.075398 | 0.0046029 | 0.0046029 | houston | N | 0.0046029 | 0
48595 | BTE_GT2_ | 1 | 162.8 | -0.020108 | houston | N | -0.075995 | 0.069608 | -0.073152 | 0.0068489 | 0.0068489 | houston | N | 0.0068489 | 0
48596 | BTE_GT3_ | 2 | 161.4 | -0.020108 | houston | N | -0.075995 | 0.069608 | -0.073152 | 0.0068489 | 0.0068489 | houston | N | 0.0068489 | 0
48597 | BTE_GT4_ | 3 | 158.9 | -0.020108 | houston | N | -0.075995 | 0.069608 | -0.073152 | 0.0068489 | 0.0068489 | houston | N | 0.0068489 | 0
48598 | BTE_ST1_ | 4 | 269.2 | -0.020108 | houston | N | -0.075995 | 0.069608 | -0.073152 | 0.0068489 | 0.0068489 | houston | N | 0.0068489 | 0
48611 | DIB_GT1_ | 1 | 64 | -0.023149 | houston | N | -0.079036 | 0.066567 | -0.076193 | 0.0038079 | 0.0038079 | houston | N | 0.0038079 | 0
48612 | DIB_GT2_ | 2 | 63.2 | -0.023149 | houston | N | -0.079036 | 0.066567 | -0.076193 | 0.0038079 | 0.0038079 | houston | N | 0.0038079 | 0
48613 | DIB_ST1_ | 3 | 82.6 | -0.023149 | houston | N | -0.079036 | 0.066567 | -0.076193 | 0.0038079 | 0.0038079 | houston | N | 0.0038079 | 0
48614 | DIB_GT3_ | 4 | 73.6 | -0.023149 | houston | N | -0.079036 | 0.066567 | -0.076193 | 0.0038079 | 0.0038079 | houston | N | 0.0038079 | 0
48641 | DPEC_GT1 | 1 | 163.2 | -0.023573 | houston | N | -0.07946 | 0.066143 | -0.076617 | 0.0033839 | 0.0033839 | houston | N | 0.0033839 | 0
48642 | DPEC_GT2 | 2 | 157.1 | -0.023573 | houston | N | -0.07946 | 0.066143 | -0.076617 | 0.0033839 | 0.0033839 | houston | N | 0.0033839 | 0
48643 | DPEC_GT3 | 3 | 157.5 | -0.023573 | houston | N | -0.07946 | 0.066143 | -0.076617 | 0.0033839 | 0.0033839 | houston | N | 0.0033839 | 0
48644 | DPEC_GT4 | 4 | 157 | -0.023573 | houston | N | -0.07946 | 0.066143 | -0.076617 | 0.0033839 | 0.0033839 | houston | N | 0.0033839 | 0
48645 | DPEC_ST5 | 5 | 269 | -0.023573 | houston | N | -0.07946 | 0.066143 | -0.076617 | 0.0033839 | 0.0033839 | houston | N | 0.0033839 | 0
48651 | EP_1_2 | 1 | 5 | -0.020825 | houston | N | -0.076712 | 0.068891 | -0.073869 | 0.0061319 | 0.0061319 | houston | N | 0.0061319 | 0
48651 | EP_1_2 | 2 | 21 | -0.020825 | houston | N | -0.076712 | 0.068891 | -0.073869 | 0.0061319 | 0.0061319 | houston | N | 0.0061319 | 0
48671 | FTR_GT1_ | 1 | 154.2 | 0.009634 | north | N | -0.046253 | 0.09935 | -0.04341 | 0.036591 | 0.036591 | houston | Y | 0.046253 | 0
48672 | FTR_GT2_ | 2 | 156 | 0.009634 | north | N | -0.046253 | 0.09935 | -0.04341 | 0.036591 | 0.036591 | houston | Y | 0.046253 | 0
48673 | FTR_GT3_ | 3 | 156 | 0.009634 | north | N | -0.046253 | 0.09935 | -0.04341 | 0.036591 | 0.036591 | houston | Y | 0.046253 | 0
48674 | FTR_CN4_ | 4 | 380 | 0.009634 | north | N | -0.046253 | 0.09935 | -0.04341 | 0.036591 | 0.036591 | houston | Y | 0.046253 | 0
48690 | GBY_GN5_ | 5 | 398 | -0.019943 | houston | Y | -0.07583 | 0.069773 | -0.072987 | 0.0070139 | 0.0070139 | houston | N | 0.0070139 | 0
48691 | GBY_7374 | A | 46 | -0.023932 | houston | Y | -0.079819 | 0.065784 | -0.076976 | 0.0030249 | 0.0030249 | houston | N | 0.0030249 | 0
48691 | GBY_7374 | B | 46 | -0.023932 | houston | Y | -0.079819 | 0.065784 | -0.076976 | 0.0030249 | 0.0030249 | houston | N | 0.0030249 | 0
48692 | GBY_8182 | C | 46 | -0.023932 | houston | Y | -0.079819 | 0.065784 | -0.076976 | 0.0030249 | 0.0030249 | houston | N | 0.0030249 | 0
48692 | GBY_8182 | D | 55 | -0.023932 | houston | Y | -0.079819 | 0.065784 | -0.076976 | 0.0030249 | 0.0030249 | houston | N | 0.0030249 | 0
48693 | GBY_8384 | E | 55 | -0.023932 | houston | Y | -0.079819 | 0.065784 | -0.076976 | 0.0030249 | 0.0030249 | houston | N | 0.0030249 | 0
48693 | GBY_8384 | F | 54 | -0.023932 | houston | Y | -0.079819 | 0.065784 | -0.076976 | 0.0030249 | 0.0030249 | houston | N | 0.0030249 | 0
48721 | LEG_1___ | 1 | 827 | 0.039111 | north | Y | -0.016776 | 0.12883 | -0.013933 | 0.066068 | 0.013933 | west | Y | 0.016776 | 2.3513
48722 | LEG_2___ | 2 | 819 | 0.039111 | north | Y | -0.016776 | 0.12883 | -0.013933 | 0.066068 | 0.013933 | west | Y | 0.016776 | 2.3286
48730 | MNS_GT | 1 | 46.1 | -0.031657 | houston | N | -0.087544 | 0.058059 | -0.084701 | -0.0047001 | 0.0047001 | houston | N | 0.0047001 | 0
48731 | CBE_GT1 | 1 | 76 | -0.04965 | houston | Y | -0.10554 | 0.040066 | -0.10269 | -0.022693 | 0.022693 | houston | N | 0.022693 | 0
48732 | CBE_GT2 | 1 | 76 | -0.04965 | houston | Y | -0.10554 | 0.040066 | -0.10269 | -0.022693 | 0.022693 | houston | N | 0.022693 | 0
48733 | CBE_ST12 | 1 | 105 | -0.04965 | houston | Y | -0.10554 | 0.040066 | -0.10269 | -0.022693 | 0.022693 | houston | N | 0.022693 | 0
48734 | CBE_GT3 | 1 | 74 | -0.04965 | houston | Y | -0.10554 | 0.040066 | -0.10269 | -0.022693 | 0.022693 | houston | N | 0.022693 | 0
48735 | CBE_GT4 | 1 | 74 | -0.04965 | houston | Y | -0.10554 | 0.040066 | -0.10269 | -0.022693 | 0.022693 | houston | N | 0.022693 | 0
48736 | CBE_ST34 | 1 | 102 | -0.04965 | houston | Y | -0.10554 | 0.040066 | -0.10269 | -0.022693 | 0.022693 | houston | N | 0.022693 | 0
48740 | PSG_GN2_ | 1 | 180 | -0.023137 | houston | N | -0.079024 | 0.066579 | -0.076181 | 0.0038199 | 0.0038199 | houston | N | 0.0038199 | 0
48741 | PSG_GT2_ | 1 | 158.6 | -0.023137 | houston | N | -0.079024 | 0.066579 | -0.076181 | 0.0038199 | 0.0038199 | houston | N | 0.0038199 | 0
48742 | PSG_GT3_ | 1 | 157 | -0.023137 | houston | N | -0.079024 | 0.066579 | -0.076181 | 0.0038199 | 0.0038199 | houston | N | 0.0038199 | 0
48761 | PR_GT1__ | 1 | 35 | -0.023407 | houston | N | -0.079294 | 0.066309 | -0.076451 | 0.0035499 | 0.0035499 | houston | N | 0.0035499 | 0
48772 | PHR_GN2_ | MB | 459 | -0.025941 | houston | Y | -0.081828 | 0.063775 | -0.078985 | 0.0010159 | 0.0010159 | houston | N | 0.0010159 | 0
48791 | PSA_GT1_ | 1 | 65 | -0.020821 | houston | N | -0.076708 | 0.068895 | -0.073865 | 0.0061359 | 0.0061359 | houston | N | 0.0061359 | 0
48792 | PSA_GT2_ | 2 | 66 | -0.020821 | houston | N | -0.076708 | 0.068895 | -0.073865 | 0.0061359 | 0.0061359 | houston | N | 0.0061359 | 0
48793 | PSA_GT3_ | 3 | 70 | -0.020821 | houston | N | -0.076708 | 0.068895 | -0.073865 | 0.0061359 | 0.0061359 | houston | N | 0.0061359 | 0
48794 | PSA_GT4_ | 4 | 63 | -0.020821 | houston | N | -0.076708 | 0.068895 | -0.073865 | 0.0061359 | 0.0061359 | houston | N | 0.0061359 | 0
48795 | PSA_GT5_ | 5 | 62 | -0.020821 | houston | N | -0.076708 | 0.068895 | -0.073865 | 0.0061359 | 0.0061359 | houston | N | 0.0061359 | 0
48796 | PSA_GN1_ | 1 | 104 | -0.020821 | houston | N | -0.076708 | 0.068895 | -0.073865 | 0.0061359 | 0.0061359 | houston | N | 0.0061359 | 0
48797 | PSA_GT6_ | 6 | 59 | -0.020821 | houston | N | -0.076708 | 0.068895 | -0.073865 | 0.0061359 | 0.0061359 | houston | N | 0.0061359 | 0
48811 | CVC_GT3_ | 3 | 156 | -0.016834 | houston | N | -0.072721 | 0.072882 | -0.069878 | 0.010123 | 0.010123 | houston | N | 0.010123 | 0
48812 | CVC_GT2_ | 2 | 154 | -0.016834 | houston | N | -0.072721 | 0.072882 | -0.069878 | 0.010123 | 0.010123 | houston | N | 0.010123 | 0
48813 | CVC_GT1_ | 1 | 154 | -0.016834 | houston | N | -0.072721 | 0.072882 | -0.069878 | 0.010123 | 0.010123 | houston | N | 0.010123 | 0
48814 | CVC_ST5_ | 1 | 162 | -0.016834 | houston | N | -0.072721 | 0.072882 | -0.069878 | 0.010123 | 0.010123 | houston | N | 0.010123 | 0
48815 | CVC_GT4_ | 4 | 157 | -0.020666 | houston | N | -0.076553 | 0.06905 | -0.07371 | 0.0062909 | 0.0062909 | houston | N | 0.0062909 | 0
48820 | SHELLG1_ | 1 | 71 | -0.022885 | houston | N | -0.078772 | 0.066831 | -0.075929 | 0.0040719 | 0.0040719 | houston | N | 0.0040719 | 0
48821 | SHELLG2 | 2 | 72 | -0.022885 | houston | N | -0.078772 | 0.066831 | -0.075929 | 0.0040719 | 0.0040719 | houston | N | 0.0040719 | 0
48822 | SHELLG3_ | 1 | 39 | -0.022885 | houston | N | -0.078772 | 0.066831 | -0.075929 | 0.0040719 | 0.0040719 | houston | N | 0.0040719 | 0
48822 | SHELLG3_ | 2 | 30 | -0.022885 | houston | N | -0.078772 | 0.066831 | -0.075929 | 0.0040719 | 0.0040719 | houston | N | 0.0040719 | 0
48841 | SJS_GT1_ | 1 | 78 | -0.023778 | houston | N | -0.079665 | 0.065938 | -0.076822 | 0.0031789 | 0.0031789 | houston | N | 0.0031789 | 0
48842 | SJS_GT2_ | 2 | 80 | -0.023778 | houston | N | -0.079665 | 0.065938 | -0.076822 | 0.0031789 | 0.0031789 | houston | N | 0.0031789 | 0
48845 | SOL_GT1 | 1 | 16.2 | -0.023153 | houston | N | -0.07904 | 0.066563 | -0.076197 | 0.0038039 | 0.0038039 | houston | N | 0.0038039 | 0
48851 | SRB_GN1_ | 1 | 165 | -0.023204 | houston | Y | -0.079091 | 0.066512 | -0.076248 | 0.0037529 | 0.0037529 | houston | N | 0.0037529 | 0
48852 | SRB_GN2_ | 2 | 169 | -0.023219 | houston | Y | -0.079106 | 0.066497 | -0.076263 | 0.0037379 | 0.0037379 | houston | N | 0.0037379 | 0
48853 | SRB_GN3_ | 3 | 213 | -0.023157 | houston | Y | -0.079044 | 0.066559 | -0.076201 | 0.0037999 | 0.0037999 | houston | N | 0.0037999 | 0
48854 | SRB_GN4_ | 4 | 228 | -0.023143 | houston | Y | -0.07903 | 0.066573 | -0.076187 | 0.0038139 | 0.0038139 | houston | N | 0.0038139 | 0
48855 | SRB_GT21 | B2 | 12 | -0.023228 | houston | Y | -0.079115 | 0.066488 | -0.076272 | 0.0037289 | 0.0037289 | houston | N | 0.0037289 | 0
48855 | SRB_GT21 | MB | 18 | -0.023228 | houston | Y | -0.079115 | 0.066488 | -0.076272 | 0.0037289 | 0.0037289 | houston | N | 0.0037289 | 0
48865 | TECO_GT1 | 1 | 50 | -0.026818 | houston | Y | -0.082705 | 0.062898 | -0.079862 | 0.00013893 | 0.00013893 | houston | N | 0.00013893 | 0
48873 | THW_ST3_ | 3 | 104 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48874 | THW_ST4_ | 4 | 104 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48875 | THW_3132 | A | 54 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48875 | THW_3132 | B | 53 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48877 | THW_3334 | C | 54 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48877 | THW_3334 | D | 57 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48879 | THW_4142 | E | 54 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48879 | THW_4142 | F | 54 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48881 | THW_4344 | G | 58 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48881 | THW_4344 | H | 58 | -0.021718 | houston | Y | -0.077605 | 0.067998 | -0.074762 | 0.0052389 | 0.0052389 | houston | N | 0.0052389 | 0
48883 | THW_GT1_ | B2 | 12 | -0.021096 | houston | Y | -0.076983 | 0.06862 | -0.07414 | 0.0058609 | 0.0058609 | houston | N | 0.0058609 | 0
48885 | THW_5152 | A | 56 | -0.019656 | houston | Y | -0.075543 | 0.07006 | -0.0727 | 0.0073009 | 0.0073009 | houston | N | 0.0073009 | 0
48885 | THW_5152 | B | 59 | -0.019656 | houston | Y | -0.075543 | 0.07006 | -0.0727 | 0.0073009 | 0.0073009 | houston | N | 0.0073009 | 0
48886 | THW_5354 | C | 56 | -0.019656 | houston | Y | -0.075543 | 0.07006 | -0.0727 | 0.0073009 | 0.0073009 | houston | N | 0.0073009 | 0
48886 | THW_5354 | D | 56 | -0.019656 | houston | Y | -0.075543 | 0.07006 | -0.0727 | 0.0073009 | 0.0073009 | houston | N | 0.0073009 | 0
48887 | THW_5556 | E | 59 | -0.019656 | houston | Y | -0.075543 | 0.07006 | -0.0727 | 0.0073009 | 0.0073009 | houston | N | 0.0073009 | 0
48887 | THW_5556 | F | 56 | -0.019656 | houston | Y | -0.075543 | 0.07006 | -0.0727 | 0.0073009 | 0.0073009 | houston | N | 0.0073009 | 0
48911 | TGF_GT1_ | 1 | 66 | -0.047265 | houston | Y | -0.10315 | 0.042451 | -0.10031 | -0.020308 | 0.020308 | houston | N | 0.020308 | 0
48921 | WAP_GN1_ | 1 | 161 | -0.030664 | houston | Y | -0.086551 | 0.059052 | -0.083708 | -0.0037071 | 0.0037071 | houston | N | 0.0037071 | 0
48922 | WAP_GN2_ | 2 | 166 | -0.030664 | houston | Y | -0.086551 | 0.059052 | -0.083708 | -0.0037071 | 0.0037071 | houston | N | 0.0037071 | 0
48923 | WAP_GN3_ | 3 | 248 | -0.030664 | houston | Y | -0.086551 | 0.059052 | -0.083708 | -0.0037071 | 0.0037071 | houston | N | 0.0037071 | 0
48924 | WAP_GN4_ | 4 | 546 | -0.030664 | houston | Y | -0.086551 | 0.059052 | -0.083708 | -0.0037071 | 0.0037071 | houston | N | 0.0037071 | 0
48925 | WAP_GN5_ | 5 | 643 | -0.030664 | houston | N | -0.086551 | 0.059052 | -0.083708 | -0.0037071 | 0.0037071 | houston | N | 0.0037071 | 0
48926 | WAP_GN6_ | 6 | 651 | -0.031536 | houston | Y | -0.087423 | 0.05818 | -0.08458 | -0.0045791 | 0.0045791 | houston | N | 0.0045791 | 0
48927 | WAP_GN7_ | 7 | 564 | -0.031536 | houston | Y | -0.087423 | 0.05818 | -0.08458 | -0.0045791 | 0.0045791 | houston | N | 0.0045791 | 0
48928 | WAP_GN8_ | 8 | 600 | -0.031536 | houston | Y | -0.087423 | 0.05818 | -0.08458 | -0.0045791 | 0.0045791 | houston | N | 0.0045791 | 0
48929 | WAPGT21_ | B1 | 13 | -0.030664 | houston | Y | -0.086551 | 0.059052 | -0.083708 | -0.0037071 | 0.0037071 | houston | N | 0.0037071 | 0
48940 | WARVUE_G | G1 | 12 | -0.020808 | houston | Y | -0.076695 | 0.068908 | -0.073852 | 0.0061489 | 0.0061489 | houston | N | 0.0061489 | 0
49803 | EXN_15GT | 1 | 34 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49804 | EXN_16GT | 2 | 34.7 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49805 | EXN_17GT | 3 | 32.7 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49826 | EXN938GT | 5 | 45.9 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49828 | EXN941GT | 10 | 17.7 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49829 | EXN942GT | 11 | 20.4 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49830 | EXN943GT | 12 | 19.9 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49831 | EXN944GT | 13 | 35 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49832 | EXN945GT | 9 | 18 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49837 | EXN_GT | 4 | 85.4 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49838 | EXN_14GT | 14 | 148 | -0.021301 | houston | N | -0.077188 | 0.068415 | -0.074345 | 0.0056559 | 0.0056559 | houston | N | 0.0056559 | 0
49851 | DOW17000 | 37 | 62 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49858 | DOW38100 | 31 | 71.4 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49859 | DOW38200 | 33 | 45 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49860 | DOW38300 | 32 | 101 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49862 | DOW39100 | 36 | 86 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49863 | DOW39200 | 35 | 88 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49865 | DOW41000 | 41 | 50 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49866 | DOW42000 | 42 | 18 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49869 | DOW49000 | 45 | 94 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49870 | DOW61000 | 61 | 70 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49871 | DOW62000 | 62 | 63 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49872 | DOW63000 | 63 | 72 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49873 | DOW64000 | 64 | 64.8 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49876 | DOW65000 | 65 | 101 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49877 | DOW66000 | 66 | 97 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49878 | DOW67000 | 67 | 103 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49882 | DOW81000 | 81 | 76 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49884 | DOW82000 | 82 | 80 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49885 | DOW83000 | 83 | 80 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
49886 | DOW84000 | 84 | 171 | -0.040095 | houston | N | -0.095982 | 0.049621 | -0.093139 | -0.013138 | 0.013138 | houston | N | 0.013138 | 0
58909 | PEARSALL | 1 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58909 | PEARSALL | 2 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58909 | PEARSALL | 3 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58909 | PEARSALL | 4 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58909 | PEARSALL | 5 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58909 | PEARSALL | 6 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58919 | PEARSALL | 1 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58919 | PEARSALL | 2 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58919 | PEARSALL | 3 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58919 | PEARSALL | 4 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58919 | PEARSALL | 5 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58919 | PEARSALL | 6 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58929 | PEARSALL | 1 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58929 | PEARSALL | 2 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58929 | PEARSALL | 3 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58929 | PEARSALL | 4 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58929 | PEARSALL | 5 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58929 | PEARSALL | 6 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58949 | PEARSALL | 1 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58949 | PEARSALL | 2 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58949 | PEARSALL | 3 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58949 | PEARSALL | 4 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58949 | PEARSALL | 5 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
58949 | PEARSALL | 6 | 8.4 | -0.076917 | south | Y | -0.1328 | 0.012799 | -0.12996 | -0.04996 | 0.012799 | south | N | 0.012799 | 0
60000 | DSKY2 | 1 | 76.5 | 0.044282 | west | Y | -0.011605 | 0.134 | -0.0087617 | 0.071239 | 0.0087617 | west | N | 0.0087617 | 0
60003 | KING_NE1 | 1 | 80 | 0.046726 | west | Y | -0.0091609 | 0.13644 | -0.0063177 | 0.073683 | 0.0063177 | west | N | 0.0063177 | 0
60005 | KING_SE1 | 1 | 40 | 0.046726 | west | Y | -0.0091609 | 0.13644 | -0.0063177 | 0.073683 | 0.0063177 | west | N | 0.0063177 | 0
60007 | KING_SW1 | 1 | 80 | 0.047121 | west | Y | -0.0087659 | 0.13684 | -0.0059227 | 0.074078 | 0.0059227 | west | N | 0.0059227 | 0
60016 | WOODWRD1 | 1 | 80 | 0.046639 | west | Y | -0.0092479 | 0.13636 | -0.0064047 | 0.073596 | 0.0064047 | west | N | 0.0064047 | 0
60017 | ORNNWP1 | 1 | 80 | 0.044604 | west | Y | -0.011283 | 0.13432 | -0.0084397 | 0.071561 | 0.0084397 | west | N | 0.0084397 | 0
60018 | DSKY1 | 1 | 84 | 0.043938 | west | Y | -0.011949 | 0.13365 | -0.0091057 | 0.070895 | 0.0091057 | west | N | 0.0091057 | 0
60019 | KING_NW1 | 1 | 80 | 0.047121 | west | Y | -0.0087659 | 0.13684 | -0.0059227 | 0.074078 | 0.0059227 | west | N | 0.0059227 | 0
60057 | CALLAHAN | 1 | 114 | -0.088024 | south | Y | -0.14391 | 0.0016921 | -0.14107 | -0.061067 | 0.0016921 | south | N | 0.0016921 | 0
60058 | BUFF_GAP | 1 | 120 | 0.053888 | west | Y | -0.0019989 | 0.1436 | 0.00084427 | 0.080845 | 0.00084427 | west | N | 0.00084427 | 0
60060 | CIRELLO | 1 | 233 | 0.053888 | west | Y | -0.0019989 | 0.1436 | 0.00084427 | 0.080845 | 0.00084427 | west | N | 0.00084427 | 0
60063 | BUFF_GAP | 1 | 170.2 | 0.053888 | west | Y | -0.0019989 | 0.1436 | 0.00084427 | 0.080845 | 0.00084427 | west | N | 0.00084427 | 0
60066 | H_HOLLOW | 1 | 222 | -0.088024 | south | Y | -0.14391 | 0.0016921 | -0.14107 | -0.061067 | 0.0016921 | south | N | 0.0016921 | 0
60068 | HHOLLOW2 | 1 | 184 | -0.088024 | south | Y | -0.14391 | 0.0016921 | -0.14107 | -0.061067 | 0.0016921 | south | N | 0.0016921 | 0
60070 | HHOLLOW3 | 1 | 224 | -0.088024 | south | Y | -0.14391 | 0.0016921 | -0.14107 | -0.061067 | 0.0016921 | south | N | 0.0016921 | 0
60072 | HHOLLOW4 | 1 | 115 | -0.088024 | south | Y | -0.14391 | 0.0016921 | -0.14107 | -0.061067 | 0.0016921 | south | N | 0.0016921 | 0
60074 | HORSH5 | 1 | 100 | -0.088024 | south | Y | -0.14391 | 0.0016921 | -0.14107 | -0.061067 | 0.0016921 | south | N | 0.0016921 | 0
60081 | WHRLWIND | 1 | 60 | 0.055605 | west | Y | -0.00028191 | 0.14532 | 0.0025613 | 0.082562 | 0.00028191 | North | Y | 0.0025613 | 0.13676
60201 | RIO DRCS | F | 0 | -0.02909 | south | N | -0.084977 | 0.060626 | -0.082134 | -0.0021331 | 0.0021331 | houston | Y | 0.060626 | 0
60202 | FRIEND_R | F | 0 | 0.033317 | west | N | -0.02257 | 0.12303 | -0.019727 | 0.060274 | 0.019727 | west | N | 0.019727 | 0
60203 | PRES0A | BT | 4.8 | 0.048578 | west | N | -0.0073089 | 0.13829 | -0.0044657 | 0.075535 | 0.0044657 | west | N | 0.0044657 | 0
71051 | L_BITTCR | W1 | 37.5 | 0.054675 | west | Y | -0.0012119 | 0.14439 | 0.0016313 | 0.081632 | 0.0012119 | North | Y | 0.0016313 | 0.015726
71054 | L_SWEETW | W1 | 107.5 | 0.054675 | west | Y | -0.0012119 | 0.14439 | 0.0016313 | 0.081632 | 0.0012119 | North | Y | 0.0016313 | 0.045081
71057 | L_SWEETW | W1 | 135 | 0.054675 | west | Y | -0.0012119 | 0.14439 | 0.0016313 | 0.081632 | 0.0012119 | North | Y | 0.0016313 | 0.056613
71059 | L_SWEETW | W1 | 119 | 0.054675 | west | Y | -0.0012119 | 0.14439 | 0.0016313 | 0.081632 | 0.0012119 | North | Y | 0.0016313 | 0.049904
71060 | L_SWEETW | W1 | 105 | 0.054675 | west | Y | -0.0012119 | 0.14439 | 0.0016313 | 0.081632 | 0.0012119 | North | Y | 0.0016313 | 0.044033
71061 | L_SWEETW | W1 | 80.5 | 0.054675 | west | Y | -0.0012119 | 0.14439 | 0.0016313 | 0.081632 | 0.0012119 | North | Y | 0.0016313 | 0.033758
76031 | L_GASCCR | W1 | 150 | 0.053256 | west | Y | -0.0026309 | 0.14297 | 0.00021227 | 0.080213 | 0.00021227 | west | N | 0.00021227 | 0
76091 | L_DIVIDE | W1 | 112.5 | 0.053085 | west | Y | -0.0028019 | 0.1428 | 4.1265e-05 | 0.080042 | 4.1265e-05 | west | N | 4.1265e-05 | 0
76095 | L_CAPRSI | W1 | 149.5 | 0.053085 | west | Y | -0.0028019 | 0.1428 | 4.1265e-05 | 0.080042 | 4.1265e-05 | west | N | 4.1265e-05 | 0
76096 | L_CAPRSI | W1 | 186 | 0.053085 | west | Y | -0.0028019 | 0.1428 | 4.1265e-05 | 0.080042 | 4.1265e-05 | west | N | 4.1265e-05 | 0
76097 | L_CAPRGE | W1 | 214.5 | 0.053085 | west | Y | -0.0028019 | 0.1428 | 4.1265e-05 | 0.080042 | 4.1265e-05 | west | N | 4.1265e-05 | 0
80003 | MILHWYS | F | 0 | -0.074448 | south | N | -0.13033 | 0.015268 | -0.12749 | -0.047491 | 0.015268 | south | N | 0.015268 | 0
80010 | EPLVT1 | F | 0 | -0.056469 | south | N | -0.11236 | 0.033247 | -0.10951 | -0.029512 | 0.029512 | houston | Y | 0.033247 | 0
80012 | LAR | F | 0 | -0.077747 | south | N | -0.13363 | 0.011969 | -0.13079 | -0.05079 | 0.011969 | south | N | 0.011969 | 0
80051 | FORPVCM0 | 8 | 28 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
80052 | FOR69CG0 | 9 | 43.6 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
80053 | FOR69CG0 | 10 | 74 | -0.068429 | south | N | -0.12432 | 0.021287 | -0.12147 | -0.041472 | 0.021287 | south | N | 0.021287 | 0
80080 | GWINDT11 | 1 | 94 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80080 | GWINDT11 | 2 | 41 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80080 | GWINDT11 | 3 | 38 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80080 | GWINDT11 | 4 | 19 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80081 | GWINDT21 | 1 | 94 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80081 | GWINDT21 | 2 | 36 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80081 | GWINDT21 | 3 | 43 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80081 | GWINDT21 | 4 | 22 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80137 | CSDR89 | 8 | 39 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
80137 | CSDR89 | 9 | 15 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
80138 | CSDR7 | 7 | 7 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
80139 | CSDR56 | 5 | 15 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
80139 | CSDR56 | 6 | 39 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
80140 | CSDR11 | 11 | 39 | -0.070606 | south | N | -0.12649 | 0.01911 | -0.12365 | -0.043649 | 0.01911 | south | N | 0.01911 | 0
80180 | PNSCALT1 | 1 | 148 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80180 | PNSCALT1 | 2 | 50 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80181 | PNSCALT2 | 1 | 55 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80181 | PNSCALT2 | 2 | 50 | -0.074406 | south | Y | -0.13029 | 0.01531 | -0.12745 | -0.047449 | 0.01531 | south | N | 0.01531 | 0
80223 | REYSHR G | 1 | 12 | -0.073074 | south | N | -0.12896 | 0.016642 | -0.12612 | -0.046117 | 0.016642 | south | N | 0.016642 | 0
80224 | VISTRONG | 1 | 15 | -0.071284 | south | N | -0.12717 | 0.018432 | -0.12433 | -0.044327 | 0.018432 | south | N | 0.018432 | 0
80225 | VISTRONG | 2 | 23 | -0.071284 | south | N | -0.12717 | 0.018432 | -0.12433 | -0.044327 | 0.018432 | south | N | 0.018432 | 0
80226 | ALCOA G | 1 | 48 | -0.068937 | south | N | -0.12482 | 0.020779 | -0.12198 | -0.04198 | 0.020779 | south | N | 0.020779 | 0
80227 | AIRCO G | 1 | 8 | -0.070862 | south | N | -0.12675 | 0.018854 | -0.12391 | -0.043905 | 0.018854 | south | N | 0.018854 | 0
80261 | NBEC81A | 1 | 180 | -0.073763 | south | Y | -0.12965 | 0.015953 | -0.12681 | -0.046806 | 0.015953 | south | N | 0.015953 | 0
80262 | NBEC91A | 1 | 180 | -0.073743 | south | Y | -0.12963 | 0.015973 | -0.12679 | -0.046786 | 0.015973 | south | N | 0.015973 | 0
80263 | B_DAVIS3 | 3 | 180 | -0.073893 | south | Y | -0.12978 | 0.015823 | -0.12694 | -0.046936 | 0.015823 | south | N | 0.015823 | 0
80264 | B_DAVIS4 | 4 | 180 | -0.073893 | south | Y | -0.12978 | 0.015823 | -0.12694 | -0.046936 | 0.015823 | south | N | 0.015823 | 0
80265 | LARECU40 | 4 | 100 | -0.077754 | south | Y | -0.13364 | 0.011962 | -0.1308 | -0.050797 | 0.011962 | south | N | 0.011962 | 0
80266 | LARECU50 | 5 | 100 | -0.077754 | south | Y | -0.13364 | 0.011962 | -0.1308 | -0.050797 | 0.011962 | south | N | 0.011962 | 0
80291 | PAPALOTE | 1 | 25 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
80291 | PAPALOTE | 2 | 25 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
80291 | PAPALOTE | 3 | 25 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
80291 | PAPALOTE | 4 | 16 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
80294 | PAPALOTE | 5 | 25 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
80294 | PAPALOTE | 6 | 25 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
80294 | PAPALOTE | 7 | 25 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
80294 | PAPALOTE | 8 | 15 | -0.073342 | south | Y | -0.12923 | 0.016374 | -0.12639 | -0.046385 | 0.016374 | south | N | 0.016374 | 0
86104 | CID-138 | EQ | 0 | -0.077754 | south | N | -0.13364 | 0.011962 | -0.1308 | -0.050797 | 0.011962 | south | N | 0.011962 | 0
86105 | CID-230 | EQ | 500 | -0.077754 | south | N | -0.13364 | 0.011962 | -0.1308 | -0.050797 | 0.011962 | south | N | 0.011962 | 0
86106 | CUF-230 | EQ | 500 | -0.077754 | south | N | -0.13364 | 0.011962 | -0.1308 | -0.050797 | 0.011962 | south | N | 0.011962 | 0
86107 | CUF-138 | EQ | 0 | -0.077754 | south | N | -0.13364 | 0.011962 | -0.1308 | -0.050797 | 0.011962 | south | N | 0.011962 | 0
88198 | BEEVILLE | F | 0 | -0.077094 | south | N | -0.13298 | 0.012622 | -0.13014 | -0.050137 | 0.012622 | south | N | 0.012622 | 0
88253 | HAMILTON | F | 0 | -0.043138 | south | N | -0.099025 | 0.046578 | -0.096182 | -0.016181 | 0.016181 | houston | Y | 0.046578 | 0
88299 | ZAPATA | F | 0 | -0.076081 | south | N | -0.13197 | 0.013635 | -0.12912 | -0.049124 | 0.013635 | south | N | 0.013635 | 0
88508 | FALFURRI | F | 0 | -0.07549 | south | N | -0.13138 | 0.014226 | -0.12853 | -0.048533 | 0.014226 | south | N | 0.014226 | 0

## GenConcentration_dec
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TEMP_SS_ to SANDOW_ 345kV [3414 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax source | PTDF calc | PTDF Weighting - Source | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.096231 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18168 | 0 | 0 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.096231 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.7338 | 787 | 0.18168 | 142.9803 | 787 | 142.9803
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.09236 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17781 | 0 | 787 | 142.9803
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.09236 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17781 | 0 | 787 | 142.9803 | Weighted Shift Factors
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.091815 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.4128 | 255 | 0.17726 | 45.2017 | 1042 | 188.1821 | North | 0.055887
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.091815 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.6804 | 149 | 0.17726 | 26.412 | 1191 | 214.5941 | South | -0.085447
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.091815 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.0477 | 153 | 0.17726 | 27.121 | 1344 | 241.7151 |  | 0.14133
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.08846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.269 | 150 | 0.17391 | 26.086 | 1494 | 267.8011
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.08846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0768 | 80 | 0.17391 | 13.9125 | 1574 | 281.7136 | Line Rating | 1072
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.083659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2549 | 0 | 0.16911 | 0 | 1574 | 281.7136 | Conc Gen | 2056
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.083659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2549 | 0 | 0.16911 | 0 | 1574 | 281.7136 | Weighted Imp. | 354.0379
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.065029 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.9249 | 168 | 0.15048 | 25.2799 | 1742 | 306.9935 | PTDF | 0.1722
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.065029 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.8526 | 90 | 0.15048 | 13.5428 | 1832 | 320.5364
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3615 | 224 | 0.14956 | 33.5016 | 2056 | 354.0379 | Concentration | 1.2184
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4898 | 226 | 0.14956 | 33.8007
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5922 | 212 | 0.14956 | 31.7069
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5281 | 211 | 0.14956 | 31.5573
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.063705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7858 | 216.4 | 0.14915 | 32.2764
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.063705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7667 | 216.1 | 0.14915 | 32.2317
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.4097 | 70 | 0.14844 | 10.391
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3467 | 69 | 0.14844 | 10.2425
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3467 | 69 | 0.14844 | 10.2425
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2837 | 68 | 0.14844 | 10.0941
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.062373 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.5532 | 73 | 0.14782 | 10.7908
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.062373 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.4224 | 119 | 0.14782 | 17.5905
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.062373 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.7865 | 205 | 0.14782 | 30.303
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.062373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.362 | 102 | 0.14782 | 15.0776
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.062373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.9878 | 96 | 0.14782 | 14.1907
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.062279 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.7367 | 60 | 0.14773 | 8.8635
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.061706 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14715 | 0
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.061589 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.3277 | 395 | 0.14704 | 58.0791
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.061589 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.7912 | 435 | 0.14704 | 63.9605
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.3789 | 217.3 | 0.14702 | 31.9465
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.6216 | 205 | 0.14702 | 30.1382
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7714 | 272.4 | 0.14702 | 40.0471
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.061476 | north | 3 | N | N | Nnorth | Nnorth | 1 | 71.1277 | 0 | 0.14692 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.061476 | north | 3 | N | N | Nnorth | Nnorth | 1 | 71.1892 | 0 | 0.14692 | 0
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.061452 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.7316 | 435 | 0.1469 | 63.9009
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.1055 | 18 | 0.14686 | 2.6436
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.1055 | 18 | 0.14686 | 2.6436
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3339 | 38 | 0.14686 | 5.5809
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.060703 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8978 | 196 | 0.14615 | 28.6453
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.060703 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.738 | 111 | 0.14615 | 16.2226
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.060651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1461 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.060651 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1461 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.060651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1461 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.4563 | 288 | 0.14606 | 42.0649
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.91 | 147 | 0.14606 | 21.4706
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.91 | 147 | 0.14606 | 21.4706
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.060184 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.2221 | 120 | 0.14563 | 17.4757
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.060176 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72211 | 0 | 0.14562 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.060176 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72211 | 0 | 0.14562 | 0
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.05977 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.7241 | 112.5 | 0.14522 | 16.3369
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.059614 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5768 | 60 | 0.14506 | 8.7036
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.059614 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.7557 | 63 | 0.14506 | 9.1388
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.1502 | 204 | 0.14501 | 29.5814
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.9716 | 201 | 0.14501 | 29.1463
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4135 | 242 | 0.14501 | 35.0916
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.059497 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.0206 | 118 | 0.14494 | 17.1034
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.059497 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.8422 | 115 | 0.14494 | 16.6685
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.059497 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.0803 | 556 | 0.14494 | 80.5887
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.059032 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14448 | 0
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.058998 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14444 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.058705 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.2066 | 242 | 0.14415 | 34.8847
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.058686 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3474 | 0 | 0.14413 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.058686 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3474 | 0 | 0.14413 | 0
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.058602 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.9623 | 170 | 0.14405 | 24.4883
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.058602 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.473 | 520 | 0.14405 | 74.9053
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1711 | 20 | 0.144 | 2.88
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1711 | 20 | 0.144 | 2.88
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1711 | 20 | 0.144 | 2.88
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.99543 | 17 | 0.144 | 2.448
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058518 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14396 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058518 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14396 | 0
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.058505 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 21.6469 | 370 | 0.14395 | 53.2621
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1907 | 0 | 0.14395 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.2492 | 0 | 0.14395 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.078 | 0 | 0.14395 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.3662 | 0 | 0.14395 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.4247 | 0 | 0.14395 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.1365 | 0 | 0.14395 | 0
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3518 | 160 | 0.1439 | 23.0233
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.118 | 156 | 0.1439 | 22.4477
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.456 | 196 | 0.1439 | 28.2036
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.118 | 156 | 0.1439 | 22.4477
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.1765 | 157 | 0.1439 | 22.5916
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.5729 | 198 | 0.1439 | 28.4913
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.058432 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.3861 | 366 | 0.14388 | 52.6596
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.38 | 0 | 0.14385 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.6486 | 0 | 0.14385 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.1626 | 0 | 0.14385 | 0
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.058384 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3354 | 40 | 0.14383 | 5.7532
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.6106 | 79 | 0.14381 | 11.3609
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.1864 | 106 | 0.14381 | 15.2437
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.5209 | 146 | 0.14381 | 20.9961
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.058362 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.4355 | 76 | 0.14381 | 10.9295
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.5632 | 558 | 0.1438 | 80.2425
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 33.7887 | 579 | 0.1438 | 83.2623
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 47.1525 | 808 | 0.1438 | 116.1934
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.058281 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 22.613 | 388 | 0.14373 | 55.7663
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.058281 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.0147 | 515 | 0.14373 | 74.0198
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.058264 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4566 | 25 | 0.14371 | 3.5928
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.058264 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3888 | 41 | 0.14371 | 5.8921
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.058263 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1653 | 20 | 0.14371 | 2.8742
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.058092 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.0126 | 224 | 0.14354 | 32.1527
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2873 | 161 | 0.14313 | 23.0442
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4603 | 164 | 0.14313 | 23.4736
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4603 | 164 | 0.14313 | 23.4736
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8816 | 414 | 0.14313 | 59.2565
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.345 | 162 | 0.14313 | 23.1873
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2873 | 161 | 0.14313 | 23.0442
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4027 | 163 | 0.14313 | 23.3305
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5932 | 409 | 0.14313 | 58.5409
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.057237 | west | 4 | Y | N | Ywest | Nwest | 1 | 37.1869 | 649.7 | 0.14268 | 92.7016
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.05681 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3736 | 165 | 0.14226 | 23.4724
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.056298 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2863 | 236 | 0.14174 | 33.4517
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.056296 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.5184 | 400 | 0.14174 | 56.6971
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.055605 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3363 | 60 | 0.14105 | 8.4631
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.3006 | 785 | 0.14061 | 110.3762
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.8522 | 795 | 0.14061 | 111.7823
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.0248 | 780 | 0.14061 | 109.6732
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.054915 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2372 | 150 | 0.14036 | 21.0543
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1137 | 0 | 0.14027 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.1269 | 0 | 0.14027 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.9492 | 0 | 0.14027 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.874 | 0 | 0.14027 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.43 | 209 | 0.14014 | 29.2884
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9182 | 126.5 | 0.14014 | 17.7272
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6176 | 249 | 0.14014 | 34.8938
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7737 | 197 | 0.14014 | 27.6067
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0503 | 37.5 | 0.14012 | 5.2546
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8776 | 107.5 | 0.14012 | 15.0631
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3811 | 135 | 0.14012 | 18.9164
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5063 | 119 | 0.14012 | 16.6745
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7409 | 105 | 0.14012 | 14.7128
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4013 | 80.5 | 0.14012 | 11.2798
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.054569 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1853 | 150 | 0.14002 | 21.0024
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.054569 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5115 | 101 | 0.14002 | 14.1416
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.054433 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.13988 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.054401 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.7201 | 50 | 0.13985 | 6.9924
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.054383 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7979 | 125 | 0.13983 | 17.4787
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.054383 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7979 | 125 | 0.13983 | 17.4787
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.054305 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5616 | 84 | 0.13975 | 11.7391
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.054175 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.8598 | 182 | 0.13962 | 25.4111
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.054175 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.2207 | 484 | 0.13962 | 67.5769
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.054166 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3624 | 99 | 0.13961 | 13.8217
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.054166 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3041 | 61 | 0.13961 | 8.5164
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3541 | 0 | 0.13961 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4754 | 0 | 0.13961 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4754 | 0 | 0.13961 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.054151 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6353 | 141 | 0.1396 | 19.6833
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.054151 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4981 | 120 | 0.1396 | 16.7517
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.054112 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4091 | 63 | 0.13956 | 8.7922
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5674 | 66 | 0.1395 | 9.2068
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7295 | 69 | 0.1395 | 9.6253
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7295 | 69 | 0.1395 | 9.6253
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6214 | 67 | 0.1395 | 9.3463
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6214 | 67 | 0.1395 | 9.3463
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5133 | 65 | 0.1395 | 9.0673
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0858 | 150 | 0.13935 | 20.9028
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8591 | 220 | 0.13935 | 30.6574
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.781 | 200 | 0.13935 | 27.8703
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.571 | 121.9 | 0.13935 | 16.987
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4666 | 120 | 0.13933 | 16.7202
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5559 | 233 | 0.13933 | 32.465
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1717 | 170.2 | 0.13933 | 23.7148
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053787 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6817 | 180 | 0.13923 | 25.0621
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053787 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6817 | 180 | 0.13923 | 25.0621
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7626 | 0 | 0.1392 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 1 | 3.9453 | 0 | 0.1392 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7841 | 0 | 0.1392 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.053736 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.0906 | 225 | 0.13918 | 31.3161
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.053649 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4379 | 120 | 0.1391 | 16.6915
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.053626 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4351 | 120 | 0.13907 | 16.6887
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.05335 | west | 8 | N | N | Nwest | Nwest | 1 | 1.3764 | 0 | 0.1388 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.053256 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9884 | 150 | 0.1387 | 20.8054
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.053247 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4055 | 214.2 | 0.13869 | 29.7082
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.053134 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.34 | 100.5 | 0.13858 | 13.9274
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.053116 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0807 | 58 | 0.13856 | 8.0366
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9721 | 112.5 | 0.13853 | 15.5848
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9362 | 149.5 | 0.13853 | 20.7105
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.8738 | 186 | 0.13853 | 25.7669
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3867 | 214.5 | 0.13853 | 29.715
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7149 | 70 | 0.13852 | 9.6962
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7149 | 70 | 0.13852 | 9.6962
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.9249 | 92.8 | 0.13852 | 12.8543
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2456 | 80 | 0.13852 | 11.0813
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2456 | 80 | 0.13852 | 11.0813
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.103 | 115 | 0.13852 | 15.9294
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0471 | 208.2 | 0.13851 | 28.8371
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.5398 | 142.1 | 0.13851 | 19.6818
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.0251 | 132.4 | 0.13851 | 18.3383
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.2162 | 136 | 0.13851 | 18.8369
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.7998 | 147 | 0.13851 | 20.3605
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.1426 | 210 | 0.13851 | 29.0864
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.052737 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34806 | 6.6 | 0.13818 | 0.91201
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.052737 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8089 | 34.3 | 0.13818 | 4.7397
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.052476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8947 | 169.5 | 0.13792 | 23.3779
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.052322 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.796 | 149 | 0.13777 | 20.5275
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.052155 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8254 | 35 | 0.1376 | 4.8161
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.052155 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5647 | 30 | 0.1376 | 4.1281
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4389 | 66 | 0.13755 | 9.0784
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.3868 | 65 | 0.13755 | 8.9409
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.491 | 67 | 0.13755 | 9.216
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.491 | 67 | 0.13755 | 9.216
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.491 | 67 | 0.13755 | 9.216
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.052105 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13755 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.052105 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13755 | 0
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.7207 | 151.5 | 0.13641 | 20.6659
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.7615 | 152.3 | 0.13641 | 20.775
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0458 | 177.5 | 0.13641 | 24.2125
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6562 | 150.7 | 0.13625 | 20.533
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6714 | 151 | 0.13625 | 20.5739
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0126 | 177.4 | 0.13625 | 24.1709
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.04995 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.7192 | 615 | 0.1354 | 83.269
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.04995 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.3207 | 587 | 0.1354 | 79.4779
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.048578 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.23317 | 0 | 0.13402 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.047121 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7697 | 80 | 0.13257 | 10.6054
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.047121 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7697 | 80 | 0.13257 | 10.6054
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5044 | 75 | 0.13217 | 9.913
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7381 | 80 | 0.13217 | 10.5738
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.869 | 40 | 0.13217 | 5.2869
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046639 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7311 | 80 | 0.13209 | 10.5669
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.046628 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7302 | 80 | 0.13207 | 10.566
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.046578 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9867 | 150 | 0.13202 | 19.8037
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.046578 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9867 | 150 | 0.13202 | 19.8037
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.044604 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5683 | 80 | 0.13005 | 10.4041
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.044282 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3876 | 76.5 | 0.12973 | 9.9242
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.043938 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6908 | 84 | 0.12938 | 10.8683
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.039111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.3448 | 827 | 0.12456 | 103.0092
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.039111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.0319 | 819 | 0.12456 | 102.0127
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033317 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11876 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.2506 | 855 | 0.11732 | 100.3075
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.2506 | 855 | 0.11732 | 100.3075
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.8541 | 152.3 | 0.11732 | 17.8676
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.8764 | 153 | 0.11732 | 17.9498
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.025139 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7708 | 150 | 0.11059 | 16.5879
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.014683 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.7982 | 463 | 0.10013 | 46.36
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.011607 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19732 | 17 | 0.097054 | 1.6499
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.011556 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.36979 | 0 | 0.097003 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.010031 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.48149 | 48 | 0.095478 | 4.5829
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.010031 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.46143 | 46 | 0.095478 | 4.392
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.010031 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0533 | 105 | 0.095478 | 10.0252
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4856 | 0 | 0.095081 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5029 | 0 | 0.095081 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5029 | 0 | 0.095081 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6609 | 0 | 0.095081 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.085447 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.085447 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.02909 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.056357 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -8.8024 | 100 | -0.0025773 | -0.25773
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055887 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055887 | 0
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.9123 | 0 | -0.072721 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6261 | 0 | -0.072721 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5924 | 0 | -0.072721 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5924 | 0 | -0.072721 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016834 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7271 | 0 | -0.072721 | 0
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1597 | 59 | -0.075543 | -4.457
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1597 | 59 | -0.075543 | -4.457
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.019943 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.9373 | 398 | -0.07583 | -30.1803
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2736 | 0 | -0.075995 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2454 | 0 | -0.075995 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1952 | 0 | -0.075995 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4131 | 0 | -0.075995 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5406 | 172 | -0.076472 | -13.1532
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5406 | 172 | -0.076472 | -13.1532
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5406 | 172 | -0.076472 | -13.1532
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.020666 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2446 | 0 | -0.076553 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.020789 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.4462 | 743 | -0.076676 | -56.9702
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.020808 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.2497 | 12 | -0.076695 | -0.92034
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3534 | 0 | -0.076708 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3742 | 0 | -0.076708 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4575 | 0 | -0.076708 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3117 | 0 | -0.076708 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2909 | 0 | -0.076708 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1654 | 0 | -0.076708 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2284 | 0 | -0.076708 | 0
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.020825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10412 | 0 | -0.076712 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.020825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43733 | 0 | -0.076712 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.021096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.25315 | 12 | -0.076983 | -0.92379
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72423 | 0 | -0.077188 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73914 | 0 | -0.077188 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69654 | 0 | -0.077188 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97772 | 0 | -0.077188 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37703 | 0 | -0.077188 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43454 | 0 | -0.077188 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42389 | 0 | -0.077188 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74553 | 0 | -0.077188 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38342 | 0 | -0.077188 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8191 | 0 | -0.077188 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1525 | 0 | -0.077188 | 0
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.021465 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.7768 | 735 | -0.077352 | -56.8537
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2587 | 104 | -0.077605 | -8.0709
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2587 | 104 | -0.077605 | -8.0709
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1511 | 53 | -0.077605 | -4.1131
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2379 | 57 | -0.077605 | -4.4235
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2596 | 58 | -0.077605 | -4.5011
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2596 | 58 | -0.077605 | -4.5011
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.022354 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8672 | 0 | -0.078241 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.022354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0178 | 0 | -0.078241 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.94311 | 42 | -0.078342 | -3.2904
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.94311 | 42 | -0.078342 | -3.2904
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.85329 | 38 | -0.078342 | -2.977
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.85329 | 38 | -0.078342 | -2.977
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.022488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0584 | 0 | -0.078375 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6248 | 0 | -0.078772 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6477 | 0 | -0.078772 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89251 | 0 | -0.078772 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68655 | 0 | -0.078772 | 0
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1647 | 0 | -0.079024 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6695 | 0 | -0.079024 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6325 | 0 | -0.079024 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.023143 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2766 | 228 | -0.07903 | -18.0188
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4815 | 0 | -0.079036 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.463 | 0 | -0.079036 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9121 | 0 | -0.079036 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7038 | 0 | -0.079036 | 0
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.023153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37508 | 0 | -0.07904 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.023157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9324 | 213 | -0.079044 | -16.8364
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.023194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4559 | 0 | -0.079081 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.023194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5099 | 0 | -0.079081 | 0
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.023204 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.8287 | 165 | -0.079091 | -13.05
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.023219 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.924 | 169 | -0.079106 | -13.3689
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.023228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.27874 | 12 | -0.079115 | -0.94938
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.023228 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.079115 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.023407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.81925 | 0 | -0.079294 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8471 | 0 | -0.07946 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7033 | 0 | -0.07946 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7127 | 0 | -0.07946 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.701 | 0 | -0.07946 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3411 | 0 | -0.07946 | 0
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.023778 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8547 | 0 | -0.079665 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.023778 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9022 | 0 | -0.079665 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1009 | 46 | -0.079819 | -3.6717
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1009 | 46 | -0.079819 | -3.6717
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1009 | 46 | -0.079819 | -3.6717
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3163 | 55 | -0.079819 | -4.39
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3163 | 55 | -0.079819 | -4.39
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2923 | 54 | -0.079819 | -4.3102
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5939 | 0 | -0.080408 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4713 | 0 | -0.080408 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5939 | 0 | -0.080408 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5939 | 0 | -0.080408 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2677 | 0 | -0.080807 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.183 | 0 | -0.080807 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.168 | 0 | -0.080807 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3581 | 0 | -0.080807 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30402 | 0 | -0.080807 | 0
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.025941 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.081828 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.026818 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3409 | 50 | -0.082705 | -4.1352
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9779 | 0 | -0.083823 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8633 | 0 | -0.083823 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4806 | 0 | -0.083823 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2798 | 0 | -0.083823 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2882 | 0 | -0.083823 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2547 | 0 | -0.083823 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6819 | 0 | -0.083823 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8164 | 0 | -0.083823 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1174 | 0 | -0.083823 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.02795 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8944 | 0 | -0.083837 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.02795 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8385 | 0 | -0.083837 | 0
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8034 | 0 | -0.083837 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5966 | 0 | -0.083837 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8705 | 0 | -0.083837 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8509 | 0 | -0.083837 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9369 | 161 | -0.086551 | -13.9347
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.0902 | 166 | -0.086551 | -14.3675
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.6047 | 248 | -0.086551 | -21.4646
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.030664 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -16.7425 | 546 | -0.086551 | -47.2568
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.030664 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -19.717 | 0 | -0.086551 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.030664 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39863 | 13 | -0.086551 | -1.1252
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.030886 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0192 | 0 | -0.086773 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1332 | 0 | -0.087379 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1332 | 0 | -0.087379 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.7155 | 0 | -0.087379 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -20.5299 | 651 | -0.087423 | -56.9123
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -17.7863 | 564 | -0.087423 | -49.3065
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -18.9216 | 600 | -0.087423 | -52.4537
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.031657 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4594 | 0 | -0.087544 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0832 | 0 | -0.092673 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0832 | 0 | -0.092673 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3775 | 0 | -0.092673 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0281 | 0 | -0.092673 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6637 | 0 | -0.092759 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6637 | 0 | -0.092759 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.55308 | 0 | -0.092759 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.038249 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7157 | 0 | -0.094136 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.038249 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38249 | 0 | -0.094136 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4859 | 0 | -0.095982 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8628 | 0 | -0.095982 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8043 | 0 | -0.095982 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0496 | 0 | -0.095982 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4482 | 0 | -0.095982 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5284 | 0 | -0.095982 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0048 | 0 | -0.095982 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72171 | 0 | -0.095982 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7689 | 0 | -0.095982 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8066 | 0 | -0.095982 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.526 | 0 | -0.095982 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8868 | 0 | -0.095982 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5982 | 0 | -0.095982 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0496 | 0 | -0.095982 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8892 | 0 | -0.095982 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1298 | 0 | -0.095982 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0472 | 0 | -0.095982 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2076 | 0 | -0.095982 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2076 | 0 | -0.095982 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8562 | 0 | -0.095982 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.040318 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.55236 | 0 | -0.096205 | 0
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.043138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4236 | 0 | -0.099025 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.043138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0784 | 0 | -0.099025 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.043138 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.099025 | 0
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.047265 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.1195 | 66 | -0.10315 | -6.808
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7734 | 76 | -0.10554 | -8.0208
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7734 | 76 | -0.10554 | -8.0208
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.2133 | 105 | -0.10554 | -11.0814
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6741 | 74 | -0.10554 | -7.8097
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6741 | 74 | -0.10554 | -7.8097
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.0643 | 102 | -0.10554 | -10.7648
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.0502 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.9166 | 0 | -0.10609 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.0502 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.6656 | 0 | -0.10609 | 0
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.051766 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4494 | 0 | -0.10765 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.051766 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5012 | 0 | -0.10765 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.051993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.941 | 422 | -0.10788 | -45.5253
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.053953 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32372 | 0 | -0.10984 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.056469 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11236 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.056749 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0215 | 0 | -0.11264 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.056749 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0215 | 0 | -0.11264 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3637 | 0 | -0.12342 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.2962 | 0 | -0.12342 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3637 | 0 | -0.12342 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4059 | 0 | -0.12432 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5427 | 0 | -0.12432 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4059 | 0 | -0.12432 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4743 | 0 | -0.12432 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3648 | 0 | -0.12432 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7107 | 0 | -0.12432 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1477 | 0 | -0.12432 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.916 | 0 | -0.12432 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9835 | 0 | -0.12432 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0637 | 0 | -0.12432 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.068937 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.309 | 0 | -0.12482 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.977 | 0 | -0.12649 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.49424 | 0 | -0.12649 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7536 | 0 | -0.12649 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0591 | 0 | -0.12649 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.49424 | 0 | -0.12649 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0591 | 0 | -0.12649 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7536 | 0 | -0.12649 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7536 | 0 | -0.12649 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.070862 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5669 | 0 | -0.12675 | 0
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.071284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0693 | 0 | -0.12717 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.071284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6395 | 0 | -0.12717 | 0
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.071885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5815 | 22 | -0.12777 | -2.811
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071885 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.79073 | 11 | -0.12777 | -1.4055
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071885 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.79073 | 11 | -0.12777 | -1.4055
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4546 | 47.7 | -0.12831 | -6.1204
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7014 | 37.3 | -0.12831 | -4.786
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3315 | 46 | -0.12831 | -5.9023
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4763 | 48 | -0.12831 | -6.1589
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.07246 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2896 | 0 | -0.12835 | 0
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.5457 | 0 | -0.12896 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.1803 | 0 | -0.12896 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.3074 | 0 | -0.12896 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5957 | 0 | -0.12896 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.7419 | 0 | -0.12896 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.2804 | 0 | -0.12896 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.073074 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.87689 | 0 | -0.12896 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.073142 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5324 | 144 | -0.12903 | -18.5802
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.073142 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.7507 | 188 | -0.12903 | -24.2574
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 25 | -0.12923 | -3.2307
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 25 | -0.12923 | -3.2307
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 25 | -0.12923 | -3.2307
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1735 | 16 | -0.12923 | -2.0677
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 25 | -0.12923 | -3.2307
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 25 | -0.12923 | -3.2307
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 25 | -0.12923 | -3.2307
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1001 | 15 | -0.12923 | -1.9384
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.073743 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.7776 | 336 | -0.12963 | -43.5556
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073743 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2737 | 180 | -0.12963 | -23.3334
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.9373 | 0 | -0.12964 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.9594 | 0 | -0.12964 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2839 | 0 | -0.12964 | 0
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2773 | 180 | -0.12965 | -23.337
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.073893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.6803 | 334 | -0.12978 | -43.3465
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.073893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.1236 | 340 | -0.12978 | -44.1252
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.073893 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3007 | 180 | -0.12978 | -23.3604
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.073893 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3007 | 180 | -0.12978 | -23.3604
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.073907 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8477 | 0 | -0.12979 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.073907 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8477 | 0 | -0.12979 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.073972 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8109 | 0 | -0.12986 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.073977 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8111 | 0 | -0.12986 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.0743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1547 | 0 | -0.13019 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9942 | 94 | -0.13029 | -12.2475
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.0506 | 41 | -0.13029 | -5.342
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8274 | 38 | -0.13029 | -4.9511
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4137 | 19 | -0.13029 | -2.4756
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9942 | 94 | -0.13029 | -12.2475
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6786 | 36 | -0.13029 | -4.6905
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1995 | 43 | -0.13029 | -5.6026
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6369 | 22 | -0.13029 | -2.8664
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -11.0121 | 148 | -0.13029 | -19.2834
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7203 | 50 | -0.13029 | -6.5146
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0923 | 55 | -0.13029 | -7.1661
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7203 | 50 | -0.13029 | -6.5146
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.074448 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13033 | 0
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.829 | 38 | -0.13033 | -4.9527
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4368 | 19.3 | -0.13033 | -2.5155
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1167 | 15 | -0.13033 | -1.955
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.074448 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4991 | 47 | -0.13033 | -6.1257
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7375 | 144 | -0.13045 | -18.7852
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7375 | 144 | -0.13045 | -18.7852
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7508 | 171 | -0.13045 | -22.3074
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.4356 | 207 | -0.13045 | -27.0042
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.1589 | 216.7 | -0.13045 | -28.2696
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -18.0455 | 242 | -0.13045 | -31.5701
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9409 | 146.5 | -0.13057 | -19.1283
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.0455 | 147.9 | -0.13057 | -19.3111
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.92 | 173 | -0.13057 | -22.5884
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.90476 | 0 | -0.13128 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.82937 | 0 | -0.13128 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.90476 | 0 | -0.13128 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.07549 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13138 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.076081 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13197 | 0
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.076364 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -48.033 | 629 | -0.13225 | -83.1858
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.077094 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13298 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.077747 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13363 | 0
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.077754 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7754 | 100 | -0.13364 | -13.3641
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.077754 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7754 | 100 | -0.13364 | -13.3641
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077807 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.8674 | 24 | -0.13369 | -3.2087
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077807 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.8674 | 24 | -0.13369 | -3.2087
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.077807 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.7896 | 23 | -0.13369 | -3.075
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.078023 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62418 | 0 | -0.13391 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.078023 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62418 | 0 | -0.13391 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.082468 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.5651 | 310 | -0.13835 | -42.89
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.082468 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -34.0593 | 413 | -0.13835 | -57.1406
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.082867 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.8153 | 396 | -0.13875 | -54.9465
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.5329 | 42 | -0.14 | -5.8802
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7011 | 44 | -0.14 | -6.1602
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7011 | 44 | -0.14 | -6.1602
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9535 | 47 | -0.14 | -6.5802
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.084188 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0103 | 0 | -0.14007 | 0
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.2063 | 49 | -0.14173 | -6.9448
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9488 | 46 | -0.14173 | -6.5196
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9488 | 46 | -0.14173 | -6.5196
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0346 | 47 | -0.14173 | -6.6613
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.085843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2198 | 154 | -0.14173 | -21.8264
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.085843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7048 | 148 | -0.14173 | -20.976
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1205 | 48 | -0.14173 | -6.803
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1205 | 48 | -0.14173 | -6.803
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.086454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0143 | 58 | -0.14234 | -8.2558
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.086454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.6944 | 89 | -0.14234 | -12.6683
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.804 | 44 | -0.14234 | -6.263
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.804 | 44 | -0.14234 | -6.263
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7175 | 43 | -0.14234 | -6.1207
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8904 | 45 | -0.14234 | -6.4053
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.086822 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.4048 | 546 | -0.14271 | -77.9191
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.086822 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -65.1165 | 750 | -0.14271 | -107.0317
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.086999 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.4086 | 407 | -0.14289 | -58.1546
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.087025 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.1882 | 209 | -0.14291 | -29.8686
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.087025 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.7974 | 216 | -0.14291 | -30.869
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0031 | 46 | -0.14291 | -6.5739
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0902 | 47 | -0.14291 | -6.7169
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0031 | 46 | -0.14291 | -6.5739
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0031 | 46 | -0.14291 | -6.5739
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.489 | 155 | -0.14291 | -22.1515
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.7944 | 170 | -0.14291 | -24.2952
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.489 | 155 | -0.14291 | -22.1515
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.087125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.8955 | 412 | -0.14301 | -58.9209
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.087125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -34.85 | 400 | -0.14301 | -57.2048
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.087255 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.9961 | 424 | -0.14314 | -60.6922
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.087255 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.0834 | 425 | -0.14314 | -60.8353
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14351 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14351 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14351 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.0347 | 114 | -0.14391 | -16.4058
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.5413 | 222 | -0.14391 | -31.9482
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -16.1964 | 184 | -0.14391 | -26.4796
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.7174 | 224 | -0.14391 | -32.236
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.1228 | 115 | -0.14391 | -16.5498
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.088608 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21266 | 0 | -0.14449 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.088608 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21266 | 0 | -0.14449 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2838 | 147 | -0.14625 | -21.4992
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.4705 | 138 | -0.14625 | -20.1829
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6512 | 140 | -0.14625 | -20.4754
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2838 | 147 | -0.14625 | -21.4992
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.4466 | 182 | -0.14625 | -26.618
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8925 | 198 | -0.14625 | -28.9581
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.090819 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.36328 | 0 | -0.14671 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.090903 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54542 | 0 | -0.14679 | 0
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21844 | 0 | -0.1469 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21844 | 0 | -0.1469 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25485 | 0 | -0.1469 | 0
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.067 | 132 | -0.1473 | -19.4441
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.2499 | 134 | -0.1473 | -19.7387
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -29.5277 | 323 | -0.1473 | -47.5792
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3143 | 142 | -0.14965 | -21.2503
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5956 | 145 | -0.14965 | -21.6992
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1582 | 151 | -0.14965 | -22.5971
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.1913 | 290 | -0.14965 | -43.3985
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8347 | 223.9 | -0.15341 | -34.3478
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.942 | 225 | -0.15341 | -34.5166
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.903 | 224.6 | -0.15341 | -34.4552
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.1078 | 226.7 | -0.15341 | -34.7773
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.10416 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -45.1021 | 433 | -0.16005 | -69.3012
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.1043 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -60.9094 | 584 | -0.16018 | -93.5474
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.1043 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -62.0567 | 595 | -0.16018 | -95.3094
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.9483 | 152.5 | -0.17358 | -26.4711
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.5953 | 149.5 | -0.17358 | -25.9503
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.3756 | 232.6 | -0.17358 | -40.3749
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.2398 | 158 | -0.17766 | -28.0699
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.4834 | 160 | -0.17766 | -28.4253
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.3099 | 175 | -0.17766 | -31.0901
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.14701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -83.6504 | 569 | -0.2029 | -115.45
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.14701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.4146 | 581 | -0.2029 | -117.8848

## GenConcentration_inc
Number of Bus | Name of Bus | ID | Area Name of Gen | AGC | Gen MW | Min MW | Max MW | L: TEMP_SS_ to SANDOW_ 345kV [3414 - 3429] C:THOUSE_ to TEMP_PEC [3405 - 3412] C:LAKE_CRK to TEMP_SS_ [3409 - 3414] | CMZ | Technology | Source Include? | Sink Include? | source-&-zone | sink-&-zone | Zone Impact | SF*Pmax | Pmax-sink | PTDF calc | PTDF Weighting - Sink | Cumulative Concentrated Capacity | Cumulative Concentrated Impact
3432 | SANDOW_4 | 4 | SOUTH | YES | 569 | 225 | 569 | -0.14701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -83.6504 | 0 | -0.2029 | 0 | 0 | 0
13432 | SANDOW_5 | 5 | SOUTH | YES | 581 | 225 | 581 | -0.14701 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -85.4146 | 0 | -0.2029 | 0 | 0 | 0
7007 | L_LOSTPI | 1 | SOUTH | YES | 165 | 110 | 158 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.2398 | 158 | -0.17766 | -28.0699 | 158 | 28.0699
7008 | L_LOSTPI | 2 | SOUTH | YES | 165 | 107 | 160 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -19.4834 | 160 | -0.17766 | -28.4253 | 318 | 56.4952 | Weighted Shift Factors
7009 | L_LOSTPI | 3 | SOUTH | YES | 180 | 72 | 175 | -0.12177 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.3099 | 175 | -0.17766 | -31.0901 | 493 | 87.5853 | North | 0.055887
7807 | L_BASTEN | 1 | SOUTH | YES | 152.5 | 83.5 | 152.5 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.9483 | 152.5 | -0.17358 | -26.4711 | 645.5 | 114.0564 | South | -0.085447
7808 | L_BASTEN | 1 | SOUTH | YES | 149.5 | 83.5 | 149.5 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.5953 | 149.5 | -0.17358 | -25.9503 | 795 | 140.0068 |  | 0.14133
7809 | L_BASTEN | 1 | SOUTH | YES | 232.6 | 42 | 232.6 | -0.11769 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.3756 | 232.6 | -0.17358 | -40.3749 | 1027.6 | 180.3817
7010 | L_FPPYD1 | 1 | SOUTH | YES | 620 | 200 | 584 | -0.1043 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -60.9094 | 0 | -0.16018 | 0 | 1027.6 | 180.3817 | Line Rating | 1072
7011 | L_FPPYD1 | 2 | SOUTH | YES | 614 | 200 | 595 | -0.1043 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -62.0567 | 0 | -0.16018 | 0 | 1027.6 | 180.3817 | Conc Gen | 2069.8
7012 | L_FPPYD2 | 3 | SOUTH | YES | 430 | 200 | 433 | -0.10416 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -45.1021 | 0 | -0.16005 | 0 | 1027.6 | 180.3817 | Weighted Imp. | 339.7289
7014 | L_HAYSEN | 1 | SOUTH | YES | 223.9 | 74 | 223.9 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.8347 | 223.9 | -0.15341 | -34.3478 | 1251.5 | 214.7295 | PTDF | 0.16414
7015 | L_HAYSEN | 2 | SOUTH | YES | 225 | 74 | 225 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.942 | 225 | -0.15341 | -34.5166 | 1476.5 | 249.2461
7016 | L_HAYSEN | 3 | SOUTH | YES | 224.6 | 74 | 224.6 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -21.903 | 224.6 | -0.15341 | -34.4552 | 1701.1 | 283.7013 | Concentration | 1.1613
7017 | L_HAYSEN | 4 | SOUTH | YES | 226.7 | 74 | 226.7 | -0.09752 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -22.1078 | 226.7 | -0.15341 | -34.7773 | 1927.8 | 318.4786
7810 | L_RIONOG | 1 | SOUTH | YES | 142 | 0 | 142 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3143 | 142 | -0.14965 | -21.2503 | 2069.8 | 339.7289
7811 | L_RIONOG | 2 | SOUTH | YES | 145 | 0 | 145 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.5956 | 145 | -0.14965 | -21.6992
7812 | L_RIONOG | 3 | SOUTH | YES | 151 | 0 | 151 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.1582 | 151 | -0.14965 | -22.5971
7813 | L_RIONOG | 4 | SOUTH | YES | 290 | 0 | 290 | -0.093763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -27.1913 | 290 | -0.14965 | -43.3985
7303 | L_WPPGS1 | 1 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7303 | L_WPPGS1 | 2 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7305 | L_WPPGS3 | 3 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7305 | L_WPPGS3 | 4 | SOUTH | YES | 48 | 0 | 50 | -0.092675 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.6338 | 50 | -0.14856 | -7.4281
7004 | L_SIMGID | 1 | SOUTH | YES | 20 | 40 | 132 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.067 | 132 | -0.1473 | -19.4441
7005 | L_SIMGID | 2 | SOUTH | YES | 20 | 32 | 134 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -12.2499 | 134 | -0.1473 | -19.7387
7006 | L_SIMGID | 3 | SOUTH | YES | 200 | 60 | 323 | -0.091417 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -29.5277 | 323 | -0.1473 | -47.5792
7605 | L_MCQUEE | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21844 | 0 | -0.1469 | 0
7605 | L_MCQUEE | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21844 | 0 | -0.1469 | 0
7605 | L_MCQUEE | 3 | SOUTH | YES | 0 | 0 | 2.8 | -0.091018 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.25485 | 0 | -0.1469 | 0
7487 | L_CANYHY | 1 | SOUTH | YES | 0 | 0 | 6 | -0.090903 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.54542 | 0 | -0.14679 | 0
7609 | L_SCHUMA | 1 | SOUTH | YES | 0 | 0 | 4 | -0.090819 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.36328 | 0 | -0.14671 | 0
7800 | L_GUADGE | 1 | SOUTH | YES | 147 | 30 | 147 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2838 | 147 | -0.14625 | -21.4992
7801 | L_GUADGE | 2 | SOUTH | YES | 138 | 30 | 138 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.4705 | 138 | -0.14625 | -20.1829
7802 | L_GUADGE | 3 | SOUTH | YES | 140 | 30 | 140 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.6512 | 140 | -0.14625 | -20.4754
7803 | L_GUADGE | 4 | SOUTH | YES | 147 | 30 | 147 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2838 | 147 | -0.14625 | -21.4992
7804 | L_GUADGE | 5 | SOUTH | YES | 182 | 30 | 182 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.4466 | 182 | -0.14625 | -26.618
7805 | L_GUADGE | 6 | SOUTH | YES | 198 | 30 | 198 | -0.090366 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -17.8925 | 198 | -0.14625 | -28.9581
7624 | L_LAKEWO | 1 | SOUTH | YES | 0 | 0 | 2.4 | -0.088608 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21266 | 0 | -0.14449 | 0
7624 | L_LAKEWO | 2 | SOUTH | YES | 0 | 0 | 2.4 | -0.088608 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.21266 | 0 | -0.14449 | 0
60057 | CALLAHAN | 1 | SOUTH | YES | 11.4 | 0 | 114 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.0347 | 0 | -0.14391 | 0
60066 | H_HOLLOW | 1 | SOUTH | YES | 22.2 | 0 | 222 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.5413 | 0 | -0.14391 | 0
60068 | HHOLLOW2 | 1 | SOUTH | YES | 18.4 | 0 | 184 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -16.1964 | 0 | -0.14391 | 0
60070 | HHOLLOW3 | 1 | SOUTH | YES | 22.4 | 0 | 224 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -19.7174 | 0 | -0.14391 | 0
60072 | HHOLLOW4 | 1 | SOUTH | YES | 11.5 | 0 | 115 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -10.1228 | 0 | -0.14391 | 0
5436 | TUTTL_WB | MB | SOUTH | YES | 0 | 20 | 61 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14351 | 0
5438 | TUTTL_WB | MB | SOUTH | YES | 0 | 25 | 95 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14351 | 0
5439 | TUTTL_WB | MB | SOUTH | YES | 0 | 40 | 151 | -0.087621 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.14351 | 0
5111 | CALAVER_ | 1 | SOUTH | YES | 424 | 80 | 424 | -0.087255 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -36.9961 | 0 | -0.14314 | 0
5112 | CALAVER_ | 2 | SOUTH | YES | 425 | 80 | 425 | -0.087255 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -37.0834 | 0 | -0.14314 | 0
5396 | CALAVER_ | 1 | SOUTH | YES | 412 | 80 | 412 | -0.087125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.8955 | 412 | -0.14301 | -58.9209
5397 | CALAVER_ | 2 | SOUTH | YES | 300 | 80 | 400 | -0.087125 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -34.85 | 400 | -0.14301 | -57.2048
5476 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.489 | 155 | -0.14291 | -22.1515
5477 | BRA_AVR1 | 1 | SOUTH | YES | 141 | 138 | 170 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -14.7944 | 170 | -0.14291 | -24.2952
5478 | BRA_AVR1 | 1 | SOUTH | YES | 128.5 | 90 | 155 | -0.087026 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.489 | 155 | -0.14291 | -22.1515
5026 | BRAUNIG_ | 1 | SOUTH | YES | 209 | 40 | 209 | -0.087025 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.1882 | 209 | -0.14291 | -29.8686
5027 | BRAUNIG_ | 2 | SOUTH | YES | 216 | 40 | 216 | -0.087025 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -18.7974 | 216 | -0.14291 | -30.869
5031 | BRA_VHBC | 1 | SOUTH | YES | 46 | 24 | 46 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0031 | 46 | -0.14291 | -6.5739
5032 | BRA_VHBC | 2 | SOUTH | YES | 47 | 24 | 47 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0902 | 47 | -0.14291 | -6.7169
5033 | BRA_VHBC | 3 | SOUTH | YES | 46 | 24 | 46 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0031 | 46 | -0.14291 | -6.5739
5034 | BRA_VHBC | 4 | SOUTH | YES | 46 | 24 | 46 | -0.087025 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0031 | 46 | -0.14291 | -6.5739
5028 | BRAUNIG_ | 3 | SOUTH | YES | 407 | 60 | 407 | -0.086999 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -35.4086 | 407 | -0.14289 | -58.1546
5401 | CALAVER_ | 1 | SOUTH | YES | 546 | 100 | 546 | -0.086822 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -47.4048 | 0 | -0.14271 | 0
5402 | CALAVER_ | 2 | SOUTH | YES | 750 | 240 | 750 | -0.086822 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -65.1165 | 0 | -0.14271 | 0
5264 | LEON_LCP | 3 | SOUTH | YES | 0 | 20 | 58 | -0.086454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -5.0143 | 58 | -0.14234 | -8.2558
5265 | LEON_LCP | 4 | SOUTH | YES | 89 | 25 | 89 | -0.086454 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -7.6944 | 89 | -0.14234 | -12.6683
5266 | LEON_LCP | 1 | SOUTH | YES | 44 | 23.1 | 44 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.804 | 44 | -0.14234 | -6.263
5267 | LEON_LCP | 2 | SOUTH | YES | 44 | 23.1 | 44 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.804 | 44 | -0.14234 | -6.263
5268 | LEON_LCP | 3 | SOUTH | YES | 43 | 23.1 | 43 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7175 | 43 | -0.14234 | -6.1207
5269 | LEON_LCP | 4 | SOUTH | YES | 45 | 23.1 | 45 | -0.086454 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.8904 | 45 | -0.14234 | -6.4053
9016 | SANDH_G1 | 1 | SOUTH | YES | 44 | 2 | 49 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.2063 | 49 | -0.14173 | -6.9448
9017 | SANDH_G2 | 2 | SOUTH | YES | 44 | 2 | 46 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9488 | 46 | -0.14173 | -6.5196
9018 | SANDH_G3 | 3 | SOUTH | YES | 44 | 2 | 46 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9488 | 46 | -0.14173 | -6.5196
9019 | SANDH_G4 | 4 | SOUTH | YES | 45 | 2 | 47 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.0346 | 47 | -0.14173 | -6.6613
9020 | SANDHG5A | 5A | SOUTH | YES | 150 | 84 | 154 | -0.085843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2198 | 154 | -0.14173 | -21.8264
9021 | SANDHG5C | 5C | SOUTH | YES | 130 | 0 | 148 | -0.085843 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7048 | 148 | -0.14173 | -20.976
9022 | SANDH_G6 | 6 | SOUTH | YES | 45 | 2 | 48 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1205 | 48 | -0.14173 | -6.803
9023 | SANDH_G7 | 7 | SOUTH | YES | 47 | 2 | 48 | -0.085843 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -4.1205 | 48 | -0.14173 | -6.803
8189 | CUERO 2 | 1 | SOUTH | YES | 0 | 0 | 12 | -0.084188 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0103 | 0 | -0.14007 | 0
9002 | DECKR_G3 | 3 | SOUTH | YES | 0 | 24 | 42 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.5329 | 42 | -0.14 | -5.8802
9003 | DECKR_G4 | 4 | SOUTH | YES | 44 | 24 | 44 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7011 | 44 | -0.14 | -6.1602
9004 | DECKR_G5 | 5 | SOUTH | YES | 44 | 24 | 44 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.7011 | 44 | -0.14 | -6.1602
9005 | DECKR_G6 | 6 | SOUTH | YES | 44 | 24 | 47 | -0.084117 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.9535 | 47 | -0.14 | -6.5802
5903 | SANMIGUE | 1 | SOUTH | YES | 396 | 180 | 396 | -0.082867 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -32.8153 | 0 | -0.13875 | 0
9000 | DECKR_G1 | 1 | SOUTH | YES | 280 | 50 | 310 | -0.082468 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.5651 | 310 | -0.13835 | -42.89
9001 | DECKR_G2 | 2 | SOUTH | YES | 400 | 50 | 413 | -0.082468 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -34.0593 | 413 | -0.13835 | -57.1406
7020 | L_AUSTPL | 1 | SOUTH | YES | 0 | 0 | 8 | -0.078023 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62418 | 0 | -0.13391 | 0
7020 | L_AUSTPL | 2 | SOUTH | YES | 0 | 0 | 8 | -0.078023 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.62418 | 0 | -0.13391 | 0
5890 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077807 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.8674 | 24 | -0.13369 | -3.2087
5891 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 24 | -0.077807 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.8674 | 24 | -0.13369 | -3.2087
5892 | PEARSALL | 1 | SOUTH | YES | 6.2 | 6 | 23 | -0.077807 | south | 11 | Y | Y | Ysouth | Ysouth | -1 | -1.7896 | 23 | -0.13369 | -3.075
80265 | LARECU40 | 4 | SOUTH | YES | 90 | 0 | 100 | -0.077754 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7754 | 100 | -0.13364 | -13.3641
80266 | LARECU50 | 5 | SOUTH | YES | 90 | 0 | 100 | -0.077754 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -7.7754 | 100 | -0.13364 | -13.3641
86104 | CID-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
86105 | CID-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
86106 | CUF-230 | EQ | SOUTH | YES | 0 | -500 | 500 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
86107 | CUF-138 | EQ | SOUTH | YES | 0 | 0 | 0 | -0.077754 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13364 | 0
80012 | LAR | F | SOUTH | YES | 0 | 0 | 0 | -0.077747 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13363 | 0
88198 | BEEVILLE | F | SOUTH | YES | 0 | 0 | 0 | -0.077094 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13298 | 0
58909 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58909 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58919 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58929 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 1 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 2 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 3 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 4 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 5 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
58949 | PEARSALL | 6 | SOUTH | YES | 8.4 | 0 | 8.4 | -0.076917 | south | 15 | Y | Y | Ysouth | Ysouth | -1 | -0.6461 | 8.4 | -0.1328 | -1.1156
8161 | COLETOU1 | 1 | SOUTH | YES | 629 | 200 | 629 | -0.076364 | south | 4 | Y | N | Ysouth | Nsouth | -1 | -48.033 | 0 | -0.13225 | 0
88299 | ZAPATA | F | SOUTH | YES | 0 | 0 | 0 | -0.076081 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13197 | 0
88508 | FALFURRI | F | SOUTH | YES | 0 | 0 | 0 | -0.07549 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13138 | 0
5728 | FALCONHY | 2 | SOUTH | YES | 0 | 0 | 12 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.90476 | 0 | -0.13128 | 0
5729 | FALCONHY | 3 | SOUTH | YES | 0 | 0 | 11 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.82937 | 0 | -0.13128 | 0
8048 | FALCONHY | 1 | SOUTH | YES | 0 | 0 | 12 | -0.075397 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.90476 | 0 | -0.13128 | 0
8933 | FGNTS001 | 1 | SOUTH | YES | 83.1 | 0 | 146.5 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.9409 | 146.5 | -0.13057 | -19.1283
8934 | FGNTS101 | 2 | SOUTH | YES | 83.9 | 0 | 147.9 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -11.0455 | 147.9 | -0.13057 | -19.3111
8935 | FGNTS201 | 3 | SOUTH | YES | 98.1 | 0 | 173 | -0.074682 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.92 | 173 | -0.13057 | -22.5884
8936 | MVGN#1 | 1 | SOUTH | YES | 165.6 | 0 | 207 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -15.4356 | 207 | -0.13045 | -27.0042
8937 | MVGN#2 | 2 | SOUTH | YES | 172.8 | 0 | 216.7 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -16.1589 | 216.7 | -0.13045 | -28.2696
8938 | MVGN#3 | 3 | SOUTH | YES | 193.6 | 0 | 242 | -0.074568 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -18.0455 | 242 | -0.13045 | -31.5701
8981 | HECN1 | 1 | SOUTH | YES | 144 | 0 | 144 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7375 | 144 | -0.13045 | -18.7852
8982 | HECN2 | 2 | SOUTH | YES | 144 | 0 | 144 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.7375 | 144 | -0.13045 | -18.7852
8983 | HECN3 | 3 | SOUTH | YES | 171 | 0 | 171 | -0.074566 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -12.7508 | 171 | -0.13045 | -22.3074
5932 | SI_RAY9 | 9 | SOUTH | YES | 38 | 32 | 38 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -2.829 | 38 | -0.13033 | -4.9527
5933 | SI_RAY6 | 6 | SOUTH | YES | 13 | 10 | 19.3 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.4368 | 19.3 | -0.13033 | -2.5155
5934 | SI_RAY5 | 5 | SOUTH | YES | 15 | 10 | 15 | -0.074448 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.1167 | 15 | -0.13033 | -1.955
5935 | SI_RAY10 | 10 | SOUTH | YES | 47 | 10 | 47 | -0.074448 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -3.4991 | 47 | -0.13033 | -6.1257
80003 | MILHWYS | F | SOUTH | YES | 0 | 0 | 0 | -0.074448 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.13033 | 0
80080 | GWINDT11 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9942 | 0 | -0.13029 | 0
80080 | GWINDT11 | 2 | SOUTH | YES | 20.5 | 0 | 41 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.0506 | 0 | -0.13029 | 0
80080 | GWINDT11 | 3 | SOUTH | YES | 19 | 0 | 38 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.8274 | 0 | -0.13029 | 0
80080 | GWINDT11 | 4 | SOUTH | YES | 9.5 | 0 | 19 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.4137 | 0 | -0.13029 | 0
80081 | GWINDT21 | 1 | SOUTH | YES | 47 | 0 | 94 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -6.9942 | 0 | -0.13029 | 0
80081 | GWINDT21 | 2 | SOUTH | YES | 18 | 0 | 36 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -2.6786 | 0 | -0.13029 | 0
80081 | GWINDT21 | 3 | SOUTH | YES | 21.5 | 0 | 43 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.1995 | 0 | -0.13029 | 0
80081 | GWINDT21 | 4 | SOUTH | YES | 11 | 0 | 22 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.6369 | 0 | -0.13029 | 0
80180 | PNSCALT1 | 1 | SOUTH | YES | 74 | 0 | 148 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -11.0121 | 0 | -0.13029 | 0
80180 | PNSCALT1 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7203 | 0 | -0.13029 | 0
80181 | PNSCALT2 | 1 | SOUTH | YES | 27.5 | 0 | 55 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -4.0923 | 0 | -0.13029 | 0
80181 | PNSCALT2 | 2 | SOUTH | YES | 25 | 0 | 50 | -0.074406 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -3.7203 | 0 | -0.13029 | 0
8517 | CELANEBI | 1 | SOUTH | YES | 28.4 | 0 | 29 | -0.0743 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.1547 | 0 | -0.13019 | 0
8511 | OXY_CC0A | 1 | SOUTH | YES | 30.8 | 0 | 38 | -0.073977 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8111 | 0 | -0.12986 | 0
8461 | KOCH_UP0 | 1 | SOUTH | YES | 38 | 0 | 38 | -0.073972 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.8109 | 0 | -0.12986 | 0
8506 | VAL #1 | 1 | SOUTH | YES | 20.9 | 0 | 25 | -0.073907 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8477 | 0 | -0.12979 | 0
8507 | VAL #2 | 2 | SOUTH | YES | 20.9 | 0 | 25 | -0.073907 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.8477 | 0 | -0.12979 | 0
8459 | B_DAVIS1 | 1 | SOUTH | YES | 334 | 50 | 334 | -0.073893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -24.6803 | 334 | -0.12978 | -43.3465
8460 | B_DAVIS2 | 2 | SOUTH | YES | 100 | 50 | 340 | -0.073893 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -25.1236 | 340 | -0.12978 | -44.1252
80263 | B_DAVIS3 | 3 | SOUTH | YES | 180 | 0 | 180 | -0.073893 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3007 | 180 | -0.12978 | -23.3604
80264 | B_DAVIS4 | 4 | SOUTH | YES | 180 | 0 | 180 | -0.073893 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.3007 | 180 | -0.12978 | -23.3604
80261 | NBEC81A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073763 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2773 | 180 | -0.12965 | -23.337
8560 | CNOPGT1 | 1 | SOUTH | YES | 148.3 | 0 | 148.3 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.9373 | 0 | -0.12964 | 0
8561 | CNOPGT2 | 2 | SOUTH | YES | 148.6 | 0 | 148.6 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.9594 | 0 | -0.12964 | 0
8562 | CNOPST1 | 3 | SOUTH | YES | 153 | 0 | 153 | -0.073751 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.2839 | 0 | -0.12964 | 0
8442 | NBEC71A | 1 | SOUTH | YES | 302.8 | 81 | 336 | -0.073743 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -24.7776 | 336 | -0.12963 | -43.5556
80262 | NBEC91A | 1 | SOUTH | YES | 180 | 0 | 180 | -0.073743 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.2737 | 180 | -0.12963 | -23.3334
80291 | PAPALOTE | 1 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 0 | -0.12923 | 0
80291 | PAPALOTE | 2 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 0 | -0.12923 | 0
80291 | PAPALOTE | 3 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 0 | -0.12923 | 0
80291 | PAPALOTE | 4 | SOUTH | YES | 9.6 | 0 | 16 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1735 | 0 | -0.12923 | 0
80294 | PAPALOTE | 5 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 0 | -0.12923 | 0
80294 | PAPALOTE | 6 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 0 | -0.12923 | 0
80294 | PAPALOTE | 7 | SOUTH | YES | 15 | 0 | 25 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.8336 | 0 | -0.12923 | 0
80294 | PAPALOTE | 8 | SOUTH | YES | 9 | 0 | 15 | -0.073342 | south | 6 | Y | N | Ysouth | Nsouth | -1 | -1.1001 | 0 | -0.12923 | 0
8173 | VICEC51A | 5 | SOUTH | YES | 143.7 | 18 | 144 | -0.073142 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -10.5324 | 144 | -0.12903 | -18.5802
8174 | VICEC61A | 6 | SOUTH | YES | 188 | 42 | 188 | -0.073142 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -13.7507 | 188 | -0.12903 | -24.2574
8926 | LGE_GT10 | 1 | SOUTH | YES | 158 | 0 | 158 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.5457 | 0 | -0.12896 | 0
8927 | LGE_GT20 | 2 | SOUTH | YES | 153 | 0 | 153 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -11.1803 | 0 | -0.12896 | 0
8928 | LGE_STG0 | 3 | SOUTH | YES | 100 | 0 | 100 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -7.3074 | 0 | -0.12896 | 0
8930 | ICPGN10A | 1 | SOUTH | YES | 145 | 0 | 145 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.5957 | 0 | -0.12896 | 0
8931 | ICPGN20A | 2 | SOUTH | YES | 147 | 0 | 147 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -10.7419 | 0 | -0.12896 | 0
8932 | ICPGN30A | 3 | SOUTH | YES | 127 | 0 | 127 | -0.073074 | south | 8 | N | N | Nsouth | Nsouth | -1 | -9.2804 | 0 | -0.12896 | 0
80223 | REYSHR G | 1 | SOUTH | YES | 12 | 0 | 12 | -0.073074 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.87689 | 0 | -0.12896 | 0
8066 | DUP1V#1 | 1 | SOUTH | YES | 73 | 0 | 73 | -0.07246 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.2896 | 0 | -0.12835 | 0
5508 | RAYBURNC | 1 | SOUTH | YES | 47.7 | 18.2 | 47.7 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4546 | 47.7 | -0.12831 | -6.1204
5509 | RAYBURNC | 1 | SOUTH | YES | 37.3 | 5.2 | 37.3 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -2.7014 | 37.3 | -0.12831 | -4.786
5511 | RAYBURNC | 1 | SOUTH | YES | 46 | 18.2 | 46 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.3315 | 46 | -0.12831 | -5.9023
5512 | RAYBURNC | 1 | SOUTH | YES | 48 | 18.2 | 48 | -0.072423 | south | 9 | Y | Y | Ysouth | Ysouth | -1 | -3.4763 | 48 | -0.12831 | -6.1589
5503 | RAYBURNG | 1 | SOUTH | YES | 6.2 | 6 | 22 | -0.071885 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -1.5815 | 22 | -0.12777 | -2.811
5505 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071885 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.79073 | 11 | -0.12777 | -1.4055
5506 | RAYBURNG | 1 | SOUTH | YES | 0 | 1 | 11 | -0.071885 | south | 13 | Y | Y | Ysouth | Ysouth | -1 | -0.79073 | 11 | -0.12777 | -1.4055
80224 | VISTRONG | 1 | SOUTH | YES | 13.2 | 0 | 15 | -0.071284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0693 | 0 | -0.12717 | 0
80225 | VISTRONG | 2 | SOUTH | YES | 20.2 | 0 | 23 | -0.071284 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.6395 | 0 | -0.12717 | 0
80227 | AIRCO G | 1 | SOUTH | YES | 7.4 | 0 | 8 | -0.070862 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.5669 | 0 | -0.12675 | 0
8147 | UCAR #2 | 10 | SOUTH | YES | 15.4 | 0 | 28 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.977 | 0 | -0.12649 | 0
8148 | UCAR #1 | 2 | SOUTH | YES | 5.1 | 0 | 7 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.49424 | 0 | -0.12649 | 0
80137 | CSDR89 | 8 | SOUTH | YES | 24.5 | 0 | 39 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7536 | 0 | -0.12649 | 0
80137 | CSDR89 | 9 | SOUTH | YES | 15 | 0 | 15 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0591 | 0 | -0.12649 | 0
80138 | CSDR7 | 7 | SOUTH | YES | 5.1 | 0 | 7 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -0.49424 | 0 | -0.12649 | 0
80139 | CSDR56 | 5 | SOUTH | YES | 15 | 0 | 15 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.0591 | 0 | -0.12649 | 0
80139 | CSDR56 | 6 | SOUTH | YES | 24.5 | 0 | 39 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7536 | 0 | -0.12649 | 0
80140 | CSDR11 | 11 | SOUTH | YES | 28.6 | 0 | 39 | -0.070606 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.7536 | 0 | -0.12649 | 0
80226 | ALCOA G | 1 | SOUTH | YES | 32.8 | 5 | 48 | -0.068937 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.309 | 0 | -0.12482 | 0
8134 | FOR69CG0 | 1 | SOUTH | YES | 75.1 | 45 | 79 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4059 | 0 | -0.12432 | 0
8138 | FOR69CG0 | 2 | SOUTH | YES | 76 | 45 | 81 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.5427 | 0 | -0.12432 | 0
8153 | FOR69CG0 | 3 | SOUTH | YES | 69.4 | 45 | 79 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4059 | 0 | -0.12432 | 0
8154 | FOR69CG0 | 4 | SOUTH | YES | 77 | 60 | 80 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.4743 | 0 | -0.12432 | 0
8155 | FOR69CG0 | 5 | SOUTH | YES | 70.3 | 60 | 78.4 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.3648 | 0 | -0.12432 | 0
8156 | FOR69CG0 | 6 | SOUTH | YES | 24.7 | 5 | 25 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.7107 | 0 | -0.12432 | 0
8157 | FOR69CG0 | 7 | SOUTH | YES | 43.7 | 5 | 46 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -3.1477 | 0 | -0.12432 | 0
80051 | FORPVCM0 | 8 | SOUTH | YES | 28 | 28 | 28 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -1.916 | 0 | -0.12432 | 0
80052 | FOR69CG0 | 9 | SOUTH | YES | 30.4 | 5 | 43.6 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -2.9835 | 0 | -0.12432 | 0
80053 | FOR69CG0 | 10 | SOUTH | YES | 69.4 | 45 | 74 | -0.068429 | south | 7 | N | N | Nsouth | Nsouth | -1 | -5.0637 | 0 | -0.12432 | 0
7031 | L_MARSFO | 1 | SOUTH | YES | 0 | 0 | 35 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3637 | 0 | -0.12342 | 0
7032 | L_MARSFO | 2 | SOUTH | YES | 0 | 0 | 34 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.2962 | 0 | -0.12342 | 0
7033 | L_MARSFO | 3 | SOUTH | YES | 0 | 0 | 35 | -0.067534 | south | 5 | N | N | Nsouth | Nsouth | -1 | -2.3637 | 0 | -0.12342 | 0
7028 | L_MARBFA | 1 | SOUTH | YES | 0 | 0 | 18 | -0.056749 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0215 | 0 | -0.11264 | 0
7029 | L_MARBFA | 2 | SOUTH | YES | 0 | 0 | 18 | -0.056749 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0215 | 0 | -0.11264 | 0
80010 | EPLVT1 | F | SOUTH | YES | 0 | 0 | 0 | -0.056469 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.11236 | 0
8262 | ELPS | 1 | SOUTH | YES | 0 | 6 | 6 | -0.053953 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.32372 | 0 | -0.10984 | 0
7000 | L_FERGUS | 1 | SOUTH | YES | 250 | 65 | 422 | -0.051993 | south | 10 | Y | Y | Ysouth | Ysouth | -1 | -21.941 | 422 | -0.10788 | -45.5253
7035 | L_WIRTZ_ | 1 | SOUTH | YES | 0 | 0 | 28 | -0.051766 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4494 | 0 | -0.10765 | 0
7036 | L_WIRTZ_ | 2 | SOUTH | YES | 0 | 0 | 29 | -0.051766 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.5012 | 0 | -0.10765 | 0
5911 | STP_GN1_ | 1 | HOUSTON | YES | 1333 | 1249 | 1333 | -0.0502 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.9166 | 0 | -0.10609 | 0
5912 | STP_GN2_ | 2 | HOUSTON | YES | 1328 | 1249 | 1328 | -0.0502 | houston | 3 | N | N | Nhouston | Nhouston | -1 | -66.6656 | 0 | -0.10609 | 0
48731 | CBE_GT1 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7734 | 76 | -0.10554 | -8.0208
48732 | CBE_GT2 | 1 | HOUSTON | YES | 76 | 0 | 76 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.7734 | 76 | -0.10554 | -8.0208
48733 | CBE_ST12 | 1 | HOUSTON | YES | 105 | 0 | 105 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.2133 | 105 | -0.10554 | -11.0814
48734 | CBE_GT3 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6741 | 74 | -0.10554 | -7.8097
48735 | CBE_GT4 | 1 | HOUSTON | YES | 74 | 0 | 74 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.6741 | 74 | -0.10554 | -7.8097
48736 | CBE_ST34 | 1 | HOUSTON | YES | 102 | 0 | 102 | -0.04965 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -5.0643 | 102 | -0.10554 | -10.7648
48911 | TGF_GT1_ | 1 | HOUSTON | YES | 66 | 0 | 66 | -0.047265 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -3.1195 | 66 | -0.10315 | -6.808
8032 | AMISTADH | 1 | SOUTH | YES | 0 | 13 | 33 | -0.043138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.4236 | 0 | -0.099025 | 0
8033 | AMISTADH | 2 | SOUTH | YES | 0 | 13 | 25 | -0.043138 | south | 5 | N | N | Nsouth | Nsouth | -1 | -1.0784 | 0 | -0.099025 | 0
88253 | HAMILTON | F | SOUTH | YES | 0 | 0 | 0 | -0.043138 | south | #N/A | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.099025 | 0
7026 | L_INKSDA | 1 | SOUTH | YES | 0 | 0 | 13.7 | -0.040318 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.55236 | 0 | -0.096205 | 0
49851 | DOW17000 | 37 | HOUSTON | YES | 39 | 0 | 62 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.4859 | 0 | -0.095982 | 0
49858 | DOW38100 | 31 | HOUSTON | YES | 45 | 0 | 71.4 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8628 | 0 | -0.095982 | 0
49859 | DOW38200 | 33 | HOUSTON | YES | 28 | 0 | 45 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8043 | 0 | -0.095982 | 0
49860 | DOW38300 | 32 | HOUSTON | YES | 63 | 0 | 101 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0496 | 0 | -0.095982 | 0
49862 | DOW39100 | 36 | HOUSTON | YES | 54 | 0 | 86 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4482 | 0 | -0.095982 | 0
49863 | DOW39200 | 35 | HOUSTON | YES | 55 | 0 | 88 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.5284 | 0 | -0.095982 | 0
49865 | DOW41000 | 41 | HOUSTON | YES | 31 | 0 | 50 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.0048 | 0 | -0.095982 | 0
49866 | DOW42000 | 42 | HOUSTON | YES | 11 | 0 | 18 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72171 | 0 | -0.095982 | 0
49869 | DOW49000 | 45 | HOUSTON | YES | 59 | 0 | 94 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.7689 | 0 | -0.095982 | 0
49870 | DOW61000 | 61 | HOUSTON | YES | 44 | 0 | 70 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8066 | 0 | -0.095982 | 0
49871 | DOW62000 | 62 | HOUSTON | YES | 40 | 0 | 63 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.526 | 0 | -0.095982 | 0
49872 | DOW63000 | 63 | HOUSTON | YES | 45 | 0 | 72 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.8868 | 0 | -0.095982 | 0
49873 | DOW64000 | 64 | HOUSTON | YES | 41 | 0 | 64.8 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.5982 | 0 | -0.095982 | 0
49876 | DOW65000 | 65 | HOUSTON | YES | 63 | 0 | 101 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.0496 | 0 | -0.095982 | 0
49877 | DOW66000 | 66 | HOUSTON | YES | 61 | 0 | 97 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8892 | 0 | -0.095982 | 0
49878 | DOW67000 | 67 | HOUSTON | YES | 65 | 0 | 103 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -4.1298 | 0 | -0.095982 | 0
49882 | DOW81000 | 81 | HOUSTON | YES | 47 | 0 | 76 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.0472 | 0 | -0.095982 | 0
49884 | DOW82000 | 82 | HOUSTON | YES | 51 | 0 | 80 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2076 | 0 | -0.095982 | 0
49885 | DOW83000 | 83 | HOUSTON | YES | 51 | 0 | 80 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2076 | 0 | -0.095982 | 0
49886 | DOW84000 | 84 | HOUSTON | YES | 107 | 0 | 171 | -0.040095 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -6.8562 | 0 | -0.095982 | 0
48520 | BSF_GT1_ | 1 | HOUSTON | YES | 71 | 0 | 71 | -0.038249 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7157 | 0 | -0.094136 | 0
48520 | BSF_GT1_ | 2 | HOUSTON | YES | 10 | 0 | 10 | -0.038249 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38249 | 0 | -0.094136 | 0
7022 | L_BUCHAN | 1 | SOUTH | YES | 0 | 0 | 18 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6637 | 0 | -0.092759 | 0
7023 | L_BUCHAN | 2 | SOUTH | YES | 0 | 0 | 18 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.6637 | 0 | -0.092759 | 0
7024 | L_BUCHAN | 3 | SOUTH | YES | 0 | 0 | 15 | -0.036872 | south | 5 | N | N | Nsouth | Nsouth | -1 | -0.55308 | 0 | -0.092759 | 0
39760 | TNSCLP1_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0832 | 0 | -0.092673 | 0
39770 | TNSCLP2_ | 1 | HOUSTON | YES | 98 | 20 | 111 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0832 | 0 | -0.092673 | 0
39775 | TNSCLP4_ | 1 | HOUSTON | YES | 105.1 | 20 | 119 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.3775 | 0 | -0.092673 | 0
39790 | TNSCLP3_ | 1 | HOUSTON | YES | 96.7 | 20 | 109.5 | -0.036786 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.0281 | 0 | -0.092673 | 0
48730 | MNS_GT | 1 | HOUSTON | YES | 43 | 0 | 46.1 | -0.031657 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4594 | 0 | -0.087544 | 0
48926 | WAP_GN6_ | 6 | HOUSTON | YES | 651 | 280 | 651 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -20.5299 | 0 | -0.087423 | 0
48927 | WAP_GN7_ | 7 | HOUSTON | YES | 564 | 277 | 564 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -17.7863 | 0 | -0.087423 | 0
48928 | WAP_GN8_ | 8 | HOUSTON | YES | 600 | 275 | 600 | -0.031536 | houston | 4 | Y | N | Yhouston | Nhouston | -1 | -18.9216 | 0 | -0.087423 | 0
48521 | BVE_GT1_ | 1 | HOUSTON | YES | 163 | 0 | 163 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1332 | 0 | -0.087379 | 0
48522 | BVE_GT2_ | 2 | HOUSTON | YES | 163 | 0 | 163 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -5.1332 | 0 | -0.087379 | 0
48523 | BVE_ST1_ | 3 | HOUSTON | YES | 245 | 0 | 245 | -0.031492 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -7.7155 | 0 | -0.087379 | 0
48510 | AK_GT1__ | 1 | HOUSTON | YES | 33.4 | 8.1 | 33 | -0.030886 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.0192 | 0 | -0.086773 | 0
48921 | WAP_GN1_ | 1 | HOUSTON | YES | 120.7 | 37 | 161 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9369 | 161 | -0.086551 | -13.9347
48922 | WAP_GN2_ | 2 | HOUSTON | YES | 83 | 37 | 166 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.0902 | 166 | -0.086551 | -14.3675
48923 | WAP_GN3_ | 3 | HOUSTON | YES | 186 | 93 | 248 | -0.030664 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.6047 | 248 | -0.086551 | -21.4646
48924 | WAP_GN4_ | 4 | HOUSTON | YES | 409.5 | 217 | 546 | -0.030664 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -16.7425 | 546 | -0.086551 | -47.2568
48925 | WAP_GN5_ | 5 | HOUSTON | YES | 581.9 | 278 | 643 | -0.030664 | houston | 1 | N | N | Nhouston | Nhouston | -1 | -19.717 | 0 | -0.086551 | 0
48929 | WAPGT21_ | B1 | HOUSTON | YES | 0 | 0 | 13 | -0.030664 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.39863 | 13 | -0.086551 | -1.1252
38711 | TNTXCTY1 | 1 | HOUSTON | YES | 100.3 | 59 | 100.3 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8034 | 0 | -0.083837 | 0
38712 | TNTXCTY2 | 1 | HOUSTON | YES | 92.9 | 59 | 92.9 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5966 | 0 | -0.083837 | 0
38713 | TNTXCTY3 | 1 | HOUSTON | YES | 102.7 | 59 | 102.7 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8705 | 0 | -0.083837 | 0
38714 | TNTXCTY4 | 1 | HOUSTON | YES | 102 | 59 | 102 | -0.02795 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.8509 | 0 | -0.083837 | 0
39470 | TNDOWCGN | 1 | HOUSTON | YES | 32 | 10 | 32 | -0.02795 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8944 | 0 | -0.083837 | 0
39480 | TNDOWCGN | 1 | HOUSTON | YES | 30 | 10 | 30 | -0.02795 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.8385 | 0 | -0.083837 | 0
38580 | TNBP_CGN | 1 | HOUSTON | YES | 70.8 | 0 | 70.8 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9779 | 0 | -0.083823 | 0
38590 | TNBP_CGN | 2 | HOUSTON | YES | 66.7 | 0 | 66.7 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8633 | 0 | -0.083823 | 0
38600 | TNBP_CGN | 5 | HOUSTON | YES | 53 | 0 | 53 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4806 | 0 | -0.083823 | 0
38611 | TNBPAMCG | 1 | HOUSTON | YES | 153.2 | 0 | 153.2 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2798 | 0 | -0.083823 | 0
38612 | TNBPAMCG | 2 | HOUSTON | YES | 153.5 | 0 | 153.5 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2882 | 0 | -0.083823 | 0
38613 | TNBPAMCG | 3 | HOUSTON | YES | 152.3 | 0 | 152.3 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.2547 | 0 | -0.083823 | 0
38614 | TNBPAMCG | 4 | HOUSTON | YES | 96 | 0 | 96 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6819 | 0 | -0.083823 | 0
38615 | TNBPAMCG | 1 | HOUSTON | YES | 244 | 0 | 244 | -0.027936 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.8164 | 0 | -0.083823 | 0
38690 | TNBP_CGN | 3 | HOUSTON | YES | 40 | 0 | 40 | -0.027936 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.1174 | 0 | -0.083823 | 0
48865 | TECO_GT1 | 1 | HOUSTON | YES | 50 | 24.9 | 50 | -0.026818 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.3409 | 50 | -0.082705 | -4.1352
48772 | PHR_GN2_ | MB | HOUSTON | YES | 0 | 72 | 459 | -0.025941 | houston | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.081828 | 0
48561 | CTL_GT2_ | 1 | HOUSTON | YES | 50 | 30.3 | 91 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.2677 | 0 | -0.080807 | 0
48562 | CTL_GT3_ | 2 | HOUSTON | YES | 30.3 | 30.3 | 87.6 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.183 | 0 | -0.080807 | 0
48563 | CTL_GT4_ | 3 | HOUSTON | YES | 30.3 | 30.3 | 87 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.168 | 0 | -0.080807 | 0
48564 | CTL_GN1_ | 4 | HOUSTON | YES | 12.9 | 12.9 | 54.5 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3581 | 0 | -0.080807 | 0
48565 | CTL_GN2_ | 5 | HOUSTON | YES | 3.4 | 3.4 | 12.2 | -0.02492 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.30402 | 0 | -0.080807 | 0
48531 | BYU_GT1_ | 1 | HOUSTON | YES | 65 | 0 | 65 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5939 | 0 | -0.080408 | 0
48532 | BYU_GT2_ | 2 | HOUSTON | YES | 60 | 0 | 60 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.4713 | 0 | -0.080408 | 0
48533 | BYU_GT3_ | 3 | HOUSTON | YES | 65 | 0 | 65 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5939 | 0 | -0.080408 | 0
48534 | BYU_GT4_ | 4 | HOUSTON | YES | 65 | 0 | 65 | -0.024521 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.5939 | 0 | -0.080408 | 0
48691 | GBY_7374 | A | HOUSTON | YES | 0 | 20 | 46 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1009 | 46 | -0.079819 | -3.6717
48691 | GBY_7374 | B | HOUSTON | YES | 0 | 20 | 46 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1009 | 46 | -0.079819 | -3.6717
48692 | GBY_8182 | C | HOUSTON | YES | 0 | 20 | 46 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1009 | 46 | -0.079819 | -3.6717
48692 | GBY_8182 | D | HOUSTON | YES | 0 | 20 | 55 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3163 | 55 | -0.079819 | -4.39
48693 | GBY_8384 | E | HOUSTON | YES | 0 | 20 | 55 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.3163 | 55 | -0.079819 | -4.39
48693 | GBY_8384 | F | HOUSTON | YES | 0 | 20 | 54 | -0.023932 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.2923 | 54 | -0.079819 | -4.3102
48841 | SJS_GT1_ | 1 | HOUSTON | YES | 49 | 49 | 78 | -0.023778 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.8547 | 0 | -0.079665 | 0
48842 | SJS_GT2_ | 2 | HOUSTON | YES | 49 | 49 | 80 | -0.023778 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -1.9022 | 0 | -0.079665 | 0
48641 | DPEC_GT1 | 1 | HOUSTON | YES | 163.2 | 98 | 163.2 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.8471 | 0 | -0.07946 | 0
48642 | DPEC_GT2 | 2 | HOUSTON | YES | 157.1 | 98 | 157.1 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7033 | 0 | -0.07946 | 0
48643 | DPEC_GT3 | 3 | HOUSTON | YES | 157.5 | 98 | 157.5 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.7127 | 0 | -0.07946 | 0
48644 | DPEC_GT4 | 4 | HOUSTON | YES | 157 | 98 | 157 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.701 | 0 | -0.07946 | 0
48645 | DPEC_ST5 | 5 | HOUSTON | YES | 269 | 0 | 269 | -0.023573 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -6.3411 | 0 | -0.07946 | 0
48761 | PR_GT1__ | 1 | HOUSTON | YES | 26 | 0 | 35 | -0.023407 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.81925 | 0 | -0.079294 | 0
48855 | SRB_GT21 | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.023228 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.27874 | 12 | -0.079115 | -0.94938
48855 | SRB_GT21 | MB | HOUSTON | YES | 0 | 0 | 18 | -0.023228 | houston | 13 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.079115 | 0
48852 | SRB_GN2_ | 2 | HOUSTON | YES | 0 | 26 | 169 | -0.023219 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.924 | 169 | -0.079106 | -13.3689
48851 | SRB_GN1_ | 1 | HOUSTON | YES | 123.7 | 26 | 165 | -0.023204 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -3.8287 | 165 | -0.079091 | -13.05
48551 | CAL_GT1_ | 1 | HOUSTON | YES | 149 | 0 | 149 | -0.023194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.4559 | 0 | -0.079081 | 0
48552 | CAL_ST1_ | 2 | HOUSTON | YES | 65.1 | 0 | 65.1 | -0.023194 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.5099 | 0 | -0.079081 | 0
48853 | SRB_GN3_ | 3 | HOUSTON | YES | 213 | 35 | 213 | -0.023157 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -4.9324 | 213 | -0.079044 | -16.8364
48845 | SOL_GT1 | 1 | HOUSTON | YES | 16.2 | 15.4 | 16.2 | -0.023153 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37508 | 0 | -0.07904 | 0
48611 | DIB_GT1_ | 1 | HOUSTON | YES | 64 | 0 | 64 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4815 | 0 | -0.079036 | 0
48612 | DIB_GT2_ | 2 | HOUSTON | YES | 63.2 | 0 | 63.2 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.463 | 0 | -0.079036 | 0
48613 | DIB_ST1_ | 3 | HOUSTON | YES | 82.6 | 30 | 82.6 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.9121 | 0 | -0.079036 | 0
48614 | DIB_GT3_ | 4 | HOUSTON | YES | 73.6 | 15 | 73.6 | -0.023149 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.7038 | 0 | -0.079036 | 0
48854 | SRB_GN4_ | 4 | HOUSTON | YES | 171 | 35 | 228 | -0.023143 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -5.2766 | 228 | -0.07903 | -18.0188
48740 | PSG_GN2_ | 1 | HOUSTON | YES | 180 | 60 | 180 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -4.1647 | 0 | -0.079024 | 0
48741 | PSG_GT2_ | 1 | HOUSTON | YES | 158.6 | 50 | 158.6 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6695 | 0 | -0.079024 | 0
48742 | PSG_GT3_ | 1 | HOUSTON | YES | 157 | 50 | 157 | -0.023137 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.6325 | 0 | -0.079024 | 0
48820 | SHELLG1_ | 1 | HOUSTON | YES | 71 | 34.5 | 71 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6248 | 0 | -0.078772 | 0
48821 | SHELLG2 | 2 | HOUSTON | YES | 72 | 34.5 | 72 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.6477 | 0 | -0.078772 | 0
48822 | SHELLG3_ | 1 | HOUSTON | YES | 39 | 0 | 39 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.89251 | 0 | -0.078772 | 0
48822 | SHELLG3_ | 2 | HOUSTON | YES | 30 | 0 | 30 | -0.022885 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.68655 | 0 | -0.078772 | 0
48500 | APD_GT1_ | 1 | HOUSTON | YES | 136 | 54.6 | 136 | -0.022488 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0584 | 0 | -0.078375 | 0
48511 | LPE_GT1_ | 1 | HOUSTON | YES | 42 | 0 | 42 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.94311 | 42 | -0.078342 | -3.2904
48512 | LPE_GT2_ | 2 | HOUSTON | YES | 42 | 0 | 42 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.94311 | 42 | -0.078342 | -3.2904
48513 | LPE_GT3_ | 3 | HOUSTON | YES | 38 | 0 | 38 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.85329 | 38 | -0.078342 | -2.977
48514 | LPE_GT4_ | 4 | HOUSTON | YES | 38 | 0 | 38 | -0.022455 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.85329 | 38 | -0.078342 | -2.977
48593 | CHE_GT1_ | 1 | HOUSTON | YES | 173 | 50 | 173 | -0.022354 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.8672 | 0 | -0.078241 | 0
48594 | CHE_GN4_ | 4 | HOUSTON | YES | 135 | 60 | 135 | -0.022354 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.0178 | 0 | -0.078241 | 0
48873 | THW_ST3_ | 3 | HOUSTON | YES | 104 | 19 | 104 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2587 | 104 | -0.077605 | -8.0709
48874 | THW_ST4_ | 4 | HOUSTON | YES | 90.4 | 19 | 104 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -2.2587 | 104 | -0.077605 | -8.0709
48875 | THW_3132 | A | HOUSTON | YES | 54 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48875 | THW_3132 | B | HOUSTON | YES | 53 | 5 | 53 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1511 | 53 | -0.077605 | -4.1131
48877 | THW_3334 | C | HOUSTON | YES | 57 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48877 | THW_3334 | D | HOUSTON | YES | 57 | 5 | 57 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2379 | 57 | -0.077605 | -4.4235
48879 | THW_4142 | E | HOUSTON | YES | 46.9 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48879 | THW_4142 | F | HOUSTON | YES | 46.9 | 5 | 54 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.1728 | 54 | -0.077605 | -4.1907
48881 | THW_4344 | G | HOUSTON | YES | 50.4 | 5 | 58 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2596 | 58 | -0.077605 | -4.5011
48881 | THW_4344 | H | HOUSTON | YES | 50.4 | 5 | 58 | -0.021718 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -1.2596 | 58 | -0.077605 | -4.5011
48582 | CBY_GN2_ | 2 | HOUSTON | YES | 551.2 | 110 | 735 | -0.021465 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.7768 | 735 | -0.077352 | -56.8537
49803 | EXN_15GT | 1 | HOUSTON | YES | 33 | 8.3 | 34 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.72423 | 0 | -0.077188 | 0
49804 | EXN_16GT | 2 | HOUSTON | YES | 32 | 8.3 | 34.7 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.73914 | 0 | -0.077188 | 0
49805 | EXN_17GT | 3 | HOUSTON | YES | 31 | 8.3 | 32.7 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.69654 | 0 | -0.077188 | 0
49826 | EXN938GT | 5 | HOUSTON | YES | 43 | 9.2 | 45.9 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.97772 | 0 | -0.077188 | 0
49828 | EXN941GT | 10 | HOUSTON | YES | 19 | 5.4 | 17.7 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.37703 | 0 | -0.077188 | 0
49829 | EXN942GT | 11 | HOUSTON | YES | 20 | 5.4 | 20.4 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43454 | 0 | -0.077188 | 0
49830 | EXN943GT | 12 | HOUSTON | YES | 19 | 5.4 | 19.9 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.42389 | 0 | -0.077188 | 0
49831 | EXN944GT | 13 | HOUSTON | YES | 33 | 5.4 | 35 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.74553 | 0 | -0.077188 | 0
49832 | EXN945GT | 9 | HOUSTON | YES | 19 | 9.2 | 18 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.38342 | 0 | -0.077188 | 0
49837 | EXN_GT | 4 | HOUSTON | YES | 81 | 21.3 | 85.4 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.8191 | 0 | -0.077188 | 0
49838 | EXN_14GT | 14 | HOUSTON | YES | 140 | 0 | 148 | -0.021301 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1525 | 0 | -0.077188 | 0
48883 | THW_GT1_ | B2 | HOUSTON | YES | 0 | 0 | 12 | -0.021096 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -0.25315 | 12 | -0.076983 | -0.92379
48651 | EP_1_2 | 1 | HOUSTON | YES | 4 | 0 | 5 | -0.020825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.10412 | 0 | -0.076712 | 0
48651 | EP_1_2 | 2 | HOUSTON | YES | 17.7 | 10 | 21 | -0.020825 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -0.43733 | 0 | -0.076712 | 0
48791 | PSA_GT1_ | 1 | HOUSTON | YES | 65 | 20.8 | 65 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3534 | 0 | -0.076708 | 0
48792 | PSA_GT2_ | 2 | HOUSTON | YES | 66 | 20.3 | 66 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3742 | 0 | -0.076708 | 0
48793 | PSA_GT3_ | 3 | HOUSTON | YES | 70 | 20.3 | 70 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.4575 | 0 | -0.076708 | 0
48794 | PSA_GT4_ | 4 | HOUSTON | YES | 63 | 20.3 | 63 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.3117 | 0 | -0.076708 | 0
48795 | PSA_GT5_ | 5 | HOUSTON | YES | 62 | 20.3 | 62 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2909 | 0 | -0.076708 | 0
48796 | PSA_GN1_ | 1 | HOUSTON | YES | 104 | 43.1 | 104 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.1654 | 0 | -0.076708 | 0
48797 | PSA_GT6_ | 6 | HOUSTON | YES | 59 | 34.5 | 59 | -0.020821 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -1.2284 | 0 | -0.076708 | 0
48940 | WARVUE_G | G1 | HOUSTON | YES | 12 | 0 | 12 | -0.020808 | houston | 6 | Y | N | Yhouston | Nhouston | -1 | -0.2497 | 0 | -0.076695 | 0
48581 | CBY_GN1_ | 1 | HOUSTON | YES | 743 | 108 | 743 | -0.020789 | houston | 10 | Y | Y | Yhouston | Yhouston | -1 | -15.4462 | 743 | -0.076676 | -56.9702
48815 | CVC_GT4_ | 4 | HOUSTON | YES | 157 | 91.8 | 157 | -0.020666 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -3.2446 | 0 | -0.076553 | 0
48583 | CBY_GT4_ | 1 | HOUSTON | YES | 172 | 0 | 172 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5406 | 172 | -0.076472 | -13.1532
48584 | CBY_GT4_ | 2 | HOUSTON | YES | 172 | 0 | 172 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5406 | 172 | -0.076472 | -13.1532
48585 | CBY_ST4_ | 3 | HOUSTON | YES | 172 | 0 | 172 | -0.020585 | houston | 9 | Y | Y | Yhouston | Yhouston | -1 | -3.5406 | 172 | -0.076472 | -13.1532
48595 | BTE_GT2_ | 1 | HOUSTON | YES | 162.8 | 130 | 162.8 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2736 | 0 | -0.075995 | 0
48596 | BTE_GT3_ | 2 | HOUSTON | YES | 161.4 | 130 | 161.4 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.2454 | 0 | -0.075995 | 0
48597 | BTE_GT4_ | 3 | HOUSTON | YES | 158.9 | 130 | 158.9 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -3.1952 | 0 | -0.075995 | 0
48598 | BTE_ST1_ | 4 | HOUSTON | YES | 269.2 | 60 | 269.2 | -0.020108 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -5.4131 | 0 | -0.075995 | 0
48690 | GBY_GN5_ | 5 | HOUSTON | YES | 199 | 81 | 398 | -0.019943 | houston | 12 | Y | Y | Yhouston | Yhouston | -1 | -7.9373 | 398 | -0.07583 | -30.1803
48885 | THW_5152 | A | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48885 | THW_5152 | B | HOUSTON | YES | 0 | 5 | 59 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1597 | 59 | -0.075543 | -4.457
48886 | THW_5354 | C | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48886 | THW_5354 | D | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48887 | THW_5556 | E | HOUSTON | YES | 0 | 5 | 59 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1597 | 59 | -0.075543 | -4.457
48887 | THW_5556 | F | HOUSTON | YES | 0 | 5 | 56 | -0.019656 | houston | 13 | Y | Y | Yhouston | Yhouston | -1 | -1.1007 | 56 | -0.075543 | -4.2304
48591 | CHE_GT2_ | 2 | HOUSTON | YES | 173 | 50 | 173 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.9123 | 0 | -0.072721 | 0
48811 | CVC_GT3_ | 3 | HOUSTON | YES | 156 | 91.8 | 156 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.6261 | 0 | -0.072721 | 0
48812 | CVC_GT2_ | 2 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5924 | 0 | -0.072721 | 0
48813 | CVC_GT1_ | 1 | HOUSTON | YES | 154 | 91.8 | 154 | -0.016834 | houston | 8 | N | N | Nhouston | Nhouston | -1 | -2.5924 | 0 | -0.072721 | 0
48814 | CVC_ST5_ | 1 | HOUSTON | YES | 162 | 91.8 | 162 | -0.016834 | houston | 7 | N | N | Nhouston | Nhouston | -1 | -2.7271 | 0 | -0.072721 | 0
8139 | JOS #1 | MB | SOUTH | YES | 0 | 45 | 255 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8285 | LAR #1 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8287 | LAR #2 | MB | SOUTH | YES | 0 | 9 | 32 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8288 | LAR #3 | MB | SOUTH | YES | 0 | 25 | 105 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8388 | BATES0A | MB | SOUTH | YES | 0 | 21 | 70 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8393 | BATES0B | MB | SOUTH | YES | 0 | 25 | 110 | 0 | south | 10 | Y | Y | mothballed | mothballed | -1 | 0 | 0 | -0.055887 | 0
8456 | COSW#1 | 1 | SOUTH | YES | 0 | 0 | 20 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055887 | 0
8457 | COSW#2 | 2 | SOUTH | YES | 0 | 0 | 14 | 0 | south | 7 | N | N | Nsouth | Nsouth | -1 | 0 | 0 | -0.055887 | 0
60074 | HORSH5 | 1 | WEST | YES | 0 | 0 | 100 | -0.088024 | south | 6 | Y | N | Ysouth | Nsouth | 1 | -8.8024 | 0 | -0.0025773 | 0
60201 | RIO DRCS | F | WEST | YES | 0 | 0 | 0 | -0.02909 | south | #N/A | N | N | Nsouth | Nsouth | 1 | 0 | 0 | 0.056357 | 0
5920 | WELSHDC1 | EQ | NORTH | YES | 400.3 | -600 | 600 | 0 | north | 1 | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.085447 | 0
6096 | NORTHDC7 | EQ | WEST | YES | 50 | -220 | 220 | 0 | west | 1 | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.085447 | 0
48671 | FTR_GT1_ | 1 | NORTH | YES | 154.2 | 0 | 154.2 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.4856 | 0 | 0.095081 | 0
48672 | FTR_GT2_ | 2 | NORTH | YES | 156 | 0 | 156 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5029 | 0 | 0.095081 | 0
48673 | FTR_GT3_ | 3 | NORTH | YES | 156 | 0 | 156 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 1.5029 | 0 | 0.095081 | 0
48674 | FTR_CN4_ | 4 | NORTH | YES | 380 | 0 | 380 | 0.009634 | north | 1 | N | N | Nnorth | Nnorth | 1 | 3.6609 | 0 | 0.095081 | 0
32883 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 48 | 0.010031 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.48149 | 48 | 0.095478 | 4.5829
32884 | BRYN_DNS | 1 | NORTH | YES | 2 | 2 | 46 | 0.010031 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.46143 | 46 | 0.095478 | 4.392
32892 | BRYN_DNS | 1 | NORTH | YES | 0 | 25 | 105 | 0.010031 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.0533 | 105 | 0.095478 | 10.0252
32798 | BRYN_TAM | 1 | NORTH | YES | 32 | 0 | 32 | 0.011556 | north | 7 | N | N | Nnorth | Nnorth | 1 | 0.36979 | 0 | 0.097003 | 0
32886 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 12 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
32887 | BRYN_ATK | MB | NORTH | YES | 0 | 12 | 51 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
32888 | BRYN_ATK | 1 | NORTH | YES | 0 | 4 | 17 | 0.011607 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 0.19732 | 17 | 0.097054 | 1.6499
32890 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 22 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
32891 | BRYN_ATK | MB | NORTH | YES | 0 | 5 | 25 | 0.011607 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.097054 | 0
990 | GIBN_CRE | 1 | NORTH | YES | 463 | 200 | 463 | 0.014683 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 6.7982 | 0 | 0.10013 | 0
6476 | LANGFORD | 1 | WEST | YES | 15 | 0 | 150 | 0.025139 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7708 | 0 | 0.11059 | 0
13691 | OAKGROVE | 1 | NORTH | YES | 855 | 250 | 855 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.2506 | 0 | 0.11732 | 0
13692 | OAKGROVE | 2 | NORTH | YES | 855 | 250 | 855 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 27.2506 | 0 | 0.11732 | 0
39960 | TNTNPONE | 1 | NORTH | YES | 152.3 | 30 | 152.3 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.8541 | 0 | 0.11732 | 0
39970 | TNTNPONE | 1 | NORTH | YES | 153 | 30 | 153 | 0.031872 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 4.8764 | 0 | 0.11732 | 0
60202 | FRIEND_R | F | WEST | YES | 0 | 0 | 0 | 0.033317 | west | #N/A | N | N | Nwest | Nwest | 1 | 0 | 0 | 0.11876 | 0
48721 | LEG_1___ | 1 | NORTH | YES | 827 | 357 | 827 | 0.039111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.3448 | 0 | 0.12456 | 0
48722 | LEG_2___ | 2 | NORTH | YES | 819 | 357 | 819 | 0.039111 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.0319 | 0 | 0.12456 | 0
60018 | DSKY1 | 1 | WEST | YES | 12.6 | 0 | 84 | 0.043938 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.6908 | 0 | 0.12938 | 0
60000 | DSKY2 | 1 | WEST | YES | 11.5 | 0 | 76.5 | 0.044282 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3876 | 0 | 0.12973 | 0
60017 | ORNNWP1 | 1 | WEST | YES | 12 | 0 | 80 | 0.044604 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5683 | 0 | 0.13005 | 0
38437 | TNSRBNMS | 1 | WEST | YES | 22.5 | 0 | 150 | 0.046578 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9867 | 0 | 0.13202 | 0
38438 | TNSRBNMS | 1 | WEST | YES | 0 | 0 | 150 | 0.046578 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9867 | 0 | 0.13202 | 0
38332 | WDWRDU2 | 1 | WEST | YES | 12 | 0 | 80 | 0.046628 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7302 | 0 | 0.13207 | 0
60016 | WOODWRD1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046639 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7311 | 0 | 0.13209 | 0
6016 | SWMESA | 1 | WEST | YES | 11.2 | 0 | 75 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.5044 | 0 | 0.13217 | 0
60003 | KING_NE1 | 1 | WEST | YES | 12 | 0 | 80 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7381 | 0 | 0.13217 | 0
60005 | KING_SE1 | 1 | WEST | YES | 6 | 0 | 40 | 0.046726 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.869 | 0 | 0.13217 | 0
60007 | KING_SW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.047121 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7697 | 0 | 0.13257 | 0
60019 | KING_NW1 | 1 | WEST | YES | 12 | 0 | 80 | 0.047121 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.7697 | 0 | 0.13257 | 0
60203 | PRES0A | BT | WEST | YES | 2.3 | -2 | 4.8 | 0.048578 | west | #N/A | N | N | Nwest | Nwest | 1 | 0.23317 | 0 | 0.13402 | 0
3381 | BBRN_1G | 1 | NORTH | YES | 615 | 225 | 615 | 0.04995 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 30.7192 | 0 | 0.1354 | 0
3382 | BBRN_2G | 2 | NORTH | YES | 587 | 225 | 587 | 0.04995 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 29.3207 | 0 | 0.1354 | 0
13131 | CALFREST | 1 | NORTH | YES | 150.7 | 40 | 150.7 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6562 | 150.7 | 0.13625 | 20.533
13132 | CALFREST | 2 | NORTH | YES | 151 | 57 | 151 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.6714 | 151 | 0.13625 | 20.5739
13133 | CALFREST | 3 | NORTH | YES | 177.4 | 40 | 177.4 | 0.050804 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0126 | 177.4 | 0.13625 | 24.1709
13134 | CALFREST | 4 | NORTH | YES | 151.5 | 40 | 151.5 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.7207 | 151.5 | 0.13641 | 20.6659
13135 | CALFREST | 5 | NORTH | YES | 152.3 | 57 | 152.3 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.7615 | 152.3 | 0.13641 | 20.775
13136 | CALFREST | 6 | NORTH | YES | 177.5 | 40 | 177.5 | 0.050962 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.0458 | 177.5 | 0.13641 | 24.2125
1002 | PBCTAGE_ | A | WEST | YES | 64 | 65 | 66 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.4389 | 66 | 0.13755 | 9.0784
1003 | PBCTBGE_ | B | WEST | YES | 65 | 64 | 65 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.3868 | 65 | 0.13755 | 8.9409
1004 | PBCTCGE_ | C | WEST | YES | 62 | 64 | 67 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.491 | 67 | 0.13755 | 9.216
1005 | PBCTDGE_ | D | WEST | YES | 65 | 64 | 67 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.491 | 67 | 0.13755 | 9.216
1006 | PBCTEGE_ | E | WEST | YES | 65 | 64 | 67 | 0.052105 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.491 | 67 | 0.13755 | 9.216
1007 | PB5GEN_6 | MB | WEST | YES | 114 | 40 | 114 | 0.052105 | west | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13755 | 0
1008 | PB6GEN_7 | MB | WEST | YES | 515 | 130 | 515 | 0.052105 | west | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.13755 | 0
7038 | L_DELAWA | 1 | WEST | YES | 3.5 | 0 | 35 | 0.052155 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8254 | 0 | 0.1376 | 0
7038 | L_DELAWA | 2 | WEST | YES | 3 | 0 | 30 | 0.052155 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.5647 | 0 | 0.1376 | 0
11147 | NOTREES_ | 1 | WEST | YES | 22.3 | 0 | 149 | 0.052322 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.796 | 0 | 0.13777 | 0
6407 | TURKTRAK | 1 | WEST | YES | 17 | 0 | 169.5 | 0.052476 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.8947 | 0 | 0.13792 | 0
1349 | WESTXWIN | 1 | WEST | YES | 0.7 | 0 | 6.6 | 0.052737 | west | 6 | Y | N | Ywest | Nwest | 1 | 0.34806 | 0 | 0.13818 | 0
1350 | NWPWRG1_ | 1 | WEST | YES | 3.4 | 1 | 34.3 | 0.052737 | west | 6 | Y | N | Ywest | Nwest | 1 | 1.8089 | 0 | 0.13818 | 0
11020 | TIEHVSG_ | 1 | WEST | YES | 208.2 | 63 | 208.2 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.0471 | 208.2 | 0.13851 | 28.8371
11021 | TIEHVCG_ | 1 | WEST | YES | 142.1 | 103 | 142.1 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.5398 | 142.1 | 0.13851 | 19.6818
11022 | TIEHVCG_ | 1 | WEST | YES | 132.4 | 103 | 132.4 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.0251 | 132.4 | 0.13851 | 18.3383
11023 | TIEHVCG_ | 1 | WEST | YES | 136 | 103 | 136 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.2162 | 136 | 0.13851 | 18.8369
11024 | TIEHVCG_ | 1 | WEST | YES | 147 | 103 | 147 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 7.7998 | 147 | 0.13851 | 20.3605
11025 | TIEHVSG_ | 1 | WEST | YES | 210 | 63 | 210 | 0.05306 | west | 9 | Y | Y | Ywest | Ywest | 1 | 11.1426 | 210 | 0.13851 | 29.0864
11001 | NAV1CT | 1 | WEST | YES | 56 | 18 | 70 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7149 | 70 | 0.13852 | 9.6962
11009 | NAV2CT | 1 | WEST | YES | 56 | 18 | 70 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 3.7149 | 70 | 0.13852 | 9.6962
11011 | NAV3ST | 1 | WEST | YES | 74 | 40 | 92.8 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.9249 | 92.8 | 0.13852 | 12.8543
11012 | NAV4CT | 1 | WEST | YES | 80 | 18 | 80 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2456 | 80 | 0.13852 | 11.0813
11013 | NAV5CT | 1 | WEST | YES | 80 | 18 | 80 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 4.2456 | 80 | 0.13852 | 11.0813
11014 | NAV6ST | 1 | WEST | YES | 115 | 40 | 115 | 0.05307 | west | 9 | Y | Y | Ywest | Ywest | 1 | 6.103 | 115 | 0.13852 | 15.9294
76091 | L_DIVIDE | W1 | WEST | YES | 11.2 | 0 | 112.5 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.9721 | 0 | 0.13853 | 0
76095 | L_CAPRSI | W1 | WEST | YES | 14.9 | 0 | 149.5 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9362 | 0 | 0.13853 | 0
76096 | L_CAPRSI | W1 | WEST | YES | 18.6 | 0 | 186 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.8738 | 0 | 0.13853 | 0
76097 | L_CAPRGE | W1 | WEST | YES | 21.5 | 0 | 214.5 | 0.053085 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.3867 | 0 | 0.13853 | 0
1328 | OCOTILLO | 1 | WEST | YES | 5.8 | 0 | 58 | 0.053116 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.0807 | 0 | 0.13856 | 0
1326 | STANTONW | 1 | WEST | YES | 10.1 | 0 | 100.5 | 0.053134 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.34 | 0 | 0.13858 | 0
1333 | MCDDONAL | 1 | WEST | YES | 21.4 | 0 | 214.2 | 0.053247 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.4055 | 0 | 0.13869 | 0
76031 | L_GASCCR | W1 | WEST | YES | 15 | 0 | 150 | 0.053256 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.9884 | 0 | 0.1387 | 0
1320 | BSP 1 | 1 | WEST | YES | 25.8 | 2.9 | 25.8 | 0.05335 | west | 8 | N | N | Nwest | Nwest | 1 | 1.3764 | 0 | 0.1388 | 0
1327 | WILDHRSE | 1 | WEST | YES | 0 | 0 | 120 | 0.053626 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4351 | 0 | 0.13907 | 0
1360 | GUNSIGHT | 1 | WEST | YES | 12 | 0 | 120 | 0.053649 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4379 | 0 | 0.1391 | 0
11320 | COYOTE_1 | 1 | WEST | YES | 22.5 | 0 | 225 | 0.053736 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.0906 | 0 | 0.13918 | 0
1045 | CALENG1G | 1 | WEST | YES | 70 | 27 | 70 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7626 | 0 | 0.1392 | 0
1046 | CALENG2G | 2 | WEST | YES | 73.4 | 27 | 73.4 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 1 | 3.9453 | 0 | 0.1392 | 0
1047 | CALENG3G | 3 | WEST | YES | 70.4 | 27 | 70.4 | 0.053751 | west | 8 | N | N | Nwest | Nwest | 1 | 3.7841 | 0 | 0.1392 | 0
11309 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053787 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6817 | 0 | 0.13923 | 0
11310 | BULLCREK | 1 | WEST | YES | 18 | 0 | 180 | 0.053787 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.6817 | 0 | 0.13923 | 0
60058 | BUFF_GAP | 1 | WEST | YES | 12 | 0 | 120 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4666 | 0 | 0.13933 | 0
60060 | CIRELLO | 1 | WEST | YES | 23.3 | 0 | 233 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 1 | 12.5559 | 0 | 0.13933 | 0
60063 | BUFF_GAP | 1 | WEST | YES | 17 | 0 | 170.2 | 0.053888 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.1717 | 0 | 0.13933 | 0
1058 | LONGSHOR | 1 | WEST | YES | 15 | 0 | 150 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.0858 | 0 | 0.13935 | 0
1058 | LONGSHOR | 2 | WEST | YES | 22 | 0 | 220 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.8591 | 0 | 0.13935 | 0
11061 | PNTHRCK1 | 1 | WEST | YES | 20 | 0 | 200 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.781 | 0 | 0.13935 | 0
11065 | ELBOWCK_ | 1 | WEST | YES | 18 | 0 | 121.9 | 0.053905 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.571 | 0 | 0.13935 | 0
1039 | MRGNAG_1 | A | WEST | YES | 66 | 66 | 66 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5674 | 66 | 0.1395 | 9.2068
1040 | MRGNBG_2 | B | WEST | YES | 69 | 69 | 69 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7295 | 69 | 0.1395 | 9.6253
1041 | MRGNCG_3 | C | WEST | YES | 69 | 69 | 69 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.7295 | 69 | 0.1395 | 9.6253
1042 | MRGNDG_4 | D | WEST | YES | 67 | 67 | 67 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6214 | 67 | 0.1395 | 9.3463
1043 | MRGNEG_5 | E | WEST | YES | 67 | 67 | 67 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.6214 | 67 | 0.1395 | 9.3463
1044 | MRGNFG_6 | F | WEST | YES | 65 | 65 | 65 | 0.054051 | west | 13 | Y | Y | Ywest | Ywest | 1 | 3.5133 | 65 | 0.1395 | 9.0673
6637 | SNYDERW1 | 1 | WEST | YES | 6.3 | 0 | 63 | 0.054112 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.4091 | 0 | 0.13956 | 0
1068 | SCURRYCW | 1 | WEST | YES | 14.1 | 1.3 | 141 | 0.054151 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.6353 | 0 | 0.1396 | 0
1073 | SCURRYCW | 2 | WEST | YES | 12 | 0 | 120 | 0.054151 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.4981 | 0 | 0.1396 | 0
1061 | CIELOGEN | 1 | WEST | YES | 9.9 | 0 | 99 | 0.054166 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.3624 | 0 | 0.13961 | 0
1062 | CIELOGEN | 1 | WEST | YES | 6.1 | 0 | 61 | 0.054166 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3041 | 0 | 0.13961 | 0
1069 | KINDERMG | 1 | WEST | YES | 25 | 5 | 25 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 1 | 1.3541 | 0 | 0.13961 | 0
1070 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4754 | 0 | 0.13961 | 0
1071 | KINDERMG | 1 | WEST | YES | 45.7 | 12 | 45.7 | 0.054166 | west | 7 | N | N | Nwest | Nwest | 1 | 2.4754 | 0 | 0.13961 | 0
3107 | STRYKER_ | 1 | NORTH | YES | 113.6 | 45 | 182 | 0.054175 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 9.8598 | 182 | 0.13962 | 25.4111
3108 | STRYKER_ | 2 | NORTH | YES | 484 | 75 | 484 | 0.054175 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 26.2207 | 484 | 0.13962 | 67.5769
36998 | RDCNYNG1 | 1 | WEST | YES | 8.4 | 0 | 84 | 0.054305 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.5616 | 0 | 0.13975 | 0
11415 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.054383 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7979 | 0 | 0.13983 | 0
11416 | LORAINE_ | 1 | WEST | YES | 1.3 | 0 | 125 | 0.054383 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.7979 | 0 | 0.13983 | 0
3309 | ASPN_G | 1 | NORTH | YES | 50 | 0 | 50 | 0.054401 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 2.7201 | 0 | 0.13985 | 0
3348 | CHAMPION | MB | NORTH | YES | 0 | 42 | 42 | 0.054433 | north | 7 | N | N | mothballed | mothballed | 1 | 0 | 0 | 0.13988 | 0
1343 | TRENTIPP | 1 | WEST | YES | 15 | 0 | 150 | 0.054569 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.1853 | 0 | 0.14002 | 0
1354 | AEPWIND_ | 1 | WEST | YES | 10.1 | 0 | 101 | 0.054569 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.5115 | 0 | 0.14002 | 0
71051 | L_BITTCR | W1 | WEST | YES | 3.8 | 0 | 37.5 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 2.0503 | 0 | 0.14012 | 0
71054 | L_SWEETW | W1 | WEST | YES | 10.8 | 0 | 107.5 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.8776 | 0 | 0.14012 | 0
71057 | L_SWEETW | W1 | WEST | YES | 13.5 | 0 | 135 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 7.3811 | 0 | 0.14012 | 0
71059 | L_SWEETW | W1 | WEST | YES | 11.9 | 0 | 119 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.5063 | 0 | 0.14012 | 0
71060 | L_SWEETW | W1 | WEST | YES | 10.5 | 0 | 105 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 5.7409 | 0 | 0.14012 | 0
71061 | L_SWEETW | W1 | WEST | YES | 8 | 0 | 80.5 | 0.054675 | west | 6 | Y | N | Ywest | Nwest | 1 | 4.4013 | 0 | 0.14012 | 0
11056 | ROSCOE_1 | 1 | WEST | YES | 20.9 | 0 | 209 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 11.43 | 0 | 0.14014 | 0
11057 | CHAMPION | 1 | WEST | YES | 12.6 | 0 | 126.5 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 6.9182 | 0 | 0.14014 | 0
11058 | PYRON_1G | 1 | WEST | YES | 24.9 | 0 | 249 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.6176 | 0 | 0.14014 | 0
11059 | INADALE_ | 1 | WEST | YES | 19.7 | 0 | 197 | 0.054689 | west | 6 | Y | N | Ywest | Nwest | 1 | 10.7737 | 0 | 0.14014 | 0
13116 | TGATEWAY | 1 | NORTH | YES | 148 | 30 | 148 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1137 | 0 | 0.14027 | 0
13117 | TGATEWAY | 2 | NORTH | YES | 130 | 30 | 130 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.1269 | 0 | 0.14027 | 0
13118 | TGATEWAY | 3 | NORTH | YES | 145 | 30 | 145 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 7.9492 | 0 | 0.14027 | 0
13119 | TGATEWAY | 4 | NORTH | YES | 399 | 65 | 399 | 0.054822 | north | 1 | N | N | Nnorth | Nnorth | 1 | 21.874 | 0 | 0.14027 | 0
6144 | MCADOO1A | 1 | WEST | YES | 15 | 0 | 150 | 0.054915 | west | 6 | Y | N | Ywest | Nwest | 1 | 8.2372 | 0 | 0.14036 | 0
3097 | MARTLAKE | 1 | NORTH | YES | 785 | 500 | 785 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.3006 | 0 | 0.14061 | 0
3098 | MARTLAKE | 2 | NORTH | YES | 795 | 461 | 795 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.8522 | 0 | 0.14061 | 0
3099 | MARTLAKE | 3 | NORTH | YES | 780 | 500 | 780 | 0.05516 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 43.0248 | 0 | 0.14061 | 0
60081 | WHRLWIND | 1 | WEST | YES | 9 | 0 | 60 | 0.055605 | west | 6 | Y | N | Ywest | Nwest | 1 | 3.3363 | 0 | 0.14105 | 0
1437 | MESQUITW | 1 | NORTH | YES | 40 | 0 | 400 | 0.056296 | west | 6 | Y | N | Ywest | Nwest | 1 | 22.5184 | 0 | 0.14174 | 0
1438 | MESQUITW | 1 | NORTH | YES | 23.6 | 0 | 236 | 0.056298 | west | 6 | Y | N | Ywest | Nwest | 1 | 13.2863 | 0 | 0.14174 | 0
1442 | COKFIELD | 1 | NORTH | YES | 16.5 | 0 | 165 | 0.05681 | west | 6 | Y | N | Ywest | Nwest | 1 | 9.3736 | 0 | 0.14226 | 0
6752 | OKLA0A | 1 | WEST | YES | 649.7 | 175 | 649.7 | 0.057237 | west | 4 | Y | N | Ywest | Nwest | 1 | 37.1869 | 0 | 0.14268 | 0
12411 | FPLEFR1A | 1 | NORTH | YES | 161 | 72 | 161 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2873 | 161 | 0.14313 | 23.0442
12412 | FPLEFR1B | 2 | NORTH | YES | 164 | 72 | 164 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4603 | 164 | 0.14313 | 23.4736
12413 | FPLEFR1C | 3 | NORTH | YES | 164 | 72 | 164 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4603 | 164 | 0.14313 | 23.4736
12414 | FPLEFR1S | 4 | NORTH | YES | 414 | 191 | 414 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.8816 | 414 | 0.14313 | 59.2565
12421 | FPLEFR2A | 1 | NORTH | YES | 162 | 72 | 162 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.345 | 162 | 0.14313 | 23.1873
12422 | FPLEFR2B | 2 | NORTH | YES | 161 | 72 | 161 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.2873 | 161 | 0.14313 | 23.0442
12423 | FPLEFR2C | 3 | NORTH | YES | 163 | 72 | 163 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.4027 | 163 | 0.14313 | 23.3305
12424 | FPLEFR2S | 4 | NORTH | YES | 409 | 191 | 409 | 0.057685 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.5932 | 409 | 0.14313 | 58.5409
3126 | TRINIDAD | 1 | NORTH | YES | 224 | 46 | 224 | 0.058092 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 13.0126 | 224 | 0.14354 | 32.1527
948 | STEAM1 | 1 | NORTH | YES | 0 | 12 | 20 | 0.058263 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.1653 | 20 | 0.14371 | 2.8742
949 | STEAM2 | 1 | NORTH | YES | 26 | 8 | 25 | 0.058264 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 1.4566 | 25 | 0.14371 | 3.5928
950 | STEAM3 | 1 | NORTH | YES | 41 | 13 | 41 | 0.058264 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3888 | 41 | 0.14371 | 5.8921
2451 | LKHB1_G | 1 | NORTH | YES | 0 | 80 | 388 | 0.058281 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 22.613 | 388 | 0.14373 | 55.7663
2452 | LKHB2_G | 2 | NORTH | YES | 515 | 80 | 515 | 0.058281 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.0147 | 515 | 0.14373 | 74.0198
1701 | MOSES_1G | 1 | NORTH | YES | 558 | 175 | 558 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 32.5632 | 0 | 0.1438 | 0
1702 | MOSES_2G | 2 | NORTH | YES | 579 | 175 | 579 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 33.7887 | 0 | 0.1438 | 0
1703 | MOSES_3G | 3 | NORTH | YES | 808 | 463 | 808 | 0.058357 | north | 4 | Y | N | Ynorth | Nnorth | 1 | 47.1525 | 0 | 0.1438 | 0
842 | OLINGER_ | 1 | NORTH | YES | 55.4 | 20 | 79 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 4.6106 | 79 | 0.14381 | 11.3609
843 | OLINGER_ | 1 | NORTH | YES | 76.2 | 25 | 106 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.1864 | 106 | 0.14381 | 15.2437
844 | OLINGER_ | 1 | NORTH | YES | 103.9 | 45 | 146 | 0.058362 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 8.5209 | 146 | 0.14381 | 20.9961
845 | OLINGER_ | 1 | NORTH | YES | 51.9 | 0 | 76 | 0.058362 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.4355 | 76 | 0.14381 | 10.9295
837 | NEWMAN_G | 1 | NORTH | YES | 0 | 15 | 40 | 0.058384 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 2.3354 | 40 | 0.14383 | 5.7532
1675 | PEC_1G | 1 | NORTH | YES | 75 | 35 | 75 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.38 | 0 | 0.14385 | 0
1676 | PEC_2G | 2 | NORTH | YES | 79.6 | 35 | 79.6 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | 1 | 4.6486 | 0 | 0.14385 | 0
1677 | PEC_3G | 3 | NORTH | YES | 88.4 | 35 | 88.4 | 0.0584 | north | 8 | N | N | Nnorth | Nnorth | 1 | 5.1626 | 0 | 0.14385 | 0
1432 | GRHAMSES | 2 | NORTH | YES | 366 | 90 | 366 | 0.058432 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 21.3861 | 366 | 0.14388 | 52.6596
1678 | LAMARPWR | 1 | NORTH | YES | 160 | 67.7 | 160 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.3518 | 160 | 0.1439 | 23.0233
1679 | LAMARPWR | 2 | NORTH | YES | 156 | 67.7 | 156 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.118 | 156 | 0.1439 | 22.4477
1680 | LAMARPWR | 3 | NORTH | YES | 196 | 129.1 | 196 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.456 | 196 | 0.1439 | 28.2036
1681 | LAMARPWR | 4 | NORTH | YES | 156 | 67.7 | 156 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.118 | 156 | 0.1439 | 22.4477
1682 | LAMARPWR | 5 | NORTH | YES | 157 | 67.7 | 157 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 9.1765 | 157 | 0.1439 | 22.5916
1683 | LAMARPWR | 6 | NORTH | YES | 198 | 129.1 | 198 | 0.058449 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.5729 | 198 | 0.1439 | 28.4913
1689 | VALLEY_3 | 3 | NORTH | YES | 194.7 | 25 | 370 | 0.058505 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 21.6469 | 370 | 0.14395 | 53.2621
11691 | KMICHICT | 1 | NORTH | YES | 140 | 80 | 140 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.1907 | 0 | 0.14395 | 0
11692 | KMICHICT | 2 | NORTH | YES | 141 | 80 | 141 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.2492 | 0 | 0.14395 | 0
11693 | KMICHIST | 3 | NORTH | YES | 309 | 60 | 309 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.078 | 0 | 0.14395 | 0
11694 | KMICHICT | 4 | NORTH | YES | 143 | 80 | 143 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.3662 | 0 | 0.14395 | 0
11695 | KMICHICT | 5 | NORTH | YES | 144 | 80 | 144 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 8.4247 | 0 | 0.14395 | 0
11696 | KMICHIST | 6 | NORTH | YES | 310 | 60 | 310 | 0.058505 | north | 1 | N | N | Nnorth | Nnorth | 1 | 18.1365 | 0 | 0.14395 | 0
12440 | PARKD_1S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058518 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14396 | 0
12449 | PARKD_2S | 1 | NORTH | YES | 0 | 0 | 0 | 0.058518 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14396 | 0
1479 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1711 | 20 | 0.144 | 2.88
1479 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 20 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1711 | 20 | 0.144 | 2.88
1482 | WFCOGEN_ | 1 | NORTH | YES | 12 | 12 | 20 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 1.1711 | 20 | 0.144 | 2.88
1482 | WFCOGEN_ | 2 | NORTH | YES | 12 | 12 | 17 | 0.058555 | west | 9 | Y | Y | Ywest | Ywest | 1 | 0.99543 | 17 | 0.144 | 2.448
1687 | VALLEY_1 | 1 | NORTH | YES | 170 | 15 | 170 | 0.058602 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 9.9623 | 170 | 0.14405 | 24.4883
1688 | VALLEY_2 | 2 | NORTH | YES | 520 | 90 | 520 | 0.058602 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 30.473 | 520 | 0.14405 | 74.9053
6948 | DENISNDM | 1 | NORTH | YES | 0 | 5 | 40 | 0.058686 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3474 | 0 | 0.14413 | 0
6948 | DENISNDM | 2 | NORTH | YES | 0 | 5 | 40 | 0.058686 | north | 5 | N | N | Nnorth | Nnorth | 1 | 2.3474 | 0 | 0.14413 | 0
1433 | GRHAMSES | 1 | NORTH | YES | 242 | 60 | 242 | 0.058705 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 14.2066 | 242 | 0.14415 | 34.8847
12357 | RNRTPL_1 | 1 | NORTH | YES | 0 | 0 | 0 | 0.058998 | north | #N/A | N | N | Nnorth | Nnorth | 1 | 0 | 0 | 0.14444 | 0
2371 | COLLIN_1 | MB | NORTH | YES | 0 | 40 | 138 | 0.059032 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14448 | 0
2413 | MTCK6_G | 6 | NORTH | YES | 0 | 30 | 118 | 0.059497 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.0206 | 118 | 0.14494 | 17.1034
2414 | MTCK7_G | 7 | NORTH | YES | 0 | 30 | 115 | 0.059497 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 6.8422 | 115 | 0.14494 | 16.6685
2417 | MTCK8_G | 8 | NORTH | YES | 338 | 60 | 556 | 0.059497 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 33.0803 | 556 | 0.14494 | 80.5887
1453 | WCPWRCO_ | 1 | NORTH | YES | 204 | 50 | 204 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.1502 | 204 | 0.14501 | 29.5814
1454 | WCPWRCO_ | 2 | NORTH | YES | 201 | 50 | 201 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.9716 | 201 | 0.14501 | 29.1463
1455 | WCPWRCO_ | 3 | NORTH | YES | 242 | 50 | 242 | 0.05956 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4135 | 242 | 0.14501 | 35.0916
923 | SPENCER_ | 1 | NORTH | YES | 48 | 20 | 60 | 0.059614 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.5768 | 60 | 0.14506 | 8.7036
924 | SPENCER_ | 1 | NORTH | YES | 52 | 20 | 63 | 0.059614 | north | 11 | Y | Y | Ynorth | Ynorth | 1 | 3.7557 | 63 | 0.14506 | 9.1388
728 | WOLFRIDG | 1 | NORTH | YES | 11.2 | 0 | 112.5 | 0.05977 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 6.7241 | 0 | 0.14522 | 0
344 | MRSSHPRD | 1 | NORTH | YES | 0 | 0 | 12 | 0.060176 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72211 | 0 | 0.14562 | 0
345 | MRSSHPRD | 2 | NORTH | YES | 0 | 0 | 12 | 0.060176 | north | 5 | N | N | Nnorth | Nnorth | 1 | 0.72211 | 0 | 0.14562 | 0
1600 | BARTNWND | 1 | NORTH | YES | 12 | 0 | 120 | 0.060184 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 7.2221 | 0 | 0.14563 | 0
580 | JCKCNTY8 | 1 | NORTH | YES | 288 | 0 | 288 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 17.4563 | 288 | 0.14606 | 42.0649
581 | JCKCNTY8 | 2 | NORTH | YES | 147 | 0 | 147 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.91 | 147 | 0.14606 | 21.4706
582 | JCKCNTY8 | 3 | NORTH | YES | 147 | 0 | 147 | 0.060612 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 8.91 | 147 | 0.14606 | 21.4706
1861 | EAGLEMNT | MB | NORTH | YES | 0 | 30 | 112 | 0.060651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1461 | 0
1862 | EAGLEMNT | MB | NORTH | YES | 0 | 40 | 100 | 0.060651 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1461 | 0
1863 | EAGLEMNT | MB | NORTH | YES | 0 | 50 | 378 | 0.060651 | north | 12 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.1461 | 0
12322 | ENNSTRAC | 1 | NORTH | YES | 196 | 130 | 196 | 0.060703 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 11.8978 | 196 | 0.14615 | 28.6453
12323 | ENNSTRAC | 2 | NORTH | YES | 111 | 100 | 111 | 0.060703 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 6.738 | 111 | 0.14615 | 16.2226
503 | NTHTEXAS | 1 | NORTH | YES | 5 | 5 | 18 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.1055 | 18 | 0.14686 | 2.6436
504 | NTHTEXAS | 2 | NORTH | YES | 5 | 5 | 18 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 1.1055 | 18 | 0.14686 | 2.6436
505 | NTHTEXAS | 3 | NORTH | YES | 15 | 15 | 38 | 0.061418 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 2.3339 | 38 | 0.14686 | 5.5809
1948 | HANDLEY_ | 4 | NORTH | YES | 234.4 | 150 | 435 | 0.061452 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.7316 | 435 | 0.1469 | 63.9009
1898 | COMCHEPK | 1 | NORTH | YES | 1157 | 1150 | 1157 | 0.061476 | north | 3 | N | N | Nnorth | Nnorth | 1 | 71.1277 | 0 | 0.14692 | 0
1899 | COMCHEPK | 2 | NORTH | YES | 1158 | 1128 | 1158 | 0.061476 | north | 3 | N | N | Nnorth | Nnorth | 1 | 71.1892 | 0 | 0.14692 | 0
1877 | WLFHOLW_ | 1 | NORTH | YES | 203.9 | 89.2 | 217.3 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.3789 | 217.3 | 0.14702 | 31.9465
1878 | WLFHOLW_ | 2 | NORTH | YES | 192.4 | 105 | 205 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 12.6216 | 205 | 0.14702 | 30.1382
1879 | WLFHOLW_ | 3 | NORTH | YES | 255.7 | 89.2 | 272.4 | 0.061569 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 16.7714 | 272.4 | 0.14702 | 40.0471
1947 | HANDLEY_ | 3 | NORTH | YES | 395 | 100 | 395 | 0.061589 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 24.3277 | 395 | 0.14704 | 58.0791
1949 | HANDLEY_ | 5 | NORTH | YES | 217.5 | 150 | 435 | 0.061589 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 26.7912 | 435 | 0.14704 | 63.9605
1889 | DECRDOVA | MB | NORTH | YES | 0 | 255 | 770 | 0.061706 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.14715 | 0
1643 | SLSTR1PP | 1 | NORTH | YES | 6 | 0 | 60 | 0.062279 | north | 6 | Y | N | Ynorth | Nnorth | 1 | 3.7367 | 0 | 0.14773 | 0
332 | RWMILLER | 1 | NORTH | YES | 73 | 18.5 | 73 | 0.062373 | north | 12 | Y | Y | Ynorth | Ynorth | 1 | 4.5532 | 73 | 0.14782 | 10.7908
333 | RWMILLER | 2 | NORTH | YES | 119 | 37 | 119 | 0.062373 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 7.4224 | 119 | 0.14782 | 17.5905
334 | RWMILLER | 3 | NORTH | YES | 205 | 65 | 205 | 0.062373 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 12.7865 | 205 | 0.14782 | 30.303
335 | RWMILLER | 4 | NORTH | YES | 102 | 0 | 102 | 0.062373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 6.362 | 102 | 0.14782 | 15.0776
336 | RWMILLER | 5 | NORTH | YES | 96 | 0 | 96 | 0.062373 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 5.9878 | 96 | 0.14782 | 14.1907
1892 | DECRDOVA | A | NORTH | YES | 65 | 68 | 70 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.4097 | 70 | 0.14844 | 10.391
1893 | DECRDOVA | B | NORTH | YES | 65 | 70 | 69 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3467 | 69 | 0.14844 | 10.2425
1894 | DECRDOVA | C | NORTH | YES | 65 | 68 | 69 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.3467 | 69 | 0.14844 | 10.2425
1895 | DECRDOVA | D | NORTH | YES | 65 | 68 | 68 | 0.062996 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 4.2837 | 68 | 0.14844 | 10.0941
1941 | MDLTHELP | 1 | NORTH | YES | 216.4 | 74 | 216.4 | 0.063705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7858 | 216.4 | 0.14915 | 32.2764
1942 | MDLTHELP | 2 | NORTH | YES | 216.1 | 74 | 216.1 | 0.063705 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.7667 | 216.1 | 0.14915 | 32.2317
1937 | MDLTHELP | 5 | NORTH | YES | 224 | 74 | 224 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.3615 | 224 | 0.14956 | 33.5016
1938 | MDLTHELP | 6 | NORTH | YES | 226 | 74 | 226 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 14.4898 | 226 | 0.14956 | 33.8007
1943 | MDLTHELP | 3 | NORTH | YES | 212 | 74 | 212 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5922 | 212 | 0.14956 | 31.7069
1944 | MDLTHELP | 4 | NORTH | YES | 211 | 74 | 211 | 0.064114 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.5281 | 211 | 0.14956 | 31.5573
366 | JNSNCNTY | 1 | NORTH | YES | 168 | 20 | 168 | 0.065029 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 10.9249 | 168 | 0.15048 | 25.2799
367 | JNSNCNTY | 2 | NORTH | YES | 90 | 20 | 90 | 0.065029 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 5.8526 | 90 | 0.15048 | 13.5428
244 | WHITNYDM | 1 | NORTH | YES | 0 | 0 | 15 | 0.083659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2549 | 0 | 0.16911 | 0
245 | WHITNYDM | 2 | NORTH | YES | 0 | 0 | 15 | 0.083659 | north | 5 | N | N | Nnorth | Nnorth | 1 | 1.2549 | 0 | 0.16911 | 0
251 | BOSQUESW | 2 | NORTH | YES | 150 | 0 | 150 | 0.08846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 13.269 | 150 | 0.17391 | 26.086
253 | BOSQUESW | 2 | NORTH | YES | 80 | 0 | 80 | 0.08846 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 7.0768 | 80 | 0.17391 | 13.9125
238 | BOSQUESW | 1 | NORTH | YES | 255 | 0 | 255 | 0.091815 | north | 9 | Y | Y | Ynorth | Ynorth | 1 | 23.4128 | 255 | 0.17726 | 45.2017
239 | BOSQUESW | 1 | NORTH | YES | 149 | 0 | 149 | 0.091815 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 13.6804 | 149 | 0.17726 | 26.412
247 | BOSQUESW | 2 | NORTH | YES | 153 | 0 | 153 | 0.091815 | north | 13 | Y | Y | Ynorth | Ynorth | 1 | 14.0477 | 153 | 0.17726 | 27.121
3416 | LAKE_CRK | MB | NORTH | YES | 0 | 33 | 75 | 0.09236 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17781 | 0
3417 | LAKE_CRK | MB | NORTH | YES | 0 | 40 | 222 | 0.09236 | north | 11 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.17781 | 0
3403 | THOUSE_1 | MB | NORTH | YES | 0 | 200 | 537 | 0.096231 | north | 10 | Y | Y | mothballed | mothballed | 1 | 0 | 0 | 0.18168 | 0
3404 | THOUSE_2 | 2 | NORTH | YES | 787 | 250 | 787 | 0.096231 | north | 10 | Y | Y | Ynorth | Ynorth | 1 | 75.7338 | 787 | 0.18168 | 142.9803

## technology
Technology
source | sink | Description
0 | 0 | Not modeled
1 | 1 | Exceptions (ex. Units that can operate in more than one region @ 50%, voltage support units, DC ties)
2 | 2 | NOIE dispatch (Put in separate column. Commorder number in the spreadsheet is not 2. It is the number that best matches the unit)
3 | 3 | Nuclear max MW
4 | 4 | Coal (bituminous, sub-bituminous, lignite) max MW Existing units and future units that are expected to be built.
5 | 5 | Hydro (most recent information) Existing units and future units that are expected to be built.
6 | 6 | Other renewable - Wind @ 10%, solar max MW, methane max MW - less than 10 MW is modeled as negative load Existing units and future units that are expected to be built.
7 | 7 | Self serve - Existing units and future units that are expected to be built.
8 | 8 | Cogeneration - Existing units and future units that are expected to be built.
9 | 9 | Combined cycle - Existing units and future units that are expected to be built.
10 | 10 | Base load natural gas (steam through boiler) Existing units and future units that are expected to be built.
11 | 11 | Cycling natural gas (steam through boiler) Existing units and future units that are expected to be built.
12 | 12 | Peaking gas (steam through boiler) Existing units and future units that are expected to be built.
13 | 13 | Combustion turbines (single cycle). Existing units and future units that are expected to be built.
14 | 14 | Diesel generator
15 | 15 | Unknown