| OGRR Number | 223 | OGRR Title | Real Time Production Potential |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | October 15, 2009 |  |  |
| Operating Guide Section Requiring Revision |  | Attachment 8A, ERCOT Data Sets |  |  |
| Proposed Effective Date |  | December 1, 2009 |  |  |
| Priority and Rank Assigned |  | Not applicable. |  |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) establishes a requirement for Wind-powered Generation Resources (WGRs) to telemeter a Real Time signal indicating the Real Time Production Potential (RTPP) which will be a function of wind and turbine availability at the time. |  |  |
| Overall Market Benefit |  | Increase wind generation production by providing more complete information to ERCOT. |  |  |
| Overall Market Impact |  | Increased costs for wind generators to provide new data and telemetry. |  |  |
| Consumer Impact |  | Some reduced costs. |  |  |
| Procedural History |  | - On 4/17/09, OGRR223 was posted. - On 5/19/09, WMS comments were posted. - On 5/20/09, the Operations Working Group (OWG) considered OGRR223. - On 6/15/09, Qualified Scheduling Entity (QSE) Managers Working Group (QMWG) comments were posted. - On 6/17/09, OWG again considered OGRR223. - On 7/22/09, a second set of WMS comments were posted. - On 7/27/09, OWG again considered OGRR223. - On 8/17/09, the CEO Revision Request Review for OGRR223 was posted. - On 8/19/09, OWG again considered OGRR223. - On 8/20/09, ERCOT comments were posted. - On 8/31/09, a revised CEO Revision Request Review for OGRR223 was posted. - On 9/2/09, an Impact Analysis for OGRR223 was posted. - On 9/15/09, OWG again considered OGRR223. - On 10/15/09, ROS considered OGRR223. |  |  |
| OWG Decision |  | On 5/20/09, OWG was in consensus to table OGRR223 for one month. On 6/17/09, OWG was in consensus to table OGRR223 for one month. On 7/27/09, OWG was in consensus to recommend approval of OGRR223 as submitted. On 8/19/09, OWG was in consensus to table OGRR223 for one month. On 9/15/09, OWG was in consensus to forward the 8/19/09 OWG Recommendation Report and Impact Analysis to ROS. |  |  |
| Summary of OWG Discussion |  | On 5/20/09, it was noted that WMS requested OGRR223 be tabled to allow for the QMWG to review data calculation and aggregation methods. On 6/17/09, there was discussion regarding the 6/15/09 QMWG comments and their request to have OWG table this OGRR to allow more time for study of the data. On 7/27/09, there was discussion regarding the status of the corresponding Protocol Revision Request (PRR) 811, Real Time Production Potential. It was noted that PRR811 was recommended for approval by PRS and that the PRR will return to PRS in August for the Impact Analysis review. It was stated that if the status of the PRR changes, the status of and recommendation for OGRR223 should be reconsidered. On 8/19/09, ERCOT Staff discussed the reasons for the delay in providing the Impact Analysis. ERCOT Staff stated that it had identified potential impacts associated with PRR811 and requested additional time pending the resolution of the language and potential impacts associated with PRR811, after which any necessary language changes could be made to the OGRR as well. On 9/15/09, ERCOT Staff stated that the associated PRR811 was recommended for approval at the August PRS meeting. |  |  |
| ROS Decision |  | On 10/15/09, ROS unanimously voted to recommend approval of OGRR223 as recommended by the OWG in the 9/15/09 OWG Recommendation Report. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 10/15/09, there was no discussion. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | Software and telemetry capital cost. | $100,000 to $200,000 per WGR. |
|  | 2 | Additional data analysis and management costs. |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Provide forecast model tuning data |  |
|  | 2 | Provide ERCOT more visibility to system conditions. |  |
|  | 3 | Provide a basis for WGR provision of Ancillary Services. |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| WMS 051909 | Recommended that OGRR223 be tabled to allow the QMWG to review data regarding RTPP and data calculation and aggregation methods. |
| QMWG 061509 | Requested that OGRR223 be tabled to allow more time for review of the data. |
| WMS 072209 | Endorsed OGRR223 as submitted. |
| ERCOT 082009 | Deferred filing of Impact Analysis for OGRR223 until a final resolution of PRR811 has been made. |

| Original Sponsor |  |
| --- | --- |
| Name | Walter Reid |
| Company | Wind Coalition |
| Market Segment | Not applicable |

Proposed Guide Language Revision

## Attachment 8A:	ERCOT Data Sets

For any required data, the following table describes how the data is to be provided to ERCOT.

| ACTION | DATA QUANTITY | PURPOSE | SUPPLIED BY | RECEIVED BY | FREQUENCY | MODE OF COMM. | FORMAT | PROTOCOLS REFERENCE / COMMENTS |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| DAY-AHEAD SCHEDULING PROCESS |  |  |  |  |  |  |  |  |
| Extend Day-Ahead Scheduling Process | Notification to extend Day-Ahead Scheduling Process to Two-Days-Ahead | Emergency Notification | ERCOT | QSE | Demand | API | XML | Protocol Section 4.4.19, Decision to Extend Day-Ahead Scheduling Process to Two-Day-Ahead Scheduling Process |
| Day Ahead Notification | Transmission Outages | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocol Section 4.4.2, Posting of Forecasted ERCOT System Conditions |
|  | Total Transmission Capacity | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocol Section 4.4.2, Posting of Forecasted ERCOT System Conditions |
|  | Weather assumptions used by ERCOT to forecast system conditions | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocol Section 4.4.2, Posting of Forecasted ERCOT System Conditions |
| Day-Ahead Notification | Ancillary Services (AS) Plan | Day-Ahead Planning | ERCOT | QSE | Daily before 0600 | API | XML | Protocol Section 4.4.3, Notification to the Market of ERCOT's Day Ahead Ancillary Services Plan |
|  | Ancillary Service Obligations | Day-Ahead Planning | ERCOT | QSE | Daily by 0600 | API | XML | Protocol Section 4.4.4, Notification to QSEs of Ancillary Service Obligations |
|  | Mandatory Balancing Energy Service Down Bid Percentage requirements | Day-Ahead Planning | ERCOT | QSE | Daily by 0600 | API | XML | Protocol Section 4.4.5, Notification to QSEs of Mandatory Balancing Energy Service Down Bid Percentage Requirements |
|  | Transmission and Distribution Loss Estimates | Day-Ahead Planning | ERCOT | QSE | Daily by 0600 | API | XML | Protocol Section 4.4.6, Notification to QSEs of Transmission Loss Factors and Distribution Loss Factors |
|  | Update of Forecasted System Conditions (total forecast system load and load forecasts in each congestion Zone) | Day-Ahead Planning | ERCOT | QSE | Daily @ 0600 | API | XML | Protocol Section 4.4.7, Update of Forecasted ERCOT System Conditions |
| QSEs Submit Balanced Schedules of Obligations and Supply | Balanced Schedules | CSC Congestion and Capacity Insufficiency | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocol Section 4.4.8, Submittal of Day-Ahead Schedules and Ancillary Services Schedules, & Protocol Section 4.4.10, Submittal of Updated Balanced Energy Schedules. |
| Self-Arranged Ancillary Services | Self Provided Regulation Up | AS (Rolled up from REP to QSE) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocol Section 4.4.8, Submittal of Day-Ahead Schedules and Ancillary Services Schedules, & Protocol Section 4.4.10, Submittal of Updated Balanced Energy Schedules. |
|  | Self Provided Regulation Down | AS (Rolled up from REP to QSE) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocol Section 4.4.8, Submittal of Day-Ahead Schedules and Ancillary Services Schedules, & Protocol Section 4.4.10, Submittal of Updated Balanced Energy Schedules. |
|  | Self Provided Responsive Reserve | AS (By Portfolio) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocol Section 4.4.8, Submittal of Day-Ahead Schedules and Ancillary Services Schedules, & Protocol Section 4.4.10, Submittal of Updated Balanced Energy Schedules. |
|  | Self Provided Non-Spinning Reserve | AS (By Portfolio, By Zone) | QSE | ERCOT | Daily before 1100, @ 1300, then as needed | API | XML | Protocol Section 4.4.8, Submittal of Day-Ahead Schedules and Ancillary Services Schedules, & Protocol Section 4.4.10, Submittal of Updated Balanced Energy Schedules. |
| Validate Schedules and Bids | Notification of invalid or mismatched schedules | Validate Schedules | ERCOT | QSE | Daily @ 1100 & 1300 | API | XML | Protocol Section 4.4.12, ERCOT Validation of QSE Day-Ahead Schedules and Bids |
|  | Corrected Schedules | Submit corrected information | QSE | ERCOT | Daily @ 1115 & 1315 | API | XML | Protocol Section 4.4.12, ERCOT Validation of QSE Day-Ahead Schedules and Bids |
|  | Notification of CSC Congestion and/or Capacity Insufficiency | Update Schedules | ERCOT | QSE | Daily by 1115 | API | XML | Protocol Section 4.4.9, ERCOT Notification of CSC Congestion and/or Capacity Insufficiency Based on 1100 Balanced Schedules |
| Procure Ancillary Services | AS Bids to ERCOT | Ancillary Services Market | QSE | ERCOT | Daily by 1300 | API | XML | Protocol Section 4.4.11, Ancillary Services Bid Submittal |
|  | Purchase Regulation Up | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocol Section 4.4.13, ERCOT Day Ahead Ancillary Services Procurement Process |
|  | Purchase Regulation Down | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocol Section 4.4.13, ERCOT Day Ahead Ancillary Services Procurement Process |
|  | Purchase Responsive Reserves | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocol Section 4.4.13, ERCOT Day Ahead Ancillary Services Procurement Process |
|  | Purchase Non-Spinning Reserves | Complete Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily by 1330 | API | XML | Protocol Section 4.4.13, ERCOT Day Ahead Ancillary Services Procurement Process |
|  | Ancillary Services Schedules | Notification of Selected Ancillary Services Bids | ERCOT | QSE | Daily by 1330 | API | XML | Protocol Section 4.4.14, ERCOT Notification of Selected Ancillary Services Bids |
|  | Publish Day-Ahead MCPs for Capacity (MCPCs) for each Day-Ahead Ancillary Service | Complete ERCOT's Day-Ahead Ancillary Services Plan | ERCOT | QSE | Daily @ 1330 | API | XML | Protocol Section 4.4.13, ERCOT Day Ahead Ancillary Services Procurement Process |
|  | Final Ancillary Services Schedules | Updated Day Ahead Ancillary Services Schedule | QSE | ERCOT | Daily @ 1500 | API | XML | Protocol Section 4.4.14, ERCOT Notification of Selected Ancillary Services Bids |
| QSE Present Resource Plan | Unit Availability Status | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocol Section 4.4.15, QSE Resource Plans |
|  | Unit Planned Net Hourly Generation MW | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocol Section 4.4.15, QSE Resource Plans |
|  | Unit Planned High Net Hourly Operating Limit MW | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 16000, then as needed | API | XML | Protocol Section 4.4.15, QSE Resource Plans |
|  | Unit Planned Low Net Hourly Operating Limit MW | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocol Section 4.4.15, QSE Resource Plans |
|  | Load acting as a Resource | Generation Planning, AS Verification | QSE | ERCOT | Daily @ 1600, then as needed | API | XML | Protocol Section 4.4.15, QSE Resource Plans |
|  | Notification to QSE for insufficient resources | Generation Planning, AS Verification | ERCOT | QSE | Daily by 1600 | API | XML | Protocol Section 4.1.15, QSE Resource Plans |
| Procure Replacement Reserve Service | Unit-Specific Replacement Reserve Service (RPRS) Bids | QSEs may submit Replacement Reserve Service (RPRS) Bids | QSE | ERCOT | Daily by 1600, then as needed | API | XML | Protocol Section 4.4.16, ERCOT Receipt of Replacement Reserve Service Bids |
|  | Resource Specific Premiums | QSEs may submit hourly Resource specific premiums | QSE | ERCOT | Daily by 1430, then as needed | API | XML | Protocol Section 4.5.3, ERCOT Receipt of Resource Specific Premiums for Operational Congestion Management |
|  | Procurement of Replacement Reserve | ERCOT purchase RPRS | ERCOT | QSE | Daily by 1800 | API | XML | Protocol Section 4.4.17, ERCOT Procurement of Replacement Reserve Service As Needed |
|  | Adjustments to schedules of Reliability Must-Run (RMR) resources | Adjustments to the QSE's schedules | ERCOT | QSE | Demand | API | XML | Protocol Section 4.5.11, Scheduling Requirements for RMR Units and Black Start Resources |
| ADJUSTMENT PERIOD |  |  |  |  |  |  |  |  |
|  |  | QSE's can make schedule adjustments and ERCOT can request additional bids. |  |  | Time T is the start of the Operating Period |  |  | The Adjustment Period (AP) begins following the close of the Day-Ahead market and continues until one (1) hour prior to the beginning of the Operating Hour. |
| Adjustment Period Schedule Changes | Submit or change Energy Schedule and Ancillary Services Schedules | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocol Section 4.5.1, Receipt of Adjustment Period Schedule Changes |
|  | Submit, change, or remove Balancing Energy Service Up and Down Bids | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocol Section 4.5.1, Receipt of Adjustment Period Schedule Changes |
|  | Submit, change, or remove RPRS Bids | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocol Section 4.5.1, Receipt of Adjustment Period Schedule Changes |
|  | Require mandatory Balancing Energy Service Down Bid Curves | Adjustment Period Scheduling Process | ERCOT | QSE | T minus 60 minutes | API | XML | Protocol Section 4.5.2, Receipt of QSE's Balancing Energy Bid Curves |
|  | Submit Balancing Energy Service Up and Down Bid Curves | Adjustment Period Scheduling Process | QSE | ERCOT | T minus 60 minutes | API | XML | Protocol Section 4.5.2, Receipt of QSE's Balancing Energy Bid Curves |
|  | Announce need to procure RPRS | Procure Submitted Bids | ERCOT | QSE | T minus 60 minutes | API | XML | Protocol Section 4.5.6, ERCOT Notice of Need to Procure Replacement Reserve Service Resources |
|  | Announce need to procure additional Ancillary Services | Procure Submitted Bids | ERCOT | QSE | T minus 60 minutes | API | XML | Protocol Section 4.5.8, ERCOT Notice of Need to Procure Additional Ancillary Services |
|  | QSE Update their Resource Plan | Update prior to close of the Adjustment Period | QSE | ERCOT | T minus 60 minutes | API | XML | Protocol Section 4.5.10, Updated Resource Plans |
|  | QSE Update their Balanced Schedules | Adjustment Period Scheduling Process | QSE | ERCOT | T | API | XML | Protocol Section 4.5.6, ERCOT Notice of Need to Procure Replacement Reserve Service Resources & Protocol Section 4.5.8, ERCOT Notice of Need to Procure Additional Ancillary Services |
|  | QSE Resubmit Corrected Balanced Schedule | Adjustment Period Scheduling Process | QSE | ERCOT | T plus 15 minutes | API | XML | Protocol Section 4.5.6, ERCOT Notice of Need to Procure Replacement Reserve Service Resources & Protocol Section 4.5.8, ERCOT Notice of Need to Procure Additional Ancillary Services |
|  | Procure RPRS | ERCOT purchase RPRS | ERCOT | QSE | T plus 30 minutes | API | XML | Protocol Section 4.5.6, ERCOT Notice of Need to Procure Replacement Reserve Service Resources |
|  | Procure additional Ancillary Services | ERCOT purchase additional ancillary service | ERCOT | QSE | T plus 30 minutes | API | XML | Protocol Section 4.5.8,ERCOT Notice of Need to Procure Additional Ancillary Services |
| OPERATING PERIOD |  |  |  |  |  |  |  |  |
|  |  |  |  |  |  |  |  | DNP 3.0 protocol will be used for new ports to RTUs or SCADA systems. |
| FCS Inputs | Frequency | Real-Time Monitoring and Control | ERCOT/QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocol Section 6.10.5, QSE Real Power Performance Criteria |
| Unit Monitoring | Generating Unit MW | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision Net Generation is preferred. If gross MW is supplied, aux load should also be provided. |
|  | Generating Unit Mvar | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU /ICCP | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision Net Generation is preferred. If gross MVar is supplied, aux load should also be provided. |
|  | Private Network Net Interchange to ERCOT | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 2 Sec | RTU | DNP 3.0 | For private networks, the net interchange shall be provided along with gross MW and MVar per generating unit. |
|  | Private Network Net Interchange High Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | For private networks, the high operating limit will reflect the maximum generation available at the point of interconnection to ERCOT. |
|  | Private Network Net Interchange Low Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | For private networks, the low operating limit will reflect the minimum generation available at the point of interconnection to ERCOT. |
| Unit Monitoring | Wind-powered Generation Resource (WGR) estimated Real Time Production Potential (RTPP) | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 Sec | ICCP |  | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit Breaker Status | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit High Operating Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Generating Unit Low Operating Limit | Real-Time Monitoring & Security Analysis | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
| NOTE: Operating Period data from QSE units can be made available to the PGCs host TDSP on request. |  |  |  |  |  |  |  |  |
|  | Load used as a Resource MW | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Load Resource Breaker Status | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Load Resource (providing Responsive Reserve) High-Set Underfrequency Relay Status | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | QSE Frequency Bias | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocols Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision |
|  | Dynamic Resource Power Schedules | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocol Section 4.9, Dynamic Schedules, & Protocol Section 6.10.4.4, Schedule Control Error |
|  | SCE | Real-Time Monitoring and Control (control only for regulation providers) | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Feedback for QSE regulation calculation. Protocol Section 6.10.5, QSE Real Power Performance Criteria |
|  | Regulation Feedback (loop-back) | Real-Time Monitoring | QSE | ERCOT | 2 sec | RTU | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision, & Protocol Section 6.7.2(8), Deployment of Regulation Service - Feedback the amount of RGS power (MW) being provided each control cycle |
|  | Responsive Reserve Availability MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Responsive Reserve Deployment. Protocols Section 6.7.3 (6), Deployment of Responsive Reserve Service |
|  | Responsive Reserve Deployment MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Responsive Reserve Deployment. Protocols Section 6.7.3 (6), Deployment of Responsive Reserve Service |
|  | Non-Spinning Reserve Availability MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Non-Spinning Reserve Deployment. Protocols Section 6.7.4 (7), Deployment of Non-Spinning Reserve Service |
|  | Non-Spinning Reserve Deployment MW | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Feedback to Non-Spinning Reserve Deployment. Protocols Section 6.7.4 (7), Deployment of Non-Spinning Reserve Service |
| Deploy Ancillary Services | Instructed Regulation Up / Down MW | FCS Instruction | ERCOT | QSE | 4 sec | RTU | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision, & Protocol Section 6.7.2(1), Deployment of Regulation Service |
|  | Instructed Responsive Reserve MW | FCS Instruction | ERCOT | QSE | 4 sec | RTU | DNP 3.0 | Protocol Section 6.5.1.1, Requirement for Operating Period Data for System Reliability and Ancillary Service Provision, & Protocol Section 6.7.3(1), Deployment of Responsive Reserve Service |
|  | SCE | Performance Monitoring | ERCOT | QSE | 10 sec | RTU | DNP 3.0 | SCE Comparison for real-time monitoring and analysis by the ERCOT and QSE. Protocol Section 6.10.4.4, Schedule Control Error |
|  | Governor Response | Monitoring | ERCOT | QSE | 10 sec | RTU | DNP 3.0 | ERCOT calculated governor response from QSE frequency bias. Protocol Section 6.10.4.4, Schedule Control Error |
|  | Generating Unit Governor Response | Real-Time Monitoring | ERCOT | QSE | 10 sec. | RTU | DNP 3.0 | Protocol Section 6.5.1.1 Requirements for Operating Period Data for System Reliability and Ancillary Service Provision. |
| FCS Control Instructions | Instructed Non-Spinning Reserve MW | Instruction | ERCOT | QSE | Every 15 minutes | API | XML | Protocol Section 6.7.4(6), Deployment of Non-Spinning Reserve Service |
|  | Instructed Balancing Energy MW (Up / Down) | Instruction | ERCOT | QSE | Every 15 minutes with 10 minutes notice | API | XML | Protocol Section 6.5.2, Balancing Energy Service, & Protocol Section 6.7.1.1(8), Creation of the Balancing Energy Bid Stack. |
|  | Unit Automatic Voltage Regulator Status | Real Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 |  |
|  | Unit High Side Bus Voltage kV | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU/ ICCP | DNP 3.0 | Protocol Section 6.5.7, Voltage Support Service, May be supplied by the TDSP. Low Side with appropriate transformer model may be substituted. |
|  | Bus Voltage at Private Network connection to ERCOT | Real-Time Monitoring | QSE | ERCOT | 10 sec | RTU | DNP 3.0 | This voltage may be supplied by the TDSP. |
| Reliability Instructions | Instructed Replacement Reserve | Instruction | ERCOT | QSE | As needed | API | XML | Protocol Section 6.5.6, Replacement Reserve Service |
|  | Instructed Voltage Support | Instruction | ERCOT | QSE | As needed | API | XML | Protocol Section 6.5.7, Voltage Support Service |
|  | Instructed Black Start | Instruction | ERCOT | QSE | As needed | API | XML | Protocol Section 6.5.8, Black Start Service |
|  | Instructed Reliability Must-Run | Instruction | ERCOT | QSE | As needed | API | XML | Protocols Section 6.5.9, Reliability Must-Run Service |
|  | Instructed Out-of-Merit Capacity | Instruction | ERCOT | QSE | As needed | API | XML | Protocol Section 6.5.10, Out-of-Merit Capacity and Out-of-Merit Energy Services |
|  | Instructed Out-of-Merit Energy | Instruction | ERCOT | QSE | As needed | API | XML | Protocol Section 6.5.10, Out-of-Merit Capacity and Out-of-Merit Energy Services |
| Security Analysis |  |  |  |  |  |  |  |  |
| Generation |  |  |  |  |  |  |  | Generating data is provided by QSEs as defined above under Operating Period Data |
| Bus |  |  |  |  |  |  |  |  |
|  | Bus Voltage kV | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
|  | Bus Frequency Hz | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
| Transformer |  |  |  |  |  |  |  |  |
|  | Transformer Flow MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is into the transformer |
|  | Transformer Flow Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is into the transformer |
|  | LTC Tap Position | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
|  | Transformer Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the computer(s) have a Network Topology Processor |
| Line |  |  |  |  |  |  |  | Circuit Breaker data may be used instead of line data. |
|  | Line Flow MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | Line Flow Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | Circuit Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the computer(s) have a Network Topology Processor |
| Shunt |  |  |  |  |  |  |  |  |
|  | Reactive Support from Shunt Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive for supplying VAR Negative for absorbing VAR |
|  | Bank Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the computer(s) have a Network Topology Processor |
| Circuit Breaker |  |  |  |  |  |  |  | Includes: Circuit Breaker (CB), Line Switch (LS), and Disconnect Switch (DCS) (where applicable) Line data may be used instead of circuit breaker data. |
|  | CB MW flow | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is from bus section to equipment (optional) |
|  | CB Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is from bus section to equipment (optional) |
|  | Switch Position | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 |  |
| Load |  |  |  |  |  |  |  | Load metering is preferred from the high side of the transformation point of the substation distribution transformer. |
|  | Load in MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Negative for Load MW |
|  | Load in Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Negative for Load Mvar |
| DC Injection |  |  |  |  |  |  |  |  |
|  | DC Injection in MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | DC Injection in Mvar | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Positive flow is out of the station |
|  | DC Tie Status | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP | Blocks 1&2 | Used if the Computer(s) have a Network Topology Processor |
| Weather Zone Tie Lines | Line Flow MW | Real-Time Monitoring | TDSP | ERCOT | 10 sec | ICCP DNP 3.0 | Blocks 1&2 | TDSP’s responsible for supplying weather zone tie line data must provide a redudant path from their normal ICCP link. This second path may be a second ICCP association to ERCOT or an RTU or other device using DNP 3.0 protocol. |

NOTE:	Real-Time data for Security Analysis can be provided to TDSPs on request.

Private Network refers to generators with self-serve private load behind a single meter at the point of injection into the ERCOT grid.

LEGEND:

Supplied by/Received by

ERCOT - ERCOT Independent System Operator

QSE - Qualified Scheduling Entity

TDSP - Transmission, Distribution Service Provider

PGC - Power Generating Company

Mode of Communication

Web Portal - Online application available to market participants via the World Wide Web

TCH - Transaction Clearinghouse.  The mechanism used to send/receive EDI transactions

API - Programmatic API. A message protocol used to automate data exchange between ERCOT and market participants

ICCP - Inter-Control Center Communication Protocol.  A standard protocol used to automate data exchange real-time control information between the ERCOT and participants

RTU - Remote Terminal Unit. Used to gather real-time control/monitoring information.

Format

EDI - Electronic Data Exchange format. EDI formats are specified by the Texas SET working group and are based on standard EDI transaction protocols.

XML - eXtensible Markup Language.  XML is a self-describing meta language used to facilitate the exchange of data. XML will format requests and receive replies using the API.

CSV - Comma Separated Values.  A generic file format where elements of data are separated by commas within a file.

Office Document - One of the common Microsoft Office file formats such as MS Word or MS Excel.