| PRR Number | 833 | PRR Title | Primary Frequency Response Requirement from Existing WGRs |
| --- | --- | --- | --- |
| Date |  | October 19, 2009 |  |
| Submitter’s Information |  |  |  |
| Name |  | Ken Donohoo on behalf of the Reliability and Operations Subcommittee (ROS) |  |
| E-mail Address |  | kdonoho1@oncor.com |  |
| Company |  | Oncor |  |
| Phone Number |  | 214-743-6823 |  |
| Cell Number |  |  |  |
| Market Segment |  | Investor Owned Utility (IOU) |  |

Comments

At its October 15, 2009, ROS voted to endorse Protocol Revision Request (PRR) 833 as submitted.

There were two opposing votes from the Independent Generator and Independent Power Marketer (IPM) Market Segments.  All Market Segments were present for the vote.

| Overall Market Benefit |  |
| --- | --- |
| Overall Market Impact |  |
| Consumer Impact |  |

Revised Proposed Protocol Language

- 5.9.1.3		Wind-powered Generation Resource (WGR) Primary Frequency Response

Wind-powered Generation Resources (WGRs) with Generation Interconnect Agreements signed after January 1, 2010 shall provide Primary Frequency Response to frequency deviations from 60.000 Hz.  The WGR automatic control system design shall have an adjustable dead band that can be set as specified in the ERCOT Operating Guides.  The Primary Frequency Response shall be similar to the droop characteristic of five-percent (5%) used by conventional generators.  For WGRs with Generation Interconnect Agreements executed prior to January 1, 2010, those not already equipped with Primary Frequency Response shall by December 1, 2011 acquire that capability.  Those WGRs that cannot technically be retrofitted with Primary Frequency Response capability shall submit an attestation to ERCOT by [three months after effective date of this PRR], explaining the technical infeasibility.  At ERCOT’s sole discretion, those WGRs for which Primary Frequency Response is technically infeasible may be granted a permanent exemption from the requirement.  ERCOT shall make a determination within one hundred eighty (180) Business Days.  If ERCOT does not grant an exemption, the WGR shall acquire the capability to provide Primary Frequency Response within twenty-four (24) months of being notified of that determination.