## Start
1. Using the Spreadsheet to Calculate/Estimate Distribution Loss Factors
This spreadsheet calculates distribution loss factors (DLFs) for all Distribution Service Providers (DSPs) at various levels of ERCOT system load. From the "Inputs - Single DSP View" Tab, the user will select the DSP-DLF code and ERCOT load level of interest and the spreadsheet will calculate the resulting distribution loss factor. The graph displays the DSP loss factors at various ERCOT load levels as well as the level specified. The "Inputs - Multiple DSP View" tab operates similar to the "Inputs - Single DSP View" tab and displays graphically all DSPs DLF curves.
2. Examining the Calculations
This spreadsheet calculates the distribution loss factors for a selected TDSP based on the following formula:
SILFi = ADLF * [K + (1 - K) * (SIELi/AAL)]
Where: i = Interval
SILF = Settlement Interval Distribution Loss Factor
ADLF = Annual Distribution Loss Factor
K = constant representing the no load loss factor
SIEL = Settlement Interval ERCOT Load (ERCOT Day Ahead Forecasted MW Load divided by 4)
AAL = ERCOT Annual interval Average Load (ERCOT will use 8,062 MWhs for year 2002 calculations)

## Inputs - Single DSP View
DSP DLF Code to Graph
Input ERCOT Load |  | CPL A | 1 | CPL A
|  | CPL B | 2 | CPL B
ERCOT MW Load | 32868 | Reliant HL&P | 3 | Reliant HL&P
|  | TNMP A | 4 | TNMP A | 14 | WTU B
|  | TNMP B | 5 | TNMP B | 14 | WTU B
DLF for DSP Selected to Graph |  | TNMP C | 6 | TNMP C
|  | TNMP D | 7 | TNMP D
WTU B | 1.15% | TNMP E | 8 | TNMP E
|  | TXU A | 9 | TXU A
|  | TXU B | 10 | TXU B
All DSP Distribution Loss Factors |  | TXU SESCO A | 11 | TXU SESCO A
|  | TXU SESCO B | 12 | TXU SESCO B
CPL A | 6.248% | WTU A | 13 | WTU A
CPL B | 2.367% | WTU B | 14 | WTU B
Reliant HL&P D | 3.412% | Sharyland | 15 | Sharyland
TNMP A | 7.953%
TNMP B | 4.521%
TNMP C | 3.347%
TNMP D | 3.735%
TNMP E | 4.242%
TXU A | 3.908%
TXU B | 1.564%
TXU SESCO A | 3.908%
TXU SESCO B | 1.564%
WTU A | 6.695%
WTU B | 1.15%
Sharyland | 11.02%

## Inputs - Multiple DSP View
Select DSP
Input ERCOT Load |  | CPL A | 1 | DSP: CPL A
|  | CPL B | 2 | DSP: CPL B
ERCOT MW Load | 50000 | Reliant HL&P | 3 | DSP: Reliant HL&P
|  | TNMP A | 4 | DSP: TNMP A | 1 | DSP: Sharyland
|  | TNMP B | 5 | DSP: TNMP B | 1 | DSP: CPL A
DLF for DSP Selected |  | TNMP C | 6 | DSP: TNMP C
|  | TNMP D | 7 | DSP: TNMP D
DSP: CPL A | 5.608% | TNMP E | 8 | DSP: TNMP E
|  | TXU A | 9 | DSP: TXU A
|  | TXU B | 10 | DSP: TXU B
All DSP Distribution Loss Factors |  | TXU SESCO A | 11 | DSP: TXU SESCO A
|  | TXU SESCO B | 12 | DSP: TXU SESCO B
CPL A | 5.608% | WTU A | 13 | DSP: WTU A
CPL B | 2.396% | WTU B | 14 | DSP: WTU B
Reliant HL&P | 3.721% | SharyLand | 15 | DSP: Sharyland
TNMP A | 10.81%
TNMP B | 5.923%
TNMP C | 4.372%
TNMP D | 4.995%
TNMP E | 5.676%
TXU A | 4.956%
TXU B | 2.235%
TXU SESCO A | 4.956%
TXU SESCO B | 2.235%
WTU A | 6.868%
WTU B | 1.124%
Sharyland | 15.26%

## TDSP and ERCOT Variables
ERCOT |  |  |  | DSP = | CPL | CPL | Reliant | TNMP | TNMP | TNMP | TNMP | TNMP | TXU | TXU | TXU SESCO | TXU SESCO | WTU | WTU | Sharyland
October 01, 2000 to Sept 30, 2001 |  |  |  | DLF Code = | A | B | D | A | B | C | D | E | A | B | A | B | A | B | A
Annual MWH | 282506011 |  |  | TDSP AAL (MWH) = | 394.2 | 76.1 | 1514 | 101.296 | 102.726 | 81.826 | 276.439 | 45.65 | 338 | 2240 | 26.617 | 4.563 | 122.1 | 87.07 | 0.4265
Interval Count | 35040 |  |  | K factor = | 1.1921 | 0.97714 | 0.829 | 0.3159 | 0.4094 | 0.4169 | 0.3577 | 0.3556 | 0.49 | 0.18 | 0.49 | 0.18 | 0.95139 | 1.043 | 0.2642
ERCOT AAL | 8062.3862 | MWhs |  | ADLF = | 6.272% | 2.366% | 3.401% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54% | 6.689% | 1.151% | 10.86%
| Hourly |  | Per Interval
| MW Load |  | MWHs
Example | 15000 |  | 3750 |  | 6.916% | 2.337% | 3.09% | 4.978% | 3.058% | 2.278% | 2.422% | 2.746% | 2.814% | 0.8646% | 2.814% | 0.8646% | 6.515% | 1.177% | 6.588%
Results: | 20000 |  | 5000 |  | 6.729% | 2.345% | 3.18% | 5.81% | 3.467% | 2.577% | 2.79% | 3.164% | 3.12% | 1.06% | 3.12% | 1.06% | 6.565% | 1.17% | 7.828%
| 25000 |  | 6250 |  | 6.542% | 2.354% | 3.27% | 6.643% | 3.877% | 2.876% | 3.157% | 3.583% | 3.426% | 1.256% | 3.426% | 1.256% | 6.616% | 1.162% | 9.067%
| 30000 |  | 7500 |  | 6.356% | 2.362% | 3.36% | 7.475% | 4.286% | 3.175% | 3.525% | 4.002% | 3.732% | 1.452% | 3.732% | 1.452% | 6.666% | 1.154% | 10.31%
at ERCOT AAL | 32249.5446 |  | 8062.3862 |  | 6.272% | 2.366% | 3.401% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54% | 6.689% | 1.151% | 10.86%
| 40000 |  | 10000 |  | 5.982% | 2.379% | 3.541% | 9.141% | 5.104% | 3.774% | 4.26% | 4.839% | 4.344% | 1.843% | 4.344% | 1.843% | 6.767% | 1.139% | 12.79%
| 45000 |  | 11250 |  | 5.795% | 2.387% | 3.631% | 9.973% | 5.514% | 4.073% | 4.627% | 5.258% | 4.65% | 2.039% | 4.65% | 2.039% | 6.817% | 1.131% | 14.02%
| 50000 |  | 12500 |  | 5.608% | 2.396% | 3.721% | 10.81% | 5.923% | 4.372% | 4.995% | 5.676% | 4.956% | 2.235% | 4.956% | 2.235% | 6.868% | 1.124% | 15.26%
| 55000 |  | 13750 |  | 5.422% | 2.404% | 3.811% | 11.64% | 6.332% | 4.672% | 5.362% | 6.095% | 5.262% | 2.431% | 5.262% | 2.431% | 6.918% | 1.116% | 16.5%
| 60000 |  | 15000 |  | 5.235% | 2.412% | 3.901% | 12.47% | 6.742% | 4.971% | 5.729% | 6.513% | 5.568% | 2.627% | 5.568% | 2.627% | 6.969% | 1.108% | 17.74%
| 65000 |  | 16250 |  | 5.048% | 2.421% | 3.992% | 13.3% | 7.151% | 5.27% | 6.097% | 6.932% | 5.874% | 2.822% | 5.874% | 2.822% | 7.019% | 1.101% | 18.98%
| 70000 |  | 17500 |  | 4.861% | 2.429% | 4.082% | 14.14% | 7.56% | 5.569% | 6.464% | 7.351% | 6.18% | 3.018% | 6.18% | 3.018% | 7.069% | 1.093% | 20.22%
| 75000 |  | 18750 |  | 4.675% | 2.437% | 4.172% | 14.97% | 7.97% | 5.869% | 6.832% | 7.769% | 6.486% | 3.214% | 6.486% | 3.214% | 7.12% | 1.085% | 21.46%

## Calculations for Graph (hidden)
ERCOT |  |  |  |  | DSP = | CPL | CPL | Reliant | TNMP | TNMP | TNMP | TNMP | TNMP | TXU | TXU | TXU SESCO | TXU SESCO | WTU | WTU | Sharyland
October 01, 2000 to Sept 30, 2001 |  |  |  |  | DLF Code = | A | B | D | A | B | C | D | E | A | B | A | B | A | B | A
Annual MWH | 282506011 |  |  |  | TDSP AAL (MWH) = | 394.2 | 76.1 | 1514 | 101.296 | 102.726 | 81.826 | 276.439 | 45.65 | 338 | 2240 | 26.617 | 4.563 | 122.1 | 87.07 | 0.4265
Interval Count | 35040 |  |  |  | K factor = | 1.1921 | 0.97714 | 0.829 | 0.3159 | 0.4094 | 0.4169 | 0.3577 | 0.3556 | 0.49 | 0.18 | 0.49 | 0.18 | 0.95139 | 1.043 | 0.2642
ERCOT AAL | 8062.3862 | MWhs |  |  | ADLF = | 6.272% | 2.366% | 3.401% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54% | 6.689% | 1.151% | 10.86%
[5 empty] | slope | -3.7351e-07 | 1.677e-08 | 1.8033e-07 | 1.6652e-06 | 8.1861e-07 | 5.9848e-07 | 7.3492e-07 | 8.3723e-07 | 6.1201e-07 | 3.9157e-07 | 6.1201e-07 | 3.9157e-07 | 1.0082e-07 | -1.5329e-08 | 2.4787e-06
[5 empty] | constant | 0.074761 | 0.023117 | 0.028194 | 0.024798 | 0.0183 | 0.013799 | 0.013199 | 0.0149 | 0.018963 | 0.002772 | 0.018963 | 0.002772 | 0.063637 | 0.012004 | 0.028703
[5 empty] | 1.177% | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15
|  |  | Graph Min | 15000 | 1.177% | 6.916% | 2.337% | 3.09% | 4.978% | 3.058% | 2.278% | 2.422% | 2.746% | 2.814% | 0.8646% | 2.814% | 0.8646% | 6.515% | 1.177% | 6.588%
|  |  | Graph Max | 65000 | 1.101% | 5.048% | 2.421% | 3.992% | 13.3% | 7.151% | 5.27% | 6.097% | 6.932% | 5.874% | 2.822% | 5.874% | 2.822% | 7.019% | 1.101% | 18.98%
1.101%
|  |  | Inputs | 32868 | 1.15% | 6.248% | 2.367% | 3.412% | 7.953% | 4.521% | 3.347% | 3.735% | 4.242% | 3.908% | 1.564% | 3.908% | 1.564% | 6.695% | 1.15% | 11.02%
|  |  | Tab |  | 1.177%: 1.15%
| 50000 | 0% | Another | 50000 | 5.608% | 5.608% | 2.396% | 3.721% | 10.81% | 5.923% | 4.372% | 4.995% | 5.676% | 4.956% | 2.235% | 4.956% | 2.235% | 6.868% | 1.124% | 15.26%
| 50000 | 16% | View |  | 1.177%: 1.124%
| Hourly |  | Per Interval
| MW Load |  | MWHs
Example | 15000 |  | 3750 |  |  | 6.916% | 2.337% | 3.09% | 4.978% | 3.058% | 2.278% | 2.422% | 2.746% | 2.814% | 0.8646% | 2.814% | 0.8646% | 6.515% | 1.177% | 6.588%
Results: | 20000 |  | 5000 |  |  | 6.729% | 2.345% | 3.18% | 5.81% | 3.467% | 2.577% | 2.79% | 3.164% | 3.12% | 1.06% | 3.12% | 1.06% | 6.565% | 1.17% | 7.828%
| 25000 |  | 6250 |  |  | 6.542% | 2.354% | 3.27% | 6.643% | 3.877% | 2.876% | 3.157% | 3.583% | 3.426% | 1.256% | 3.426% | 1.256% | 6.616% | 1.162% | 9.067%
| 30000 |  | 7500 |  |  | 6.356% | 2.362% | 3.36% | 7.475% | 4.286% | 3.175% | 3.525% | 4.002% | 3.732% | 1.452% | 3.732% | 1.452% | 6.666% | 1.154% | 10.31%
at ERCOT AAL | 32249.5446 |  | 8062.3862 |  |  | 6.272% | 2.366% | 3.401% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54% | 6.689% | 1.151% | 10.86%
| 40000 |  | 10000 |  |  | 5.982% | 2.379% | 3.541% | 9.141% | 5.104% | 3.774% | 4.26% | 4.839% | 4.344% | 1.843% | 4.344% | 1.843% | 6.767% | 1.139% | 12.79%
| 45000 |  | 11250 |  |  | 5.795% | 2.387% | 3.631% | 9.973% | 5.514% | 4.073% | 4.627% | 5.258% | 4.65% | 2.039% | 4.65% | 2.039% | 6.817% | 1.131% | 14.02%
| 50000 |  | 12500 |  |  | 5.608% | 2.396% | 3.721% | 10.81% | 5.923% | 4.372% | 4.995% | 5.676% | 4.956% | 2.235% | 4.956% | 2.235% | 6.868% | 1.124% | 15.26%
| 55000 |  | 13750 |  |  | 5.422% | 2.404% | 3.811% | 11.64% | 6.332% | 4.672% | 5.362% | 6.095% | 5.262% | 2.431% | 5.262% | 2.431% | 6.918% | 1.116% | 16.5%
| 60000 |  | 15000 |  |  | 5.235% | 2.412% | 3.901% | 12.47% | 6.742% | 4.971% | 5.729% | 6.513% | 5.568% | 2.627% | 5.568% | 2.627% | 6.969% | 1.108% | 17.74%
| 65000 |  | 16250 |  |  | 5.048% | 2.421% | 3.992% | 13.3% | 7.151% | 5.27% | 6.097% | 6.932% | 5.874% | 2.822% | 5.874% | 2.822% | 7.019% | 1.101% | 18.98%
| 70000 |  | 17500 |  |  | 4.861% | 2.429% | 4.082% | 14.14% | 7.56% | 5.569% | 6.464% | 7.351% | 6.18% | 3.018% | 6.18% | 3.018% | 7.069% | 1.093% | 20.22%
| 75000 |  | 18750 |  |  | 4.675% | 2.437% | 4.172% | 14.97% | 7.97% | 5.869% | 6.832% | 7.769% | 6.486% | 3.214% | 6.486% | 3.214% | 7.12% | 1.085% | 21.46%