## Line Loss Summary
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Line Losses
ZONE | SERVICE AREA | VOLTAGE (kV) | LENGTH OF OH LINE (Miles) | LENGTH OF UG LINE (Miles) | TOTAL LENGTH OF LINE (Miles) | LOSS DATA SOURCE | LINE (1) LOSSES (kW) AT PEAK | AVERAGE (2) (3) ANNUAL HOURLY DEMAND LOSSES (kW) | AVERAGE ANNUAL ENERGY LOSSES (kWh)
ZONE 1 & 2 | Rural | 4.16 | 152.929 | 0.919 | 153.848 | AVG ZONE 1&2/Rural | 529.9353 | 240.8797 | 2110106.0966
ZONE 1 & 2 | Rural | 12.5 | 1177.923 | 34.117 | 1212.04 | AVG ZONE 1&2/Rural | 4174.9181 | 1897.6901 | 16623764.9711
ZONE 1 & 2 | Rural | 22 | 1535.685 | 19.462 | 1555.147 | AVG ZONE 1&2/Rural | 5356.7633 | 2434.8924 | 21329657.6214
ZONE 1 & 2 | Rural | 25 | 87.405 | 16.133 | 103.538 | AVG ZONE 1&2/Rural | 356.6406 | 162.1094 | 1420078.0317
ZONE 1 & 2 | Urban | 12.5 | 138.306 | 169.97 | 308.276 | MAX ZONE 1&2/Urban | 3006.523 | 1366.6014 | 11971428.1327
ZONE 1 & 2 | Urban | 25 | 25.059 | 33.168 | 58.227 | MAX ZONE 1&2/Urban | 567.8704 | 258.1229 | 2261156.7098
ZONE 6 | Rural | 12.5 | 730.373 | 48.261 | 778.634 | AVG ZONE 1&2/Rural | 2682.0346 | 1219.1066 | 10679374.125
ZONE 6 | Urban | 12.5 | 1100.267 | 258.453 | 1358.72 | AVG ZONE 6/Urban | 10907.7668 | 4958.0758 | 43432744.0786
ZONE 8 | Rural | 2.4 Delta | 10.92 | 0 | 10.92 | AVG ZONE 8/Rural | 13.8497 | 8.3938 | 73529.3942
ZONE 8 | Rural | 4.16 | 45.375 | 0.152 | 45.527 | AVG ZONE 8/Rural | 57.7414 | 34.9948 | 306554.2792
ZONE 8 | Rural | 12.5 | 788.454 | 2.99 | 791.444 | AVG ZONE 8/Rural | 1003.7796 | 608.3513 | 5329157.3114
ZONE 8 | Rural | 25 | 512.048 | 0 | 512.048 | AVG ZONE 8/Rural | 649.4248 | 393.5908 | 3447855.2405
ZONE 8 | Rural | 4.16 | 6.026 | 0 | 6.026 | AVG ZONE 8/Rural | 7.6427 | 4.6319 | 40575.836
ZONE 8 | Rural | 12.5 | 46.898 | 0.886 | 47.784 | AVG ZONE 8/Rural | 60.6039 | 36.7296 | 321751.7006
TOTALS |  |  | 6357.668 | 584.511 | 6942.179 |  | 29375.4944 | 13624.1705 | 119347733.529
Notes:
(1) Based on distribution circuit information provided by TNMP.
(2) Annual Interval Average Load Factor for Zones 1, 2 & 6 (Max-to-Avg Ratio) provided by TNMP = | [5 empty] | 2.2
(3) Annual Interval Average Load Factor for Zone 8 (Max-to-Avg Ratio) provided by TNMP = | [5 empty] | 1.65
(4) A "Rural" distribution model was not provided for Zone 6. AVG Zone 1&2/Rural was assumed.

## Line DB
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Line Losses
ZONE | SERVICE AREA | SUBSTATION NAME | CIRCUIT NUMBER | VOLTAGE (kV) | LINE LENGTH (Miles)
[5 empty] | OH | UG | TOTAL
Zone 1 & 2 | Rural | CLIFTON #2 | 4160 | 4.16 | 5.927 | 0.044 | 5.971
Zone 1 & 2 | Rural | CLIFTON #2 | 4165 | 4.16 | 6.22 | 0.119 | 6.339
Zone 1 & 2 | Rural | CLIFTON 1 4KV | 407 | 4.16 | 4.047 | 0.025 | 4.072
Zone 1 & 2 | Rural | CLIFTON 1 4KV | 405 | 4.16 | 2.165 | 0 | 2.165
Zone 1 & 2 | Rural | CLIFTON 1 4KV | 490 | 4.16 | 2.664 | 0 | 2.664
Zone 1 & 2 | Rural | GATESVILLE 1 | 422 | 4.16 | 2.92 | 0.031 | 2.951
Zone 1 & 2 | Rural | GATESVILLE 1 | 413 | 4.16 | 2.07 | 0 | 2.07
Zone 1 & 2 | Rural | GATESVILLE 1 | 419 | 4.16 | 4.942 | 0 | 4.942
Zone 1 & 2 | Rural | GATESVILLE 2 | 426 | 4.16 | 3.167 | 0.041 | 3.208
Zone 1 & 2 | Rural | GATESVILLE 2 | 429 | 4.16 | 4.336 | 0 | 4.336
Zone 1 & 2 | Rural | HICO CITY | 390 | 4.16 | 12.505 | 0 | 12.505
Zone 1 & 2 | Rural | HICO CITY | 395 | 4.16 | 16.703 | 0.122 | 16.825
Zone 1 & 2 | Rural | IREDELL | 330 | 4.16 | 4.778 | 0 | 4.778
Zone 1 & 2 | Rural | MERIDIAN | 680 | 4.16 | 7.787 | 0 | 7.787
Zone 1 & 2 | Rural | MERIDIAN | 690 | 4.16 | 6.998 | 0.057 | 7.055
Zone 1 & 2 | Rural | WHITNEY #1 | 460 | 4.16 | 1.094 | 0 | 1.094
Zone 1 & 2 | Rural | BOGATA | 416 | 4.16 | 4.95 | 0 | 4.95
Zone 1 & 2 | Rural | BOGATA | 464 | 4.16 | 4.18 | 0 | 4.18
Zone 1 & 2 | Rural | BOGATA | 412 | 4.16 | 4.17 | 0 | 4.17
Zone 1 & 2 | Rural | DETROIT | 479 | 4.16 | 4.17 | 0.17 | 4.34
Zone 1 & 2 | Rural | DETROIT | 474 | 4.16 | 1.46 | 0 | 1.46
Zone 1 & 2 | Rural | FRONTIER | 4236 | 4.16 | 10.24 | 0.31 | 10.55
Zone 1 & 2 | Rural | TRENTON | 4120 | 4.16 | 5.198 | 0 | 5.198
Zone 1 & 2 | Rural | SAINT JO | 401 | 4.16 | 10.286 | 0 | 10.286
Zone 1 & 2 | Rural | SAINT JO | 408 | 4.16 | 19.952 | 0 | 19.952
Zone 1 & 2 | Rural | LAKE WHITNEY | 12355 | 12.5 | 19.613 | 0 | 19.613
Zone 1 & 2 | Rural | LAKE WHITNEY | 1230 | 12.5 | 28.592 | 0.356 | 28.948
Zone 1 & 2 | Rural | LANE CHAPEL | 1260 | 12.5 | 58.049 | 0 | 58.049
Zone 1 & 2 | Rural | WALNUT SPRINGS | 1270 | 12.5 | 14.908 | 0 | 14.908
Zone 1 & 2 | Rural | BRYSON | 1230 | 12.5 | 51.321 | 0.009 | 51.33
Zone 1 & 2 | Rural | BRYSON | 1233 | 12.5 | 43.476 | 0 | 43.476
Zone 1 & 2 | Rural | GRAHAM | 12605 | 12.5 | 30.199 | 0.048 | 30.247
Zone 1 & 2 | Rural | GRAHAM | 1245 | 12.5 | 37.223 | 0 | 37.223
Zone 1 & 2 | Rural | OLNEY | 1690 | 12.5 | 2.603 | 0 | 2.603
Zone 1 & 2 | Rural | OLNEY | 1431 | 12.5 | 2.24 | 0 | 2.24
Zone 1 & 2 | Rural | OLNEY | 1685 | 12.5 | 58.057 | 0.594 | 58.651
Zone 1 & 2 | Rural | OLNEY SWCH STA | 1201 | 12.5 | 59.816 | 0.01 | 59.826
Zone 1 & 2 | Rural | OLNEY SWCH STA | 1202 | 12.5 | 10.873 | 0.06 | 10.933
Zone 1 & 2 | Rural | OLNEY SWCH STA | 1211 | 12.5 | 2.148 | 0.138 | 2.286
Zone 1 & 2 | Rural | OLNEY SWCH STA | 1218 | 12.5 | 2.547 | 0.089 | 2.636
Zone 1 & 2 | Rural | THURBER | 1447 | 12.5 | 64.553 | 0.482 | 65.035
Zone 1 & 2 | Rural | CRAWFORD | 1275 | 12.5 | 40.621 | 0.044 | 40.665
Zone 1 & 2 | Rural | MINTER | 12312 | 12.5 | 18.76 | 0.16 | 18.92
Zone 1 & 2 | Rural | MOBIL | 13932 | 12.5 | 1.52 | 0 | 1.52
Zone 1 & 2 | Rural | MOBIL | 12108 | 12.5 | 30.79 | 0 | 30.79
Zone 1 & 2 | Rural | TALCO CITY | 13403 | 12.5 | 30.79 | 0 | 30.79
Zone 1 & 2 | Rural | TALCO CITY | 13399 | 12.5 | 3.85 | 0 | 3.85
Zone 1 & 2 | Rural | TALCO WEST | 14558 | 12.5 | 0.715 | 12.5 | 13.215
Zone 1 & 2 | Rural | TALCO WEST | 14548 | 12.5 | 3.942 | 12.5 | 16.442
Zone 1 & 2 | Rural | LONE OAK | 13384 | 12.5 | 12.7 | 0.235 | 12.935
Zone 1 & 2 | Rural | LONE OAK | 13388 | 12.5 | 6.542 | 0 | 6.542
Zone 1 & 2 | Rural | TXU EMORY | 1201 | 12.5 | 65.387 | 0.374 | 65.761
Zone 1 & 2 | Rural | LEONARD | 12682 | 12.5 | 4.108 | 0.123 | 4.231
Zone 1 & 2 | Rural | LEONARD | 14631 | 12.5 | 3.959 | 0.146 | 4.105
Zone 1 & 2 | Rural | LEONARD | 12678 | 12.5 | 28.847 | 0.463 | 29.31
Zone 1 & 2 | Rural | LEONARD | 14635 | 12.5 | 25.732 | 0.792 | 26.524
Zone 1 & 2 | Rural | NOCONA | 13610 | 12.5 | 12.687 | 0.284 | 12.971
Zone 1 & 2 | Rural | NOCONA | 12490 | 12.5 | 32.297 | 0.329 | 32.626
Zone 1 & 2 | Rural | NOCONA | 13374 | 12.5 | 74.955 | 0.21 | 75.165
Zone 1 & 2 | Rural | NOCONA | 12486 | 12.5 | 10.171 | 0.05 | 10.221
Zone 1 & 2 | Rural | NOCONA | 13370 | 12.5 | 87.442 | 0.124 | 87.566
Zone 1 & 2 | Rural | PETROLIA | 12260 | 12.5 | 35.007 | 0.077 | 35.084
Zone 1 & 2 | Rural | PRINCETON | 12717 | 12.5 | 7.86 | 0.009 | 7.869
Zone 1 & 2 | Rural | PILOT POINT | 12119 | 12.5 | 4.857 | 0.101 | 4.958
Zone 1 & 2 | Rural | PILOT POINT | 12115 | 12.5 | 5.884 | 0.403 | 6.287
Zone 1 & 2 | Rural | WHITEWRIGHT | 13563 | 12.5 | 5.594 | 0.227 | 5.821
Zone 1 & 2 | Rural | WHITEWRIGHT | 12574 | 12.5 | 51.442 | 1.715 | 53.157
Zone 1 & 2 | Rural | WHITEWRIGHT | 12698 | 12.5 | 35.006 | 0.646 | 35.652
Zone 1 & 2 | Rural | WHITEWRIGHT | 12573 | 12.5 | 19.084 | 0.222 | 19.306
Zone 1 & 2 | Rural | WHITEWRIGHT | 12575 | 12.5 | 31.156 | 0.597 | 31.753
Zone 1 & 2 | Rural | CLIFTON #2 | 24370 | 22 | 11.967 | 0.101 | 12.068
Zone 1 & 2 | Rural | CLIFTON #2 | 23165 | 22 | 6.632 | 0.622 | 7.254
Zone 1 & 2 | Rural | CLIFTON 1 22KV | 22495 | 22 | 7.034 | 0.046 | 7.08
Zone 1 & 2 | Rural | CLIFTON 1 22KV | 22485 | 22 | 29.292 | 0.157 | 29.449
Zone 1 & 2 | Rural | CLIFTON 1 22KV | 22480 | 22 | 19.955 | 0 | 19.955
Zone 1 & 2 | Rural | HANDLEY | 22820 | 22 | 11.482 | 0.382 | 11.864
Zone 1 & 2 | Rural | HANDLEY | 22825 | 22 | 29.46 | 0 | 29.46
Zone 1 & 2 | Rural | GLEN ROSE | 22305 | 22 | 63.645 | 1.112 | 64.757
Zone 1 & 2 | Rural | GLEN ROSE | 22295 | 22 | 28.421 | 0.845 | 29.266
Zone 1 & 2 | Rural | GLEN ROSE | 23875 | 22 | 39.27 | 1.501 | 40.771
Zone 1 & 2 | Rural | GLEN ROSE | 22300 | 22 | 77.113 | 3.212 | 80.325
Zone 1 & 2 | Rural | CORYELL CO | 22155 | 22 | 17.397 | 0.97 | 18.367
Zone 1 & 2 | Rural | CORYELL CO | 22160 | 22 | 15.029 | 0 | 15.029
Zone 1 & 2 | Rural | CORYELL CO | 22175 | 22 | 1.739 | 0 | 1.739
Zone 1 & 2 | Rural | CORYELL CO | 22365 | 22 | 55.151 | 0.419 | 55.57
Zone 1 & 2 | Rural | GATESVILLE 2 | 23065 | 22 | 4.682 | 0 | 4.682
Zone 1 & 2 | Rural | GATESVILLE 2 | 22725 | 22 | 18.396 | 0.542 | 18.938
Zone 1 & 2 | Rural | PRISON | 24105 | 22 | 15.029 | 0 | 15.029
Zone 1 & 2 | Rural | HAMILTON CITY | 23825 | 22 | 2.645 | 0 | 2.645
Zone 1 & 2 | Rural | HAMILTON CITY | 22780 | 22 | 13.846 | 0.012 | 13.858
Zone 1 & 2 | Rural | HAMILTON CITY | 22785 | 22 | 5.168 | 0 | 5.168
Zone 1 & 2 | Rural | HAMILTON CITY | 23820 | 22 | 12.527 | 0.029 | 12.556
Zone 1 & 2 | Rural | HAMILTON | 24015 | 22 | 53.287 | 0.052 | 53.339
Zone 1 & 2 | Rural | HAMILTON | 2345 | 22 | 44.729 | 0.012 | 44.741
Zone 1 & 2 | Rural | HAMILTON | 2340 | 22 | 41.222 | 0.016 | 41.238
Zone 1 & 2 | Rural | MERIDIAN | 23210 | 22 | 86.259 | 0.306 | 86.565
Zone 1 & 2 | Rural | MERIDIAN | 23205 | 22 | 8.113 | 0 | 8.113
Zone 1 & 2 | Rural | WALNUT SPRINGS | 2200 | 22 | 22.56 | 0 | 22.56
Zone 1 & 2 | Rural | WALNUT SPRINGS | 2210 | 22 | 50.967 | 0 | 50.967
Zone 1 & 2 | Rural | WALNUT SPRINGS | 2215 | 22 | 21.498 | 0 | 21.498
Zone 1 & 2 | Rural | THURBER | 22890 | 22 | 28.606 | 0.359 | 28.965
Zone 1 & 2 | Rural | THURBER | 1490 | 22 | 71.404 | 0.414 | 71.818
Zone 1 & 2 | Rural | CRAWFORD | 2229 | 22 | 19.548 | 0 | 19.548
Zone 1 & 2 | Rural | CRAWFORD | 2230 | 22 | 0.701 | 0 | 0.701
Zone 1 & 2 | Rural | CRAWFORD | 23180 | 22 | 9.385 | 0.083 | 9.468
Zone 1 & 2 | Rural | VALLEY MILLS | 22565 | 22 | 17.489 | 0 | 17.489
Zone 1 & 2 | Rural | VALLEY MILLS | 22570 | 22 | 12.726 | 0.106 | 12.832
Zone 1 & 2 | Rural | VALLEY MILLS | 22575 | 22 | 19.548 | 0 | 19.548
Zone 1 & 2 | Rural | HILL CO | 22125 | 22 | 24.352 | 0.089 | 24.441
Zone 1 & 2 | Rural | HILL CO | 23340 | 22 | 58.149 | 0.045 | 58.194
Zone 1 & 2 | Rural | WHITNEY #1 | 22455 | 22 | 45.823 | 0.384 | 46.207
Zone 1 & 2 | Rural | WHITNEY #1 | 22450 | 22 | 52.054 | 0.17 | 52.224
Zone 1 & 2 | Rural | WHITNEY #1 | 22460 | 22 | 19.947 | 0.072 | 20.019
Zone 1 & 2 | Rural | EXXON | 22237 | 22 | 8.359 | 0 | 8.359
Zone 1 & 2 | Rural | RED RIVER | 2252 | 22 | 87.62 | 0.53 | 88.15
Zone 1 & 2 | Rural | RED RIVER | 2262 | 22 | 10.07 | 0.07 | 10.14
Zone 1 & 2 | Rural | RED RIVER | 2229 | 22 | 3.84 | 0 | 3.84
Zone 1 & 2 | Rural | TALCO CITY | 2262 | 22 | 9.967 | 0.079 | 10.046
Zone 1 & 2 | Rural | TXU POD DEPORT | 22164 | 22 | 97.86 | 1.56 | 99.42
Zone 1 & 2 | Rural | PETROLIA STEP-UP | 22495 | 22 | 26.037 | 1.01 | 27.047
Zone 1 & 2 | Rural | CLIMAX | 2270 | 22 | 50.92 | 1.475 | 52.395
Zone 1 & 2 | Rural | CLIMAX | 22110 | 22 | 16.818 | 1.25 | 18.068
Zone 1 & 2 | Rural | PRINCETON | 22 | 22 | 15.374 | 0.959 | 16.333
Zone 1 & 2 | Rural | BLUE RIDGE | 22700 | 22 | 14.573 | 0.471 | 15.044
Zone 1 & 2 | Rural | TALCO WEST | 13909 | 25 | 8.359 | 0 | 8.359
Zone 1 & 2 | Rural | KRUGERVILLE | 2604 | 25 | 57.135 | 13.4 | 70.535
Zone 1 & 2 | Rural | KRUGERVILLE | 2608 | 25 | 21.911 | 2.733 | 24.644
Zone 1 & 2 | Rural | PILOT POINT | 2608PP | 25 |  | 0 | 0
Zone 1 & 2 | Rural | TALCO WEST | 14562 |  | 0.033 | 0 | 0.033
Zone 1 & 2 | Urban | JONES STREET | 1411 | 12.5 | 12.063 | 8.06 | 20.123
Zone 1 & 2 | Urban | JONES STREET | 1412 | 12.5 | 11.699 | 0.818 | 12.517
Zone 1 & 2 | Urban | JONES STREET | 1413 | 12.5 | 12.623 | 1.91 | 14.533
Zone 1 & 2 | Urban | SOUTH | 1107 | 12.5 | 9.329 | 11.653 | 20.982
Zone 1 & 2 | Urban | SOUTH | 1108 | 12.5 | 9.161 | 15.891 | 25.052
Zone 1 & 2 | Urban | SOUTH | 1109 | 12.5 | 5.933 | 3.295 | 9.228
Zone 1 & 2 | Urban | SOUTH | 1102 | 12.5 | 10.284 | 10.433 | 20.717
Zone 1 & 2 | Urban | SOUTH | 1103 | 12.5 | 13.673 | 3.008 | 16.681
Zone 1 & 2 | Urban | SOUTH | 1104 | 12.5 | 2.82 | 8.892 | 11.712
Zone 1 & 2 | Urban | TI | 1033 | 12.5 | 4.794 | 16.461 | 21.255
Zone 1 & 2 | Urban | TI | 1032 | 12.5 | 3.105 | 10.133 | 13.238
Zone 1 & 2 | Urban | TI | 1012 | 12.5 | 10.869 | 11.064 | 21.933
Zone 1 & 2 | Urban | WEST | 1233 | 12.5 | 1.862 | 3.46 | 5.322
Zone 1 & 2 | Urban | WEST | 1234 | 12.5 | 7.183 | 8.058 | 15.241
Zone 1 & 2 | Urban | WEST | 1235 | 12.5 | 6.102 | 10.86 | 16.962
Zone 1 & 2 | Urban | WEST | 1221 | 12.5 | 1.717 | 5.974 | 7.691
Zone 1 & 2 | Urban | WEST | 1223 | 12.5 | 4.176 | 7.182 | 11.358
Zone 1 & 2 | Urban | WEST | 1222 | 12.5 | 2.815 | 14.161 | 16.976
Zone 1 & 2 | Urban | WEST | 1201 | 12.5 | 7.08 | 2.148 | 9.228
Zone 1 & 2 | Urban | WEST | 1202 | 12.5 | 0.897 | 9.48 | 10.377
Zone 1 & 2 | Urban | WEST | 1203 | 12.5 | 0.121 | 7.029 | 7.15
Zone 1 & 2 | Urban | LAKEPOINTE | 2532 | 25 | 1.208 | 6.705 | 7.913
Zone 1 & 2 | Urban | LAKEPOINTE | 2512 | 25 | 0.668 | 9.939 | 10.607
Zone 1 & 2 | Urban | LAKEPOINTE | 2516 | 25 | 0.231 | 7.337 | 7.568
Zone 1 & 2 | Urban | LAKEPOINTE | 2508 | 25 | 17.849 | 1.344 | 19.193
Zone 1 & 2 | Urban | LAKEPOINTE | 2536 | 25 | 5.103 | 7.843 | 12.946
Zone 6 | Rural | ANGLETON | 1153 | 12.5 | 15.251 | 1.086 | 16.337
Zone 6 | Rural | ANGLETON | 1154 | 12.5 | 6.323 | 0.026 | 6.349
Zone 6 | Rural | ANGLETON | 1155 | 12.5 | 72.624 | 1.01 | 73.634
Zone 6 | Rural | ANGLETON | 1243 | 12.5 | 30.234 | 0.407 | 30.641
Zone 6 | Rural | ANGLETON | 1245 | 12.5 | 16.903 | 1.103 | 18.006
Zone 6 | Rural | ANGLETON | 1241 | 12.5 | 24.381 | 0.942 | 25.323
Zone 6 | Rural | ANGLETON | 1244 | 12.5 | 67.282 | 0.186 | 67.468
Zone 6 | Rural | ANGLETON | 1242 | 12.5 | 8.116 | 0.131 | 8.247
Zone 6 | Rural | ANGLETON | 1240 | 12.5 | 39.021 | 9.35 | 48.371
Zone 6 | Rural | BRAZORIA | 1270 | 12.5 | 36.861 | 0.343 | 37.204
Zone 6 | Rural | BRAZORIA | 1290 | 12.5 | 18.565 | 0.031 | 18.596
Zone 6 | Rural | BRAZORIA | 1271 | 12.5 | 56.808 | 1.386 | 58.194
Zone 6 | Rural | BRAZORIA | 1291 | 12.5 | 26.954 | 0.741 | 27.695
Zone 6 | Rural | CLEMONS DOME | 1175 | 12.5 | 1.646 | 0 | 1.646
Zone 6 | Rural | OLD OCEAN | 1261 | 12.5 | 16.582 | 0.053 | 16.635
Zone 6 | Rural | SWEENY | 1263 | 12.5 | 7.702 | 0.114 | 7.816
Zone 6 | Rural | SWEENY | 1128 | 12.5 | 75.069 | 0.412 | 75.481
Zone 6 | Rural | SWEENY | 1264 | 12.5 | 37.39 | 1.776 | 39.166
Zone 6 | Rural | SWEENY | 1129 | 12.5 | 49.431 | 0.378 | 49.809
Zone 6 | Rural | WEST COLUMBIA LOCAL | 1233 | 12.5 | 13.879 | 1.223 | 15.102
Zone 6 | Rural | WEST COLUMBIA LOCAL | 1237 | 12.5 | 32.734 | 1.573 | 34.307
Zone 6 | Rural | WEST COLUMBIA LOCAL | 1235 | 12.5 | 51.067 | 0.34 | 51.407
Zone 6 | Rural | WEST COLUMBIA LOCAL | 1234 | 12.5 | 25.55 | 25.65 | 51.2
Zone 6 | Urban | DICKINSON | 1279 | 12.5 | 51.913 | 4.778 | 56.691
Zone 6 | Urban | DICKINSON | 1267 | 12.5 | 20.319 | 7.243 | 27.562
Zone 6 | Urban | DICKINSON | 1277 | 12.5 | 48.427 | 1.36 | 49.787
Zone 6 | Urban | DICKINSON | 1272 | 12.5 | 21.372 | 0.744 | 22.116
Zone 6 | Urban | DICKINSON | 1266 | 12.5 | 14.482 | 0.495 | 14.977
Zone 6 | Urban | DICKINSON | 1274 | 12.5 | 3.273 | 0.082 | 3.355
Zone 6 | Urban | LEAGUE CITY | 1285 | 12.5 | 10.987 | 4.622 | 15.609
Zone 6 | Urban | LEAGUE CITY | 1284 | 12.5 | 25.863 | 6.552 | 32.415
Zone 6 | Urban | LEAGUE CITY | 1283 | 12.5 | 11.109 | 4.14 | 15.249
Zone 6 | Urban | LEAGUE CITY | 1282 | 12.5 | 24.869 | 3.366 | 28.235
Zone 6 | Urban | LEAGUE CITY | 1280 | 12.5 | 7.308 | 10.404 | 17.712
Zone 6 | Urban | LEAGUE CITY | 1281 | 12.5 | 26.378 | 3.959 | 30.337
Zone 6 | Urban | SOUTH SHORE | 1192 | 12.5 | 3.599 | 15.415 | 19.014
Zone 6 | Urban | SOUTH SHORE | 1195 | 12.5 | 5.406 | 12.154 | 17.56
Zone 6 | Urban | SOUTH SHORE | 1190 | 12.5 | 5.203 | 19.461 | 24.664
Zone 6 | Urban | ALVIN | 1115 | 12.5 | 76.608 | 4.822 | 81.43
Zone 6 | Urban | ALVIN | 1259 | 12.5 | 9.829 | 0.228 | 10.057
Zone 6 | Urban | ALVIN | 1257 | 12.5 | 48.226 | 2.67 | 50.896
Zone 6 | Urban | ALVIN | 1116 | 12.5 | 76.608 | 4.822 | 81.43
Zone 6 | Urban | ALVIN | 1232 | 12.5 | 12.17 | 1.622 | 13.792
Zone 6 | Urban | ALVIN | 1230 | 12.5 | 43.746 | 1.222 | 44.968
Zone 6 | Urban | ALVIN | 1254 | 12.5 | 13.218 | 3.84 | 17.058
Zone 6 | Urban | ALVIN | 1117 | 12.5 | 43.953 | 1.45 | 45.403
Zone 6 | Urban | ALVIN | 1231 | 12.5 | 20.236 | 1.143 | 21.379
Zone 6 | Urban | FRIENDSWOOD | 1252 | 12.5 | 17.221 | 20.035 | 37.256
Zone 6 | Urban | FRIENDSWOOD | 1251 | 12.5 | 17.884 | 18.093 | 35.977
Zone 6 | Urban | FRIENDSWOOD | 1253 | 12.5 | 15.987 | 9.419 | 25.406
Zone 6 | Urban | FRIENDSWOOD | 1108 | 12.5 | 17.785 | 7.061 | 24.846
Zone 6 | Urban | FRIENDSWOOD | 1109 | 12.5 | 16.571 | 7.17 | 23.741
Zone 6 | Urban | FRIENDSWOOD | 1107 | 12.5 | 9.643 | 16.4 | 26.043
Zone 6 | Urban | MAGNOLIA | 1150 | 12.5 | 0.563 | 3.434 | 3.997
Zone 6 | Urban | MAGNOLIA | 1149 | 12.5 | 12.281 | 15.238 | 27.519
Zone 6 | Urban | MAGNOLIA | 1146 | 12.5 | 0 | 0.003 | 0.003
Zone 6 | Urban | MAGNOLIA | 1145 | 12.5 | 7.769 | 11.05 | 18.819
Zone 6 | Urban | MAGNOLIA | 1144 | 12.5 | 11.497 | 11.582 | 23.079
Zone 6 | Urban | FREEWAY PARK | 1298 | 12.5 | 18.706 | 1.721 | 20.427
Zone 6 | Urban | FREEWAY PARK | 1297 | 12.5 | 9.455 | 0.622 | 10.077
Zone 6 | Urban | FREEWAY PARK | 1101 | 12.5 | 16.084 | 2.683 | 18.767
Zone 6 | Urban | FREEWAY PARK | 1103 | 12.5 | 19.665 | 0.114 | 19.779
Zone 6 | Urban | FREEWAY PARK | 1102 | 12.5 | 11.048 | 4.454 | 15.502
Zone 6 | Urban | FREEWAY PARK | 1299 | 12.5 | 14.575 | 0.463 | 15.038
Zone 6 | Urban | HEIGHTS | 1132 | 12.5 | 23.287 | 1.18 | 24.467
Zone 6 | Urban | HEIGHTS | 1134 | 12.5 | 9.371 | 0.206 | 9.577
Zone 6 | Urban | HEIGHTS | 1222 | 12.5 | 10.679 | 0 | 10.679
Zone 6 | Urban | HEIGHTS | 1224 | 12.5 | 12.336 | 0.821 | 13.157
Zone 6 | Urban | LAMARQUE | 1205 | 12.5 | 13.188 | 0 | 13.188
Zone 6 | Urban | LAMARQUE | 1201 | 12.5 | 10.645 | 0.027 | 10.672
Zone 6 | Urban | LAMARQUE | 1203 | 12.5 | 10.727 | 0.041 | 10.768
Zone 6 | Urban | LAMARQUE | 1204 | 12.5 | 28.635 | 0.356 | 28.991
Zone 6 | Urban | LAMARQUE | 1110 | 12.5 | 5.01 | 0 | 5.01
Zone 6 | Urban | LAMARQUE | 1202 | 12.5 | 14.465 | 0 | 14.465
Zone 6 | Urban | NORTHSIDE | 1228 | 12.5 | 14.075 | 3.367 | 17.442
Zone 6 | Urban | NORTHSIDE | 1292 | 12.5 | 12.917 | 2.538 | 15.455
Zone 6 | Urban | NORTHSIDE | 1293 | 12.5 | 6.612 | 0.045 | 6.657
Zone 6 | Urban | NORTHSIDE | 1294 | 12.5 | 10.155 | 0.224 | 10.379
Zone 6 | Urban | NORTHSIDE | 1295 | 12.5 | 24.67 | 1.386 | 26.056
Zone 6 | Urban | TEJAS | 1214 | 12.5 | 5.131 | 0.964 | 6.095
Zone 6 | Urban | TEJAS | 1212 | 12.5 | 18.996 | 0.784 | 19.78
Zone 6 | Urban | TEJAS | 1215 | 12.5 | 14.586 | 0.023 | 14.609
Zone 6 | Urban | TEJAS | 1217 | 12.5 | 12.896 | 0.355 | 13.251
Zone 6 | Urban | UNION CARBIDE | 1130 | 12.5 | 0.05 | 0 | 0.05
Zone 8 | Rural | C C MITCHELL | 4 | 4.16 | 0.945 | 0 | 0.945
Zone 8 | Rural | N M MITCHELL | A4 | 4.16 | 0.85 | 0 | 0.85
Zone 8 | Rural | N M MITCHELL | B4 | 4.16 | 1.434 | 0 | 1.434
Zone 8 | Rural | KERMIT NO. 1 | 4K04 | 4.16 | 7.3 | 0 | 7.3
Zone 8 | Rural | KERMIT NO. 1 | 4K02 | 4.16 | 2.803 | 0 | 2.803
Zone 8 | Rural | KERMIT NO. 1 | 4K05 | 4.16 | 2.289 | 0.065 | 2.354
Zone 8 | Rural | KERMIT NO. 1 | 4K03 | 4.16 | 3.359 | 0 | 3.359
Zone 8 | Rural | KERMIT NO. 2 | 4K06 | 4.16 | 1.631 | 0 | 1.631
Zone 8 | Rural | KERMIT NO. 2 | 4K07 | 4.16 | 3.74 | 0.039 | 3.779
Zone 8 | Rural | SANDERSON | 4S27 | 4.16 | 12.724 | 0 | 12.724
Zone 8 | Rural | SANDERSON | 4S28 | 4.16 | 1.372 | 0 | 1.372
Zone 8 | Rural | SANDERSON | 4S26 | 4.16 | 6.928 | 0.048 | 6.976
Zone 8 | Rural | AIRPORT | 12F271 | 12.5 | 43.711 | 0 | 43.711
Zone 8 | Rural | AIRPORT | 12F44 | 12.5 | 24.078 | 0.818 | 24.896
Zone 8 | Rural | BELDING | 12F161 | 12.5 | 3.088 | 0 | 3.088
Zone 8 | Rural | BELDING | 12F164 | 12.5 | 31.768 | 0 | 31.768
Zone 8 | Rural | HARRELL | 12 | 12.5 | 0.352 | 0 | 0.352
Zone 8 | Rural | 16TH STREET | 1314 | 12.5 | 1.427 | 0 | 1.427
Zone 8 | Rural | 16TH STREET | 1272 | 12.5 | 4.555 | 0 | 4.555
Zone 8 | Rural | 16TH STREET | 1271 | 12.5 | 82.623 | 0.054 | 82.677
Zone 8 | Rural | CALIFORNIA | 12K87 | 12.5 | 34.198 | 0 | 34.198
Zone 8 | Rural | CALIFORNIA | 12K86 | 12.5 | 13.635 | 0 | 13.635
Zone 8 | Rural | KERMIT NO. 2 | 1248 | 12.5 | 24.83 | 0 | 24.83
Zone 8 | Rural | KERMIT NO. 2 | 1298 | 12.5 | 25.162 | 0.252 | 25.414
Zone 8 | Rural | KEYSTONE | 12K437 | 12.5 | 24.779 | 0.062 | 24.841
Zone 8 | Rural | KEYSTONE | 12K434 | 12.5 | 0.675 | 0 | 0.675
Zone 8 | Rural | WICKETT | 12K446 | 12.5 | 30.489 | 0 | 30.489
Zone 8 | Rural | WICKETT | 12K449 | 12.5 | 19.891 | 0 | 19.891
Zone 8 | Rural | PECOS MAIN | 12P362 | 12.5 | 13.121 | 0.22 | 13.341
Zone 8 | Rural | PECOS MAIN | 1201 | 12.5 | 8.548 | 0 | 8.548
Zone 8 | Rural | PECOS MAIN | 1203 | 12.5 | 14.147 | 0 | 14.147
Zone 8 | Rural | PECOS MAIN | 1202 | 12.5 | 52.048 | 0.14 | 52.188
Zone 8 | Rural | REEVES CO. NO. 4 | 1337 | 12.5 | 38.173 | 0 | 38.173
Zone 8 | Rural | REEVES CO. NO. 4 | 1228 | 12.5 | 79.152 | 0 | 79.152
Zone 8 | Rural | STAFFORD | 1283 | 12.5 | 4.767 | 1.139 | 5.906
Zone 8 | Rural | STAFFORD | 1250 | 12.5 | 3.976 | 0.083 | 4.059
Zone 8 | Rural | STAFFORD | 1299 | 12.5 | 3.508 | 0.124 | 3.632
Zone 8 | Rural | STAFFORD | 1282 | 12.5 | 6.902 | 0 | 6.902
Zone 8 | Rural | STAFFORD | 1350 | 12.5 | 46.705 | 0.098 | 46.803
Zone 8 | Rural | TOYAH | 12P259 | 12.5 | 75.811 | 0 | 75.811
Zone 8 | Rural | TOYAH | 12P260 | 12.5 | 4.763 | 0 | 4.763
Zone 8 | Rural | WORSHAM FIELD | 1398 | 12.5 | 33.446 | 0 | 33.446
Zone 8 | Rural | WORSHAM FIELD | 1397 | 12.5 | 33.22 | 0 | 33.22
Zone 8 | Rural | ARMADILLO | 12S112 | 12.5 | 0.163 | 0 | 0.163
Zone 8 | Rural | DOWNIE | 12S101 | 12.5 | 0.214 | 0 | 0.214
Zone 8 | Rural | DOWNIE | 12S100 | 12.5 | 4.529 | 0 | 4.529
Zone 8 | Rural | GOMEZ | 25F61 | 25 | 16.912 | 0 | 16.912
Zone 8 | Rural | GOMEZ | 25F05 | 25 | 33.745 | 0 | 33.745
Zone 8 | Rural | PUCKETT | 25F18 | 25 | 37.789 | 0 | 37.789
Zone 8 | Rural | PUCKETT | 25F14 | 25 | 33.765 | 0 | 33.765
Zone 8 | Rural | WINKLER CO. NO. 6 | 25K11 | 25 | 23.631 | 0 | 23.631
Zone 8 | Rural | COCHISE | 25P47 | 25 | 27.735 | 0 | 27.735
Zone 8 | Rural | COCHISE | 25P48 | 25 | 20.519 | 0 | 20.519
Zone 8 | Rural | FLAT TOP | 2603 | 25 | 23.95 | 0 | 23.95
Zone 8 | Rural | FLAT TOP | 2602 | 25 | 70.221 | 0 | 70.221
Zone 8 | Rural | FLAT TOP | 2601 | 25 | 84.753 | 0 | 84.753
Zone 8 | Rural | LONE STAR | 25P171 | 25 | 4.899 | 0 | 4.899
Zone 8 | Rural | LONE STAR | 25P174 | 25 | 7.054 | 0 | 7.054
Zone 8 | Rural | PYOTE | 25P217 | 25 | 45.483 | 0 | 45.483
Zone 8 | Rural | PYOTE | 25P312 | 25 | 81.592 | 0 | 81.592
Zone 8 | Rural | PECOS MAIN | 203 | 2.4 Delta | 4.266 | 0 | 4.266
Zone 8 | Rural | PECOS MAIN | 204 | 2.4 Delta | 2.174 | 0 | 2.174
Zone 8 | Rural | PECOS MAIN | 205 | 2.4 Delta | 0.563 | 0 | 0.563
Zone 8 | Rural | PECOS MAIN | 206 | 2.4 Delta | 3.917 | 0 | 3.917
Zone 8 | Urban | FORT STOCKTON | A4 | 4.16 | 0.027 | 0 | 0.027
Zone 8 | Urban | FORT STOCKTON | 4F52 | 4.16 | 5.999 | 0 | 5.999
Zone 8 | Urban | FORT STOCKTON | 12F114 | 12.5 | 8.432 | 0.012 | 8.444
Zone 8 | Urban | FORT STOCKTON | 12F130 | 12.5 | 38.466 | 0.874 | 39.34
TOTALS |  |  |  |  | 6357.701 | 584.511 | 6942.212
Notes:
(1) Unable to identify substation transformer serving circuits.

## Model Stats - Summary
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Line Losses - Summary of Distribution Model Statistics (1)
LOOKUP TABLE
ZONE | SERVICE AREA | VOLTAGE (kV) | ID | LENGTH OF OH LINE (Miles) |  |  | LENGTH OF UG LINE (Miles) |  |  | OH LINE LOSSES (kW)/MILE |  |  | UG LINE LOSSES (kW)/MILE |  |  | TOTAL LINE LOSSES (kW)/MILE |  |  | ID | LINE LOSSES (kW)/MILE
|  |  |  | MAX | MIN | AVG | MAX | MIN | AVG | MAX | MIN | AVG | MAX | MIN | AVG | MAX | MIN | AVG
ZONE 1 & 2 | Rural | 4.16 | ZONE 1&2/Rural/4.16kV | 13.3184 | 13.3184 | 13.3184 |  |  |  | 5.1283 | 5.1283 | 5.1283 |  |  |  | 5.1283 | 5.1283 | 5.1283 | MAX ZONE 1&2/Rural | 13.4543
ZONE 1 & 2 | Rural | 12.5 | ZONE 1&2/Rural/12.5kV | 28.9203 | 3.9578 | 15.7085 | 0.79223 | 0.12386 | 0.38139 | 13.4543 | 0.4826 | 3.6178 |  |  |  | 13.4543 | 0.4826 | 3.6178 | MIN ZONE 1&2/Rural | 0.4826
ZONE 1 & 2 | Rural | 22 | ZONE 1&2/Rural/22kV | 91.1437 | 3.8436 | 34.9847 | 0.57197 | 0.079924 | 0.32595 | 1.9802 | 1.195 | 1.5876 |  |  |  | 1.9802 | 1.195 | 1.5876 | AVG ZONE 1&2/Rural | 3.4445
ZONE 1 & 2 | Urban | 12.5 | ZONE 1&2/Urban/25kV |  |  |  | 0.11496 | 0.11496 | 0.11496 | [9 empty] | MAX ZONE 1&2/Urban | 9.7527
ZONE 1 & 2 | Urban | 25 | ZONE 1&2/Urban/25kV | 17.8364 | 0.30265 | 5.0284 | 9.9473 | 1.3034 | 6.7348 | 8.5973 | 0.066083 | 3.7262 | 2.7032 | 0.46668 | 1.2946 | 9.7527 | 0.11549 | 4.7619 | MIN ZONE 1&2/Urban | 0.11549
ZONE 6 | Urban | 12.5 | ZONE 6/Urban/12.5kV | 22.7057 | 0.56288 | 12.5314 | 18.8216 | 3.4354 | 11.1108 | 13.3103 | 0.40861 | 7.5343 | 1.4202 | 0.15422 | 0.49371 | 13.5497 | 0.61237 | 8.028 | AVG ZONE 1&2/Urban | 4.7619
ZONE 8 | Rural | 12.5 | ZONE 8/Rural/12.5kV | 38.0782 | 9.3799 | 28.5857 | 0.87424 | 0.0125 | 0.44337 | 1.3897 | 1.1392 | 1.2225 | 0.18302 | 0.18302 | 0.18302 | 1.3897 | 1.1642 | 1.2683 | MAX ZONE 6/Urban | 13.5497
[19 empty] | MIN ZONE 6/Urban | 0.61237
MAXIMUM |  |  |  | 91.1437 |  |  | 18.8216 |  |  | 13.4543 |  |  | 2.7032 |  |  | 13.5497 |  |  | AVG ZONE 6/Urban | 8.028
MINIMUM |  |  |  |  | 0.30265 |  |  | 0.0125 |  |  | 0.066083 |  |  | 0.15422 |  |  | 0.11549 |  | MAX ZONE 8/Rural | 1.3897
AVERAGE | [5 empty] | 18.3595 |  |  | 3.1852 |  |  | 3.8028 |  |  | 0.65713 |  |  | 4.0653 | MIN ZONE 8/Rural | 1.1642
[19 empty] | AVG ZONE 8/Rural | 1.2683
Notes:
(1) Based on distribution models for Friendswood, Magnolia, Leonard, Red
River, Lakepointe, Ft. Stockton and Worsham Substations provided
by Texas NM.

## Model Stats
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Line Losses - Distribution Model Statistics (1)
ZONE | SERVICE AREA | SUBSTATION | FEEDER | VOLTAGE (kV) | LENGTH OF OH LINE (Miles) |  |  |  | LENGTH OF UG LINE (Miles) |  |  |  | TOTAL LENGTH OF LINE (Miles) |  |  |  | LOSSES ON OH LINE (kW) |  |  |  | LOSSES ON UG LINE (kW) |  |  |  | TOTAL LOSSES (kW) |  |  |  | ALLOCATED LOADS (KW) |  |  |  | OH LINE (2) | UG LINE (2) | TOTAL LINE
[5 empty] | 1-PHASE | 2-PHASE | 3-PHASE | TOTAL | 1-PHASE | 2-PHASE | 3-PHASE | TOTAL | 1-PHASE | 2-PHASE | 3-PHASE | TOTAL | 1-PHASE | 2-PHASE | 3-PHASE | TOTAL | 1-PHASE | 2-PHASE | 3-PHASE | TOTAL | 1-PHASE | 2-PHASE | 3-PHASE | TOTAL | A-PHASE | B-PHASE | C-PHASE | TOTAL | LOSSES/MILE | LOSSES/MILE | LOSSES/MILE
Zone 2 | Rural | RED RVR-XFMR9 | OCB2252 | 4.16 | 5.8519 | 4.0186 | 3.4479 | 13.3184 | 0 | 0 | 0 |  | 5.8519 | 4.0186 | 3.4479 | 13.3184 | 1.04 | 10.79 | 56.47 | 68.3 | 0 | 0 | 0 |  | 1.04 | 10.79 | 56.47 | 68.3 | 532.9642 | 893.7449 | 789.2433 | 2215.9523 | 5.1283 |  | 5.1283
Zone 2 | Rural | LEONARD-XFMR2 | OCD7 | 12.5 | 1.6498 | 0.84129 | 1.6167 | 4.1078 | 0.12386 | 0 | 0 | 0.12386 | 1.7737 | 0.84129 | 1.6167 | 4.2316 | 0.01 | 0.11 | 5.12 | 5.24 | 0 | 0 | 0 |  | 0.01 | 0.11 | 5.12 | 5.24 | 335.5322 | 158.8695 | 480.9321 | 975.3337 | 1.2756 |  | 1.2756
Zone 2 | Rural | LEONARD-XFMR2 | R12678 | 12.5 | 16.8663 | 1.4759 | 10.578 | 28.9203 | 0.37197 | 0 | 0.091288 | 0.46326 | 17.2383 | 1.4759 | 10.6693 | 29.3835 | 0.8 | 1.1 | 65.45 | 67.35 | 0 | 0 | 0 |  | 0.8 | 1.1 | 65.45 | 67.35 | 1113.8369 | 821.5725 | 1011.4165 | 2946.8259 | 2.3288 |  | 2.3288
Zone 2 | Rural | LEONARD-XFMR4 | R14635 | 12.5 | 14.6616 | 2.4547 | 8.6822 | 25.7985 | 0.74754 | 0 | 0.044697 | 0.79223 | 15.4091 | 2.4547 | 8.7269 | 26.5907 | 0.57 | 4.44 | 342.09 | 347.1 | 0 | 0 | 0 |  | 0.57 | 4.44 | 342.09 | 347.1 | 879.7686 | 833.7223 | 1104.3967 | 2817.8876 | 13.4543 |  | 13.4543
Zone 2 | Rural | LEONARD-XFMR4 | R14361 | 12.5 | 1.0347 | 0.63049 | 2.2926 | 3.9578 | 0.14621 | 0 | 0 | 0.14621 | 1.1809 | 0.63049 | 2.2926 | 4.104 | 0 | 0 | 1.91 | 1.91 | 0 | 0 | 0 |  | 0 | 0 | 1.91 | 1.91 | 350.3172 | 362.7858 | 154.6664 | 867.7694 | 0.4826 |  | 0.4826
Zone 2 | Rural | RED RVR-XFMR9 | OCB2262 | 12.5 | 1.3759 | 0.68258 | 13.6996 | 15.7581 | 0 | 0 | 0 |  | 1.3759 | 0.68258 | 13.6996 | 15.7581 | 0 | 0.41 | 8.22 | 8.63 | 0 | 0 | 0 |  | 0 | 0.41 | 8.22 | 8.63 | 309.6433 | 166.0615 | 163.5675 | 639.2723 | 0.54765 |  | 0.54765
Zone 2 | Rural | RED RVR-XFMR9 | OCB2229 | 22 | 0.051326 | 0 | 3.7922 | 3.8436 | 0 | 0 | 0 |  | 0.051326 | 0 | 3.7922 | 3.8436 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Zone 2 | Rural | RED RVR-XFMR9 | OCB2252 | 22 | 63.882 | 4.1157 | 23.146 | 91.1437 | 0.57197 | 0 | 0 | 0.57197 | 64.454 | 4.1157 | 23.146 | 91.7157 | 6 | 0.27 | 174.21 | 180.48 | 0 | 0 | 0 |  | 6 | 0.27 | 174.21 | 180.48 | 1417.7165 | 1432.307 | 682.2557 | 3532.2792 | 1.9802 |  | 1.9802
Zone 2 | Rural | RED RVR-XFMR9 | OCB2262 | 22 | 2.8786 | 0.56818 | 6.5201 | 9.9669 | 0.079924 | 0 | 0 | 0.079924 | 2.9585 | 0.56818 | 6.5201 | 10.0468 | 0 | 0 | 11.91 | 11.91 | 0 | 0 | 0 |  | 0 | 0 | 11.91 | 11.91 | 12.8708 | 31.8377 | 48.8929 | 93.6014 | 1.195 |  | 1.195
Zone 2 | Urban | LP-XFMR8 | VCB2508 | 12.5 | 0 | 0 | 0 |  | 0.11496 | 0 | 0 | 0.11496 | 0.11496 | 0 | 0 | 0.11496 | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0 |  | 0 | 0 | 0
Zone 2 | Urban | LP-XFMR6 | VCB2532 | 25 | 0 | 0 | 1.2085 | 1.2085 | 1.6727 | 0.019697 | 5.0583 | 6.7508 | 1.6727 | 0.019697 | 6.2669 | 7.9593 | 0 | 0 | 10.39 | 10.39 | 1.91 | 0.13 | 5.76 | 7.8 | 1.91 | 0.13 | 16.15 | 18.19 | 3223.281 | 3252.9465 | 3164.7691 | 9640.9965 | 8.5973 | 1.1554 | 9.7527
Zone 2 | Urban | LP-XFMR6 | VCB2536 | 25 | 0.13466 | 0.036553 | 4.9549 | 5.1261 | 0.99886 | 0 | 7.2167 | 8.2155 | 1.1335 | 0.036553 | 12.1716 | 13.3417 | 0 | 0 | 18.07 | 18.07 | 0.01 | 0 | 7 | 7.01 | 0.01 | 0 | 25.07 | 25.08 | 2210.7462 | 2269.4552 | 2284.1508 | 6764.3522 | 3.5251 | 0.85326 | 4.3783
Zone 2 | Urban | LP-XFMR8 | VCB2508 | 25 | 3.978 | 2.2549 | 11.6034 | 17.8364 | 0.097917 | 0.05 | 1.1555 | 1.3034 | 4.0759 | 2.3049 | 12.7589 | 19.1398 | 0 | 0.04 | 2.02 | 2.06 | 0 | 0 | 0 |  | 0 | 0.04 | 2.02 | 2.06 | 1803.2951 | 1772.9702 | 1949.2494 | 5525.5148 | 0.11549 |  | 0.11549
Zone 2 | Urban | LP-XFMR8 | VCB2512 | 25 | 0.081818 | 0 | 0.58674 | 0.66856 | 3.6989 | 0.31989 | 5.9286 | 9.9473 | 3.7807 | 0.31989 | 6.5153 | 10.6159 | 0 | 0 | 4.23 | 4.23 | 2.24 | 2.11 | 22.54 | 26.89 | 2.24 | 2.11 | 26.77 | 31.12 | 3612.0707 | 3497.7517 | 3411.4976 | 10521.3201 | 6.327 | 2.7032 | 9.0303
Zone 2 | Urban | LP-XFMR8 | VCB2516 | 25 | 0 | 0 | 0.30265 | 0.30265 | 1.8549 | 0.061742 | 5.5403 | 7.457 | 1.8549 | 0.061742 | 5.843 | 7.7597 | 0 | 0 | 0.02 | 0.02 | 0.53 | 0.14 | 2.81 | 3.48 | 0.53 | 0.14 | 2.83 | 3.5 | 1759.0119 | 1671.7984 | 1700.4492 | 5131.2596 | 0.066083 | 0.46668 | 0.53276
Zone 6 | Urban | FW EAST XFMR | 1107-OCD | 12.5 | 0.017235 | 0 | 2.4514 | 2.4687 | 5.4557 | 0.31231 | 0.0028409 | 5.7708 | 5.4729 | 0.31231 | 2.4543 | 8.2395 | 0 | 0 | 3.26 | 3.26 | 0.65 | 0.21 | 0.03 | 0.89 | 0.65 | 0.21 | 3.29 | 4.15 | 819.5121 | 979.5256 | 802.6494 | 2601.6871 | 1.3206 | 0.15422 | 1.4748
Zone 6 | Urban | FW EAST XFMR | 1108-OCD | 12.5 | 7.01 | 2.0146 | 8.7511 | 17.7758 | 7.2337 | 0.47178 | 0.12292 | 7.8284 | 14.2438 | 2.4864 | 8.8741 | 25.6042 | 3.8 | 2.45 | 174.41 | 180.66 | 1.4 | 0.31 | 0.39 | 2.1 | 5.2 | 2.76 | 174.8 | 182.76 | 2979.481 | 2528.1063 | 3260.1061 | 8767.6934 | 10.1633 | 0.26825 | 10.4315
Zone 6 | Urban | FW EAST XFMR | 1109-OCD | 12.5 | 5.0019 | 3.3273 | 8.121 | 16.4501 | 13.1123 | 0.63144 | 1.3953 | 15.139 | 18.1142 | 3.9587 | 9.5162 | 31.5891 | 0.99 | 3.29 | 98.47 | 102.75 | 4 | 0.8 | 16.7 | 21.5 | 4.99 | 4.09 | 115.17 | 124.25 | 3273.807 | 3649.3498 | 3454.6207 | 10377.7775 | 6.2462 | 1.4202 | 7.6663
Zone 6 | Urban | FW WEST XFMR | 1251-OCD | 12.5 | 7.2095 | 1.6623 | 8.8042 | 17.6759 | 15.1411 | 0.62443 | 0.80152 | 16.567 | 22.3506 | 2.2867 | 9.6057 | 34.243 | 1.53 | 0.51 | 198.08 | 200.12 | 4 | 0.55 | 6.38 | 10.93 | 5.53 | 1.06 | 204.46 | 211.05 | 3688.8492 | 3982.1109 | 3319.0649 | 10990.0249 | 11.3216 | 0.65974 | 11.9813
Zone 6 | Urban | FW WEST XFMR | 1252-OCD | 12.5 | 5.8108 | 2.7913 | 7.9653 | 16.5674 | 16.2504 | 1.2106 | 1.3606 | 18.8216 | 22.0612 | 4.0019 | 9.3259 | 35.389 | 0.3 | 1.67 | 89.41 | 91.38 | 3.62 | 0.68 | 6.85 | 11.15 | 3.92 | 2.35 | 96.26 | 102.53 | 2811.1608 | 2460.793 | 2664.9848 | 7936.9386 | 5.5156 | 0.5924 | 6.108
Zone 6 | Urban | FW WEST XFMR | 1253-OCD | 12.5 | 8.8826 | 5.1311 | 8.692 | 22.7057 | 9.3299 | 0.39659 | 0.047538 | 9.7741 | 18.2125 | 5.5277 | 8.7396 | 32.4797 | 5.17 | 15.5 | 281.55 | 302.22 | 1.32 | 0.35 | 0.67 | 2.34 | 6.49 | 15.85 | 282.22 | 304.56 | 2986.8799 | 3593.4284 | 2977.7497 | 9558.0581 | 13.3103 | 0.23941 | 13.5497
Zone 6 | Urban | MAG EAST XFMR | 1144-OCD | 12.5 | 2.1913 | 4.0769 | 5.1133 | 11.3814 | 7.4655 | 1.2684 | 0.32367 | 9.0576 | 9.6568 | 5.3453 | 5.4369 | 20.439 | 0.33 | 12.62 | 83.9 | 96.85 | 1.92 | 3.07 | 0.35 | 5.34 | 2.25 | 15.69 | 84.25 | 102.19 | 2903.3577 | 3620.6815 | 3082.9059 | 9606.9451 | 8.5095 | 0.58956 | 9.099
Zone 6 | Urban | MAG EAST XFMR | 1145-OCD | 12.5 | 2.6884 | 1.5729 | 3.385 | 7.6464 | 8.3587 | 1.7725 | 0.22481 | 10.3561 | 11.0472 | 3.3455 | 3.6098 | 18.0025 | 2.32 | 4 | 75.76 | 82.08 | 1.6 | 0.57 | 0.61 | 2.78 | 3.92 | 4.57 | 76.37 | 84.86 | 2725.4946 | 2328.8334 | 3293.8698 | 8348.1978 | 10.7345 | 0.26844 | 11.0029
Zone 6 | Urban | MAG WEST XFMR | 1149-OCD | 12.5 | 5.1722 | 1.3504 | 5.5568 | 12.0794 | 11.5589 | 1.8913 | 0.90814 | 14.3583 | 16.7311 | 3.2417 | 6.465 | 26.4377 | 0.62 | 0.21 | 93.54 | 94.37 | 2.2 | 1.11 | 4.46 | 7.77 | 2.82 | 1.32 | 98 | 102.14 | 3459.1517 | 2752.4395 | 2064.4481 | 8276.0394 | 7.8125 | 0.54115 | 8.3537
Zone 6 | Urban | MAG WEST XFMR | 1150-OCD | 12.5 | 0 | 0 | 0.56288 | 0.56288 | 3.3767 | 0.037311 | 0.021402 | 3.4354 | 3.3767 | 0.037311 | 0.58428 | 3.9983 | 0 | 0 | 0.23 | 0.23 | 0.64 | 0.03 | 0.03 | 0.7 | 0.64 | 0.03 | 0.26 | 0.93 | 325.5712 | 367.6779 | 372.1474 | 1065.3966 | 0.40861 | 0.20376 | 0.61237
Zone 8 | Rural | Worsham Sub | OCD3 | 12.5 | 0 | 0 | 33.3676 | 33.3676 | 0 | 0 | 0 |  | 0 | 0 | 33.3676 | 33.3676 | 0 | 0 | 39.94 | 39.94 | 0 | 0 | 0 |  | 0 | 0 | 39.94 | 39.94 | 269.338 | 136.1754 | 232.0902 | 637.6037 | 1.197 |  | 1.197
Zone 8 | Rural | Worsham Sub | OCD4 | 12.5 | 0 | 2.2498 | 31.267 | 33.5169 | 0 | 0 | 0 |  | 0 | 2.2498 | 31.267 | 33.5169 | 0 | 0 | 46.58 | 46.58 | 0 | 0 | 0 |  | 0 | 0 | 46.58 | 46.58 | 258.014 | 237.1542 | 221.433 | 716.6013 | 1.3897 |  | 1.3897
Zone 8 | Rural | Ft. Stockton | 114-OCD3 | 12.5 | 1.1674 | 2.3669 | 5.8456 | 9.3799 | 0.0125 | 0 | 0 | 0.0125 | 1.1799 | 2.3669 | 5.8456 | 9.3924 | 0.03 | 0.37 | 10.52 | 10.92 | 0 | 0 | 0 |  | 0.03 | 0.37 | 10.52 | 10.92 | 743.8935 | 1415.5662 | 1245.9468 | 3405.4066 | 1.1642 |  | 1.1642
Zone 8 | Rural | Ft. Stockton | OCD3 | 12.5 | 13.9598 | 5.6182 | 18.5002 | 38.0782 | 0.72973 | 0.055114 | 0.089394 | 0.87424 | 14.6896 | 5.6733 | 18.5896 | 38.9525 | 2.99 | 0.49 | 39.9 | 43.38 | 0.16 | 0 | 0 | 0.16 | 3.15 | 0.49 | 39.9 | 43.54 | 1044.4599 | 1086.6734 | 880.5108 | 3011.6441 | 1.1392 | 0.18302 | 1.3222
TOTALS |  |  |  |  | 171.5578 | 49.2405 | 240.8152 | 461.6135 | 108.5049 | 9.1231 | 30.3335 | 147.9615 | 280.0627 | 58.3636 | 271.1487 | 609.575 | 26.5 | 58.27 | 1935.66 | 2020.43 | 26.2 | 10.06 | 74.58 | 110.84 | 52.7 | 68.33 | 2010.24 | 2131.27 | 45850.0251 | 46304.3388 | 44818.015 | 136972.3789
AVERAGES | [32 empty] | 4.6391 | 0.68658 | 5.0205
Notes:
(1) Based on distribution models for Friendswood, Magnolia, Leonard, Red River,
Lakepointe, Ft. Stockton and Worsham Substations provided by Texas NM.