## General Information
CenterPoint Energy
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses.
According to this protocol, using Method 1, at 0600 of the Day Ahead period, ERCOT will calculate Distribution Loss Factors for each
Settlement Interval as a percentage to be applied to the load for the Operating Day and publish the factors to the MIS. Distribution Loss
Factors will be calculated from the data provided by Distribution Service Providers as follows:
SILFi = ADLF * [ K + ( 1 - K) * (SIELi / AAL)]
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
ADLF = Annual Distribution Loss Factor
K = a factor provided by the DSP
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load
And where:
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
(ERCOT will use the Distribution Loss Factors calculated for each Settlement Interval of the Operating Day for settlement purposes.
The calculations will be done a day ahead based on forcasted load levels.)
For CenterPoint Energy:
Loss Factors:
ADLF = 3.401 %
K = 0.829
AAL = 8,239 MWh's (for 15 min, which corresponds to 1,514 MWh's for CenterPoint Energy)
(Note: ERCOT uses ERCOT load (MWh's) in the equation, not CenterPoint Energy load.)
Customer Coding:
CenterPoint Energy has designated one distribution loss factor for all of its distribution level customers. Each distribution ESI-ID
account has been coded with a "D", which corresponds to the distribution loss information shown above and provided to ERCOT.
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
Annual Interval Average Load for CenterPoint Energy:
The annual interval average load for the entire DSP (CenterPoint Energy) service area used to calculate the annual loss factor is
1,514 MWh's. This corresponds to the AAL for ERCOT of 8,239 MWh's.
Portion of Loss Factor that is not sensitive to load:
CenterPoint Energy has 134.74 MW's of no-load losses for one hour, which corresponds to 33.685 MWh's for 15 minutes. Therefore,
based on the annual interval average load for CenterPoint Energy of 1,514 MWh's, which has total losses of 51.491 MWh's (3.401%),
the portion of the loss factor that is not sensitive to load is approximately 65% at moderate load levels. At high load levels, 3000 MWh's
for 15 minutes (or 12,000 MW load for 1 hour) on the CenterPoint Energy distribution system, total losses will be 114.27 MWh's
(3.809%). At that load level the portion of the losses that is not sensitive to load is approximately 29%.
Note: Although K has been defined as the ratio of no load losses to total losses at average load levels, this value, 0.65, has been
adjusted to 0.829 to provide a better fit to the loss curve. The K equation is a straight line and the choice of K affects the slope of the line.
By adjusting K to be 0.829, CenterPoint Energy will more accurately forecast losses at high load levels and at low load levels.
Methodology upon which the calculation of loss factor was made:
Over the years CenterPoint Energy has developed system loss equations for each part of the system. The equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 7.
A graph of the losses in MW's for the load on the CenterPoint Energy distribution system is shown in Tab 1.
A graph of the losses in % for the load on the CenterPoint Energy distribution system is shown in Tab 2.
As you can see, the shape of the curve is somewhat different when using % as opposed to MW's.
Since ERCOT is going to use the K Factor equations in Method 1 based on ERCOT load, not individual TDU load, the load on the
CenterPoint Energy system had to be scaled to match the load on the ERCOT system. Initially, the peak load and the average annual
load (AAL) for both ERCOT and CenterPoint Energy was determined by reviewing annual peak load readings and annual energy
consumption. Essentially, AAL = Annual Total System MWh's / 365 days * 24 hours * 4 intervals. See Tab 3 for a comparison
between ERCOT load and HL&P load.
The CenterPoint Energy peak load is approximately twice its AAL value, whereas the ERCOT peak is less than twice its AAL value.
So the shape of the Reliant Energy load curve is somewhat different that the shape of the ERCOT load curve as load increases on the
respective systems. To resolve this the CenterPoint Energy load was scaled to match the ERCOT load so the the "AAL points"
matched and the "peak load points" matched. See the spreadsheet in Tab 7 for the results of the scaling.
The constants for the straight line K Factor equation were selected to make the best fit to the distribution % loss curve. The best fit is
a K constant of 0.829 and a loss factor of 3.401% based on an AAL for ERCOT of 8,239 MWh's. See Tab 5 for a graph of the final
results based on ERCOT MWh's for 15 minute intervals. (See Tab 4 for a graph of the results based on ERCOT hourly load.)
Future Considerations:
Since the K Factor equation results in a straight line approximation of the % loss curve, it may be more accurate to simply use a chart
that represents the curve itself rather than using the straight line equation that is simply a best fit. An example of this chart is shown
in Tab 6. This may be something to consider in the future.
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-207-6710,
or email at richard-moffatt@reliantenergy.com.
CenterPoint Energy Distribution Loss Factor 03.xls

## 3) ERCOT Load Comparison
ERCOT / CenterPont Energy Loading Comparison For 2000
| CNP | CNP | CNP | ERCOT | ERCOT | ERCOT
| Annual | Avg Hr | Avg 15 Min | Annual | Avg Hr | Avg 15 Min
| (GWH's) | (MWH's) | (MWH's) | (GWH's) | (MWH's) | (MWH's)
CNP Annual GWH's | 73744 | 8418.2648 | 2104.5662
Less Transmission Customers | 20706 | 2363.6986 | 590.9247
Total Annual GWH's | 53038 | 6054.5662 | 1513.6416 | 288713 | 32958.105 | 8239.5263
CNP Distribution Peak Load MW's - Coincident |  | 12291.79
ERCOT Peak Load MW's - Coincident |  |  |  |  | 57099
Distribution Substation Peak MW's (9/9/2000) |  | 12414
Coincidence Factor |  | 0.985
Load on Low Side of Substation Transformers |  | 12227.79
Losses on Substation Transformers |  | 64
Total CNP Distribution Peak Load - Coincident |  | 12291.79

## 6) Alternative Chart
Distribution Loss Factor
Alternative Chart For CenterPoint Energy
| ERCOT | Distribution | ERCOT | CNP | CNP
| 15 Min Interval | Loss Factor | Load (1 Hour) | Load (1 Hour) | 15 Min Interval
| (MWH's) | (%) | (MW) | (MW) | (MWH's)
1 | 4656.25 | 6.155% | 18625 | 2400 | 600
2 | 5046 | 5.446% | 20184 | 2800 | 700
3 | 5435.75 | 4.937% | 21743 | 3200 | 800
4 | 5825.5 | 4.561% | 23302 | 3600 | 900
5 | 6215.25 | 4.279% | 24861 | 4000 | 1000
6 | 6605 | 4.065% | 26420 | 4400 | 1100
7 | 6994.75 | 3.901% | 27979 | 4800 | 1200
8 | 7384.5 | 3.777% | 29538 | 5200 | 1300
9 | 7774.25 | 3.684% | 31097 | 5600 | 1400
10 | 8164 | 3.615% | 32656 | 6000 | 1500
11 | 8553.75 | 3.566% | 34215 | 6400 | 1600
12 | 8943.5 | 3.533% | 35774 | 6800 | 1700
13 | 9333.25 | 3.514% | 37333 | 7200 | 1800
14 | 9723 | 3.507% | 38892 | 7600 | 1900
15 | 10112.75 | 3.509% | 40451 | 8000 | 2000
16 | 10502.5 | 3.52% | 42010 | 8400 | 2100
17 | 10892.25 | 3.538% | 43569 | 8800 | 2200
18 | 11282 | 3.562% | 45128 | 9200 | 2300
19 | 11671.75 | 3.591% | 46687 | 9600 | 2400
20 | 12061.5 | 3.625% | 48246 | 10000 | 2500
21 | 12451.25 | 3.664% | 49805 | 10400 | 2600
22 | 12841 | 3.706% | 51364 | 10800 | 2700
23 | 13230.75 | 3.752% | 52923 | 11200 | 2800
24 | 13620.5 | 3.8% | 54482 | 11600 | 2900
25 | 14010.25 | 3.851% | 56041 | 12000 | 3000
26 | 14400 | 3.905% | 57600 | 12400 | 3100
27 | 14789.75 | 3.96% | 59159 | 12800 | 3200
2001-02-01

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07
| 2001 Modified | 19.73 | 2.9981e-07 | 0 | 1.413e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | 24.527 | 0.6132% | 17.5682 | 0.4392% | 123.8449 | 3.096% | 5.2106 | 0.1303% | 171.1506 | 4.279%
2001 M | 4000 |  | 24.527 | 0.6132% | 22.3316 | 0.5583% | 123.8237 | 3.096% | 5.1977 | 0.1299% | 175.8799 | 4.397%
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | 37.047 | 0.9262% | 63.5816 | 1.59% | 146.7291 | 3.668% | 19.1626 | 0.4791% | 266.5203 | 3.507%
2001 M | 7600 |  | 37.047 | 0.9262% | 80.8211 | 2.021% | 146.5835 | 3.665% | 19.0736 | 0.4768% | 283.5252 | 3.731%
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | 57.3382 | 1.433% | 138.015 | 3.45% | 183.3105 | 4.583% | 41.5077 | 1.038% | 420.1714 | 3.752%
2001 M | 11200 |  | 57.3382 | 1.433% | 175.4365 | 4.386% | 182.8467 | 4.571% | 41.2247 | 1.031% | 456.8461 | 4.079%
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | 2001
| 19.73 | 2.9981e-07 | 0 | 1.413e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | 2001 Modified

## 7) Loss Analyis 2001
CenterPoint Energy Distribution Loss Analysis |  |  |  |  | CenterPoint Energy Distribution Loss Factor 04.xls | [7 empty] | K = | 0 | K = | 0.85 | K = | 1 |  |  |  |  | K = | 0.829 |  | 0.829 | Alternate Chart For CenterPoint Energy
| Input to | Sub Trf | PELCAR | Pri Conductor |  | Dist Trf | Input to | Sec Conductor |  | Tangent | Difference |  |  | Tangent | Difference | K Formula | Difference | K Formula | Losses Based | Difference | HL&P | ERCOT |  | K Formula | ERCOT | K Formula |  | ERCOT | Distribution | ERCOT | HL&P | HL&P
| Sub Trfs | Losses | Input to Dist Sys | Losses | Input to Dist Trfs | Losses | Secondary | Losses | Total Losses | To MW Curve | Losses - Tangent |  | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.85 | Loss - (K=0.85) | K = 1.0 | On K = 0.85 | Loss - (K=0.85) | Load | Load |  | K = 0.829 | 15 Min | K = 0.829 |  | 15 Min | Loss Factor | Load | Load | 15 Min
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) |  | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW) | (MW) | (MW) | Scaling | (%) | (MWH's) | (%) |  | (MWH's) | (%) | (MW) | (MW) | (MWH's)
| 0 | 19.73 | -19.73 | 0.00043272 | -19.7304 | 115.0102 | -134.7407 | 0.0064352 | 134.7471 |  |  | #DIV/0!
| 50 | 19.7307 | 30.2693 | 0.0010185 | 30.2682 | 115.0105 | -84.7423 | 0.0025455 | 134.7448 |  |  | 269.5%
| 135 | 19.7355 | 115.2645 | 0.014769 | 115.2498 | 115.0175 | 0.23228 | 1.9124e-08 | 134.7677 |  |  | 99.83%
| 500 | 19.805 | 480.195 | 0.25632 | 479.9387 | 115.1399 | 364.7988 | 0.047171 | 135.2484 |  |  | 27.05%
| 1000 | 20.0298 | 979.9702 | 1.0675 | 978.9027 | 115.5504 | 863.3522 | 0.26421 | 136.912 |  |  | 13.69%
1 | 2400 | 21.4569 | 2378.5431 | 6.2888 | 2372.2543 | 118.1839 | 2254.0703 | 1.801 | 147.7306 | 84.1643 | 63.5663 | 6.155% | 6.155% | 1.107% | 5.048% | 3.147% | 3.009% | 3.507% | 75.5264 | 72.2042 | 2400 | 18625 |  | 3.147% | 4656.25 | 3.149% | 1 | 4656.25 | 6.155% | 18625 | 2400 | 600
2 | 2800 | 22.0805 | 2777.9195 | 8.578 | 2769.3415 | 119.3354 | 2650.0061 | 2.4892 | 152.4831 | 98.1917 | 54.2914 | 5.446% | 5.446% | 1.292% | 4.154% | 3.175% | 2.271% | 3.507% | 88.8893 | 63.5938 | 2800 | 20184 |  | 3.174% | 5046 | 3.176% | 2 | 5046 | 5.446% | 20184 | 2800 | 700
3 | 3200 | 22.8001 | 3177.1999 | 11.2212 | 3165.9788 | 120.6631 | 3045.3157 | 3.2872 | 157.9716 | 112.2191 | 45.7525 | 4.937% | 4.937% | 1.477% | 3.46% | 3.202% | 1.734% | 3.507% | 102.4737 | 55.4978 | 3200 | 21743 |  | 3.202% | 5435.75 | 3.204% | 3 | 5435.75 | 4.937% | 21743 | 3200 | 800
4 | 3600 | 23.6155 | 3576.3845 | 14.2179 | 3562.1665 | 122.1665 | 3440 | 4.1945 | 164.1945 | 126.2465 | 37.948 |  | 4.561% | 1.661% | 2.9% | 3.23% | 1.331% | 3.507% | 116.2796 | 47.9149 | 3600 | 23302 |  | 3.23% | 5825.5 | 3.231% | 4 | 5825.5 | 4.561% | 23302 | 3600 | 900
5 | 4000 | 24.527 | 3975.473 | 17.5682 | 3957.9049 | 123.8449 | 3834.06 | 5.2106 | 171.1506 | 140.2738 | 30.8767 |  | 4.279% | 1.846% | 2.433% | 3.258% | 1.021% | 3.507% | 130.307 | 40.8436 | 4000 | 24861 |  | 3.257% | 6215.25 | 3.259% | 5 | 6215.25 | 4.279% | 24861 | 4000 | 1000
6 | 4400 | 25.5343 | 4374.4657 | 21.2715 | 4353.1942 | 125.6978 | 4227.4964 | 6.3348 | 178.8384 | 154.3012 | 24.5372 |  | 4.065% | 2.03% | 2.034% | 3.285% | 0.7791% | 3.507% | 144.5559 | 34.2825 | 4400 | 26420 |  | 3.285% | 6605 | 3.286% | 6 | 6605 | 4.065% | 26420 | 4400 | 1100
7 | 4800 | 26.6376 | 4773.3624 | 25.3278 | 4748.0346 | 127.7245 | 4620.3101 | 7.5668 | 187.2567 | 168.3286 | 18.928 |  | 3.901% | 2.215% | 1.686% | 3.313% | 0.5881% | 3.507% | 159.0262 | 28.2304 | 4800 | 27979 |  | 3.313% | 6994.75 | 3.314% | 7 | 6994.75 | 3.901% | 27979 | 4800 | 1200
8 | 5200 | 27.8369 | 5172.1631 | 29.7367 | 5142.4264 | 129.9245 | 5012.502 | 8.9059 | 196.4039 | 182.356 | 14.0479 |  | 3.777% | 2.399% | 1.378% | 3.341% | 0.4363% | 3.507% | 173.7181 | 22.6858 | 5200 | 29538 |  | 3.341% | 7384.5 | 3.341% | 8 | 7384.5 | 3.777% | 29538 | 5200 | 1300
9 | 5600 | 29.132 | 5570.868 | 34.498 | 5536.3699 | 132.2971 | 5404.0729 | 10.3517 | 206.2788 | 196.3834 | 9.8954 |  | 3.684% | 2.584% | 1.1% | 3.368% | 0.3151% | 3.507% | 188.6314 | 17.6474 | 5600 | 31097 |  | 3.368% | 7774.25 | 3.369% | 9 | 7774.25 | 3.684% | 31097 | 5600 | 1400
10 | 6000 | 30.5232 | 5969.4768 | 39.6115 | 5929.8654 | 134.8418 | 5795.0236 | 11.9036 | 216.88 | 210.4108 | 6.4692 |  | 3.615% | 2.769% | 0.8461% | 3.396% | 0.2186% | 3.507% | 203.7662 | 13.1138 | 6000 | 32656 | 32658 | 3.396% | 8164 | 3.396% | 10 | 8164 | 3.615% | 32656 | 6000 | 1500
11 | 6400 | 32.0102 | 6367.9898 | 45.0768 | 6322.913 | 137.5579 | 6185.3551 | 13.5611 | 228.2061 | 224.4382 | 3.7679 |  | 3.566% | 2.953% | 0.6126% | 3.424% | 0.1419% | 3.507% | 219.1225 | 9.0836 | 6400 | 34215 |  | 3.424% | 8553.75 | 3.424% | 11 | 8553.75 | 3.566% | 34215 | 6400 | 1600
12 | 6800 | 33.5932 | 6766.4068 | 50.8938 | 6715.513 | 140.4449 | 6575.0681 | 15.3238 | 240.2557 | 238.4655 | 1.7902 |  | 3.533% | 3.138% | 0.3955% | 3.451% | 0.0817% | 3.507% | 234.7003 | 5.5554 | 6800 | 35774 |  | 3.452% | 8943.5 | 3.451% | 12 | 8943.5 | 3.533% | 35774 | 6800 | 1700
13 | 7200 | 35.2722 | 7164.7278 | 57.0621 | 7107.6657 | 143.5022 | 6964.1636 | 17.1912 | 253.0276 | 252.4929 | 0.53467 |  | 3.514% | 3.322% | 0.192% | 3.479% | 0.03511% | 3.507% | 250.4996 | 2.528 | 7200 | 37333 |  | 3.479% | 9333.25 | 3.479% | 13 | 9333.25 | 3.514% | 37333 | 7200 | 1800
14 | 7600 | 37.047 | 7562.953 | 63.5816 | 7499.3714 | 146.7291 | 7352.6423 | 19.1626 | 266.5203 | 266.5203 | 0 |  | 3.507% | 3.507% | 0% | 3.507% | 0% | 3.507% | 266.5203 | 0 | 7600 | 38892 |  | 3.507% | 9723 | 3.506% | 14 | 9723 | 3.507% | 38892 | 7600 | 1900
15 | 8000 | 38.9178 | 7961.0822 | 70.4519 | 7890.6303 | 150.1252 | 7740.5051 | 21.2376 | 280.7325 | 280.5477 | 0.18484 |  | 3.509% | 3.691% | -0.1823% | 3.535% | -0.02538% | 3.507% | 282.7625 | -2.03 | 8000 | 40451 |  | 3.535% | 10112.75 | 3.534% | 15 | 10112.75 | 3.509% | 40451 | 8000 | 2000
16 | 8400 | 40.8846 | 8359.1154 | 77.6728 | 8281.4426 | 153.6897 | 8127.7528 | 23.4158 | 295.6629 | 294.5751 | 1.0878 |  | 3.52% | 3.876% | -0.3562% | 3.562% | -0.04242% | 3.507% | 299.2263 | -3.5634 | 8400 | 42010 |  | 3.562% | 10502.5 | 3.561% | 16 | 10502.5 | 3.52% | 42010 | 8400 | 2100
17 | 8800 | 42.9473 | 8757.0527 | 85.2441 | 8671.8086 | 157.4222 | 8514.3864 | 25.6965 | 311.3101 | 308.6025 | 2.7076 |  | 3.538% | 4.061% | -0.5229% | 3.59% | -0.05229% | 3.507% | 315.9115 | -4.6014 | 8800 | 43569 |  | 3.59% | 10892.25 | 3.589% | 17 | 10892.25 | 3.538% | 43569 | 8800 | 2200
18 | 9200 | 45.1059 | 9154.8941 | 93.1655 | 9061.7286 | 161.322 | 8900.4066 | 28.0793 | 327.6728 | 322.6299 | 5.0429 |  | 3.562% | 4.245% | -0.6835% | 3.618% | -0.05593% | 3.507% | 332.8182 | -5.1454 | 9200 | 45128 |  | 3.618% | 11282 | 3.616% | 18 | 11282 | 3.562% | 45128 | 9200 | 2300
19 | 9600 | 47.3605 | 9552.6395 | 101.4367 | 9451.2028 | 165.3885 | 9285.8142 | 30.5638 | 344.7496 | 336.6572 | 8.0923 |  | 3.591% | 4.43% | -0.8386% | 3.645% | -0.05413% | 3.507% | 349.9463 | -5.1968 | 9600 | 46687 |  | 3.646% | 11671.75 | 3.644% | 19 | 11671.75 | 3.591% | 46687 | 9600 | 2400
20 | 10000 | 49.711 | 9950.289 | 110.0576 | 9840.2314 | 169.6212 | 9670.6102 | 33.1493 | 362.5392 | 350.6846 | 11.8545 |  | 3.625% | 4.614% | -0.9889% | 3.673% | -0.04757% | 3.507% | 367.296 | -4.7568 | 10000 | 48246 |  | 3.673% | 12061.5 | 3.671% | 20 | 12061.5 | 3.625% | 48246 | 10000 | 2500
21 | 10400 | 52.1574 | 10347.8426 | 119.0277 | 10228.8148 | 174.0195 | 10054.7953 | 35.8355 | 381.0402 | 364.712 | 16.3282 |  | 3.664% | 4.799% | -1.135% | 3.701% | -0.0368% | 3.507% | 384.8671 | -3.8269 | 10400 | 49805 |  | 3.701% | 12451.25 | 3.699% | 21 | 12451.25 | 3.664% | 49805 | 10400 | 2600
22 | 10800 | 54.6998 | 10745.3002 | 128.347 | 10616.9532 | 178.5828 | 10438.3704 | 38.6218 | 400.2514 | 378.7394 | 21.512 |  | 3.706% | 4.983% | -1.277% | 3.728% | -0.0223% | 3.507% | 402.6598 | -2.4084 | 10800 | 51364 |  | 3.729% | 12841 | 3.726% | 22 | 12841 | 3.706% | 51364 | 10800 | 2700
23 | 11200 | 57.3382 | 11142.6618 | 138.015 | 11004.6468 | 183.3105 | 10821.3363 | 41.5077 | 420.1714 | 392.7668 | 27.4046 |  | 3.752% | 5.168% | -1.416% | 3.756% | -0.004486% | 3.507% | 420.6739 | -0.50249 | 11200 | 52923 |  | 3.757% | 13230.75 | 3.754% | 23 | 13230.75 | 3.752% | 52923 | 11200 | 2800
24 | 11600 | 60.0724 | 11539.9276 | 148.0317 | 11391.8959 | 188.202 | 11203.6939 | 44.4928 | 440.7989 | 406.7942 | 34.0047 |  | 3.8% | 5.353% | -1.553% | 3.784% | 0.01629% | 3.507% | 438.9095 | 1.8894 | 11600 | 54482 |  | 3.784% | 13620.5 | 3.781% | 24 | 13620.5 | 3.8% | 54482 | 11600 | 2900
25 | 12000 | 62.9026 | 11937.0974 | 158.3967 | 11778.7007 | 193.2567 | 11585.444 | 47.5765 | 462.1325 | 420.8215 | 41.311 |  | 3.851% | 5.537% | -1.686% | 3.811% | 0.03972% | 3.507% | 457.3666 | 4.766 | 12000 | 56041 |  | 3.812% | 14010.25 | 3.809% | 25 | 14010.25 | 3.851% | 56041 | 12000 | 3000
26 | 12400 | 65.8288 | 12334.1712 | 169.1097 | 12165.0615 | 198.4742 | 11966.5874 | 50.7584 | 484.171 | 434.8489 | 49.3221 |  | 3.905% | 5.722% | -1.817% | 3.839% | 0.06553% | 3.507% | 476.0451 | 8.1259 | 12400 | 57600 | 57600 | 3.84% | 14400 | 3.836% | 26 | 14400 | 3.905% | 57600 | 12400 | 3100
27 | 12800 | 68.8509 | 12731.1491 | 180.1705 | 12550.9786 | 203.8537 | 12347.1249 | 54.038 | 506.913 | 448.8763 | 58.0367 |  | 3.96% | 5.906% | -1.946% | 3.867% | 0.0935% | 3.507% | 494.9452 | 11.9678 | 12800 | 59159 |  | 3.867% | 14789.75 | 3.864% | 27 | 14789.75 | 3.96% | 59159 | 12800 | 3200
| % Losses at Peak = | 0.5379% |  | 1.415% |  | 1.624% |  | 0.4377% | [15 empty] | HL&P Load |  | ERCOT Load
| 400 | [18 empty] | CNP Increment = | 400 | 1559 | = ERCOT Increment |  |  | Test Column
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor | [18 empty] | DLF = 3.401
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | [12 empty] | CNP | ERCOT |  | Loss Factor |  | AAL = 8,239
| 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | [11 empty] | Annual Avg Hour = | 6055 | 32955.3467 |  | 3.401%
[20 empty] | Avg 15 Min Interval = | 1513.75 | 8238.8367 |  | 3.401%
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | 2001 | [9 empty] | Peak Scaling: 57,099 /12,292 *12,400 = 57,600
| 19.73 | 2.9981e-07 | 0 | 1.413e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | 2001 Modified | [9 empty] | ERCOT Peak / CNP Peak * 12,400 = 57,600

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 21.4569 | 2378.5431 | 7.994 | 2370.5491 | 118.1793 | 2252.3697 | 1.7982 | 149.4285 | 89.5343 | 59.8942 | 6.226% | 1.178% | 5.048% | 3.22% | 3.006% | 3.731% | 77.2822 | 72.1463
2 | 2800 | 22.0805 | 2777.9195 | 10.9039 | 2767.0156 | 119.3281 | 2647.6875 | 2.4849 | 154.7974 | 104.4567 | 50.3407 | 5.528% | 1.374% | 4.154% | 3.259% | 2.269% | 3.731% | 91.2621 | 63.5352
3 | 3200 | 22.8001 | 3177.1999 | 14.2637 | 3162.9363 | 120.6522 | 3042.284 | 3.2807 | 160.9967 | 119.379 | 41.6176 | 5.031% | 1.571% | 3.46% | 3.299% | 1.733% | 3.731% | 105.5562 | 55.4405
4 | 3600 | 23.6155 | 3576.3845 | 18.073 | 3558.3114 | 122.151 | 3436.1604 | 4.1852 | 168.0247 | 134.3014 | 33.7233 | 4.667% | 1.767% | 2.9% | 3.338% | 1.329% | 3.731% | 120.1644 | 47.8603
5 | 4000 | 24.527 | 3975.473 | 22.3316 | 3953.1414 | 123.8237 | 3829.3178 | 5.1977 | 175.8799 | 149.2238 | 26.6561 | 4.397% | 1.963% | 2.434% | 3.377% | 1.02% | 3.731% | 135.0868 | 40.7931
6 | 4400 | 25.5343 | 4374.4657 | 27.0391 | 4347.4266 | 125.6695 | 4221.7571 | 6.3176 | 184.5605 | 164.1462 | 20.4143 | 4.195% | 2.16% | 2.035% | 3.416% | 0.7781% | 3.731% | 150.3233 | 34.2372
7 | 4800 | 26.6376 | 4773.3624 | 32.1952 | 4741.1672 | 127.6877 | 4613.4794 | 7.5444 | 194.0649 | 179.0686 | 14.9964 | 4.043% | 2.356% | 1.687% | 3.456% | 0.5873% | 3.731% | 165.874 | 28.1909
8 | 5200 | 27.8369 | 5172.1631 | 37.7995 | 5134.3636 | 129.8777 | 5004.4859 | 8.8774 | 204.3915 | 193.9909 | 10.4006 | 3.931% | 2.553% | 1.378% | 3.495% | 0.4356% | 3.731% | 181.7389 | 22.6527
9 | 5600 | 29.132 | 5570.868 | 43.8518 | 5527.0161 | 132.2387 | 5394.7774 | 10.3161 | 215.5387 | 208.9133 | 6.6254 | 3.849% | 2.749% | 1.1% | 3.534% | 0.3147% | 3.731% | 197.9179 | 17.6208
10 | 6000 | 30.5232 | 5969.4768 | 50.3518 | 5919.1251 | 134.77 | 5784.3551 | 11.8598 | 227.5047 | 223.8357 | 3.669 | 3.792% | 2.945% | 0.8465% | 3.574% | 0.2182% | 3.731% | 214.411 | 13.0937
11 | 6400 | 32.0102 | 6367.9898 | 57.299 | 6310.6908 | 137.4708 | 6173.22 | 13.508 | 240.288 | 238.7581 | 1.5299 | 3.754% | 3.142% | 0.6129% | 3.613% | 0.1417% | 3.731% | 231.2183 | 9.0696
12 | 6800 | 33.5932 | 6766.4068 | 64.6932 | 6701.7136 | 140.3405 | 6561.3732 | 15.2601 | 253.8869 | 253.6804 | 0.20647 | 3.734% | 3.338% | 0.3957% | 3.652% | 0.08158% | 3.731% | 248.3398 | 5.5471
13 | 7200 | 35.2722 | 7164.7278 | 72.534 | 7092.1939 | 143.3783 | 6948.8156 | 17.1155 | 268.2999 | 268.6028 | -0.30297 | 3.726% | 3.534% | 0.1921% | 3.691% | 0.03506% | 3.731% | 265.7754 | 2.5244
14 | 7600 | 37.047 | 7562.953 | 80.8211 | 7482.1318 | 146.5835 | 7335.5484 | 19.0736 | 283.5252 | 283.5252 | 0 | 3.731% | 3.731% | 0% | 3.731% | 0% | 3.731% | 283.5252 | 0
15 | 8000 | 38.9178 | 7961.0822 | 89.5543 | 7871.5279 | 149.9554 | 7721.5725 | 21.1339 | 299.5613 | 298.4476 | 1.1138 | 3.745% | 3.927% | -0.1824% | 3.77% | -0.02535% | 3.731% | 301.5891 | -2.0278
16 | 8400 | 40.8846 | 8359.1154 | 98.7331 | 8260.3823 | 153.4932 | 8106.8891 | 23.2957 | 316.4066 | 313.37 | 3.0367 | 3.767% | 4.123% | -0.3565% | 3.809% | -0.04239% | 3.731% | 319.9672 | -3.5606
17 | 8800 | 42.9473 | 8757.0527 | 108.3573 | 8648.6954 | 157.1964 | 8491.499 | 25.5585 | 334.0595 | 328.2923 | 5.7672 | 3.796% | 4.32% | -0.5235% | 3.848% | -0.05227% | 3.731% | 338.6595 | -4.6
18 | 9200 | 45.1059 | 9154.8941 | 118.4265 | 9036.4676 | 161.0642 | 8875.4035 | 27.9218 | 352.5183 | 343.2147 | 9.3036 | 3.832% | 4.516% | -0.6843% | 3.888% | -0.05595% | 3.731% | 357.6659 | -5.1475
19 | 9600 | 47.3605 | 9552.6395 | 128.9404 | 9423.6991 | 165.0958 | 9258.6034 | 30.3849 | 371.7815 | 358.1371 | 13.6444 | 3.873% | 4.712% | -0.8396% | 3.927% | -0.05422% | 3.731% | 376.9864 | -5.2049
20 | 10000 | 49.711 | 9950.289 | 139.8987 | 9810.3903 | 169.2905 | 9641.0998 | 32.9473 | 391.8475 | 373.0595 | 18.788 | 3.918% | 4.909% | -0.9902% | 3.966% | -0.04774% | 3.731% | 396.6211 | -4.7736
21 | 10400 | 52.1574 | 10347.8426 | 151.301 | 10196.5416 | 173.6477 | 10022.8938 | 35.6085 | 412.7147 | 387.9819 | 24.7328 | 3.968% | 5.105% | -1.137% | 4.005% | -0.03707% | 3.731% | 416.57 | -3.8553
22 | 10800 | 54.6998 | 10745.3002 | 163.1471 | 10582.1531 | 178.1667 | 10403.9864 | 38.3678 | 434.3814 | 402.9042 | 31.4772 | 4.022% | 5.301% | -1.279% | 4.045% | -0.0227% | 3.731% | 436.833 | -2.4516
23 | 11200 | 57.3382 | 11142.6618 | 175.4365 | 10967.2253 | 182.8467 | 10784.3786 | 41.2247 | 456.8461 | 417.8266 | 39.0195 | 4.079% | 5.498% | -1.419% | 4.084% | -0.005036% | 3.731% | 457.4102 | -0.56405
24 | 11600 | 60.0724 | 11539.9276 | 188.1691 | 11351.7585 | 187.6871 | 11164.0713 | 44.1786 | 480.1073 | 432.749 | 47.3583 | 4.139% | 5.694% | -1.555% | 4.123% | 0.01557% | 3.731% | 478.3015 | 1.8058
25 | 12000 | 62.9026 | 11937.0974 | 201.3444 | 11735.7529 | 192.6872 | 11543.0658 | 47.2291 | 504.1633 | 447.6714 | 56.4919 | 4.201% | 5.89% | -1.689% | 4.163% | 0.0388% | 3.731% | 499.507 | 4.6563
26 | 12400 | 65.8288 | 12334.1712 | 214.9622 | 12119.209 | 197.8462 | 11921.3629 | 50.3755 | 529.0126 | 462.5938 | 66.4189 | 4.266% | 6.087% | -1.821% | 4.202% | 0.0644% | 3.731% | 521.0267 | 7.986
27 | 12800 | 68.8509 | 12731.1491 | 229.0221 | 12502.127 | 203.1634 | 12298.9636 | 53.6172 | 554.6536 | 477.5161 | 77.1375 | 4.333% | 6.283% | -1.95% | 4.241% | 0.09213% | 3.731% | 542.8605 | 11.7932
| % Losses at Peak = | 0.5379% |  | 1.799% |  | 1.625% |  | 0.4359%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 19.73 | 2.9981e-07 | 0 | 1.413e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | 2001
| 19.73 | 2.9981e-07 | 0 | 1.413e-06 | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | 2001 Modified