## ADLF Submittal to ERCOT
Sharyland Utilities, L.P.
McAllen, Texas
Purpose:
This documentation summarizes the calculations required to develop the Annual Distribution Loss Factors (ADLF) for Sharyland Utilities, L.P. (SULP), a Distribution Service Provider (DSP), for submittal to ERCOT.
Sharyland Utilities operates a compact system that is currrently under development. As such, SULP's operating characteristics are unique within ERCOT. Loads are relatively low and losses are higher, in comparison to existing Investor Owned Utilities.
Results:
DLF Code: | A
ADLF = | 10.86%
K = | 0.2642
Methodology:
The DSP loss factors were calculated based upon actual energy sales and energy purchases.
'No Load' losses were calculated based upon actual equipment purchases and estimated load factors.
System Factors:
Net Energy Purchases | 14913744 | kWh | Jan. - November 21, 2001
Net Energy Sales | 13452260 | kWh | Jan. - November 21, 2001
Net Losses | 1461483 | kWh | 10.86% | Net Losses as a percent of Sales
Load Losses | 1075244 | kWh | 7.993% | Load Losses as a percent of Sales
No Load Losses | 386239 | kWh | 2.871% | No Load Losses as a percent of Sales
K Factor |  |  | 0.26428 | No Load Losses / Net Losses