## Method
Calculation of TXU Electric Distribution Loss Factors
Per ERCOT Protocol Section 13.3.1.1 (Method 1)
Docket 23640
Schedule FF-9.1
kWh Sales by Rate Class |  |  |  |  | Input Requirement |  | TXU Electric |  | Equipment
Forecast Year (July 2001 through June 2002) |  |  |  |  | Responsibility Factors |  | Loss |  | Voltage-
[5 empty] | Total | Dist. Sys. | Factors |  | Level
|  | At Meter * | At Source ** |  | System *** | Only | for ERCOT |  | Factors
| Secondary | 78485653466 | 83854349646 |  | 1.0684 | 1.0387 | 0.038684 |  | 1.0229 | =Rs
| Primary | 11835445699 | 12361778387 |  | 1.0445 | 1.0154 | 0.015417 |  | 1.0154 | =Rp
| High Voltage | 10610810839 | 10914413967 |  | 1.0286 |  |  |  | 1.0286 | =Rt
| Total Tariff | 100931910004 | 107130542000
Annual Average MWh/Hour
| Secondary | 8959.5495 | 9572.4143
| Primary | 1351.0783 | 1411.1619
* | At Meter: FF-9.1, Attachment 1, Page 3 of 3
** | At Source: FF-9.1, Attachment 2, Page 3 of 3
*** | Ratio of "At Source" to "At Meter" energy.
Note 1: 1.068404 = Total Input required at transmission level per unit of Secondary Sale
|  | = Rt x Rp x Rs | = (kWh at Source) / (kWh at Meter) |  |  | = (83,854,349,646) / (78,485,653,466)
|  | i.e., for every MWh of Secondary Sales, |  |  | 1.0684 | MWh must be input
into the High Voltage system (due to losses caused by Secondary Sales
at secondary, primary and high voltage levels)
Note 2: 1.044471 = Total Input required at transmission level per unit of Primary Sale
|  | = Rt x Rp | = (kWh at Source) / (kWh at Meter) |  |  | = (12,361,778,387) / (11,835,445,699)
Calculation of Primary and Secondary Loss Factors
Secondary Sales
| 1.0684 | = | Rt x Rp x Rs | = | Rp x Rs |  |  | = | 1.0387
| 1.0286 |  | Rt
|  | i.e., for every MWh of Secondary Sales, |  |  | 1.0387 | MWh must be input
into the Distribution System, due to losses caused by Secondary Sales
at secondary and primary voltage levels.
| Secondary Sales Loss Factor = |  | 1.0387 | - | 1 | = | 0.038684
Primary Sales
| 1.0445 | = | Rt x Rp | = | Rp |  |  | = | 1.0154
| 1.0286 |  | Rt
|  | i.e., for every MWh of Primary Sales, |  |  | 1.0154 | MWh must be input
into the Distribution System, due to losses caused by Primary Sales
at the primary voltage level.
| Primary Sales Loss Factor = |  | 1.0154 | - | 1 | = | 0.015417
TXU Electric utilized 2 codes for Distribution loss factor. These
codes and their definitions are as follows:
Code A is assigned to any premise that receives delivery service at
secondary voltage defined as voltages less than 5 kv
Code B is assigned to any premise that receives delivery service at
distribution voltage defined as greater than 5 kV and less than 60 kV.

## Diag
Calculation of TXU Electric Distribution Loss Factors
Per ERCOT Protocol Section 13.3.1.1 (Method 1)
System Input
H V | = High Voltage Input = HVi
Losses |  | HVi | = | Rt | = | HVi | = |  | HVi
|  | HVo |  |  |  | HVs + Pi |  |  | HVs+(Rp)(Ps)+(Rp)(Rs)(Ss)
High Voltage Output = HVo
[6 empty] | ==> | HVi = | (Rt)(HVs) + (Rt)(Rp)(Ps) + (Rt)(Rp)(Rs)(Ss)
High Voltage Sales = HVs
Loss Ratio (reference Page 1)
| Primary Input = Pi | [5 empty] | High Voltage | 1.0286 | = Rt
[7 empty] | Primary | 1.0445 | = (Rt)(Rp)
Primary | [6 empty] | Secondary | 1.0684 | = (Rt)(Rp)(Rs)
Losses
|  | Pi | = | Rp | = | Pi | ==> | Pi = | (Rp)(Ps) + (Rp)(Si)
| Primary Output = Po | Po |  |  |  | Ps + Si
[8 empty] | Pi = | (Rp)(Ps) + (Rp)(Rs)(Ss)
Primary Sales = Ps
Secondary | Secondary Input = Si
Losses |  | Si | = | Rs |  | ==> |  |  | Si = (Rs)(Ss)
| Secondary Output | Ss
= Secondary Sales = Ss
Ss / Si = Fraction of Secondary Input available for Sales after losses
1
2
3
4
5
6
7
8
9

## A1P3
Calculation of TXU Electric Distribution Loss Factors
Loss Factor Derivation
PL = Losses in primary voltage equipment
Po = Primary output
Rp = Primary Input / Output Ratio = Pi / Po
Rs = Secondary Input / Output Ratio = Si / Ss
Si = Secondary Input
SL = Losses in secondary voltage equipment
Ss = Secondary Sales
Losses in secondary-voltage equipment
SL + Ss = Si = Rs x Ss
SL = Rs x Ss - Ss = (Losses in secondary equipment due to secondary sales)
Losses in primary-voltage equipment
Si + PL + Ps = Pi = Rp x Ps + Rp x Rs x Ss
Si + PL = Rp x Ps - Ps + Rp x Rs x Ss
PL = (Rp - 1) Ps + Rp x Rs x Ss - Rs x Ss
= PLp + PLs
= (Primary Losses due to Primary Sales) + (Primary Losses due to Secondary Sales)
(Primary Losses due to Primary Sales) = PLp = (Rp - 1) Ps
(Primary Losses due to Secondary Sales) = PLs = Rp x Rs x Ss - Rs x Ss
Total Losses due to Secondary Sales
= PLs + SL
PLs = Rp x Rs x Ss - Rs x Ss
SL = Rs x Ss - Ss
Sum = Rp x Rs x Ss - Ss
| = | Ss (Rp x Rs - 1)

## Load_and_NoLoad
Calculation of TXU Electric Distribution Loss Factors
Portion of Loss Factor Not Sensitive to Load
|  | Input Reqmt. (2) | Energy Loss Fraction (3) |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter (1) |  |  |  | 78485653466
| Input to Sec. Level | 1.0229 |  |  | 80284047391.1007
| Losses due to Sec. Sales |  | 0.29599 | 0.70401 |  | 532299479.315 | 1266094445.7857 | 1798393925.1007
Primary | Output (=Sec. Input) |  |  |  | 80284047391.1007
| Input to Pri. Level due to Sec. | 1.0154 |  |  | 81521797213.4181
| Losses due to Sec. Sales |  | 0.81916 | 0.18084 |  | 1013917250.6532 | 223832571.6642 | 1237749822.3174
| Pri. Sales (1) |  |  |  | 11835445699
|  | 1.0154 |  |  | 12017914337.3787
| Losses due to Pri. Sales |  | 0.81916 | 0.18084 |  | 149471320.3101 | 32997318.0686 | 182468638.3787
| Total Input |  |  |  | 93539711550.7968
Distribution System (excludes High Voltage)
Losses, kWh
|  |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 1546216729.9682 | 1489927017.4499 | 3036143747.4181
|  |  |  | Primary Sales |  | 149471320.3101 | 32997318.0686 | 182468638.3787
High Voltage Sales
|  |  |  | Total |  | 1695688050.2783 | 1522924335.5185 | 3218612385.7968
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.50927 | 0.49073
NOTES: |  |  |  | Primary Sales |  | 0.81916 | 0.18084
(1) | Docket 23640, FF-9.1.1
(2) | Extracted from FF-9.1.1 by Voltage Level (= Input / Output)
(3) | Docket 23640, Exhibit DAW-FF-1 (see next page)

## DAW-FF-1
Calculation of TXU Electric Distribution Loss Factors
Portion of Loss Factor Not Sensitive to Load
(Based on Allocation of Electrical Losses for 1999 *)
Energy Losses, MWh *
| Load | No-Load | Total
Gen. UMT | 189241 | 76138 | 265379
Trans. Line & Auto Load Loss
345 kV | 1121313 |  | 1121313
138 kV | 805389 |  | 805389
69 kV | 135689 |  | 135689
Auto No-Load Loss
345/138 kV |  | 85591 | 85591
138/69 kV |  | 32118 | 32118
Corona & Insulator
345 kV |  | 82379 | 82379
138 kV |  | 31545 | 31545
69 kV |  | 7350 | 7350
Shunt Reactor, 345 kV
Line |  | 4446 | 4446
Tertiary |  | 3911 | 3911
Total Transmission | 2251632 | 323478 | 2575110
Dist. Substation | 320993 | 225303 | 546296
Primary Feeders | 699585 |  | 699585
Line Transformers | 231169 | 1289755 | 1520924
Residential Sec. Lines | 108748 |  | 108748
Residential Services | 91400 |  | 91400
Commercial Services | 110930 |  | 110930
Total Primary & Sec | 1562825 | 1515058 | 3077883
Total | 3814457 | 1838536 | 5652993
Distribution System
Primary | 1020578 | 225303 | 1245881
Secondary | 542247 | 1289755 | 1832002
Total Primary & Sec | 1562825 | 1515058 | 3077883
Transmission | 0.87438 | 0.12562
Primary | 0.81916 | 0.18084
Secondary | 0.29599 | 0.70401
* From: TXU Electric Fuel Factor Filing - PUC Docket 23640,
Exhibit DAW-FF-1 & workpapers