## Start
ERCOT Distribution Loss Factor Estimates for 2004
1. Using the Spreadsheet to Calculate/Estimate Distribution Loss Factors
This spreadsheet calculates distribution loss factors (DLF) for all Distribution Service Providers (DSP) at various levels of ERCOT system load. From the "Inputs - Single DSP View" Tab, the user will select the DSP-DLF code and ERCOT load level of interest and the spreadsheet will calculate the resulting distribution loss factor. The graph displays the DSP loss factors at various ERCOT load levels as well as the level specified.
The "Inputs - Multiple DSP View" tab operates similar to the "Inputs - Single DSP View" tab and displays graphically all DSPs' DLF curves.
2. Examining the Calculations
This spreadsheet calculates the distribution loss factors for a selected TDSP based on the following formula:
SILFi = ADLF * [K + (1 - K) * (SIELi/AAL)]
Where: i = Interval
SILF = Settlement Interval Distribution Loss Factor
ADLF = Annual Distribution Loss Factor
K = constant representing the no load loss factor
SIEL = Settlement Interval ERCOT Load (ERCOT Day Ahead Forecasted MW Load divided by 4)
AAL = ERCOT Annual interval Average Load (ERCOT will use 8,073 MWh for year 2004 calculations)
Distribution Loss Factor Methodologies
Pursuant to Protocol Section 13.13.1.1 ERCOT is required to post annual Distribution Loss Factor (DLF) Methodologies submitted by TDSPs participating in the competitive retail electric market. DLF Methodologies are submitted to ERCOT prior to October 30 for review, approval, and posting by January 1st of the following year. These DLF Methodologies provide the ERCOT market with insight into the derivations that each TDSP uses for the Annual Distribution Loss Factor and “K” factor magnitudes that they submitted to ERCOT.
The table below contains DLF Methodologies for the calendar year 2004.
DSP | DLF Methodology
AEP-TCC/AEP-TNC | Requested that the DLF methodologies they submitted in the reference document to be utilized for the calendar year 2004. (Methodology is referenced in AEP_SILF for 04.doc and in AEP TCC & TNC SILF for 04.xls included in this zip file)
CenterPoint | Requested that the DLF methodologies utilized in 2003 be used in 2004. (Methodology is referenced in CenterPoint Energy Distribution Loss Factor 04.xls included in this zip file)
Nueces EC | Requested that the DLF methodology they submitted in the reference document to be utilized for the calendar year 2004. (Methodology is referenced in NEC Distribution Loss ERCOT Submittal 6-04.doc in this zip file)
TNMP | Requested that the DLF methodologies utilized in 2003 be used in 2004. (Methodology is referenced in TNMP Losses.zip included in this zip file)
TXU Electric Delivery | Requested that the DLF methodologies utilized in 2003 be used for 2004. (Methodology is referenced in TXU_SESCO_DLF_2001.doc, TXUE_DLF_2001.doc, TXUE_DLF_Attachment_2001.xls included in this zip file)
Sharyland Utilities | Requested that the DLF methodologies they submitted in the reference document Sharyland_DLF_2002.xls, included in this zip file, be utilized for calendar year 2004.

## Inputs - Single DSP View
DSP DLF Code to Graph
Input ERCOT Load |  | AEP - TCC A | 1 | AEP - TCC A
|  | AEP - TCC B | 2 | AEP - TCC B
ERCOT MW Load | 32293 | AEP - TNC A | 3 | AEP - TNC A
|  | AEP - TNC B | 4 | AEP - TNC B | 6 | TXU SESCO B
|  | CenterPoint | 5 | CenterPoint | 6 | Nueces EC
DLF for DSP Selected to Graph |  | Nueces EC | 6 | Nueces EC
|  | Sharyland | 7 | Sharyland
Nueces EC | 9.719% | TNMP A | 8 | TNMP A
|  | TNMP B | 9 | TNMP B
|  | TNMP C | 10 | TNMP C
All DSP Distribution Loss Factors |  | TNMP D | 11 | TNMP D
|  | TNMP E | 12 | TNMP E
AEP - TCC A | 6.271% | TXU A | 13 | TXU A
AEP - TCC B | 2.365% | TXU B | 14 | TXU B
AEP - TNC A | 6.688% | TXU SESCO A | 15 | TXU SESCO A
AEP - TNC B | 1.151% | TXU SESCO B | 16 | TXU SESCO B
CenterPoint | 3.401%
Nueces EC | 9.719%
Sharyland | 10.86%
TNMP A | 7.849%
TNMP B | 4.469%
TNMP C | 3.31%
TNMP D | 3.689%
TNMP E | 4.189%
TXU A | 3.869%
TXU B | 1.54%
TXU SESCO A | 3.869%
TXU SESCO B | 1.54%

## Inputs - Multiple DSP View
Select DSP
Input ERCOT Load |  | AEP - TCC A | 1 | 5 | AEP - TCC A
|  | AEP - TCC B | 2 | 6 | AEP - TCC B
ERCOT MW Load | 32293 | AEP - TNC A | 3 | 7 | AEP - TNC A
|  | AEP - TNC B | 4 | 8 | AEP - TNC B | 5 | TXU SESCO B
|  | CenterPoint | 5 | 9 | CenterPoint | 5 | CenterPoint
DLF for DSP Selected |  | Nueces EC | 6 | 10 | Nueces EC
|  | Sharyland | 7 | 11 | Sharyland
CenterPoint | 3.401% | TNMP A | 8 | 12 | TNMP A
|  | TNMP B | 9 | 13 | TNMP B
|  | TNMP C | 10 | 14 | TNMP C
All DSP Distribution Loss Factors |  | TNMP D | 11 | 15 | TNMP D
|  | TNMP E | 12 | 16 | TNMP E
AEP - TCC A | 6.271% | TXU A | 13 | 17 | TXU A
AEP - TCC B | 2.365% | TXU B | 14 | 18 | TXU B
AEP - TNC A | 6.688% | TXU SESCO A | 15 | 19 | TXU SESCO A
AEP - TNC B | 1.151% | TXU SESCO B | 16 | 20 | TXU SESCO B
CenterPoint | 3.401%
Nueces EC | 9.719%
Sharyland | 10.86%
TNMP A | 7.849%
TNMP B | 4.469%
TNMP C | 3.31%
TNMP D | 3.689%
TNMP E | 4.189%
TXU A | 3.869%
TXU B | 1.54%
TXU SESCO A | 3.869%
TXU SESCO B | 1.54%
LR

## TDSP and ERCOT Variables
ERCOT |  |  |  | DSP = | AEP - TCC | AEP - TCC | AEP - TNC | AEP - TNC | CenterPoint | Nueces EC | Sharyland | TNMP | TNMP | TNMP | TNMP | TNMP | TXU | TXU | TXU SESCO | TXU SESCO
October 01, 2002 to September 30, 2003 |  |  |  | DLF Code = | A | B | A | B | D | B | A | A | B | C | D | E | A | B | A | B
Annual MWh | 282959594 |  |  | DSP AAL (MWh) = | 394.2 | 76.1 | 122.1 | 87.07 | 1514 | 6.47 | 0.4265 | 101.296 | 102.726 | 81.826 | 276.439 | 45.65 | 338 | 2240 | 26.617 | 4.563
Interval Count | 35040 |  |  | K factor = | 0.6394 | 0.4979 | 0.4572 | 0.7086 | 0.829 | 0.43 | 0.2642 | 0.3159 | 0.4094 | 0.4169 | 0.3577 | 0.3556 | 0.49 | 0.18 | 0.49 | 0.18
ERCOT AAL | 8075.3309 | MWh |  | ADLF = | 6.272% | 2.366% | 6.689% | 1.151% | 3.401% | 9.72% | 10.86% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54%
| Hourly |  | Per Interval
| MW Load |  | MWh
Example | 15000 |  | 3750 |  | 5.06% | 1.73% | 4.744% | 0.9714% | 3.089% | 6.752% | 6.582% | 4.974% | 3.056% | 2.276% | 2.421% | 2.744% | 2.813% | 0.8636% | 2.813% | 0.8636%
Results: | 20000 |  | 5000 |  | 5.41% | 1.913% | 5.306% | 1.023% | 3.18% | 7.61% | 7.82% | 5.805% | 3.465% | 2.575% | 2.787% | 3.162% | 3.118% | 1.059% | 3.118% | 1.059%
| 25000 |  | 6250 |  | 5.76% | 2.097% | 5.868% | 1.075% | 3.27% | 8.468% | 9.057% | 6.636% | 3.873% | 2.874% | 3.154% | 3.58% | 3.424% | 1.255% | 3.424% | 1.255%
| 30000 |  | 7500 |  | 6.11% | 2.281% | 6.43% | 1.127% | 3.36% | 9.325% | 10.29% | 7.467% | 4.282% | 3.172% | 3.521% | 3.998% | 3.729% | 1.45% | 3.729% | 1.45%
at ERCOT AAL | 32301.3235 |  | 8075.3309 |  | 6.272% | 2.366% | 6.689% | 1.151% | 3.401% | 9.72% | 10.86% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54%
| 40000 |  | 10000 |  | 6.811% | 2.649% | 7.554% | 1.231% | 3.54% | 11.04% | 12.77% | 9.13% | 5.099% | 3.77% | 4.255% | 4.834% | 4.34% | 1.841% | 4.34% | 1.841%
| 45000 |  | 11250 |  | 7.161% | 2.833% | 8.116% | 1.283% | 3.63% | 11.9% | 14.01% | 9.961% | 5.508% | 4.069% | 4.622% | 5.251% | 4.646% | 2.036% | 4.646% | 2.036%
| 50000 |  | 12500 |  | 7.511% | 3.017% | 8.678% | 1.335% | 3.72% | 12.76% | 15.24% | 10.79% | 5.917% | 4.368% | 4.989% | 5.669% | 4.951% | 2.232% | 4.951% | 2.232%
| 55000 |  | 13750 |  | 7.861% | 3.201% | 9.24% | 1.387% | 3.81% | 13.61% | 16.48% | 11.62% | 6.325% | 4.666% | 5.355% | 6.087% | 5.257% | 2.427% | 5.257% | 2.427%
| 60000 |  | 15000 |  | 8.211% | 3.384% | 9.802% | 1.439% | 3.9% | 14.47% | 17.72% | 12.45% | 6.734% | 4.965% | 5.722% | 6.505% | 5.562% | 2.623% | 5.562% | 2.623%
| 65000 |  | 16250 |  | 8.561% | 3.568% | 10.36% | 1.491% | 3.99% | 15.33% | 18.96% | 13.29% | 7.142% | 5.264% | 6.089% | 6.923% | 5.868% | 2.818% | 5.868% | 2.818%
| 70000 |  | 17500 |  | 8.911% | 3.752% | 10.93% | 1.542% | 4.08% | 16.19% | 20.19% | 14.12% | 7.551% | 5.563% | 6.456% | 7.341% | 6.173% | 3.014% | 6.173% | 3.014%
| 75000 |  | 18750 |  | 9.261% | 3.936% | 11.49% | 1.594% | 4.17% | 17.04% | 21.43% | 14.95% | 7.96% | 5.861% | 6.823% | 7.759% | 6.479% | 3.209% | 6.479% | 3.209%

## Calculations for Graph (hidden)
ERCOT |  |  |  |  | DSP = | AEP - TCC | AEP - TCC | AEP - TNC | AEP - TNC | CenterPoint | Nueces EC | Sharyland | TNMP | TNMP | TNMP | TNMP | TNMP | TXU | TXU | TXU SESCO | TXU SESCO
October 01, 2002 to Sept 30, 2003 |  |  |  |  | DLF Code = | A | B | A | B | D | A | A | A | B | C | D | E | A | B | A | B
Annual MWH | 282959594 |  |  |  | TDSP AAL (MWH) = | 394.2 | 76.1 | 122.1 | 87.07 | 1514 | 6.47 | 0.4265 | 101.296 | 102.726 | 81.826 | 276.439 | 45.65 | 338 | 2240 | 26.617 | 4.563
Interval Count | 35040 |  |  |  | K factor = | 0.6394 | 0.4979 | 0.4572 | 0.7086 | 0.829 | 0.43 | 0.2642 | 0.3159 | 0.4094 | 0.4169 | 0.3577 | 0.3556 | 0.49 | 0.18 | 0.49 | 0.18
ERCOT AAL | 8075.3309 | MWhs |  |  | ADLF = | 6.272% | 2.366% | 6.689% | 1.151% | 3.401% | 9.72% | 10.86% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54%
[5 empty] | slope | 7.0013e-07 | 3.6775e-07 | 1.124e-06 | 1.0384e-07 | 1.8005e-07 | 1.7152e-06 | 2.4747e-06 | 1.6625e-06 | 8.173e-07 | 5.9752e-07 | 7.3374e-07 | 8.3589e-07 | 6.1103e-07 | 3.9094e-07 | 6.1103e-07 | 3.9094e-07
[5 empty] | constant | 0.0401 | 0.011779 | 0.030581 | 0.008156 | 0.028194 | 0.041796 | 0.028703 | 0.024798 | 0.0183 | 0.013799 | 0.013199 | 0.0149 | 0.018963 | 0.002772 | 0.018963 | 0.002772
[5 empty] | 0.6681% | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16
|  |  | Graph Min | 10000 | 5.895% | 4.71% | 1.546% | 4.182% | 0.9194% | 2.999% | 5.895% | 5.345% | 4.142% | 2.647% | 1.977% | 2.054% | 2.326% | 2.507% | 0.6681% | 2.507% | 0.6681%
|  |  | Graph Max | 75000 | 17.04% | 9.261% | 3.936% | 11.49% | 1.594% | 4.17% | 17.04% | 21.43% | 14.95% | 7.96% | 5.861% | 6.823% | 7.759% | 6.479% | 3.209% | 6.479% | 3.209%
3.209%
|  |  | Inputs | 32293 | 9.719% | 6.271% | 2.365% | 6.688% | 1.151% | 3.401% | 9.719% | 10.86% | 7.849% | 4.469% | 3.31% | 3.689% | 4.189% | 3.869% | 1.54% | 3.869% | 1.54%
|  |  | Tab |  | 0.6681%: 3.31%
| 32293 | 0% | Another | 32293 | 3.401% | 6.271% | 2.365% | 6.688% | 1.151% | 3.401% | 9.719% | 10.86% | 7.849% | 4.469% | 3.31% | 3.689% | 4.189% | 3.869% | 1.54% | 3.869% | 1.54%
| 32293 | 16% | View |  | 0.6681%: 1.54%
| Hourly |  | Per Interval
| MW Load |  | MWHs
Example | 15000 |  | 3750 |  |  | 5.06% | 1.73% | 4.744% | 0.9714% | 3.089% | 6.752% | 6.582% | 4.974% | 3.056% | 2.276% | 2.421% | 2.744% | 2.813% | 0.8636% | 2.813% | 0.8636%
Results: | 20000 |  | 5000 |  |  | 5.41% | 1.913% | 5.306% | 1.023% | 3.18% | 7.61% | 7.82% | 5.805% | 3.465% | 2.575% | 2.787% | 3.162% | 3.118% | 1.059% | 3.118% | 1.059%
| 25000 |  | 6250 |  |  | 5.76% | 2.097% | 5.868% | 1.075% | 3.27% | 8.468% | 9.057% | 6.636% | 3.873% | 2.874% | 3.154% | 3.58% | 3.424% | 1.255% | 3.424% | 1.255%
| 30000 |  | 7500 |  |  | 6.11% | 2.281% | 6.43% | 1.127% | 3.36% | 9.325% | 10.29% | 7.467% | 4.282% | 3.172% | 3.521% | 3.998% | 3.729% | 1.45% | 3.729% | 1.45%
at ERCOT AAL | 32301.3235 |  | 8075.3309 |  |  | 6.272% | 2.366% | 6.689% | 1.151% | 3.401% | 9.72% | 10.86% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54%
| 40000 |  | 10000 |  |  | 6.811% | 2.649% | 7.554% | 1.231% | 3.54% | 11.04% | 12.77% | 9.13% | 5.099% | 3.77% | 4.255% | 4.834% | 4.34% | 1.841% | 4.34% | 1.841%
| 45000 |  | 11250 |  |  | 7.161% | 2.833% | 8.116% | 1.283% | 3.63% | 11.9% | 14.01% | 9.961% | 5.508% | 4.069% | 4.622% | 5.251% | 4.646% | 2.036% | 4.646% | 2.036%
| 50000 |  | 12500 |  |  | 7.511% | 3.017% | 8.678% | 1.335% | 3.72% | 12.76% | 15.24% | 10.79% | 5.917% | 4.368% | 4.989% | 5.669% | 4.951% | 2.232% | 4.951% | 2.232%
| 55000 |  | 13750 |  |  | 7.861% | 3.201% | 9.24% | 1.387% | 3.81% | 13.61% | 16.48% | 11.62% | 6.325% | 4.666% | 5.355% | 6.087% | 5.257% | 2.427% | 5.257% | 2.427%
| 60000 |  | 15000 |  |  | 8.211% | 3.384% | 9.802% | 1.439% | 3.9% | 14.47% | 17.72% | 12.45% | 6.734% | 4.965% | 5.722% | 6.505% | 5.562% | 2.623% | 5.562% | 2.623%
| 65000 |  | 16250 |  |  | 8.561% | 3.568% | 10.36% | 1.491% | 3.99% | 15.33% | 18.96% | 13.29% | 7.142% | 5.264% | 6.089% | 6.923% | 5.868% | 2.818% | 5.868% | 2.818%
| 70000 |  | 17500 |  |  | 8.911% | 3.752% | 10.93% | 1.542% | 4.08% | 16.19% | 20.19% | 14.12% | 7.551% | 5.563% | 6.456% | 7.341% | 6.173% | 3.014% | 6.173% | 3.014%
| 75000 |  | 18750 |  |  | 9.261% | 3.936% | 11.49% | 1.594% | 4.17% | 17.04% | 21.43% | 14.95% | 7.96% | 5.861% | 6.823% | 7.759% | 6.479% | 3.209% | 6.479% | 3.209%