## ADLF calculation
Summary of ADLF AND K factors
Texas Central Company (AEP-TCC)
a | b | c | d | e | f
SERV LEVL CODE | DLF CODE | ENERGY SYSTEM LOSS FACTOR* | ENERGY DISTRIB LOSS FACTOR | ERCOT ADLF | K factor
(Formula) |  | Divide by transmission loss factor |  | (d-1)/d
Secondary | A | 1.0977 | 1.0669 | 0.062715 | 0.63936
Primary | B | 1.0538 | 1.0242 | 0.023658 | 0.49795
Transmission | T | 1.0288 | 1
* From CPL 1998 System Loss Study
Texas North Company (AEP-TNC)
a | b | c | d | e | f
SERV LEVL CODE | DLF CODE | ENERGY SYSTEM LOSS FACTOR* | ENERGY DISTRIB LOSS FACTOR | ERCOT ADLF | K factor
(Formula) |  |  |  | (d-1)/d
Secondary | A | 1.1246 | 1.0717 | 0.066888 | 0.45715
PrImary* | B | 1.0779 | 1.0272 | 0.026486 | 0.70861
Transmission* | C | 1.0576 | 1.0079 | 0.0077966 | 0
Primary | B | 1.0616 | 1.0116 | 0.01151 | 0.70861
Transmission | T | 1.0494 | 1
* From WTU 1998 System Loss Study

## Loss ratios
Calculation of AEP TCC Electric Distribution Loss Factors
Ratio of No-Load and Load losses on primary and secondary systems
Energy Losses, MWh *
| Load | No-Load | Total
Dist. Substation | 21573.9522 | 166663.5957 | 188237.548
Primary Feeders | 178072.1141 | 31350.6415 | 209422.7556
Line Transformers | 21573.9522 | 166663.5957 | 188237.548
Residential Sec. Lines | 57378.5101 | 12396.4595 | 69774.9696
Total Primary & Sec | 278598.5286 | 377074.2925 | 655672.8211
Distribution System
Primary | 199646.0663 | 198014.2372 | 397660.3035
Secondary | 78952.4623 | 179060.0553 | 258012.5176
Total Primary & Sec | 278598.5286 | 377074.2925 | 655672.8211
Primary ratio | 0.50205 | 0.49795
Secondary ratio | 0.306 | 0.694
* From Summary of Conductor Information and Summary of Transformer Information in 1998 Loss Analysis
Calculation of AEP TNC Electric Distribution Loss Factors
Ratio of No-Load and Load losses on primary and secondary systems
Energy Losses, MWh *
| Load | No-Load | Total
Dist. Substation | 13101.2284 | 64979.2507 | 78080.4791
Primary Feeders | 83828.9249 | 3325.4634 | 87154.3883
Line Transformers | 11127.311 | 112221.2064 | 123348.5174
Residential Sec. Lines | 36895.4214 | 4562.4165 | 41457.8379
Total Primary & Sec | 144952.8858 | 185088.337 | 330041.2228
Distribution System
Primary | 96930.1533 | 68304.7141 | 165234.8674
Secondary | 48022.7324 | 116783.6229 | 164806.3553
Total Primary & Sec | 144952.8858 | 185088.337 | 330041.2228
Primary ratio | 0.58662 | 0.41338
Secondary ratio | 0.29139 | 0.70861
* From Summary of Conductor Information and Summary of Transformer Information in 1998 Loss Analysis

## Load_and_NoLoad
Calculation of AEP TCC Electric Distribution Loss Factors
Portion of Loss Factor Not Sensitive to Load
|  | Input Reqmt. | Energy Loss Fraction (3) |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter (1) |  |  |  | 12584687000
| Input to Sec. Level | 1.0669 |  |  | 13426740991.857
| Losses due to Sec. Sales |  | 0.306 | 0.694 |  | 257670583.8783 | 584383407.9787 | 842053991.857
Primary | Output (=Sec. Input) |  |  |  | 13426740991.857
| Input to Pri. Level due to Sec. | 1.0242 |  |  | 13752084352.8307
| Losses due to Sec. Sales |  | 0.50205 | 0.49795 |  | 163339215.9853 | 162004144.9884 | 325343360.9737
| Pri. Sales (1) |  |  |  | 2529402000
|  | 1.0242 |  |  | 2590691939.862
| Losses due to Pri. Sales |  | 0.50205 | 0.49795 |  | 30770723.8743 | 30519215.9877 | 61289939.862
| Total Input |  |  |  | 16342776292.6927
Distribution System
Losses, kWh
|  |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 421009799.8635 | 746387552.9671 | 1167397352.8307
|  |  |  | Primary Sales |  | 30770723.8743 | 30519215.9877 | 61289939.862
|  |  |  | Total |  | 451780523.7378 | 776906768.9549 | 1228687292.6927
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.36064 | 0.63936 | k for DLF Code A
|  |  |  | Primary Sales |  | 0.50205 | 0.49795 | k for DLF Code B
Calculation of AEP TNC Electric Distribution Loss Factors
Portion of Loss Factor Not Sensitive to Load
|  | Input Reqmt. | Energy Loss Fraction (3) |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter (1) |  |  |  | 3806750000
| Input to Sec. Level | 1.0717 |  |  | 4079629260.25
| Losses due to Sec. Sales |  | 0.58662 | 0.41338 |  | 160076556.1443 | 112802704.1057 | 272879260.25
Primary | Output (=Sec. Input) |  |  |  | 4079629260.25
| Input to Pri. Level due to Sec. | 1.0116 |  |  | 4127132463.3563
| Losses due to Sec. Sales |  | 0.29139 | 0.70861 |  | 13841903.1749 | 33661299.9315 | 47503203.1064
| Pri. Sales (1) |  |  |  | 2895162000
|  | 1.0116 |  |  | 2928873266.328
| Losses due to Pri. Sales |  | 0.29139 | 0.70861 |  | 9823086.7373 | 23888179.5907 | 33711266.328
| Total Input |  |  |  | 7056005729.6844
Distribution System
Losses, kWh
|  |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 173918459.3192 | 146464004.0372 | 320382463.3564
|  |  |  | Primary Sales |  | 9823086.7373 | 23888179.5907 | 33711266.328
|  |  |  | Total |  | 183741546.0565 | 170352183.6278 | 354093729.6844
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.54285 | 0.45715 | k for DLF Code A
|  |  |  | Primary Sales |  | 0.29139 | 0.70861 | k for DLF Code B