## Sub Loss Summary
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Substation Transformer Losses
ZONE | SERVICE AREA | VOLTAGE (kV) | NON-COINCIDENT PEAK LOAD (kW) | AVERAGE ANNUAL ENERGY LOSS (kWh) (1)
|  |  |  | NO-LOAD LOSS (kWh) | LOAD LOSS (kWh) | TOTAL LOSS (kWh)
ZONE 1 & 2 | Rural | 4.16 | 28060 | 512898 | 282312.4651 | 795210.4651
ZONE 1 & 2 | Rural | 12.5 | 69945 | 1899991.44 | 655245.738 | 2555237.178
ZONE 1 & 2 | Rural | 22 | 131846 | 5288788.68 | 2099402.8162 | 7388191.4962
ZONE 1 & 2 | Rural | 25 | 17664 | 93732 | 483030.2921 | 576762.2921
ZONE 1 & 2 | Urban | 12.5 | 179600 | 1278346.8 | 3622192.5011 | 4900539.3011
ZONE 1 & 2 | Urban | 25 | 71410 | 711925.2 | 738538.2723 | 1450463.4723
ZONE 6 | Rural | 12.5 | 116352 | 1895664 | 2191583.0534 | 4087247.0534
ZONE 6 | Urban | 12.5 | 393083 | 4913484 | 7417329.748 | 12330813.748
ZONE 8 | Rural | 2.4 | 2304 | 239148 | 5898.9843 | 245046.9843
ZONE 8 | Rural | 4.16 | 7386 | 318864 | 31558.5734 | 350422.5734
ZONE 8 | Rural | 12.5 | 55047 | 1314770.88 | 565943.2507 | 1880714.1307
ZONE 8 | Rural | 25 | 11342 | 552720.96 | 58350.8786 | 611071.8386
TOTALS |  |  | 1084039 | 19020333.96 | 18151386.5733 | 37171720.5333
Notes:
(1) Totals do not include losses for Mobil #1 Substation [TAB North-Zone2] and Sycamore Substation
[TAB Central-Zone1]. Substations were not classified as Rural or Urban.

## North-Zone2
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Substation Transformer Losses
SUBSTATION NAME | TRANSFORMER LOCATION | SERVICE AREA | TRANSFORMER DATA SOURCE | TRANSFORMER RATING (MVA) | TRANSFORMER HIGH-SIDE VOLTAGE RATING (kV) | TRANSFORMER LOW-SIDE VOLTAGE RATING (kV) | TRANSFORMER PERCENT IMPEDANCE (%Z) | TRANSFORMER NO-LOAD LOSSES (kW) | TRANSFORMER LOAD LOSSES (kW) | TRANSFORMER BASE RATING (kVA) | SUMMER 2000 LOAD DATA SOURCE | NON-COINCIDENT PEAK LOAD (kW) | POWER FACTOR AT PEAK | LOOK-UP CODE | AVERAGE ANNUAL HOURLY DEMAND LOSS (kW) |  |  | AVERAGE ANNUAL ENERGY LOSS (kWh)
[15 empty] | NO-LOAD (1) LOSS (kW) | LOAD (2) (3) LOSS (kW) | TOTAL LOSS (kW) | NO-LOAD LOSS (kWh) | LOAD LOSS (kWh) | TOTAL LOSS (kWh)
Bryson |  | Rural | Lone Oak |  | 66 | 12.5 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 952 | 99.6% | Rural/12.5 | 3.3 | 2.6272 | 5.9272 | 28908 | 23014.0627 | 51922.0627
Bryson |  | Rural | Lone Oak |  | 66 | 12.5 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 952 | 99.6% | Rural/12.5 | 3.3 | 2.6272 | 5.9272 | 28908 | 23014.0627 | 51922.0627
Bryson |  | Rural | Lone Oak |  | 66 | 12.5 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 952 | 99.6% | Rural/12.5 | 3.3 | 2.6272 | 5.9272 | 28908 | 23014.0627 | 51922.0627
Olney Station #1 (4) | North | Rural | NCR Xfmr Loss.xls |  | 66 | 12.5 | 10.47 | 17 | 82.2 | 12000 | NTBU Station Load 2000.xls | 2880 | 98.7% | Rural/12.5 | 17 | 2.2092 | 19.2092 | 148920 | 19352.6936 | 168272.6936
Olney Station #2 | South | Rural | NCR Xfmr Loss.xls |  | 66 | 12.5 | 7.05 | 16 | 67.6 | 12000 | master01prs.xls | 7344 | 99.9% | Rural/12.5 | 16 | 11.5318 | 27.5318 | 140160 | 101018.2845 | 241178.2845
Graham |  | Rural | Petrolia |  | 66 | 12.5 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 744 | 99.9% | Rural/12.5 | 9.1 | 0.068126 | 9.1681 | 79716 | 596.7843 | 80312.7843
Climax #1 Dist. | North | Rural | Talco West Middle |  | 138 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 8100 | 98.7% | Rural/22 | 12.209 | 16.4486 | 28.6576 | 106950.84 | 144089.4561 | 251040.2961
Climax #2 Dist. | South | Rural | Talco West Middle |  | 138 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 9396 | 98.7% | Rural/22 | 12.209 | 22.1332 | 34.3422 | 106950.84 | 193886.7722 | 300837.6122
Krugerville |  | Rural | NCR Xfmr Loss.xls | 15 / 20 / 25 | 138 | 26.4 | 10.64 | 10.7 | 83.5 | 15000 | master01prs.xls | 17664 | 97.7% | Rural/25 | 10.7 | 55.1404 | 65.8404 | 93732 | 483030.2921 | 576762.2921
Nocona | East | Rural | Whitewright #1 |  | 66 | 12.5 | 7.27 | 12.648 | 21.785 | 7500 | master01prs.xls | 5832 | 99.9% | Rural/12.5 | 12.648 | 5.9995 | 18.6475 | 110796.48 | 52555.7838 | 163352.2638
Nocona | West | Rural | Whitewright #1 |  | 66 | 12.5 | 7.27 | 12.648 | 21.785 | 7500 | master01prs.xls | 6156 | 99.7% | Rural/12.5 | 12.648 | 6.7115 | 19.3595 | 110796.48 | 58792.695 | 169589.175
Nocona | Middle | Rural | Whitewright #1 |  | 66 | 12.5 | 7.27 | 12.648 | 21.785 | 7500 |  |  |  | Rural/12.5
Whitewright #1 |  | Rural | NCR Xfmr Loss.xls |  | 66 | 12.5 | 7.27 | 12.648 | 21.785 | 7500 | master01prs.xls | 5796 | 98.1% | Rural/12.5 | 12.648 | 6.1451 | 18.7931 | 110796.48 | 53831.3414 | 164627.8214
Whitewright #2 |  | Rural | Whitewright #1 |  | 66 | 12.5 | 7.27 | 12.648 | 21.785 | 7500 | master01prs.xls | 8100 | 98.1% | Rural/12.5 | 12.648 | 12.0017 | 24.6497 | 110796.48 | 105135.2825 | 215931.7625
Lone Oak |  | Rural | NCR Xfmr Loss.xls |  | 66 | 12.5 | 6.68 | 3.36 | 9.893 | 1250 | master01prs.xls | 756 | 98.1% | Rural/12.5 | 3.36 | 1.7092 | 5.0692 | 29433.6 | 14972.5229 | 44406.1229
Lone Oak |  | Rural | NCR Xfmr Loss.xls |  | 66 | 12.5 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 756 | 98.1% | Rural/12.5 | 3.3 | 1.7078 | 5.0078 | 28908 | 14960.4153 | 43868.4153
Lone Oak |  | Rural | NCR Xfmr Loss.xls |  | 66 | 12.5 | 6.77 | 3.3 | 9.849 | 1250 | master01prs.xls | 756 | 98.1% | Rural/12.5 | 3.3 | 1.7016 | 5.0016 | 28908 | 14905.9312 | 43813.9312
Leonard LTC |  | Rural | Whitewright #1 |  | 66 | 12.5 | 7.27 | 12.648 | 21.785 | 7500 | master01prs.xls | 3744 | 98.8% | Rural/12.5 | 12.648 | 2.528 | 15.176 | 110796.48 | 22144.927 | 132941.407
Leonard |  | Rural | Petrolia |  | 66 | 12.5 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 3888 | 99.4% | Rural/12.5 | 9.1 | 1.8792 | 10.9792 | 79716 | 16461.9861 | 96177.9861
Leonard #2 | Northern | Rural | Petrolia |  | 66 | 12.5 |  | 9.1 | 3.8 | 3750 |  |  |  | Rural/12.5
Princeton (4) |  | Rural | Petrolia |  | 22 | 12.5 |  | 9.1 | 3.8 | 2500 | NTBU Station Load 2000.xls | 2484 | 98.7% | Rural/12.5 | 9.1 | 1.7505 | 10.8505 | 79716 | 15333.9443 | 95049.9443
Trenton |  | Rural | Petrolia |  | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 1128 | 99.9% | Rural/4.16 | 9.1 | 0.1566 | 9.2566 | 79716 | 1371.7966 | 81087.7966
Blue Ridge 69 KV |  | Rural | NCR Xfmr Loss.xls | 3.75 / 4.69 / 5.25 | 66 | 22 | 7.26 | 4.5 | 13.5 | 3750 | master01prs.xls | 1896 | 98.7% | Rural/22 | 4.5 | 1.6102 | 6.1102 | 39420 | 14105.7122 | 53525.7122
Frontier |  | Rural | Petrolia |  | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 1584 | 99.1% | Rural/4.16 | 9.1 | 0.31381 | 9.4138 | 79716 | 2748.9417 | 82464.9417
Detroit (4) |  | Rural | NCR Xfmr Loss.xls |  | 22 | 4.16 | 5 | 1.15 | 3.85 | 333 | NTBU Station Load 2000.xls | 288 | 98.7% | Rural/4.16 | 1.15 | 1.3437 | 2.4937 | 10074 | 11770.756 | 21844.756
Detroit (4) |  | Rural | NCR Xfmr Loss.xls |  | 22 | 4.16 | 5 | 1.15 | 3.85 | 333 | NTBU Station Load 2000.xls | 288 | 98.7% | Rural/4.16 | 1.15 | 1.3437 | 2.4937 | 10074 | 11770.756 | 21844.756
Detroit (4) |  | Rural | NCR Xfmr Loss.xls |  | 22 | 4.16 | 5 | 1.15 | 3.85 | 333 | NTBU Station Load 2000.xls | 288 | 98.7% | Rural/4.16 | 1.15 | 1.3437 | 2.4937 | 10074 | 11770.756 | 21844.756
Red River County #1 | South | Rural | Olney Station #1 (North) |  | 66 | 22 | 10.47 | 17 | 82.2 | 12000 | master01prs.xls | 6768 | 98.2% | Rural/22 | 17 | 12.3249 | 29.3249 | 148920 | 107966.3639 | 256886.3639
Red River County #2 | North | Rural | Talco West Middle |  | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 |  |  |  | Rural/22
Red River County #3 |  | Rural | Talco West Middle |  | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 |  |  |  | Rural/22
Minter (4) |  | Rural | NCR Xfmr Loss.xls |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 500 | NTBU Station Load 2000.xls | 276 | 98.7% | Rural/12.5 | 1.4 | 0.76774 | 2.1677 | 12264 | 6725.4142 | 18989.4142
Minter (4) |  | Rural | NCR Xfmr Loss.xls |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 500 | NTBU Station Load 2000.xls | 276 | 98.7% | Rural/12.5 | 1.4 | 0.76774 | 2.1677 | 12264 | 6725.4142 | 18989.4142
Minter (4) |  | Rural | NCR Xfmr Loss.xls |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 500 | NTBU Station Load 2000.xls | 276 | 98.7% | Rural/12.5 | 1.4 | 0.76774 | 2.1677 | 12264 | 6725.4142 | 18989.4142
Bogata (4) |  | Rural | Minter |  | 22 | 4.16 | 5 | 1.4 | 5.4 | 833 | NTBU Station Load 2000.xls | 762 | 98.7% | Rural/4.16 | 1.4 | 2.1084 | 3.5084 | 12264 | 18469.7416 | 30733.7416
Bogata (4) |  | Rural | Minter |  | 22 | 4.16 | 5 | 1.4 | 5.4 | 833 | NTBU Station Load 2000.xls | 762 | 98.7% | Rural/4.16 | 1.4 | 2.1084 | 3.5084 | 12264 | 18469.7416 | 30733.7416
Bogata (4) |  | Rural | Minter |  | 22 | 4.16 | 5 | 1.4 | 5.4 | 833 | NTBU Station Load 2000.xls | 762 | 98.7% | Rural/4.16 | 1.4 | 2.1084 | 3.5084 | 12264 | 18469.7416 | 30733.7416
Talco (4) |  | Rural | Petrolia |  | 22 | 12.5 |  | 9.1 | 3.8 | 2500 | NTBU Station Load 2000.xls | 1701 | 98.7% | Rural/12.5 | 9.1 | 0.82083 | 9.9208 | 79716 | 7190.5039 | 86906.5039
Mobil #1 (4) |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 1000 | NTBU Station Load 2000.xls | 216 | 98.7% | Rural/12.5 | 1.4 | 0.11756 | 1.5176 | 12264 | 1029.7893 | 13293.7893
Mobil #1 (4) |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 1000 | NTBU Station Load 2000.xls | 216 | 98.7% | Rural/12.5 | 1.4 | 0.11756 | 1.5176 | 12264 | 1029.7893 | 13293.7893
Mobil #1 (4) |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 1000 | NTBU Station Load 2000.xls | 216 | 98.7% | Rural/12.5 | 1.4 | 0.11756 | 1.5176 | 12264 | 1029.7893 | 13293.7893
Talco West (#1) | Middle | Rural | NCR Xfmr Loss.xls |  | 138 | 12.5 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 2880 | 94.4% | Rural/12.5 | 12.209 | 2.2732 | 14.4822 | 106950.84 | 19913.035 | 126863.875
Talco West (#2) | East | Rural | NCR Xfmr Loss.xls |  | 12.5 | 22 | 5.25 | 2.862 | 16.443 | 5000 | master01prs.xls | 2160 | 97% | Rural/22 | 2.862 | 1.4825 | 4.3445 | 25071.12 | 12986.3322 | 38057.4522
Petrolia |  | Rural | NCR Xfmr Loss.xls |  | 66 | 12.5 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 3960 | 98.7% | Rural/12.5 | 9.1 | 1.9772 | 11.0772 | 79716 | 17320.4253 | 97036.4253
Petrolia Step-up |  | Rural | Minter |  | 22 | 12.7 | 5 | 1.4 | 5.4 | 1000 | NTBU Station Load 2000.xls | 0 | 0% | Rural/12.5
Petrolia Step-up |  | Rural | Minter |  | 22 | 12.7 | 5 | 1.4 | 5.4 | 1000 | NTBU Station Load 2000.xls | 0 | 0% | Rural/12.5
Petrolia Step-up |  | Rural | Minter |  | 22 | 12.7 | 5 | 1.4 | 5.4 | 1000 | NTBU Station Load 2000.xls | 0 | 0% | Rural/12.5
Pilot Point (4) |  | Rural | Petrolia |  | 22 | 12.47 |  | 9.1 | 3.8 | 3750 | NTBU Station Load 2000.xls | 3276 | 98.7% | Rural/12.5 | 9.1 | 1.3532 | 10.4532 | 79716 | 11853.7556 | 91569.7556
Pilot Point | Northern | Rural | Petrolia |  | 22 | 12.5 |  | 9.1 | 3.8 | 3750 |  |  |  | Rural/12.5
Saint Jo |  | Rural | Lone Oak |  | 66 | 4.16 | 6.77 | 3.3 | 9.885 | 833 | master01prs.xls | 816 | 98.8% | Rural/4.16 | 3.3 | 4.417 | 7.717 | 28908 | 38693.189 | 67601.189
Saint Jo |  | Rural | Lone Oak |  | 66 | 4.16 | 6.77 | 3.3 | 9.885 | 833 | master01prs.xls | 816 | 98.8% | Rural/4.16 | 3.3 | 4.417 | 7.717 | 28908 | 38693.189 | 67601.189
Saint Jo |  | Rural | Lone Oak |  | 66 | 4.16 | 6.77 | 3.3 | 9.885 | 833 | master01prs.xls | 816 | 98.8% | Rural/4.16 | 3.3 | 4.417 | 7.717 | 28908 | 38693.189 | 67601.189
Mobile | Northern | Rural | NCR Xfmr Loss.xls |  | 69 | 12.47 | [7 empty] | Rural/12.5
Climax, Spare |  | Rural | Talco West Middle |  | 138 | 22 | 7.79 | 12.209 | 30.223 | 7500 |  |  |  | Rural/22
Minter, Spare |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 333 |  |  |  | Rural/12.5
Minter, Spare |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 333 |  |  |  | Rural/12.5
Minter, Spare |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 333 |  |  |  | Rural/12.5
Exxon |  | Rural | Petrolia |  | 22 | 12.5 |  | 9.1 | 3.8 | 3750 |  |  |  | Rural/12.5
Mobil #2 |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 1000 |  |  |  | Rural/12.5
Mobil #2 |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 1000 |  |  |  | Rural/12.5
Mobil #2 |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 1000 |  |  |  | Rural/12.5
Mobil #2 |  | Rural | Minter |  | 22 | 12.5 | 5 | 1.4 | 5.4 | 1000 |  |  |  | Rural/12.5
TOTALS | [9 empty] | 214496 |  |  |  |  | 286.539 | 206.1227 | 492.6617 | 2510081.64 | 1805634.8372 | 4315716.4772
Notes:
(1) Annual No-Load Losses [Column O & Q] is based on transformer losses [Column I].
(2) Annual Load Losses [Column P & R] is based on transformer losses [Column J], the peak load [Column M], the annual interval average load factor [See Note #3], and power factor [Column N].
(3) Annual Interval Average Load Factor for Zones 1, 2 & 6 (Max-to-Avg Ratio) provided by TNMP = |  |  |  | 2.2
(4) Assumed power factor for peak substation loads not provided |  |  | 98.7%
(5) Substation transformers were not in-service.

## Lewisville-Zone2
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Substation Transformer Losses
SUBSTATION NAME | TRANSFORMER LOCATION | SERVICE AREA | TRANSFORMER DATA SOURCE | TRANSFORMER RATING (MVA) | TRANSFORMER HIGH-SIDE VOLTAGE RATING (kV) | TRANSFORMER LOW-SIDE VOLTAGE RATING (kV) | TRANSFORMER LOW-SIDE CONFIGURATION | TRANSFORMER PERCENT IMPEDANCE (%Z) | TRANSFORMER NO-LOAD LOSSES (kW) | TRANSFORMER LOAD LOSSES (kW) | TRANSFORMER BASE RATING (kVA) | SUMMER 2000 LOAD DATA SOURCE | NON-COINCIDENT PEAK LOAD (kW) | POWER FACTOR AT PEAK | LOOK-UP CODE | AVERAGE ANNUAL HOURLY DEMAND LOSS (kW) |  |  | AVERAGE ANNUAL ENERGY LOSS (kWh)
[16 empty] | NO-LOAD (2) LOSS (kW) | LOAD (3) (4) LOSS (kW) | TOTAL LOSS (kW) | NO-LOAD LOSS (kWh) | LOAD LOSS (kWh) | TOTAL LOSS (kWh)
West Substation | East | Urban | NCR Xfmr Loss.xls | 12/16/20 | 140.27 | 13.0/7.51 | GRDY | 8.44 | 17.8 | 57.15 | 12000 | master01prs.xls | 18180 | 98.7% | Urban/12.5 | 17.8 | 61.2047 | 79.0047 | 155928 | 536152.8519 | 692080.8519
West Substation | Middle | Urban | NCR Xfmr Loss.xls | 25/33.3/41.7 | 140.27 | 13.0/7.51 | GRDY | 12.74 | 16.47 | 98.69 | 25000 | master01prs.xls | 29320 | 98.6% | Urban/12.5 | 16.47 | 63.4665 | 79.9365 | 144277.2 | 555966.5451 | 700243.7451
West Substation | West | Urban | NCR Xfmr Loss.xls (1) | 25/33.3/41.7 | 140.27 | 13.0/7.51 | GRDY | 12.22 | 16.9 | 112.6 | 25000 | master01prs.xls | 26700 | 99.2% | Urban/12.5 | 16.9 | 59.3246 | 76.2246 | 148044 | 519683.5584 | 667727.5584
South Substation | East | Urban | NCR Xfmr Loss.xls | 25/33.3/41.7 | 140.27 | 13.0/7.51 | GRDY | 10.01 | 20 | 81.5 | 25000 | master01prs.xls | 32820 | 99.8% | Urban/12.5 | 20 | 64.1019 | 84.1019 | 175200 | 561532.7463 | 736732.7463
South Substation | West | Urban | NCR Xfmr Loss.xls (1) | 25/33.3/41.7 | 140.27 | 13.0/7.51 | GRDY | 9.94 | 27.26 | 102.4 | 25000 | master01prs.xls | 31830 | 99.8% | Urban/12.5 | 27.26 | 75.7547 | 103.0147 | 238797.6 | 663610.9741 | 902408.5741
TI Substation | North | Urban | NCR Xfmr Loss.xls (1) | 25/33.3/41.7 | 140.27 | 25.98/15.0 | GRDY | 12.74 | 16.47 | 98.69 | 25000 | master01prs.xls | 26260 | 96.1% | Urban/25 | 16.47 | 53.5936 | 70.0636 | 144277.2 | 469480.1397 | 613757.3397
TI Substation | South | Urban | West Substation (East) | 12/16/20 | 138 | 12.47/7.2 | GRDY | 8.44 | 17.8 | 57.15 | 12000 | master01prs.xls | 12660 | 98.3% | Urban/12.5 | 17.8 | 29.9221 | 47.7221 | 155928 | 262117.2143 | 418045.2143
Lake Pointe Substation | North | Urban | NCR Xfmr Loss.xls | 45/60/75 | 140.27 | 25.98/15.0 | GRDY | 10.04 | 32.4 | 130.6 | 45000 | master01prs.xls | 21930 | 98.2% | Urban/25 | 32.4 | 14.6201 | 47.0201 | 283824 | 128071.903 | 411895.903
Lake Pointe Substation | South | Urban | NCR Xfmr Loss.xls | 45/60/76 | 140.27 | 25.98/15.0 | GRDY | 10.04 | 32.4 | 130.6 | 45000 | master01prs.xls | 23220 | 99.1% | Urban/25 | 32.4 | 16.0943 | 48.4943 | 283824 | 140986.2297 | 424810.2297
Jones Substation | South | Urban | NCR Xfmr Loss.xls (1) | 25/33.3/41.7 | 140.7 | 13.0/7.51 | GRDY | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 28090 | 99.1% | Urban/12.5 | 29.7 | 59.7179 | 89.4179 | 260172 | 523128.6111 | 783300.6111
Jones Substation (5) | North (Future) | Urban | [12 empty] | Urban/
TOTALS | [10 empty] | 264000 |  |  |  |  | 227.2 | 497.8003 | 725.0003 | 1990272 | 4360730.7734 | 6351002.7734
Notes:
(1) Information provided had a base rating of 26 MVA.
(2) Annual No-Load Losses [Column P & R] is based on transformer losses [Column J].
(3) Annual Load Losses [Column Q & S] is based on transformer losses [Column K], the peak load [Column N], the annual interval average load factor [See Note #4], and power factor [Column O].
(4) Annual Interval Average Load Factor for Zones 1, 2 & 6 (Max-to-Avg Ratio) provided by TNMP = |  |  |  | 2.2
(5) Substation transformers were not in-service.

## Central-Zone1
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Substation Transformer Losses
SUBSTATION NAME | SERVICE AREA | TRANSFORMER DATA SOURCE | TRANSFORMER HIGH-SIDE VOLTAGE RATING (kV) | TRANSFORMER LOW-SIDE VOLTAGE RATING (kV) | TRANSFORMER PERCENT IMPEDANCE (%Z) | TRANSFORMER NO-LOAD LOSSES (kW) | TRANSFORMER LOAD LOSSES (kW) | TRANSFORMER BASE RATING (kVA) | SUMMER 2000 LOAD DATA SOURCE | NON-COINCIDENT PEAK LOAD (kW) | POWER FACTOR AT PEAK | LOOK-UP CODE | AVERAGE ANNUAL HOURLY DEMAND LOSS (kW) |  |  | AVERAGE ANNUAL ENERGY LOSS (kWh)
[13 empty] | NO-LOAD (1) LOSS (kW) | LOAD (2) (3) LOSS (kW) | TOTAL LOSS (kW) | NO-LOAD LOSS (kWh) | LOAD LOSS (kWh) | TOTAL LOSS (kWh)
Clifton #1-22 KV (#2) | Rural | Lone Oak | 66 | 22 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 1276.6667 | 99.7% | Rural/22 | 9.885 | 4.7152 | 14.6002 | 86592.6 | 41305.016 | 127897.616
Clifton #1-22 KV (#2) | Rural | Lone Oak | 66 | 22 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 1276.6667 | 99.7% | Rural/22 | 9.885 | 4.7152 | 14.6002 | 86592.6 | 41305.016 | 127897.616
Clifton #1-22 KV (#2) | Rural | Lone Oak | 66 | 22 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 1276.6667 | 99.7% | Rural/22 | 9.885 | 4.7152 | 14.6002 | 86592.6 | 41305.016 | 127897.616
Clifton #1-4 KV (#1) | Rural | Petrolia | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 3264 | 99.8% | Rural/4.16 | 3.8 | 1.3138 | 5.1138 | 33288 | 11509.109 | 44797.109
Clifton #2-4 KV (#1) | Rural | Petrolia | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 4138 | 99.6% | Rural/4.16 | 3.8 | 2.1201 | 5.9201 | 33288 | 18572.2612 | 51860.2612
Clifton #2-22 KV (#2) | Rural | Blue Ridge 69 KV | 66 | 22 | 7.26 | 4.5 | 13.5 | 3750 | master01prs.xls | 4061 | 97.7% | Rural/22 | 13.5 | 7.5392 | 21.0392 | 118260 | 66043.4132 | 184303.4132
Handley | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 6077 | 98.8% | Rural/22 | 30.223 | 9.2397 | 39.4627 | 264753.48 | 80939.5999 | 345693.0799
Lane's Chapel | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 500 |  |  |  | Rural/12.5
Lane's Chapel | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 500 |  |  |  | Rural/12.5
Lane's Chapel | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 500 |  |  |  | Rural/12.5
Hill County | Rural | Talco West Middle | 138 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 4824 | 100% | Rural/22 | 30.223 | 5.6834 | 35.9064 | 264753.48 | 49786.4394 | 314539.9194
Lake Whitney #1 | Rural | Petrolia | 66 | 12.5 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 1584 | 97.2% | Rural/12.5 | 3.8 | 0.32619 | 4.1262 | 33288 | 2857.461 | 36145.461
Lake Whitney #2 | Rural | Whitewright #1 | 66 | 12.5 | 7.27 | 12.648 | 21.785 | 7500 | master01prs.xls | 2976 | 99.7% | Rural/12.5 | 21.785 | 1.5685 | 23.3535 | 190836.6 | 13740.1666 | 204576.7666
Whitney-22 KV (#1) | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 6595 | 99.4% | Rural/22 | 30.223 | 10.751 | 40.974 | 264753.48 | 94178.8321 | 358932.3121
Whitney-22 KV (#2) | Rural | Blue Ridge 69 KV | 66 | 22 | 7.26 | 4.5 | 13.5 | 3750 | master01prs.xls | 4363 | 100% | Rural/22 | 13.5 | 8.3065 | 21.8065 | 118260 | 72765.0923 | 191025.0923
Whitney 4 KV | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 500 |  |  |  | Rural/4.16
Whitney 4 KV | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 500 |  |  |  | Rural/4.16
Whitney 4 KV | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 500 |  |  |  | Rural/4.16
Meridian 4 KV (#1) | Rural | Petrolia | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 2928 | 99.8% | Rural/4.16 | 3.8 | 1.0573 | 4.8573 | 33288 | 9261.5473 | 42549.5473
Meridian 22 KV (#2) | Rural | Blue Ridge 69 KV | 66 | 22 | 7.26 | 4.5 | 13.5 | 3750 | master01prs.xls | 4119 | 100% | Rural/22 | 13.5 | 7.4034 | 20.9034 | 118260 | 64853.9216 | 183113.9216
Walnut Springs 22 KV | Rural | Lone Oak | 66 | 22 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 1152 | 100% | Rural/22 | 9.885 | 3.8163 | 13.7013 | 86592.6 | 33430.5122 | 120023.1122
Walnut Springs 22 KV | Rural | Lone Oak | 66 | 22 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 1152 | 100% | Rural/22 | 9.885 | 3.8163 | 13.7013 | 86592.6 | 33430.5122 | 120023.1122
Walnut Springs 22 KV | Rural | Lone Oak | 66 | 22 | 6.77 | 3.3 | 9.885 | 1250 | master01prs.xls | 1152 | 100% | Rural/22 | 9.885 | 3.8163 | 13.7013 | 86592.6 | 33430.5122 | 120023.1122
Walnut Springs 12 KV | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 100 |  |  |  | Rural/12.5
Walnut Springs 12 KV | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 100 |  |  |  | Rural/12.5
Walnut Springs 12 KV | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 100 |  |  |  | Rural/12.5
Valley Mills | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 6322 | 99.4% | Rural/22 | 30.223 | 9.8794 | 40.1024 | 264753.48 | 86543.1471 | 351296.6271
Crawford | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 333 |  |  |  | Rural/12.5
Crawford | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 333 |  |  |  | Rural/12.5
Crawford | Rural | Minter | 22 | 12.5 | 5 | 1.4 | 5.4 | 333 |  |  |  | Rural/12.5
Coryell County #1 | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 6048 | 99.3% | Rural/22 | 30.223 | 9.0598 | 39.2828 | 264753.48 | 79363.6326 | 344117.1126
Coryell County #2 | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 3600 | 99.9% | Rural/22 | 30.223 | 3.1715 | 33.3945 | 264753.48 | 27782.447 | 292535.927
Gatesville #1 | Rural | Petrolia | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 2966 | 100% | Rural/4.16 | 3.8 | 1.0805 | 4.8805 | 33288 | 9465.5266 | 42753.5266
Gatesville #2-4 KV | Rural | Petrolia | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 2966 | 100% | Rural/4.16 | 3.8 | 1.0805 | 4.8805 | 33288 | 9465.5266 | 42753.5266
Gatesville #2-22 KV | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 6710 | 99.2% | Rural/22 | 30.223 | 11.1741 | 41.3971 | 264753.48 | 97885.4554 | 362638.9354
State School (Hilltop) | Rural | Petrolia | 22 | 4.16 |  | 9.1 | 3.8 | 3750 |  |  |  | Rural/4.16
Sycamore | Rural | Olney Station #1 (North) | 66 | 22 | 10.47 | 17 | 82.2 | 9600 | master01prs.xls | 5400 | 99.9% | Rural/22 | 82.2 | 11.8458 | 94.0458 | 720072 | 103768.9256 | 823840.9256
Mountain View | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 667 |  |  |  | Rural/4.16
Mountain View | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 667 |  |  |  | Rural/4.16
Mountain View | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 667 |  |  |  | Rural/4.16
Hamilton #2 | Rural | Blue Ridge 69 KV | 66 | 22 | 7.26 | 4.5 | 13.5 | 3750 | master01prs.xls | 3355 | 99.8% | Rural/22 | 13.5 | 4.9314 | 18.4314 | 118260 | 43199.2916 | 161459.2916
Hamilton #1 | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 4680 | 96.8% | Rural/22 | 30.223 | 5.7086 | 35.9316 | 264753.48 | 50007.7669 | 314761.2469
Hamilton County | Rural | Blue Ridge 69 KV | 66 | 22 | 7.26 | 4.5 | 13.5 | 3750 | master01prs.xls | 4584 | 97.3% | Rural/22 | 13.5 | 9.6853 | 23.1853 | 118260 | 84843.035 | 203103.035
Hico | Rural | Petrolia | 66 | 4.16 |  | 9.1 | 3.8 | 3750 | master01prs.xls | 3488 | 99.9% | Rural/4.16 | 3.8 | 1.4973 | 5.2973 | 33288 | 13116.6963 | 46404.6963
Glen Rose #1 | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 5933 | 99.1% | Rural/22 | 30.223 | 8.7537 | 38.9767 | 264753.48 | 76682.7815 | 341436.2615
Glen Rose #2 | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 8064 | 99.9% | Rural/22 | 30.223 | 15.9134 | 46.1364 | 264753.48 | 139401.2062 | 404154.6862
Glen Rose #3 | Rural | Talco West Middle | 66 | 22 | 7.79 | 12.209 | 30.223 | 7500 | master01prs.xls | 6912 | 99.7% | Rural/22 | 30.223 | 11.7384 | 41.9614 | 264753.48 | 102828.5264 | 367582.0064
Iredell | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 200 |  |  |  | Rural/4.16
Iredell | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 200 |  |  |  | Rural/4.16
Iredell | Rural | Detroit | 22 | 4.16 | 5 | 1.15 | 3.85 | 200 |  |  |  | Rural/4.16
Thurber 12 KV | Rural | Lone Oak | 66 | 12.5 | 6.77 | 3.3 | 9.885 | 833 |  |  |  | Rural/12.5
Thurber 12 KV | Rural | Lone Oak | 66 | 12.5 | 6.77 | 3.3 | 9.885 | 833 |  |  |  | Rural/12.5
Thurber 12 KV | Rural | Lone Oak | 66 | 12.5 | 6.77 | 3.3 | 9.885 | 833 |  |  |  | Rural/12.5
Thurber 22 KV | Rural | Blue Ridge 69 KV | 66 | 22 | 7.26 | 4.5 | 13.5 | 3750 | master01prs.xls | 4593 | 99.6% | Rural/22 | 13.5 | 9.2795 | 22.7795 | 118260 | 81288.0812 | 199548.0812
TOTALS | [7 empty] | 168999 |  |  |  |  | 603.348 | 195.7028 | 799.0508 | 5285328.48 | 1714356.4742 | 6999684.9542
Notes:
(1) Annual No-Load Losses [Column M & O] is based on transformer losses [Column G].
(2) Annual Load Losses [Column N & P] is based on transformer losses [Column H], the peak load [Column K], the annual interval average load factor [See Note #3], and power factor [Column L].
(3) Annual Interval Average Load Factor for Zones 1, 2 & 6 (Max-to-Avg Ratio) provided by TNMP = |  |  |  |  | 2.2
(4) Substation transformers were not in-service.

## Gulf Coast-Zone6
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Substation Transformer Losses
SUBSTATION NAME | TRANSFORMER LOCATION | SERVICE AREA | TRANSFORMER DATA SOURCE | TRANSFORMER RATING (MVA) | TRANSFORMER HIGH-SIDE VOLTAGE RATING (kV) | TRANSFORMER LOW-SIDE VOLTAGE RATING (kV) | TRANSFORMER PERCENT IMPEDANCE (%Z) | TRANSFORMER NO-LOAD LOSSES (kW) | TRANSFORMER LOAD LOSSES (kW) | TRANSFORMER BASE RATING (kVA) | SUMMER 2000 LOAD DATA SOURCE | NON-COINCIDENT PEAK LOAD (kW) | POWER FACTOR AT PEAK | LOOK-UP CODE | AVERAGE ANNUAL HOURLY DEMAND LOSS (kW) |  |  | AVERAGE ANNUAL ENERGY LOSS (kWh)
[15 empty] | NO-LOAD (1) LOSS (kW) | LOAD (2) (3) LOSS (kW) | TOTAL LOSS (kW) | NO-LOAD LOSS (kWh) | LOAD LOSS (kWh) | TOTAL LOSS (kWh)
Angleton (5) | East | Rural | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 16560 | 98.5% | Rural/12.5 | 17.8 | 50.9893 | 68.7893 | 155928 | 446666.49 | 602594.49
Angleton (5) | Middle | Rural | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 22800 | 97.9% | Rural/12.5 | 29.7 | 40.3137 | 70.0137 | 260172 | 353147.8887 | 613319.8887
Angleton (5) | West | Rural | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 24000 | 99.9% | Rural/12.5 | 29.7 | 42.8983 | 72.5983 | 260172 | 375788.7814 | 635960.7814
Brazoria (5) (6) | East | Rural | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 7344 | 100% | Rural/12.5 | 17.8 | 9.7296 | 27.5296 | 155928 | 85231.5731 | 241159.5731
Brazoria (5) (6) | West | Rural | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 11520 | 98.3% | Rural/12.5 | 17.8 | 24.7759 | 42.5759 | 155928 | 217036.6565 | 372964.6565
Clemons Dome (5) (8) |  | Rural | Olney Station #1 (North) | 7.5 | 69 | 12.5 | 7.5 | 17 | 82.2 | 7500 | master01prs.xls | 2880 | 98.7% | Rural/12.5 | 17 | 5.6556 | 22.6556 | 148920 | 49542.8956 | 198462.8956
Dickinson (5) | East | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 18960 | 98.2% | Urban/12.5 | 29.7 | 27.7078 | 57.4078 | 260172 | 242720.2408 | 502892.2408
Dickinson (5) | West | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 25200 | 100% | Urban/12.5 | 29.7 | 47.2008 | 76.9008 | 260172 | 413478.9315 | 673650.9315
League City (5) | North | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 15408 | 100% | Urban/12.5 | 29.7 | 17.6458 | 47.3458 | 260172 | 154576.989 | 414748.989
League City (5) | South | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 14400 | 99.9% | Urban/12.5 | 29.7 | 15.4434 | 45.1434 | 260172 | 135283.9613 | 395455.9613
South Shore (5) | East | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 12 | 29.7 | 102.2 | 25000 | master01prs.xls | 11520 | 97.9% | Urban/12.5 | 29.7 | 10.2917 | 39.9917 | 260172 | 90155.4278 | 350327.4278
South Shore (5) | West | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 12 | 29.7 | 102.2 | 25000 | master01prs.xls | 21120 | 96.2% | Urban/12.5 | 29.7 | 35.825 | 65.525 | 260172 | 313826.7704 | 573998.7704
Alvin (5) | East | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 24000 | 99.5% | Urban/12.5 | 29.7 | 43.2439 | 72.9439 | 260172 | 378816.2719 | 638988.2719
Alvin (5) | Middle | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 18720 | 99.2% | Urban/12.5 | 29.7 | 26.4689 | 56.1689 | 260172 | 231867.9105 | 492039.9105
Alvin (5) | West | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 24960 | 99.7% | Urban/12.5 | 29.7 | 46.5851 | 76.2851 | 260172 | 408085.4863 | 668257.4863
Friendswood #1 (4) |  | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 9.25 | 29.7 | 102.2 | 25000 | master01prs.xls | 32400 | 99.1% | Urban/12.5 | 29.7 | 79.4495 | 109.1495 | 260172 | 695977.2044 | 956149.2044
Friendswood #2 (4) |  | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 9.29 | 29.7 | 102.2 | 25000 | master01prs.xls | 31680 | 99.4% | Urban/12.5 | 29.7 | 75.4998 | 105.1998 | 260172 | 661378.2076 | 921550.2076
Magnolia (4) | East | Urban | West Substation (East) | 12/16/20 | 138 | 12.5 | 8.43 | 17.8 | 57.15 | 12000 | master01prs.xls | 20160 | 99.7% | Urban/12.5 | 17.8 | 73.7602 | 91.5602 | 155928 | 646138.9281 | 802066.9281
Magnolia (4) | West | Urban | West Substation (East) | 12/16/20 | 138 | 12.5 | 8.5 | 17.8 | 57.15 | 12000 | master01prs.xls | 11869 | 96.9% | Urban/12.5 | 17.8 | 27.0652 | 44.8652 | 155928 | 237091.4395 | 393019.4395
Old Ocean (4) |  | Rural | Olney Station #1 (North) | 3.75 | 69 | 12.5 | 7 | 17 | 82.2 | 3750 | master01prs.xls | 2880 | 100% | Rural/12.5 | 17 | 22.038 | 39.038 | 148920 | 193052.6124 | 341972.6124
Sweeny (5) | North | Rural | Olney Station #1 (North) | 12/16/20 | 69 | 12.5 | 7.2 | 17 | 82.2 | 12000 | master01prs.xls | 8448 | 100% | Rural/12.5 | 17 | 18.518 | 35.518 | 148920 | 162217.8202 | 311137.8202
Sweeny (5) | South | Rural | Olney Station #1 (North) | 10 | 69 | 12.5 | 7.5 | 17 | 82.2 | 10000 | master01prs.xls | 6240 | 97.4% | Rural/12.5 | 17 | 15.3356 | 32.3356 | 148920 | 134339.7416 | 283259.7416
Freeway Park (5) | North | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 14801 | 99% | Urban/12.5 | 29.7 | 16.6135 | 46.3135 | 260172 | 145533.8545 | 405705.8545
Freeway Park (5) | South | Urban | Jones Substation (North) | 25/33/42 | 138 | 12.5 | 10 | 29.7 | 102.2 | 25000 | master01prs.xls | 22800 | 100% | Urban/12.5 | 29.7 | 38.6383 | 68.3383 | 260172 | 338471.4156 | 598643.4156
Heights (5) (6) (7) | East | Urban | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 8928 | 95.2% | Urban/12.5 | 17.8 | 15.8659 | 33.6659 | 155928 | 138985.545 | 294913.545
Heights (5) (6) (7) | West | Urban | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 6336 | 84.4% | Urban/12.5 | 17.8 | 10.1666 | 27.9666 | 155928 | 89059.5737 | 244987.5737
Lamarque (5) | East | Urban | Olney Station #1 (North) | 12/16/20 | 69 | 12.5 | 10 | 17 | 82.2 | 12000 | master01prs.xls | 13392 | 98.7% | Urban/12.5 | 17 | 47.7687 | 64.7687 | 148920 | 418453.6176 | 567373.6176
Lamarque (5) | West | Urban | Olney Station #1 (North) | 12/16/20 | 69 | 12.5 | 10 | 17 | 82.2 | 12000 | master01prs.xls | 10080 | 96.2% | Urban/12.5 | 17 | 28.4877 | 45.4877 | 148920 | 249552.354 | 398472.354
Northside (5) | East | Urban | Olney Station #1 (North) | 12/16/20 | 69 | 12.5 | 10 | 17 | 82.2 | 12000 | master01prs.xls | 12240 | 88.4% | Urban/12.5 | 17 | 49.7445 | 66.7445 | 148920 | 435761.6998 | 584681.6998
Northside (5) | West | Urban | Olney Station #1 (North) | 12/16/20 | 69 | 12.5 | 10 | 17 | 82.2 | 12000 | master01prs.xls | 15963 | 94.1% | Urban/12.5 | 17 | 74.6683 | 91.6683 | 148920 | 654094.551 | 803014.551
Tejas (5) | East | Urban | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 10226 | 86.1% | Urban/12.5 | 17.8 | 25.447 | 43.247 | 155928 | 222915.5896 | 378843.5896
Tejas (5) | West | Urban | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 7920 | 92.8% | Urban/12.5 | 17.8 | 13.1397 | 30.9397 | 155928 | 115103.7781 | 271031.7781
W Columbia Local (5) | East | Rural | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 6480 | 91.4% | Rural/12.5 | 17.8 | 9.0675 | 26.8675 | 155928 | 79431.5044 | 235359.5044
W Columbia Local (5) | West | Rural | West Substation (East) | 12/16/20 | 138 | 12.5 | 10 | 17.8 | 57.15 | 12000 | master01prs.xls | 7200 | 92.8% | Rural/12.5 | 17.8 | 10.8593 | 28.6593 | 155928 | 95127.0893 | 251055.0893
TOTALS | [9 empty] | 588250 |  |  |  |  | 777.3 | 1096.9079 | 1874.2079 | 6809148 | 9608912.8014 | 16418060.8014
Notes:
(1) Annual No-Load Losses [Column O & Q] is based on transformer losses [Column I].
(2) Annual Load Demand Losses [Column P & R] is based on transformer losses [Column J], the peak load [Column M], the annual interval average load factor [See Note #3], and power factor [Column N].
(3) Annual Interval Average Load Factor for Zones 1, 2 & 6 (Max-to-Avg Ratio) provided by TNMP = |  |  |  | 2.2
(4) Rating, High-side and Low-side voltage, and Impedance from distribution system model equipment database.
(5) Impedance from "Load Source Data."
(6) Transformers have a tertiary winding at 69 kV.
(7) Load data for two substation transformers was provided; however, transformer characteristics for only one was shown in spreadsheet (frm View Transformers.xls). Characteristics given were assumed for both transformers.
(8) Assumed power factor for peak substation loads not provided |  |  | 98.7%

## Wext TX-Zone8
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Estimated Distribution Substation Transformer Losses
SUBSTATION NAME | SERVICE AREA | TRANSFORMER DATA SOURCE | TRANSFORMER HIGH-SIDE VOLTAGE RATING (kV) | TRANSFORMER LOW-SIDE VOLTAGE RATING (kV) | TRANSFORMER PERCENT IMPEDANCE (%Z) | TRANSFORMER NO-LOAD LOSSES (kW) | TRANSFORMER LOAD LOSSES (kW) | TRANSFORMER BASE RATING (kVA) | SUMMER 2000 LOAD DATA SOURCE | NON-COINCIDENT PEAK LOAD (kW) | POWER FACTOR AT PEAK | LOOK-UP CODE | AVERAGE ANNUAL HOURLY DEMAND LOSS (kW) |  |  | AVERAGE ANNUAL ENERGY LOSS (kWh)
[13 empty] | NO-LOAD (1) LOSS (kW) | LOAD (2) (3) LOSSES (kW) | TOTAL LOSS (kW) | NO-LOAD LOSS (kWh) | LOAD LOSS (kWh) | TOTAL LOSS (kWh)
Airport (4) | Rural | Whitewright #1 | 69 | 12.5 | 7.8 | 12.648 | 21.785 | 7500 | master01prs.xls | 5256 | 96.4% | Rural/12.5 | 12.648 | 6.9776 | 19.6256 | 110796.48 | 61124.0109 | 171920.4909
Belding (4) | Rural | Petrolia | 69 | 12.5 | 6.9 | 9.1 | 3.8 | 3750 | master01prs.xls | 2336 | 94.2% | Rural/12.5 | 9.1 | 1.0071 | 10.1071 | 79716 | 8822.3665 | 88538.3665
C C Mitchell | Rural |  | 69 | 4.16 | [7 empty] | Rural/4.16
Ft Stockton 12kV (4) | Rural | Whitewright #1 | 69 | 12.5 | 7.59 | 12.648 | 21.785 | 7500 | master01prs.xls | 6472 | 99.9% | Rural/12.5 | 12.648 | 9.8514 | 22.4994 | 110796.48 | 86298.1012 | 197094.5812
Ft Stockton 4kV (4) | Rural | Petrolia | 69 | 4.16 | 6.7 | 9.1 | 3.8 | 3750 | master01prs.xls | 1704 | 99.8% | Rural/4.16 | 9.1 | 0.47744 | 9.5774 | 79716 | 4182.3399 | 83898.3399
Gomez (4) | Rural | Petrolia | 69 | 25 | 7 | 9.1 | 3.8 | 3750 | master01prs.xls | 1944 | 90.7% | Rural/25 | 9.1 | 0.75234 | 9.8523 | 79716 | 6590.5122 | 86306.5122
Harrell | Rural |  | 69 | 12.5 | [7 empty] | Rural/12.5
N M Mitchell | Rural |  | 69 | 4.16 | [7 empty] | Rural/4.16
Puckett (4) | Rural | Petrolia | 69 | 25 | 6.7 | 9.1 | 3.8 | 3750 | master01prs.xls | 1717 | 98% | Rural/25 | 9.1 | 0.50272 | 9.6027 | 79716 | 4403.821 | 84119.821
16th Street (4) | Rural | Whitewright #1 | 69 | 12.5 | 7.5 | 12.648 | 21.785 | 7500 | master01prs.xls | 8016 | 99.5% | Rural/12.5 | 12.648 | 15.2342 | 27.8822 | 110796.48 | 133451.8059 | 244248.2859
California (4) | Rural | Petrolia | 69 | 12.5 | 7.1 | 9.1 | 3.8 | 2500 | master01prs.xls | 2214 | 99.8% | Rural/12.5 | 9.1 | 1.8135 | 10.9135 | 79716 | 15886.1219 | 95602.1219
Kermit #1 4kV (4) | Rural | Petrolia | 69 | 4.16 | 7 | 9.1 | 3.8 | 3750 | master01prs.xls | 2304 | 98% | Rural/4.16 | 9.1 | 0.90521 | 10.0052 | 79716 | 7929.65 | 87645.65
Kermit #2 12kV (4) | Rural | Whitewright #1 | 69 | 12.5 | 7.5 | 12.648 | 21.785 | 7500 | master01prs.xls | 4284 | 99.6% | Rural/12.5 | 12.648 | 4.3424 | 16.9904 | 110796.48 | 38039.5567 | 148836.0367
Kermit #2 4kV (4) | Rural | Petrolia | 69 | 4.16 | 6.9 | 9.1 | 3.8 | 2500 | master01prs.xls | 1632 | 95.5% | Rural/4.16 | 9.1 | 1.0761 | 10.1761 | 79716 | 9426.6484 | 89142.6484
Keystone (4) | Rural | Petrolia | 69 | 12.5 | 6.9 | 9.1 | 3.8 | 3750 | master01prs.xls | 2664 | 100% | Rural/12.5 | 9.1 | 1.1623 | 10.2623 | 79716 | 10181.4507 | 89897.4507
Wickett (4) | Rural | Petrolia | 69 | 12.5 | 7.6 | 9.1 | 3.8 | 2000 | master01prs.xls | 810 | 99.1% | Rural/12.5 | 9.1 | 0.38465 | 9.4846 | 79716 | 3369.508 | 83085.508
Winkler Co. #6 (4) | Rural | Minter | 69 | 25 | 6.9 | 1.4 | 5.4 | 500 | master01prs.xls | 205 | 85.6% | Rural/25 | 1.4 | 0.75081 | 2.1508 | 12264 | 6577.0949 | 18841.0949
Cochise (4) | Rural | Petrolia | 69 | 25 | 7 | 9.1 | 3.8 | 3750 | master01prs.xls | 960 | 96.4% | Rural/25 | 9.1 | 0.16241 | 9.2624 | 79716 | 1422.7534 | 81138.7534
Flat Top (4) | Rural | Whitewright #1 | 69 | 25 | 7.16 | 12.648 | 21.785 | 7500 | master01prs.xls | 1584 | 96.5% | Rural/25 | 12.648 | 0.63242 | 13.2804 | 110796.48 | 5540.0148 | 116336.4948
Lone Star (4) | Rural | Petrolia | 69 | 25 | 8.14 | 9.1 | 3.8 | 3750 | master01prs.xls | 2340 | 82.2% | Rural/25 | 9.1 | 1.3272 | 10.4272 | 79716 | 11625.9728 | 91341.9728
Pecos Main #1 (4) | Rural | Petrolia | 69 | 12.5 | 7.1 | 9.1 | 3.8 | 3750 | master01prs.xls | 4356 | 96.1% | Rural/12.5 | 9.1 | 3.3649 | 12.4649 | 79716 | 29476.1115 | 109192.1115
Pecos Main #2 (4) | Rural | Petrolia | 69 | 12.5 | 7.3 | 9.1 | 3.8 | 3750 | master01prs.xls | 3096 | 93.5% | Rural/12.5 | 9.1 | 1.7956 | 10.8956 | 79716 | 15729.6806 | 95445.6806
Pecos Main 2.4kV (4) | Rural | Petrolia | 69 | 2.4 | 9.4 | 9.1 | 3.8 | 2500 | master01prs.xls | 768 | 98.4% | Rural/2.4 | 9.1 | 0.22447 | 9.3245 | 79716 | 1966.3281 | 81682.3281
Pecos Main 2.4kV (4) | Rural | Petrolia | 69 | 2.4 | 9.3 | 9.1 | 3.8 | 2500 | master01prs.xls | 768 | 98.4% | Rural/2.4 | 9.1 | 0.22447 | 9.3245 | 79716 | 1966.3281 | 81682.3281
Pecos Main 2.4kV (4) | Rural | Petrolia | 69 | 2.4 | 9.4 | 9.1 | 3.8 | 2500 | master01prs.xls | 768 | 98.4% | Rural/2.4 | 9.1 | 0.22447 | 9.3245 | 79716 | 1966.3281 | 81682.3281
Pyote (4) | Rural | Whitewright #1 | 69 | 25 | 9.5 | 12.648 | 21.785 | 7500 | master01prs.xls | 2592 | 78.9% | Rural/25 | 12.648 | 2.5332 | 15.1812 | 110796.48 | 22190.7095 | 132987.1895
Reeves C0. #4 (4) | Rural | Petrolia | 69 | 12.5 | 7.3 | 9.1 | 3.8 | 3750 | master01prs.xls | 2340 | 92.8% | Rural/12.5 | 9.1 | 1.0413 | 10.1413 | 79716 | 9121.7252 | 88837.7252
Stafford North (4) | Rural | Whitewright #1 | 69 | 12.5 | 7.04 | 12.648 | 21.785 | 7500 | master01prs.xls | 5448 | 98.9% | Rural/12.5 | 12.648 | 7.1225 | 19.7705 | 110796.48 | 62393.1359 | 173189.6159
Stafford South (4) | Rural | Whitewright #1 | 69 | 12.5 | 7.25 | 12.648 | 21.785 | 7500 | master01prs.xls | 6192 | 95.4% | Rural/12.5 | 12.648 | 9.8882 | 22.5362 | 110796.48 | 86620.432 | 197416.912
Toyah (4) | Rural | Minter | 69 | 12.5 | 6.5 | 1.4 | 5.4 | 500 |  |  |  | Rural/12.5
Toyah (4) | Rural | Minter | 69 | 12.5 | 6.5 | 1.4 | 5.4 | 500 |  |  |  | Rural/12.5
Toyah (4) | Rural | Minter | 69 | 12.5 | 6.1 | 1.4 | 5.4 | 500 |  |  |  | Rural/12.5
Worsham Field (4) | Rural | Petrolia | 69 | 12.5 | 7.1 | 9.1 | 3.8 | 3750 | master01prs.xls | 1440 | 90.3% | Rural/12.5 | 9.1 | 0.41647 | 9.5165 | 79716 | 3648.3014 | 83364.3014
Armadillo (5) | Rural | Minter | 69 | 12.5 | 4 | 1.4 | 5.4 | 500 | master01prs.xls | 123 | 98.7% | Rural/12.5 | 1.4 | 0.2033 | 1.6033 | 12264 | 1780.9422 | 14044.9422
Downie | Rural |  | 69 | 12.5 | [7 empty] | Rural/12.5
Sanderson (4) | Rural | Petrolia | 69 | 4.16 | 6.8 | 9.1 | 3.8 | 2500 | master01prs.xls | 1746 | 99.1% | Rural/4.16 | 9.1 | 1.1438 | 10.2438 | 79716 | 10019.9352 | 89735.9352
TOTALS | [7 empty] | 124500 |  |  |  |  | 276.884 | 75.5424 | 352.4264 | 2425503.84 | 661751.687 | 3087255.527
Notes:
(1) Annual No-Load Losses [Column M & O] is based on transformer losses [Column G].
(2) Annual Load Losses [Column N & P] is based on transformer losses [Column H], the peak load [Column K], the annual interval average load factor [See Note #3], and power factor [Column L].
(3) Annual Interval Average Load Factor for Zone 8 (Max-to-Avg Ratio) provided by TNMP = |  |  |  | 1.65
(4) Rating, High-side and Low-side voltage, and Impedance from distribution system model equipment database.
(5) Assumed power factor for peak substation loads not provided |  |  | 98.7%
(6) Substation transformers were not in-service.