## Attachment A - Summary
Calculation of TXU Electric Delivery Distribution Loss Factors
Per ERCOT Protocol Section 13.3.1.1 (Method 1)
Attachment A
|  | Input Requirement |  | TXU Electric
Service | DLF | Responsibility Factors |  | Loss
Level | Code | Total | Dist. Sys. | Factors | K Factor
|  | System * | Only | for ERCOT **
Secondary | A | 1.0684 | 1.0387 | 0.038684 | 0.49073
Primary | B | 1.0445 | 1.0154 | 0.015417 | 0.18083
Transmission | T | 1.0286
* From Docket 23640, Schedule FF-9.1
** Loss Factors as a Fraction of Sales by Voltage Level

## Attachment B - K Factors
Calculation of TXU Electric Distribution Loss Factors
Portion of Loss Factor Not Sensitive to Load
Attachment B
|  | Input Reqmt. (2) | Energy Loss Fraction (3) |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter (1) |  |  |  | 80915292116
| Input to Sec. Level | 1.0229 |  |  | 82769357965.7824
| Losses due to Sec. Sales |  | 0.29599 | 0.70401 |  | 548777591.3165 | 1305288258.4659 | 1854065849.7824
Primary | Output (=Sec. Input) |  |  |  | 82769357965.7824
| Input to Pri. Level due to Sec. | 1.0154 |  |  | 84045424151.3398
| Losses due to Sec. Sales |  | 0.81916 | 0.18084 |  | 1045304547.9655 | 230761637.5919 | 1276066185.5574
| Pri. Sales (1) |  |  |  | 11892200814
|  | 1.0154 |  |  | 12075544453.5251
| Losses due to Pri. Sales |  | 0.81916 | 0.18084 |  | 150188087.7381 | 33155551.787 | 183343639.5251
| Total Input |  |  |  | 96120968604.8649
Distribution System (excludes High Voltage)
Losses, kWh
|  |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 1594082139.282 | 1536049896.0578 | 3130132035.3398
|  |  |  | Primary Sales |  | 150188087.7381 | 33155551.787 | 183343639.5251
High Voltage Sales
|  |  |  | Total |  | 1744270227.0201 | 1569205447.8448 | 3313475674.8649
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.50927 | 0.49073 | K(A)
NOTES: |  |  |  | Primary Sales |  | 0.81916 | 0.18084 | K(B)
(1) | Sales Figures Updated to 12 Month Ending 12/31/2003
(2) | Extracted from FF-9.1.1 by Voltage Level (= Input / Output)
(3) | Docket 23640, Exhibit DAW-FF-1 (see next page)

## Attachment C - Loss Ratios
Calculation of TXU Electric Distribution Loss Factors
Portion of Loss Factor Not Sensitive to Load
Attachment C
Energy Losses, MWh *
| Load | No-Load | Total
Dist. Substation | 320993 | 225303 | 546296
Primary Feeders | 699585 |  | 699585
Line Transformers | 231169 | 1289755 | 1520924
Residential Sec. Lines | 108748 |  | 108748
Residential Services | 91400 |  | 91400
Commercial Services | 110930 |  | 110930
Total Primary & Sec | 1562825 | 1515058 | 3077883
Distribution System
Primary | 1020578 | 225303 | 1245881
Secondary | 542247 | 1289755 | 1832002
Total Primary & Sec | 1562825 | 1515058 | 3077883
Primary | 0.81916 | 0.18084
Secondary | 0.29599 | 0.70401
* From: TXU Electric Fuel Factor Filing - PUC Docket 23640,
Exhibit DAW-FF-1 & workpapers
(Based on allocation of Electrical Losses for 1999)

## Attachment D - AIAL
The Annual Interval Average Load
For The Entire DSP Service Area
Area Used To Calculate The Annual Loss Factor
Attachment D
The Annual Loss Factor Calculations were based on the following “At Meter” values:
Primary Sales | = | 11,835,446 MWh* in 8,760 Hours
| = | 1,351 MWh / Hour
| = | 338 MWh / Quarter-Hour
Secondary Sales | = | 78,485,653 MWh* in 8,760 Hours
| = | 8,960 MWh / Hour
| = | 2,240 MWh / Quarter-Hour
* Reference Schedule FF-9.1 found in TXU Electric Fuel Factor Docket 23640
(twelve-months ended 6/30/2002)