## Calculation Summary
NEC Loss Factor Calculations
Definition | Name | Value | Units | Equation
NEC total 2004 purchases | ATM | 235005 | MWH | na
NEC total 2004 sales | ATMS | 209111.845 | MWH | na
NEC 2004 Annual distribution loss factor | ADLF | 11.0181 | % | 100 x (1-(sales/purchase))
NEC member load leaving (sold) | NECL | 7005.687 | MWH | na
NEC member load gain (sold) | NECG | 85917 | MWH | na
Estimated 2004 combined usage (sold) | ATMC | 288023.158 | MWH | ATMS + (NECG/1000)-(NECL/1000)
NEC load system annual sales increase after gains | ASI | 137.7364 | % | 100*(ATMC/ATMS)
Primary metered annual total metered sales | PATMS | 11249.573 | MWH
Secondary metered annual total metered sales | SATMS | 276773.585 | MWH | ATMC-PATMS
Estimated combined Average Annual Load (sold) | AAL | 32.8794 | MWatt | ATMC/8760
NEC Average Annual Load (sold) | NAAL | 23.8712 | MWatt | ATMS/8760
NEC 2004 primary metered average annual load (sold) | NPAAL | 0.966 | MWatt
Primary metered combined annual average load | PAAL | 1.2842 | MWatt | PATMS/8760
Secondary metered combined annual average load | SAAL | 31.5952 | MWatt | SATMS/8760
Primary metered combined no load loss | PNLL | 11.7305 | kWatt | (NPAAL/NAAL)*(TNLL+CNLL)
Secondary metered dist xfmr NEC 2004 no load loss | SNLL | 682.046 | kWatt
Secondary metered combined no load loss | SCNLL | 1217.9798 | kWatt | ((ASI/100)*SNLL)+(SAAL/AAL)*(TNLL+CNLL)
NEC Distribution transformer load losses at NAAL | DTLL | 24.672 | kWatt
NEC Distribution transformer no load losses | DTNLL | 892.7996 | kWatt | (PNLL+SCNLL)*100/ASI
Primary metered annual distribution losses | PLOSS | 960.6033 | MWH | ((PAAL/AAL)*ASI*(ATM-ATMS-((DTLL+DTNLL)*(8760/1000)))
Primary metered annual distribution loss factor | PADLF | 7.8672 | % | 100*(PLOSS/(PATMS+PLOSS))
Primary metered K factor | PRIK | 0.10697 | (factor) | (PNLL*8760)/(PLOSS*1000)
Secondary metered annual distribution losses | SLOSS | 34703.7 | MWH | ASI*(ATM-ATMS)-PLOSS
Secondary metered annual distribution loss factor (2004) | SADLF | 10.7533 | % | 100*(SLOSS/(SLOSS+ATMC))
Secondary metered K factor | SECK | 0.30745 | (factor) | (SCNLL*8760)/(SLOSS*1000) | (Blue Curves)
Average ADLF over 4 years | AADL | 10.04 |  | averaged over 4 years
Distribution combined capacitive no load loss | CNLL | 35.416 | kWatt
STEC transformer and regulator no load loss | TNLL | 254.46 | kWatt
Applicable Secondary Metered K Factor | 0.87 | (Yellow Curves) |  | These factors best adjust the ERCOT profiles to provide load
Applicable Primary Metered K Factor | 0.35 |  |  | curves most closely approximating expected levels. ERCOT
approval is requested for these factors.