## ADLF Submittal to ERCOT
Sharyland Utilities, L.P.
McAllen, Texas
Purpose:
This documentation summarizes the calculations required to develop the Annual Distribution Loss Factors (ADLF) for Sharyland Utilities, L.P. (SULP), a Transmission Distribution Service Provider (TDSP), for submittal to ERCOT.
Results:
DLF Code: | A
ADLF = | 6.293%
K = | 0.2673
Methodology:
The TDSP loss factors were calculated based upon actual metered energy into the SULP System and actual metered data submitted to ERCOT and the REPs representing sales to the end consumer.
'No Load' losses were calculated based upon actual equipment purchases and estimated load factors.
System Factors:
Net Energy Purchases | 52614074 | kWh | Oct. 2003 - Sept. 2004
Net Energy Sales | 48727179 | kWh | Oct. 2003 - Sept. 2004
Net Losses | 3886895 | kWh | 7.977% | Net Losses as a percent of Sales
Load Losses | 3066880 | kWh | 6.294% | Load Losses as a percent of Sales
No Load Losses | 820015 | kWh | 1.683% | No Load Losses as a percent of Sales
K Factor |  |  | 0.26738 | No Load Losses / Load Losses