## System Loss Summary
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Summary of System Losses
12 MONTHS ENDING SEPTEMBER 30, 1999 (1) |  |  |  | SETTLEMENT INTERVAL DISTRIBUTION LOSS FACTOR (SILFi) | [8 empty] | ZONE 1 & 2 - CALANDER YEAR 1999 (1) | [8 empty] | ZONE 6 - CALANDER YEAR 1999 (1) | [8 empty] | ZONE 8 - CALANDER YEAR 1999 (1)
ANNUAL ENERGY PURCHASES (kWh) |  |  |  | SILFi = ADLF * [K+(1-K) * (SIELi/AAL)] | [8 empty] | ZONE 1 & 2 LOAD SUMMARY | [8 empty] | ZONE 6 LOAD SUMMARY | [8 empty] | ZONE 8 LOAD SUMMARY
Total Purchases | 6216045000 | [11 empty] | Adjusted Total Purchases (MWh) |  |  | 1787236 | [5 empty] | Adjusted Total Purchases (MWh) |  |  | 3138402 | [5 empty] | Adjusted Total Purchases (MWh) |  |  | 399890
less Market Sales Power | -117575000 |  |  | Where: | [8 empty] | Adjusted Rural Purchases (MWh) (4) |  |  | 887353.1288 | [5 empty] | Adjusted Rural Purchases (MWh) (4) |  |  | 716792.8185 | [5 empty] | Adjusted Rural Purchases (MWh) (4) |  |  | 399890
Net Generation | 1823698400 |  |  | i = | Interval | [7 empty] | Adjusted Urban Purchases (MWh) (4) |  |  | 899882.8712 | [5 empty] | Adjusted Urban Purchases (MWh) (4) |  |  | 2421609.1815 | [5 empty] | Adjusted Urban Purchases (MWh) (4) |  |  | 0
Total kWh @ Source | 7922168400 |  |  | SILF = | Settlement Interval Distribution Loss Factor | [7 empty] | Maximum Interval Load (MWh) |  |  | 464 | [5 empty] | Maximum Interval Load (MWh) |  |  | 693 | [5 empty] | Maximum Interval Load (MWh) |  |  | 77
Less Buy/Sell Contracts * | -2460980983 |  |  | ADLF = | Annual Distribution Loss Factor | [7 empty] | Annual Interval Average Load (MWh) |  |  | 204.0224 | [5 empty] | Annual Interval Average Load (MWh) |  |  | 358.2651 | [5 empty] | Annual Interval Average Load (MWh) |  |  | 45.6495
Adjusted Total kWh @ Source | 5461187417 |  |  | K = | Load/No-Load Sensitivity Factor | [7 empty] | Average Annual Load Factor |  |  | 43.97% | [5 empty] | Average Annual Load Factor |  |  | 51.7% | [5 empty] | Average Annual Load Factor |  |  | 59.29%
|  |  |  | SIEL = | Settlement Interval Estimated ERCOT System Load | [7 empty] | Max-to-Average Ratio |  |  | 2.2743 | [5 empty] | Max-to-Average Ratio |  |  | 1.9343 | [5 empty] | Max-to-Average Ratio |  |  | 1.6868
ANNUAL ENERGY SALES (kWh) |  |  |  | AAL = | Annual Interval Estimated ERCOT System Load
Total Sales | 7602226607
Less Buy/Sell Contracts * | -2460980983 |  | SYSTEM FACTORS |  |  |  |  | RURAL (4) | URBAN (4) | TOTAL |  | ZONE 1 & 2 FACTORS |  |  |  |  | RURAL (4) | URBAN (4) | TOTAL |  | ZONE 6 FACTORS |  |  |  |  | RURAL (4) | URBAN (4) | TOTAL |  | ZONE 8 FACTORS |  |  |  |  | RURAL (4) | URBAN (4) | TOTAL
Adjusted Sales | 5141245624 |  | AAL (kWh) = (Annual Purchases/(365 days * 24 hrs) = |  |  |  |  | 253009.857 | 370413.364 | 623423.221 |  | AAL (kWh) = (Annual Purchases/(365 days * 24 hrs) = |  |  |  |  | 101296.019 | 102726.355 | 204022.374 |  | AAL (kWh) = (Annual Purchases/(365 days * 24 hrs) = |  |  |  |  | 81825.664 | 276439.404 | 358265.068 |  | AAL (kWh) = (Annual Purchases/(365 days * 24 hrs) = |  |  |  |  | 45649.543 | 0 | 45649.543
Used By Company | 8757000 |  | ADLF = ADLFNo-Load + ADLFLoad = (Annual Losses/Purchases) = |  |  |  |  | 4.97% | 4% | 4.39% |  | ADLF = ADLFNo-Load + ADLFLoad = (Annual Losses/Purchases) = |  |  |  |  | 7.85% | 4.47% | 6.15% |  | ADLF = ADLFNo-Load + ADLFLoad = (Annual Losses/Purchases) = |  |  |  |  | 3.31% | 3.69% | 3.61% |  | ADLF = ADLFNo-Load + ADLFLoad = (Annual Losses/Purchases) = |  |  |  |  | 4.19% | 0% | 4.19%
Total kWh @ Sales | 5150002624 |  | ADLFNo-Load = ADLF * K = (Annual No-Load Losses/Purchases) = |  |  |  |  | 1.71% | 1.49% | 1.58% |  | ADLFNo-Load = ADLF * K = (Annual No-Load Losses/Purchases) = |  |  |  |  | 2.48% | 1.83% | 2.15% |  | ADLFNo-Load = ADLF * K = (Annual No-Load Losses/Purchases) = |  |  |  |  | 1.38% | 1.32% | 1.33% |  | ADLFNo-Load = ADLF * K = (Annual No-Load Losses/Purchases) = |  |  |  |  | 1.49% | 0% | 1.49%
|  |  | ADLFLoad = ADLF * (1-K) = (Annual Load Losses/Purchases) = |  |  |  |  | 3.26% | 2.51% | 2.81% |  | ADLFLoad = ADLF * (1-K) = (Annual Load Losses/Purchases) = |  |  |  |  | 5.37% | 2.64% | 4% |  | ADLFLoad = ADLF * (1-K) = (Annual Load Losses/Purchases) = |  |  |  |  | 1.93% | 2.38% | 2.27% |  | ADLFLoad = ADLF * (1-K) = (Annual Load Losses/Purchases) = |  |  |  |  | 2.7% | 0% | 2.7%
ANNUAL SYSTEM LOSSES (kWh) | 311184793 | (2) | K = ADLFNo-Load/ADLF = 1 - (ADLFLoad/ADLF) = |  |  |  |  | 34.41% | 37.25% | 35.99% |  | K = ADLFNo-Load/ADLF = 1 - (ADLFLoad/ADLF) = |  |  |  |  | 31.59% | 40.94% | 34.96% |  | K = ADLFNo-Load/ADLF = 1 - (ADLFLoad/ADLF) = |  |  |  |  | 41.69% | 35.77% | 36.84% |  | K = ADLFNo-Load/ADLF = 1 - (ADLFLoad/ADLF) = |  |  |  |  | 35.56% | 0% | 35.56%
TYPE |  | TOTAL SYSTEM | [8 empty] | ESTIMATED ZONE 1 & 2 | [8 empty] | ESTIMATED ZONE 6 | [8 empty] | ESTIMATED ZONE 8
|  | RURAL |  |  | URBAN |  |  | TOTAL |  |  | RURAL |  |  | URBAN |  |  | TOTAL |  |  | RURAL |  |  | URBAN |  |  | TOTAL |  |  | RURAL |  |  | URBAN |  |  | TOTAL
|  | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES | ESTIMATED ANNUAL ENERGY LOSSES (kWh) | PERCENT (3) OF TOTAL ENERGY PURCHASED | PERCENT OF TOTAL SYSTEM ENERGY LOSSES
Substation Transformer Losses
Core |  | 10249086.12 | 0.4624% | 3.294% | 6903756 | 0.2128% | 2.219% | 17152842.12 | 0.3141% | 5.512% | 7795410.12 | 0.8785% | 2.505% | 1990272 | 0.2212% | 0.6396% | 9785682.12 | 0.5475% | 3.145% | 1895664 | 0.2645% | 0.6092% | 4913484 | 0.2029% | 1.579% | 6809148 | 0.217% | 2.188% | 558012 | 0.1395% | 0.1793% | 0 | 0% | 0% | 558012 | 0.1395% | 0.1793%
Winding |  | 5749031.9225 | 0.2594% | 1.847% | 11778060.5215 | 0.363% | 3.785% | 17527092.444 | 0.3209% | 5.632% | 3519991.3114 | 0.3967% | 1.131% | 4360730.7734 | 0.4846% | 1.401% | 7880722.0848 | 0.4409% | 2.532% | 2191583.0534 | 0.3057% | 0.7043% | 7417329.748 | 0.3063% | 2.384% | 9608912.8014 | 0.3062% | 3.088% | 37457.5577 | 0.009367% | 0.01204% | 0 | 0% | 0% | 37457.5577 | 0.009367% | 0.01204%
Distribution Line Losses |  | 61682404.6078 | 2.783% | 19.82% | 57665328.9212 | 1.777% | 18.53% | 119347733.529 | 2.185% | 38.35% | 41483606.7208 | 4.675% | 13.33% | 14232584.8426 | 1.582% | 4.574% | 55716191.5634 | 3.117% | 17.9% | 10679374.125 | 1.49% | 3.432% | 43432744.0786 | 1.794% | 13.96% | 54112118.2036 | 1.724% | 17.39% | 9519423.762 | 2.381% | 3.059% | 0 | 0% | 0% | 9519423.762 | 2.381% | 3.059%
Distribution Transformer Losses
Core |  | 27558607.0614 | 1.243% | 8.856% | 41412326.8792 | 1.276% | 13.31% | 68970933.9406 | 1.263% | 22.16% | 14183755.3242 | 1.598% | 4.558% | 14454259.9764 | 1.606% | 4.645% | 28638015.3006 | 1.602% | 9.203% | 7981508.9062 | 1.114% | 2.565% | 26958066.9029 | 1.113% | 8.663% | 34939575.8091 | 1.113% | 11.23% | 5393342.831 | 1.349% | 1.733% | 0 | 0% | 0% | 5393342.831 | 1.349% | 1.733%
Winding |  | 172388.1595 | 0.007778% | 0.0554% | 247286.5199 | 0.007621% | 0.07947% | 419674.6794 | 0.007685% | 0.1349% | 82846.6809 | 0.009336% | 0.02662% | 206495.6541 | 0.02295% | 0.06636% | 289342.3351 | 0.01619% | 0.09298% | 48364.6123 | 0.006747% | 0.01554% | 40790.8657 | 0.001684% | 0.01311% | 89155.478 | 0.002841% | 0.02865% | 41176.8663 | 0.0103% | 0.01323% | 0 | 0% | 0% | 41176.8663 | 0.0103% | 0.01323%
Service and Secondary Line Losses |  | 4703826.627 | 0.2122% | 1.512% | 11637777.1575 | 0.3587% | 3.74% | 16341603.7845 | 0.2992% | 5.251% | 2589297.5411 | 0.2918% | 0.8321% | 4950878.2376 | 0.5502% | 1.591% | 7540175.7787 | 0.4219% | 2.423% | 896730.5798 | 0.1251% | 0.2882% | 6686898.9199 | 0.2761% | 2.149% | 7583629.4997 | 0.2416% | 2.437% | 1217798.5061 | 0.3045% | 0.3913% | 0 | 0% | 0% | 1217798.5061 | 0.3045% | 0.3913%
TOTALS |  | 110115344.4982 | 4.968% | 35.39% | 129644535.9993 | 3.995% | 41.66% | 239759880.4975 | 4.39% | 77.05% | 69654907.6984 | 7.85% | 22.38% | 40195221.4841 | 4.467% | 12.92% | 109850129.1825 | 6.146% | 35.3% | 23693225.2767 | 3.305% | 7.614% | 89449314.5151 | 3.694% | 28.74% | 113142539.7918 | 3.605% | 36.36% | 16767211.5231 | 4.193% | 5.388% | 0 | 0% | 0% | 16767211.5231 | 4.193% | 5.388%
Notes:
(1) Energy purchases and sales provided by TNMP.
(2) Based on adjusted energy purchases and sales.
(3) Based on estimated energy purchases by Service Area.
(4) Rural and Urban allocation based on "Service Area-to
-Zone" ratio calculated from substation demands.
Note on B18: TNMP User: excludes market purchases for Amoco

## Sub Loading
TEXAS - NEW MEXICO POWER CO.
Evaluation of System Losses
Summary of System Losses
ZONE | SERVICE AREA | NON-COINCIDENT PEAK LOAD (kW) | SERVICE AREA-TO-ZONE (%)
ZONE 1 & 2 | Rural | 247515 | 49.65%
ZONE 1 & 2 | Urban | 251010 | 50.35%
ZONE 6 | Rural | 116352 | 22.84%
ZONE 6 | Urban | 393083 | 77.16%
ZONE 8 | Rural | 76079 | 100%
ZONE 8 | Urban | 0 | 0%
RURAL |  | 439946 | 40.58%
URBAN |  | 644093 | 59.42%
TOTAL |  | 1084039 | 100%
Notes:
(1) Based on substation load data (See SPREADSHEET [Texas - NM Sub Xfmr Losses.xls], TAB [System - Summary])