## Start
ERCOT Distribution Loss Factor Estimates for 2007
1. Using the Spreadsheet to Calculate/Estimate Distribution Loss Factors
This spreadsheet calculates distribution loss factors (DLF) for all Distribution Service Providers (DSP) at various levels of ERCOT system load. From the "Inputs - Single DSP View" Tab, the user will select the DSP-DLF code and ERCOT load level of interest and the spreadsheet will calculate the resulting distribution loss factor. The graph displays the DSP loss factors at various ERCOT load levels as well as the level specified.
The "Inputs - Multiple DSP View" tab operates similar to the "Inputs - Single DSP View" tab and displays graphically all DSPs' DLF curves.
2. Examining the Calculations
This spreadsheet calculates the distribution loss factors for a selected TDSP based on the following formula:
SILFi = ADLF * [K + (1 - K) * (SIELi/AAL)]
Where: i = Interval
SILF = Settlement Interval Distribution Loss Factor
ADLF = Annual Distribution Loss Factor
K = constant representing the no load loss factor
SIEL = Settlement Interval ERCOT Load (ERCOT Day Ahead Forecasted MW Load divided by 4)
AAL = ERCOT Annual interval Average Load (ERCOT will use 8,794 MWh for year 2007 calculations)
Distribution Loss Factor Methodologies
The DLF Methodology approved for 2006 will be utilized for year 2007 until the new factors and methodology, based on the revised protocols, are approved and posted for year 2007.

## Inputs - Single DSP View
DSP DLF Code to Graph
Input ERCOT Load |  | AEP - TCC A | 1 | AEP - TCC A
|  | AEP - TCC B | 2 | AEP - TCC B
ERCOT MW Load | 34040 | AEP - TNC A | 3 | AEP - TNC A |  | TXU SESCO B
|  | AEP - TNC B | 4 | AEP - TNC B | 4 | TXU SESCO B
|  | CenterPoint D | 5 | CenterPoint D | 4 | AEP - TNC B
|  | CenterPoint E | 6 | CenterPoint E
DLF for DSP Selected to Graph |  | Nueces EC A | 7 | Nueces EC A
|  | Nueces EC B | 8 | Nueces EC B
AEP - TNC B | 1.14% | Sharyland | 9 | Sharyland
|  | TNMP A | 10 | TNMP A
|  | TNMP B | 11 | TNMP B
All DSP Distribution Loss Factors |  | TNMP C | 12 | TNMP C
|  | TNMP D | 13 | TNMP D
AEP - TCC A | 6.199% | TNMP E | 14 | TNMP E
AEP - TCC B | 2.327% | TXU A | 15 | TXU A
AEP - TNC A | 6.572% | TXU B | 16 | TXU B
AEP - TNC B | 1.14% | TXU SESCO A | 17 | TXU SESCO A
CenterPoint D | 3.63% | TXU SESCO B | 18 | TXU SESCO B
CenterPoint E | 1.222%
Nueces EC A | 7.705%
Nueces EC B | 9.998%
Sharyland | 6.144%
TNMP A | 7.677%
TNMP B | 4.385%
TNMP C | 3.248%
TNMP D | 3.614%
TNMP E | 4.103%
TXU A | 3.806%
TXU B | 1.499%
TXU SESCO A | 3.806%
TXU SESCO B | 1.499%

## Inputs - Multiple DSP View
DSP DLF Code to Graph
Input ERCOT Load |  | AEP - TCC A | 1 | 5 | AEP - TCC A
|  | AEP - TCC B | 2 | 6 | AEP - TCC B
ERCOT MW Load | 34040 | AEP - TNC A | 3 | 7 | AEP - TNC A |  | TXU SESCO B
|  | AEP - TNC B | 4 | 8 | AEP - TNC B | 7 | TXU SESCO B
|  | CenterPoint D | 5 | 9 | CenterPoint D
|  | CenterPoint E | 6 | 10 | CenterPoint E | 7 | Nueces EC A
DLF for DSP Selected |  | Nueces EC A | 7 | 11 | Nueces EC A
|  | Nueces EC B | 8 | 12 | Nueces EC B
Nueces EC A | 7.705% | Sharyland | 9 | 13 | Sharyland
|  | TNMP A | 10 | 14 | TNMP A
|  | TNMP B | 11 | 15 | TNMP B
All DSP Distribution Loss Factors |  | TNMP C | 12 | 16 | TNMP C
|  | TNMP D | 13 | 17 | TNMP D
AEP - TCC A | 6.199% | TNMP E | 14 | 18 | TNMP E
AEP - TCC B | 2.327% | TXU A | 15 | 19 | TXU A
AEP - TNC A | 6.572% | TXU B | 16 | 20 | TXU B
AEP - TNC B | 1.14% | TXU SESCO A | 17 | 21 | TXU SESCO A
CenterPoint D | 3.63% | TXU SESCO B | 18 | 22 | TXU SESCO B
CenterPoint E | 1.222%
Nueces EC A | 7.705%
Nueces EC B | 9.998%
Sharyland | 6.144%
TNMP A | 7.677%
TNMP B | 4.385%
TNMP C | 3.248%
TNMP D | 3.614%
TNMP E | 4.103%
TXU A | 3.806%
TXU B | 1.499%
TXU SESCO A | 3.806%
TXU SESCO B | 1.499%

## TDSP and ERCOT Variables
ERCOT |  |  |  | DSP = | AEP - TCC | AEP - TCC | AEP - TNC | AEP - TNC | CenterPoint | CenterPoint | Nueces EC | Nueces EC | Sharyland | TNMP | TNMP | TNMP | TNMP | TNMP | TXU-ED | TXU-ED | TXU SESCO | TXU SESCO
September 1, 2005 to August 31, 2006 |  |  |  | DLF Code = | A | B | A | B | D | E | A | B | A | A | B | C | D | E | A | B | A | B
Annual MWh | 308136142 |  |  | DSP AAL (MWh) = | 413.553 | 69.642 | 100.798 | 75.389 | 1517 | 98 | 1.28 | 31.6 | 1.4974 | 101.296 | 102.726 | 81.826 | 276.439 | 45.65 | 2240 | 338 | 26.617 | 4.563
Interval Count | 35040 |  |  | K factor = | 0.6394 | 0.4979 | 0.4572 | 0.7086 | 0.83 | 0.31 | 0.35 | 0.87 | 0.2673 | 0.3159 | 0.4094 | 0.4169 | 0.3577 | 0.3556 | 0.49 | 0.18 | 0.49 | 0.18
ERCOT AAL | 8793.8397 | MWh |  | ADLF = | 6.272% | 2.366% | 6.689% | 1.151% | 3.65% | 1.25% | 7.87% | 10.04% | 6.293% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.868% | 1.542% | 3.87% | 1.54%
| Hourly |  | Per Interval
| MW Load |  | MWh
Example | 15000 |  | 3750 |  | 4.974% | 1.684% | 4.606% | 0.9586% | 3.294% | 0.7553% | 4.936% | 9.291% | 3.648% | 4.77% | 2.956% | 2.203% | 2.331% | 2.641% | 2.737% | 0.8168% | 2.737% | 0.8168%
Results: | 20000 |  | 5000 |  | 5.296% | 1.853% | 5.122% | 1.006% | 3.382% | 0.8779% | 5.663% | 9.477% | 4.304% | 5.533% | 3.331% | 2.477% | 2.667% | 3.025% | 3.017% | 0.9965% | 3.017% | 0.9965%
| 25000 |  | 6250 |  | 5.617% | 2.022% | 5.639% | 1.054% | 3.471% | 1.001% | 6.39% | 9.662% | 4.959% | 6.297% | 3.706% | 2.752% | 3.004% | 3.409% | 3.297% | 1.176% | 3.297% | 1.176%
| 30000 |  | 7500 |  | 5.939% | 2.191% | 6.155% | 1.102% | 3.559% | 1.123% | 7.117% | 9.848% | 5.615% | 7.06% | 4.082% | 3.026% | 3.341% | 3.793% | 3.578% | 1.356% | 3.578% | 1.356%
at ERCOT AAL | 35175.3587 |  | 8793.8397 |  | 6.272% | 2.366% | 6.689% | 1.151% | 3.65% | 1.25% | 7.87% | 10.04% | 6.293% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.868% | 1.542% | 3.868% | 1.542%
| 40000 |  | 10000 |  | 6.582% | 2.529% | 7.187% | 1.197% | 3.735% | 1.368% | 8.572% | 10.22% | 6.925% | 8.587% | 4.832% | 3.575% | 4.015% | 4.56% | 4.139% | 1.715% | 4.139% | 1.715%
| 45000 |  | 11250 |  | 6.903% | 2.698% | 7.703% | 1.245% | 3.823% | 1.491% | 9.299% | 10.4% | 7.581% | 9.35% | 5.207% | 3.849% | 4.352% | 4.944% | 4.419% | 1.895% | 4.419% | 1.895%
| 50000 |  | 12500 |  | 7.225% | 2.866% | 8.219% | 1.292% | 3.912% | 1.614% | 10.03% | 10.59% | 8.236% | 10.11% | 5.583% | 4.123% | 4.689% | 5.328% | 4.699% | 2.075% | 4.699% | 2.075%
| 55000 |  | 13750 |  | 7.546% | 3.035% | 8.735% | 1.34% | 4% | 1.736% | 10.75% | 10.78% | 8.892% | 10.88% | 5.958% | 4.398% | 5.026% | 5.712% | 4.98% | 2.255% | 4.98% | 2.255%
| 60000 |  | 15000 |  | 7.868% | 3.204% | 9.251% | 1.388% | 4.088% | 1.859% | 11.48% | 10.96% | 9.547% | 11.64% | 6.333% | 4.672% | 5.363% | 6.096% | 5.26% | 2.434% | 5.26% | 2.434%
| 65000 |  | 16250 |  | 8.189% | 3.373% | 9.767% | 1.435% | 4.176% | 1.981% | 12.21% | 11.15% | 10.2% | 12.4% | 6.708% | 4.946% | 5.7% | 6.479% | 5.541% | 2.614% | 5.541% | 2.614%
| 70000 |  | 17500 |  | 8.51% | 3.542% | 10.28% | 1.483% | 4.264% | 2.104% | 12.93% | 11.33% | 10.86% | 13.17% | 7.084% | 5.221% | 6.036% | 6.863% | 5.821% | 2.794% | 5.821% | 2.794%
| 75000 |  | 18750 |  | 8.832% | 3.711% | 10.8% | 1.531% | 4.353% | 2.227% | 13.66% | 11.52% | 11.51% | 13.93% | 7.459% | 5.495% | 6.373% | 7.247% | 6.101% | 2.974% | 6.101% | 2.974%

## Calculations for Graph (hidden)
ERCOT |  |  |  |  | DSP = | AEP - TCC | AEP - TCC | AEP - TNC | AEP - TNC | CenterPoint | CenterPoint | Nueces EC | Nueces EC | Sharyland | TNMP | TNMP | TNMP | TNMP | TNMP | TXU-ED | TXU-ED | TXU SESCO | TXU SESCO
September 01, 2004 to August 31, 2005 |  |  |  |  | DLF Code = | A | B | A | B | D | E | A | B | A | A | B | C | D | E | A | B | A | B
Annual MWH | 308136142 |  |  |  | TDSP AAL (MWH) = | 413.553 | 69.642 | 100.798 | 75.389 | 1517 | 98 | 1.28 | 31.6 | 1.4974 | 101.296 | 102.726 | 81.826 | 276.439 | 45.65 | 2240 | 338 | 26.617 | 4.563
Interval Count | 35040 |  |  |  | K factor = | 0.6394 | 0.4979 | 0.4572 | 0.7086 | 0.83 | 0.31 | 0.35 | 0.87 | 0.2673 | 0.3159 | 0.4094 | 0.4169 | 0.3577 | 0.3556 | 0.4907 | 0.1808 | 0.49 | 0.18
ERCOT AAL | 8793.8397 | MWhs |  |  | ADLF = | 6.272% | 2.366% | 6.689% | 1.151% | 3.65% | 1.25% | 7.87% | 10.04% | 6.293% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54%
[5 empty] | slope | 6.4292e-07 | 3.377e-07 | 1.0322e-06 | 9.5351e-08 | 1.764e-07 | 2.452e-07 | 1.4543e-06 | 3.7106e-07 | 1.3108e-06 | 1.5267e-06 | 7.5052e-07 | 5.487e-07 | 6.7379e-07 | 7.6759e-07 | 5.6033e-07 | 3.5865e-07 | 5.611e-07 | 3.59e-07
[5 empty] | constant | 0.0401 | 0.011779 | 0.030581 | 0.008156 | 0.030295 | 0.003875 | 0.027545 | 0.087348 | 0.016821 | 0.024798 | 0.0183 | 0.013799 | 0.013199 | 0.0149 | 0.01899 | 0.0027843 | 0.018963 | 0.002772
0.6362%
[5 empty] | 0.6362% | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
|  |  | Graph Min | 10000 | 0.9109% | 4.653% | 1.516% | 4.09% | 0.9109% | 3.206% | 0.6327% | 4.209% | 9.106% | 2.993% | 4.007% | 2.581% | 1.929% | 1.994% | 2.258% | 2.459% | 0.6371% | 2.457% | 0.6362%
|  |  | Graph Max | 75000 | 1.531% | 8.832% | 3.711% | 10.8% | 1.531% | 4.353% | 2.227% | 13.66% | 11.52% | 11.51% | 13.93% | 7.459% | 5.495% | 6.373% | 7.247% | 6.102% | 2.968% | 6.105% | 2.97%
2.97%
2.97%
|  |  | Inputs | 34040 | 1.14% | 6.199% | 2.327% | 6.572% | 1.14% | 3.63% | 1.222% | 7.705% | 9.998% | 6.144% | 7.677% | 4.385% | 3.248% | 3.614% | 4.103% | 3.806% | 1.499% | 3.806% | 1.499%
|  |  | Tab |  | 0.6362% 0.6362%: 1.499%
1.499%
| 34040 | 0% | Another | 34040 | 7.705% | 6.199% | 2.327% | 6.572% | 1.14% | 3.63% | 1.222% | 7.705% | 9.998% | 6.144% | 7.677% | 4.385% | 3.248% | 3.614% | 4.103% | 3.806% | 1.499% | 3.806% | 1.499%
| 34040 | 16% | View |  | 0.6362% 0.6362%: 1.499%
1.499%
| Hourly |  | Per Interval
| MW Load |  | MWHs
Example | 15000 |  | 3750 |  |  | 4.974% | 1.684% | 4.606% | 0.9586% | 3.294% | 0.7553% | 4.936% | 9.291% | 3.648% | 4.77% | 2.956% | 2.203% | 2.331% | 2.641% | 2.74% | 0.8164% | 2.738% | 0.8157%
Results: | 20000 |  | 5000 |  |  | 5.296% | 1.853% | 5.122% | 1.006% | 3.382% | 0.8779% | 5.663% | 9.477% | 4.304% | 5.533% | 3.331% | 2.477% | 2.667% | 3.025% | 3.02% | 0.9957% | 3.019% | 0.9952%
| 25000 |  | 6250 |  |  | 5.617% | 2.022% | 5.639% | 1.054% | 3.471% | 1.001% | 6.39% | 9.662% | 4.959% | 6.297% | 3.706% | 2.752% | 3.004% | 3.409% | 3.3% | 1.175% | 3.299% | 1.175%
| 30000 |  | 7500 |  |  | 5.939% | 2.191% | 6.155% | 1.102% | 3.559% | 1.123% | 7.117% | 9.848% | 5.615% | 7.06% | 4.082% | 3.026% | 3.341% | 3.793% | 3.58% | 1.354% | 3.58% | 1.354%
at ERCOT AAL | 35175.3587 |  | 8793.8397 |  |  | 6.272% | 2.366% | 6.689% | 1.151% | 3.65% | 1.25% | 7.87% | 10.04% | 6.293% | 7.85% | 4.47% | 3.31% | 3.69% | 4.19% | 3.87% | 1.54% | 3.87% | 1.54%
| 40000 |  | 10000 |  |  | 6.582% | 2.529% | 7.187% | 1.197% | 3.735% | 1.368% | 8.572% | 10.22% | 6.925% | 8.587% | 4.832% | 3.575% | 4.015% | 4.56% | 4.14% | 1.713% | 4.141% | 1.713%
| 45000 |  | 11250 |  |  | 6.903% | 2.698% | 7.703% | 1.245% | 3.823% | 1.491% | 9.299% | 10.4% | 7.581% | 9.35% | 5.207% | 3.849% | 4.352% | 4.944% | 4.421% | 1.892% | 4.421% | 1.893%
| 50000 |  | 12500 |  |  | 7.225% | 2.866% | 8.219% | 1.292% | 3.912% | 1.614% | 10.03% | 10.59% | 8.236% | 10.11% | 5.583% | 4.123% | 4.689% | 5.328% | 4.701% | 2.072% | 4.702% | 2.072%
| 55000 |  | 13750 |  |  | 7.546% | 3.035% | 8.735% | 1.34% | 4% | 1.736% | 10.75% | 10.78% | 8.892% | 10.88% | 5.958% | 4.398% | 5.026% | 5.712% | 4.981% | 2.251% | 4.982% | 2.252%
| 60000 |  | 15000 |  |  | 7.868% | 3.204% | 9.251% | 1.388% | 4.088% | 1.859% | 11.48% | 10.96% | 9.547% | 11.64% | 6.333% | 4.672% | 5.363% | 6.096% | 5.261% | 2.43% | 5.263% | 2.431%
| 65000 |  | 16250 |  |  | 8.189% | 3.373% | 9.767% | 1.435% | 4.176% | 1.981% | 12.21% | 11.15% | 10.2% | 12.4% | 6.708% | 4.946% | 5.7% | 6.479% | 5.541% | 2.61% | 5.543% | 2.611%
| 70000 |  | 17500 |  |  | 8.51% | 3.542% | 10.28% | 1.483% | 4.264% | 2.104% | 12.93% | 11.33% | 10.86% | 13.17% | 7.084% | 5.221% | 6.036% | 6.863% | 5.821% | 2.789% | 5.824% | 2.79%
| 75000 |  | 18750 |  |  | 8.832% | 3.711% | 10.8% | 1.531% | 4.353% | 2.227% | 13.66% | 11.52% | 11.51% | 13.93% | 7.459% | 5.495% | 6.373% | 7.247% | 6.102% | 2.968% | 6.105% | 2.97%