## Attachment A- Summary
Attachment A
Summary of SILF equation coefficients- 2008
Texas Central Company (AEP-TCC)
a | b | c | d | e | f | g | h | I | J
SERV LEVL CODE | DLF CODE | ENERGY SYSTEM LOSS FACTOR* | ENERGY DISTRIB LOSS FACTOR | Average Dist Losses | Load Loss Factor | No-Load Loss Factor | F1 | F2 | F3
(Formula) |  | Divide by transmission loss factor |  | (d-1)/d | (Att C) | (Att C) | e*f |  | e*g
Secondary | A | 1.0978 | 1.0694 | 0.064885 | 0.45573 | 0.54427 | 0.02957 | 0 | 0.035315
Primary | B | 1.0614 | 1.0339 | 0.032834 | 0.65959 | 0.34041 | 0.021657 | 0 | 0.011177
Transmission | T | 1.0266 | 1
* From TCC 2005 System Loss Study
Texas North Company (AEP-TNC)
a | b | c | d | e | f | g | h | I | J
SERV LEVL CODE | DLF CODE | ENERGY SYSTEM LOSS FACTOR* | ENERGY DISTRIB LOSS FACTOR | Average Dist Losses | Load Loss Factor | No-Load Loss Factor | F1 | F2 | F3
(Formula) |  |  |  | (d-1)/d | (Att C) | (Att C) | e*f |  | e*g
Secondary | A | 1.1222 | 1.077 | 0.071467 | 0.39729 | 0.60271 | 0.028393 | 0 | 0.043074
Primary | B | 1.0751 | 1.0318 | 0.030833 | 0.28427 | 0.71573 | 0.0087649 | 0 | 0.022068
Transmission | T | 1.042 | 1
* From TNC 2005 System Loss Study

## Attachment B- Loss ratios
Attachment B
Calculation of AEP TCC Electric Distribution Loss Factors- 2008
Ratio of No-Load and Load losses on primary and secondary systems
Energy Losses, MWh *
| Load | No-Load | Total
Dist. Substation | 61523 | 151155 | 212678
Primary Feeders | 273409 | 21702 | 295111
Line Transformers | 33628 | 310129 | 343757
Residential Sec. Lines | 72195 | 12657 | 84852
Total Primary & Sec | 440755 | 495643 | 936398
Distribution System
Primary | 334932 | 172857 | 507789
Secondary | 105823 | 322786 | 428609
Total Primary & Sec | 440755 | 495643 | 936398
Primary ratio | 0.65959 | 0.34041
Secondary ratio | 0.2469 | 0.7531
* From Summary of Sales and Calculated Losses in 2005 Loss Analysis for TCC
Calculation of AEP TNC Electric Distribution Loss Factors- 2008
Ratio of No-Load and Load losses on primary and secondary systems
Energy Losses, MWh *
| Load | No-Load | Total
Dist. Substation | 20293 | 53320 | 73613
Primary Feeders | 48508 | 20309 | 68817
Line Transformers | 7190 | 89736 | 96926
Residential Sec. Lines | 29762 | 3302 | 33064
Total Primary & Sec | 105753 | 166667 | 272420
Distribution System
Primary | 68801 | 73629 | 142430
Secondary | 36952 | 93038 | 129990
Total Primary & Sec | 105753 | 166667 | 272420
Primary ratio | 0.48305 | 0.51695
Secondary ratio | 0.28427 | 0.71573
* From Summary of Sales and Calculated Losses in 2005 Loss Analysis for TNC

## Atchmt C- TCC&TNC
Attachment C
AEP TCC- Calculation of Electric Distribution Loss Factors- 2008
Portion of Loss Factor Not Sensitive to Load
|  | Input Reqmt. | Energy Loss Fraction |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales* | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter |  |  |  | 15332134000
| Input to Sec. Level | 1.0343 |  |  | 15857649303.3093
| Losses due to Sec. Sales |  | 0.2469 | 0.7531 |  | 129749039.1991 | 395766264.1101 | 525515303.3093
Primary | Output (=Sec. Input) |  |  |  | 15857649303.3093
| Input to Pri. Level due to Sec. | 1.0339 |  |  | 16395984781.858
| Losses due to Sec. Sales |  | 0.65959 | 0.34041 |  | 355080118.9102 | 183255359.6386 | 538335478.5487
| Pri. Sales |  |  |  | 2689188000
|  | 1.0339 |  |  | 2780480554.224
| Losses due to Pri. Sales |  | 0.65959 | 0.34041 |  | 60215557.5866 | 31076996.6374 | 91292554.224
| Total Input |  |  |  | 19176465336.082
Distribution System
| * Deliveries at the distribution primary |  |  |  |  | Losses, kWh
| and secondary level are from calendar 2005 |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 484829158.1093 | 579021623.7487 | 1063850781.858
|  |  |  | Primary Sales |  | 60215557.5866 | 31076996.6374 | 91292554.224
|  |  |  | Total |  | 545044715.6959 | 610098620.3861 | 1155143336.082
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.45573 | 0.54427
|  |  |  | Primary Sales |  | 0.65959 | 0.34041
AEP TNC- Calculation of Electric Distribution Loss Factors- 2008
Portion of Loss Factor Not Sensitive to Load
|  | Input Reqmt. | Energy Loss Fraction |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales* | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter |  |  |  | 3651478000
| Input to Sec. Level | 1.0438 |  |  | 3811273115.798
| Losses due to Sec. Sales |  | 0.48305 | 0.51695 |  | 77189242.1682 | 82605873.6298 | 159795115.798
Primary | Output (=Sec. Input) |  |  |  | 3811273115.798
| Input to Pri. Level due to Sec. | 1.0318 |  |  | 3932524958.704
| Losses due to Sec. Sales |  | 0.28427 | 0.71573 |  | 34468021.379 | 86783821.5269 | 121251842.906
| Pri. Sales |  |  |  | 2562797000
|  | 1.0318 |  |  | 2644329823.758
| Losses due to Pri. Sales |  | 0.28427 | 0.71573 |  | 23177174.425 | 58355649.333 | 81532823.758
| Total Input |  |  |  | 6576854782.462
Distribution System
| * Deliveries at the distribution primary |  |  |  |  | Losses, kWh
| and secondary level are from calendar 2005 |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 111657263.5473 | 169389695.1567 | 281046958.704
|  |  |  | Primary Sales |  | 23177174.425 | 58355649.333 | 81532823.758
|  |  |  | Total |  | 134834437.9723 | 227745344.4897 | 362579782.462
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.39729 | 0.60271
|  |  |  | Primary Sales |  | 0.28427 | 0.71573