## 1) General Information
CenterPoint Energy Distribution Loss Factor for 2009
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was revised in September, 2006.
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
AAL value for use in 2009 = 9,043 MWH
AAL value used in 2008 = 8,794 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = 0.016850
F2 = 0.001400
F3 = 0.017100
AAL for ERCOT (15 mins) = 9,043
For "E" Primary Customers
F1 = 0.011200
F2 = 0.000100
F3 = 0.001370
AAL for ERCOT (15 mins) = 9,043
Assumptions
Assume AAL for CNP corresponds to AAL for ERCOT
However, peak for CNP is proportionately greater than peak for ERCOT
Ratio of Peak to AAL
|  | CNP | ERCOT
|  | 1.9962 | 1.7214
Ratio of Peak to AAL for CNP is not proportional to ERCOT
| CNP Peak (15 mins) |  | 3464.25
| CNP AAL (15 mins) |  | 1735.3829
| ERCOT Peak (15mins) |  | 15567
| ERCOT AAL (15 mins) |  | 9043
See Tab 2 - ERCOT Load Comparison
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak. See Tab 3 - Loss Analysis.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 4) Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2007 as follows.
1. Substation Transformer Losses
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
This database contains test data for every substation transformer.
The total no-load losses was 18.586 MW, which is a slight decrease from the 20.295 MW used in 2006.
Also, the database provided the total "Load" losses for the transformers on the system at rated load.
This value was 49.203 MW at 15,269 MVA, which was also a slight decrease from the value use in 2006.
This resulted in a total of 67.789 MW of substation transformer losses at approximately 15,200 MW at CNP.
The constants in the system loss equations were adjusted to match this result. See Tab 3.
The result was a total overall decrease in losses for substation transformers as compared to 2006.
2. Primary Conductor Losses
The primary conductor losses for 2007 are considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
3. Distribution Transformer Losses
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers.
Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses.
Since the no load losses used in the TLM program were based on older/higher values from 1985 and the spreadsheet
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for no-load losses. The load losses from both methods were comparable.
The result was a decrease in no-load losses from 2006, and a slight decrease in load
losses from 2006. The constants in the system loss equation for distribution transformers were adjusted accordingly.
The no-load losses decreased from 133.297 MW to 120.235 MW. The load losses at peak decreased from 100.1 MW to 91.3 MW.
Total distribution transformer losses decreased from approximately 233.4 MW in 2006 to 211.534 MW at peak.
4. Secondary Conductor Losses
The secondary losses for 2007 are considered to be similar to the losses in 2006, so there is no change in the constants for
the system loss equations accordingly. CNP has not made any changes to our policy regarding the loading of secondary conductor.
5. AAL for ERCOT
The AAL for ERCOT was updated based on information from ERCOT. The new value for 2009 is 9,043 MWH for 15 minutes.
The loss calculations for CNP, as shown in items 1 - 4 above, will be the same for use in 2009 with the exception that, as stated
earlier, the % losses, and as a result DLF, will be increased an amount that is consistent the the higher peak loading at CNP. The
individual A and B constants for CNP will not be recalculated for 2009. See Tab 3.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were continually adjusted to get a curve fit in the most critical areas. See graphs in Tab 3 - Loss Analysis or in Tab 5 - Graphs.
Overall results:
|  |  |  | 2006* | 2007 | 2008 for use in 2009
For "E" Primary Customers |  |  | DLF at AAL | 1.33% | 1.265% | 1.267%
|  |  | DLF at ERCOT Peak | 2.05% | 1.963% | 2.018%
|  |  |  | 2006* | 2007 | 2008 for use in 2009
For "D" Secondary Customers |  |  | DLF at AAL | 3.75% | 3.48% | 3.535%
|  |  | DLF at ERCOT Peak | 4.21% | 3.967% | 4.034%
* Calculated losses for 2006. The K equation used in the previous protocols, called for a straight line equivalent which would have differed slightly.
The overall losses for primary customers for 2009 are comparable to 2007, and somewhat less than 2006.
The overall losses for secondary customers in 2009 are somewhat greater than in 2007, but less than 2006.
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-945-4162
or email at richard.moffatt@centerpointenergy.com.
CenterPoint Energy Distribution Loss Factor For 2009 R2.xls

## 2) ERCOT Load Comparison
ERCOT / CenterPont Energy Loading Comparison For 2005/2006 and information on 2008 AAL
Peak Load | 2006 |  |  |  | 2003
ERCOT peak (MW) = | 62429.5 | (on 8/17/2006 at 17:00) |  |  | 60095
Peak Interval = | 15607.37
CNP peak (MW) = | 13669 | (on 8/17/2006 at 16:31) |  |  | 13146 | 21.88% | = CNP peak relative to ERCOT peak
Peak interval = | 3417.25 | 21.9% | = CNP peak relative to ERCOT peak
Average Annual Load (AAL)
ERCOT Annual Total System MWH = | 308136141.9135 | (for 9/1/2005 - 8/31/2006)
Intervals per year = | 35040
AAL value = | 8794 | for 15 mins | 35176 | for 1 hour
Assume AAL (Average Annual Load) for CNP is proportional to peak in a manner that is similar to ERCOT
AAL for CNP would coorespond to | 1925.4555 | for 15 mins | 7701.822 | for 1 hour
New information for calculation of 2009 DLF
CenterPoint Energy | 2006 | 2007 | 2008 |  | Ratio of Peak to AAL
CNP Peak MW (one hour) | 13552 | 13857 | 13635
[5 empty] | CNP | ERCOT
CNP Peak (15 mins) |  | 3464.25 |  |  | 1.9962 | 1.7214
CNP MWH for year (2007) |  | 60807815.2698 |  |  | Ratio of Peak to AAL for CNP is not proportional to ERCOT
Hours in year |  | 8760
CNP AAL (one hour) |  | 6941.5314 |  |  | So the DLF will need to be adjusted accordingly
CNP AAL (15 mins) |  | 1735.3829
ERCOT |  | 2007 | 2008
ERCOT Peak (one hour) on 8/4/2008 |  |  | 62268
ERCOT Peak (15mins) on 8/4/2008 |  |  | 15567
ERCOT MWH for one year ((9/1/2007 - 8/31/2008) |  | 317743062 | MWH for year
Hours in year |  | 8784
ERCOT AAL (one hour) |  | 36172.9351
ERCOT AAL (15 mins) |  | 9043.2338
AAL for ERCOT to be used for 2009 |  |  | 9043 | AAL for 15 Mins
Assume AAL for CNP corresponds to AAL for ERCOT
However, peak for CNP is proportionately greater than peak for ERCOT
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so 2008 % Losses above AAL (and DLF) are proportionately increased
See Tab 3 - Loss Analysis.

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 3) Loss Analysis 2008
|  | CenterPoint Energy Distribution Loss Factor For 2009 R2.xls | [14 empty] | Using F1, F2 & F3 Coefficients
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  | 2007 | Secondary | 2007 | 2007 | 2008 | 2009 | 2009 | 2007 | 2008 | Adjustment for % Losses |  |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri |  | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL |  |  |  |  | No Load Losses | [8 empty] | No Load Losses |  | 0% |  |  |  | 0%
[5 empty] | Primary Customers | [8 empty] | Secondary Customers
|  |  |  | 50 | 18.5865 | 31.4135 | 0.0011244 | 18.5877 | 37.18% | 31.4123 | 120.2355 | -88.8232 | 0.0027965 | 138.826 | 277.7% | 277.7%
|  |  |  | 135 | 18.5899 | 116.4101 | 0.01544 | 18.6053 | 13.78% | 116.3947 | 120.242 | -3.8473 | 5.2466e-06 | 138.8473 | 102.8% | 102.8%
|  |  |  | 500 | 18.6393 | 481.3607 | 0.26401 | 18.9033 | 3.781% | 481.0967 | 120.3539 | 360.7428 | 0.046128 | 139.3033 | 27.86% | 27.86%
1302.7387 | 5210.9549 |  | 250 | 1000 | 18.799 | 981.201 | 1.097 | 19.896 | 1.99% | 980.104 | 120.7287 | 859.3754 | 0.26178 | 140.8864 | 14.09% | 14.09%
3126.573 | 12506.2918 | 1 | 600 | 2400 | 19.8129 | 2380.1871 | 6.455 | 26.2679 | 1.094% | 2373.7321 | 123.1306 | 2250.6015 | 1.7954 | 151.1939 | 6.3% | 6.3% | 5.668% | 0.7935% | 1.094% | 1.094% |  |  |  | 26.2679 | 151.1939
3647.6685 | 14590.6738 | 2 | 700 | 2800 | 20.2559 | 2779.7441 | 8.804 | 29.06 | 1.038% | 2770.94 | 124.1808 | 2646.7593 | 2.4831 | 155.7239 | 5.562% | 5.562% | 5.059% | 0.8014% | 1.038% | 1.038% |  |  |  | 29.06 | 155.7239
4168.7639 | 16675.0558 | 3 | 800 | 3200 | 20.7671 | 3179.2329 | 11.5164 | 32.2835 | 1.009% | 3167.7165 | 125.3917 | 3042.3248 | 3.2808 | 160.956 | 5.03% | 5.03% | 4.626% | 0.8235% | 1.009% | 1.009% |  |  |  | 32.2835 | 160.956
4689.8594 | 18759.4378 | 4 | 900 | 3600 | 21.3465 | 3578.6535 | 14.5919 | 35.9384 | 0.9983% | 3564.0616 | 126.7628 | 3437.2988 | 4.188 | 166.8892 | 4.636% | 4.636% | 4.311% | 0.855% | 0.9983% | 0.9983% |  |  |  | 35.9384 | 166.8892
5210.9549 | 20843.8197 | 5 | 1000 | 4000 | 21.994 | 3978.006 | 18.0303 | 40.0243 | 1.001% | 3959.9757 | 128.2937 | 3831.682 | 5.2041 | 173.5221 | 4.338% | 4.338% | 4.078% | 0.8931% | 1.001% | 1.001% |  |  |  | 40.0243 | 173.5221
5732.0504 | 22928.2017 | 6 | 1100 | 4400 | 22.7097 | 4377.2903 | 21.8315 | 44.5412 | 1.012% | 4355.4588 | 129.9837 | 4225.4751 | 6.3288 | 180.8536 | 4.11% | 4.11% | 3.906% | 0.9361% | 1.012% | 1.012% |  |  |  | 44.5412 | 180.8536
6253.1459 | 25012.5837 | 7 | 1200 | 4800 | 23.4935 | 4776.5065 | 25.9952 | 49.4887 | 1.031% | 4750.5113 | 131.8324 | 4618.6789 | 7.5614 | 188.8825 | 3.935% | 3.935% | 3.778% | 0.9826% | 1.031% | 1.031% |  |  |  | 49.4887 | 188.8825
6774.2414 | 27096.9657 | 8 | 1300 | 5200 | 24.3455 | 5175.6545 | 30.5213 | 54.8668 | 1.055% | 5145.1332 | 133.8392 | 5011.294 | 8.9016 | 197.6076 | 3.8% | 3.8% | 3.685% | 1.032% | 1.055% | 1.055% |  |  |  | 54.8668 | 197.6076
7295.3369 | 29181.3476 | 9 | 1400 | 5600 | 25.2657 | 5574.7343 | 35.4096 | 60.6753 | 1.083% | 5539.3247 | 136.0036 | 5403.3212 | 10.3488 | 207.0276 | 3.697% | 3.697% | 3.619% | 1.083% | 1.083% | 1.083% |  | 0 |  | 60.6753 | 207.0276
7816.4324 | 31265.7296 | 10 | 1500 | 6000 | 26.254 | 5973.746 | 40.6599 | 66.9139 | 1.115% | 5933.0861 | 138.3251 | 5794.7611 | 11.9025 | 217.1414 | 3.619% | 3.619% | 3.575% | 1.137% | 1.115% | 1.131% |  | 1 |  | 67.8567 | 217.1414
8337.5279 | 33350.1116 | 11 | 1600 | 6400 | 27.3105 | 6372.6895 | 46.272 | 73.5824 | 1.15% | 6326.4176 | 140.8031 | 6185.6145 | 13.5623 | 227.9478 | 3.562% | 3.562% | 3.548% | 1.191% | 1.15% | 1.181% |  | 2 |  | 75.5939 | 227.9478
8858.6234 | 35434.4935 | 12 | 1700 | 6800 | 28.4351 | 6771.5649 | 52.2457 | 80.6808 | 1.186% | 6719.3192 | 143.4372 | 6575.882 | 15.3276 | 239.4457 | 3.521% | 3.521% | 3.536% | 1.247% | 1.186% | 1.234% | 0 | 3 |  | 83.8865 | 239.4457
9379.7189 | 37518.8755 | 13 | 1800 | 7200 | 29.6279 | 7170.3721 | 58.5809 | 88.2088 | 1.225% | 7111.7912 | 146.2268 | 6965.5644 | 17.1981 | 251.6337 | 3.495% | 3.515% | 3.536% | 1.304% | 1.225% | 1.288% | 1 | 4 |  | 92.7345 | 253.1137
9900.8144 | 39603.2575 | 14 | 1900 | 7600 | 30.8889 | 7569.1111 | 65.2773 | 96.1662 | 1.265% | 7503.8338 | 149.1714 | 7354.6624 | 19.1731 | 264.5107 | 3.48% | 3.522% | 3.547% | 1.361% | 1.265% | 1.344% | 2 | 5 |  | 102.1376 | 267.6352
10421.9099 | 41687.6395 | 15 | 2000 | 8000 | 32.218 | 7967.782 | 72.3348 | 104.5528 | 1.307% | 7895.4472 | 152.2705 | 7743.1767 | 21.2523 | 278.0756 | 3.476% | 3.538% | 3.566% | 1.42% | 1.307% | 1.401% | 3 | 6 |  | 112.0957 | 283.009
10943.0054 | 43772.0214 | 16 | 2100 | 8400 | 33.6153 | 8366.3847 | 79.7532 | 113.3685 | 1.35% | 8286.6315 | 155.5236 | 8131.1079 | 23.4351 | 292.3272 | 3.48% | 3.562% | 3.592% | 1.479% | 1.35% | 1.46% | 4 | 7 |  | 122.6085 | 299.2339
11464.1009 | 45856.4034 | 17 | 2200 | 8800 | 35.0807 | 8764.9193 | 87.5323 | 122.613 | 1.393% | 8677.387 | 158.9302 | 8518.4568 | 25.7211 | 307.2642 | 3.492% | 3.594% | 3.625% | 1.538% | 1.393% | 1.519% | 5 | 8 |  | 133.6759 | 316.3087
11985.1963 | 47940.7854 | 18 | 2300 | 9200 | 36.6143 | 9163.3857 | 95.6719 | 132.2862 | 1.438% | 9067.7138 | 162.4896 | 8905.2242 | 28.1097 | 322.8856 | 3.51% | 3.633% | 3.663% | 1.598% | 1.438% | 1.579% | 6 | 9 |  | 145.2976 | 334.2322
12506.2918 | 50025.1674 | 19 | 2400 | 9600 | 38.2161 | 9561.7839 | 104.1718 | 142.3879 | 1.483% | 9457.6121 | 166.2015 | 9291.4106 | 30.6006 | 339.1901 | 3.533% | 3.677% | 3.707% | 1.658% | 1.483% | 1.64% | 7 | 10 |  | 157.4736 | 353.0034
13027.3873 | 52109.5493 | 20 | 2500 | 10000 | 39.886 | 9960.114 | 113.0319 | 152.9179 | 1.529% | 9847.0821 | 170.0653 | 9677.0168 | 33.1933 | 356.1765 | 3.562% | 3.726% | 3.754% | 1.719% | 1.529% | 1.702% | 8 | 11 |  | 170.2036 | 372.621
13548.4828 | 54193.9313 | 21 | 2600 | 10400 | 41.6241 | 10358.3759 | 122.2519 | 163.876 | 1.576% | 10236.124 | 174.0805 | 10062.0435 | 35.8872 | 373.8438 | 3.595% | 3.78% | 3.806% | 1.779% | 1.576% | 1.764% | 9 | 12 |  | 183.4874 | 393.0838
14069.5783 | 56278.3133 | 22 | 2700 | 10800 | 43.4303 | 10756.5697 | 131.8317 | 175.2621 | 1.623% | 10624.7379 | 178.2466 | 10446.4913 | 38.6819 | 392.1906 | 3.631% | 3.837% | 3.861% | 1.841% | 1.623% | 1.827% | 10 | 13 |  | 197.3249 | 414.3906
14590.6738 | 58362.6953 | 23 | 2800 | 11200 | 45.3047 | 11154.6953 | 141.7711 | 187.0759 | 1.67% | 11012.9241 | 182.5631 | 10830.361 | 41.577 | 411.216 | 3.672% | 3.898% | 3.919% | 1.902% | 1.67% | 1.89% | 11 | 14 |  | 211.7159 | 436.5404
15111.7693 | 60447.0772 | 24 | 2900 | 11600 | 47.2473 | 11552.7527 | 152.0699 | 199.3172 | 1.718% | 11400.6828 | 187.0294 | 11213.6533 | 44.5719 | 430.9186 | 3.715% | 3.961% | 3.979% | 1.964% | 1.718% | 1.954% | 12 | 15 |  | 226.6601 | 459.5319
15632.8648 | 62531.4592 | 25 | 3000 | 12000 | 49.258 | 11950.742 | 162.7279 | 211.9859 | 1.767% | 11788.0141 | 191.6451 | 11596.3689 | 47.6663 | 451.2974 | 3.761% | 4.028% | 4.042% | 2.025% | 1.767% | 2.018% | 13 | 16 |  | 242.1574 | 483.364
16153.9603 | 64615.8412 | 26 | 3100 | 12400 | 51.3369 | 12348.6631 | 173.745 | 225.0819 | 1.815% | 12174.9181 | 196.4097 | 11978.5084 | 50.8596 | 472.3511 | 3.809% | 4.097% | 4.107% | 2.087% | 1.815% | 2.082% | 14 | 17 |  | 258.2076 | 508.0356
16675.0558 | 66700.2231 | 27 | 3200 | 12800 | 53.4839 | 12746.5161 | 185.1209 | 238.6048 | 1.864% | 12561.3952 | 201.3226 | 12360.0726 | 54.1513 | 494.0787 | 3.86% | 4.168% | 4.174% | 2.15% | 1.864% | 2.147% | 15 | 18 |  | 274.8105 | 533.5454
17196.1513 | 68784.6051 | 28 | 3300 | 13200 | 55.6991 | 13144.3009 | 196.8554 | 252.5545 | 1.913% | 12947.4455 | 206.3833 | 12741.0621 | 57.5411 | 516.479 | 3.913% | 4.242% | 4.243% | 2.212% | 1.913% | 2.212% | 16 | 19 |  | 291.966 | 559.8923
17717.2468 | 70868.9871 | 29 | 3400 | 13600 | 57.9825 | 13542.0175 | 208.9484 | 266.9309 | 1.963% | 13333.0691 | 211.5914 | 13121.4777 | 61.0285 | 539.5508 | 3.967% | 4.317% | 4.314% | 2.274% | 1.963% | 2.277% | 17 | 20 |  | 309.6738 | 587.0753
18238.3423 | 72953.3691 | 30 | 3500 | 14000 | 60.334 | 13939.666 | 221.3998 | 281.7338 | 2.012% | 13718.2662 | 216.9463 | 13501.32 | 64.613 | 563.293 | 4.024% | 4.394% | 4.386% | 2.337% | 2.012% | 2.342% | 18 | 21 |  | 327.9338 | 615.093
18759.4378 | 75037.751 | 31 | 3600 | 14400 | 62.7537 | 14337.2463 | 234.2092 | 296.9629 | 2.062% | 14103.0371 | 222.4475 | 13880.5897 | 68.2941 | 587.7044 | 4.081% | 4.472% | 4.46% | 2.399% | 2.062% | 2.408% | 19 | 22 |  | 346.7457 | 643.9444
19280.5333 | 77122.133 | 32 | 3700 | 14800 | 65.2415 | 14734.7585 | 247.3765 | 312.618 | 2.112% | 14487.382 | 228.0945 | 14259.2875 | 72.0714 | 612.7839 | 4.14% | 4.552% | 4.535% | 2.462% | 2.112% | 2.474% | 20 | 23 |  | 366.1095 | 673.6284
19801.6287 | 79206.515 | 33 | 3800 | 15200 | 67.7975 | 15132.2025 | 260.9016 | 328.6991 | 2.162% | 14871.3009 | 233.8869 | 14637.4141 | 75.9444 | 638.5304 | 4.201% | 4.633% | 4.611% | 2.525% | 2.162% | 2.54% | 21 | 24 |  | 386.0248 | 704.1437
20322.7242 | 81290.897 | 34 | 3900 | 15600 | 70.4217 | 15529.5783 | 274.7842 | 345.2059 | 2.213% | 15254.7941 | 239.824 | 15014.9701 | 79.9128 | 664.9427 | 4.262% | 4.715% | 4.688% | 2.588% | 2.213% | 2.606% | 22 | 25 |  | 406.4916 | 735.4893
9043 | 36172 | 35 | 1735.3825 | 6941.53
9043 | 36172 | AAL | 1735.3825 | 6941.53 | 28.8494 | 6912.6806 | 54.4459 | 83.2953 | 1.2% | 6858.2347 | 144.4065 | 6713.8282 | 15.9775 | 243.6792 | 3.51% |  | 3.535% | 1.267% | 1.2%
15567 | 62268 | Peak | 3464.25 | 13857 | 59.4855 | 13797.5145 | 216.9073 | 276.3928 | 1.995% | 13580.6072 | 215.0151 | 13365.5922 | 63.3204 | 554.7282 | 4.003% |  | 4.034% | 2.018% | 1.995%
Adjustment for % Losses
[15 empty] | Secondary | Primary |  | 2009 |  |  |  | 2007
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so 2008 % Losses above AAL is proportionately increased ---> | [14 empty] | 0.37% | 0.33% |  | For Secondary Distribution Customers "D" |  |  |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor | [5 empty] | Secondary Constants |  |  |  | Secondary Constants
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant
|  |  | 2008 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.01685 | right |  | F1 = | 0.0159 | right
|  |  | 2007 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | 0.0014 | middle |  | F2 = | 0.00201 | middle
[17 empty] | F3 = | 0.0171 | left |  | F3 = | 0.017 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 |  |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 |  |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001 |  |  |  | For Primary Distribution Customers "E" |  |  |  | For Primary Distribution Customers "E"
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 |  |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006 |  |  |  | Primary Constants |  |  |  | Primary Constants
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Base Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Base Value |  |  | F1 = | 0.0112 | right |  | F1 = | 0.0102 | right
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated | [6 empty] | F2 = | 0.0001 | middle |  | F2 = | 0.000379 | middle
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review. | [6 empty] | F3 = | 0.00137 | left |  | F3 = | 0.00221 | left
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 9,043 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
AAL for ERCOT = 9,043 for 15 minutes
2009
Secondary Constants
F1 = | 0.01685 | right
F2 = | 0.0014 | middle
F3 = | 0.0171 | left

## 4) Loss Equations
System Loss Equations For CenterPoint Energy
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
| A = | 2.13e-07
| B = | 18.586 | Total No-Load Losses For Substation Transformers = 18.586 MW
Primary Conductor
| A = | 1.1394e-06
| B = | 0
Distribution Transformers
| A = | 5.139e-07
| B = | 120.235 | Total No-Load Losses For Distribution Transformers = 120.235 MW
Secondary Conductor
| A = | 3.5446e-07
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified