## Attachment A- Summary
Attachment A
Summary of SILF equation coefficients- 2007
Texas Central Company (AEP-TCC)
a | b | c | d | e | f | g | h | I | J
SERV LEVL CODE | DLF CODE | ENERGY SYSTEM LOSS FACTOR* | ENERGY DISTRIB LOSS FACTOR | Average Dist Losses | Load Loss Factor | No-Load Loss Factor | F1 | F2 | F3
(Formula) |  | Divide by transmission loss factor |  | (d-1)/d | (Att C) | (Att C) | e*f |  | e*g
Secondary | A | 1.0977 | 1.0669 | 0.062715 | 0.38 | 0.62 | 0.023832 | 0 | 0.038883
Primary | B | 1.0538 | 1.0242 | 0.023658 | 0.5021 | 0.4979 | 0.011879 | 0 | 0.011779
Transmission | T | 1.0288 | 1
* From CPL 1998 System Loss Study
Texas North Company (AEP-TNC)
a | b | c | d | e | f | g | h | I | J
SERV LEVL CODE | DLF CODE | ENERGY SYSTEM LOSS FACTOR* | ENERGY DISTRIB LOSS FACTOR | Average Dist Losses | Load Loss Factor | No-Load Loss Factor | F1 | F2 | F3
(Formula) |  |  |  | (d-1)/d | (Att C) | (Att C) | e*f |  | e*g
Secondary | A | 1.1246 | 1.0717 | 0.066888 | 0.5358 | 0.4642 | 0.035839 | 0 | 0.03105
Primary | B | 1.0616 | 1.0116 | 0.01151 | 0.2914 | 0.7086 | 0.003354 | 0 | 0.0081559
Transmission | T | 1.0494 | 1
* From WTU 1998 System Loss Study

## Attachment B- Loss ratios
Attachment B
Calculation of AEP TCC Electric Distribution Loss Factors- 2007
Ratio of No-Load and Load losses on primary and secondary systems
Energy Losses, MWh *
| Load | No-Load | Total
Dist. Substation | 21573.9522 | 166663.5957 | 188237.548
Primary Feeders | 178072.1141 | 31350.6415 | 209422.7556
Line Transformers | 21573.9522 | 166663.5957 | 188237.548
Residential Sec. Lines | 57378.5101 | 12396.4595 | 69774.9696
Total Primary & Sec | 278598.5286 | 377074.2925 | 655672.8211
Distribution System
Primary | 199646.0663 | 198014.2372 | 397660.3035
Secondary | 78952.4623 | 179060.0553 | 258012.5176
Total Primary & Sec | 278598.5286 | 377074.2925 | 655672.8211
Primary ratio | 0.50205 | 0.49795
Secondary ratio | 0.306 | 0.694
* From Summary of Conductor Information and Summary of Transformer Information in 1998 Loss Analysis
Calculation of AEP TNC Electric Distribution Loss Factors- 2007
Ratio of No-Load and Load losses on primary and secondary systems
Energy Losses, MWh *
| Load | No-Load | Total
Dist. Substation | 13101.2284 | 64979.2507 | 78080.4791
Primary Feeders | 83828.9249 | 3325.4634 | 87154.3883
Line Transformers | 11127.311 | 112221.2064 | 123348.5174
Residential Sec. Lines | 36895.4214 | 4562.4165 | 41457.8379
Total Primary & Sec | 144952.8858 | 185088.337 | 330041.2228
Distribution System
Primary | 96930.1533 | 68304.7141 | 165234.8674
Secondary | 48022.7324 | 116783.6229 | 164806.3553
Total Primary & Sec | 144952.8858 | 185088.337 | 330041.2228
Primary ratio | 0.58662 | 0.41338
Secondary ratio | 0.29139 | 0.70861
* From Summary of Conductor Information and Summary of Transformer Information in 1998 Loss Analysis

## Atchmt C- TCC&TNC
Attachment C
Calculation of AEP TCC Electric Distribution Loss Factors- 2007
Portion of Loss Factor Not Sensitive to Load
|  | Input Reqmt. | Energy Loss Fraction |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales* | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter |  |  |  | 14490914185
| Input to Sec. Level | 1.0417 |  |  | 15094754741.882
| Losses due to Sec. Sales |  | 0.306 | 0.694 |  | 184776689.3403 | 419063867.5416 | 603840556.882
Primary | Output (=Sec. Input) |  |  |  | 15094754741.882
| Input to Pri. Level due to Sec. | 1.0242 |  |  | 15460515744.0325
| Losses due to Sec. Sales |  | 0.50205 | 0.49795 |  | 183630964.9918 | 182130037.1588 | 365761002.1505
| Pri. Sales |  |  |  | 2440274517
|  | 1.0242 |  |  | 2499404808.8214
| Losses due to Pri. Sales |  | 0.50205 | 0.49795 |  | 29686468.7147 | 29443823.1067 | 59130291.8214
| Total Input |  |  |  | 17959920552.854
Distribution System
| * Deliveries at the distribution primary |  |  |  |  | Losses, kWh
| and secondary level are from calendar 2003 |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 368407654.3321 | 601193904.7004 | 969601559.0325
Average Load |  |  |  | Primary Sales |  | 29686468.7147 | 29443823.1067 | 59130291.8214
Secondary | 1764.3197 | MW |  | Total |  | 398094123.0468 | 630637727.8071 | 1028731850.854
Primary | 285.2263 | MW
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.37996 | 0.62004
|  |  |  | Primary Sales |  | 0.50205 | 0.49795
Calculation of AEP TNC Electric Distribution Loss Factors- 2007
Portion of Loss Factor Not Sensitive to Load
|  | Input Reqmt. | Energy Loss Fraction |  | Energy, kWh
Voltage Level | At | Responsibility Factor | Load | No- Load | Sales* | Load Losses | No-Load Losses | Total
Secondary | Sec. Sales @ Meter |  |  |  | 3531974343
| Input to Sec. Level | 1.0593 |  |  | 3741589788.3339
| Losses due to Sec. Sales |  | 0.58662 | 0.41338 |  | 122964708.1752 | 86650737.1587 | 209615445.3339
Primary | Output (=Sec. Input) |  |  |  | 3741589788.3339
| Input to Pri. Level due to Sec. | 1.0116 |  |  | 3785156859.8293
| Losses due to Sec. Sales |  | 0.29139 | 0.70861 |  | 12694958.3569 | 30872113.1385 | 43567071.4954
| Pri. Sales |  |  |  | 2641641331
|  | 1.0116 |  |  | 2672400602.6582
| Losses due to Pri. Sales |  | 0.29139 | 0.70861 |  | 8962908.4394 | 21796363.2187 | 30759271.6582
| Total Input |  |  |  | 6457557462.4874
Distribution System
| * Deliveries at the distribution primary |  |  |  |  | Losses, kWh
| and secondary level are from calendar 2003 |  |  | Losses due to: |  | Load | No-Load | Total
|  |  |  | Secondary Sales |  | 135659666.5321 | 117522850.2972 | 253182516.8293
Average Load |  |  |  | Primary Sales |  | 8962908.4394 | 21796363.2187 | 30759271.6582
Secondary | 432.029 | MW |  | Total |  | 144622574.9715 | 139319213.5159 | 283941788.4874
Primary | 304.9687 | MW
|  |  |  | Distribution System |  | Fraction of Total Loss
[6 empty] | Load | No-Load
|  |  |  | Secondary Sales |  | 0.53582 | 0.46418
|  |  |  | Primary Sales |  | 0.29139 | 0.70861