| PRR Number | 830 | PRR Title | Reactive Power Capability Requirement |
| --- | --- | --- | --- |
| Date |  | October 21, 2009 |  |
| Submitter’s Information |  |  |  |
| Name |  | Walter J. Reid |  |
| E-mail Address |  | w.j.reid@ieee.org |  |
| Company |  | Wind Coalition |  |
| Phone Number |  | 512-335-0664 |  |
| Cell Number |  | 512-335-0664 |  |
| Market Segment |  | N/A |  |

Comments

ERCOT’s proposed changes include a redefinition of a Wind-powered Generation Resource (WGR) and subsequent changes that are intended to improve the modeling of wind-powered generation reactive capabilities.  The Wind Coalition strongly supports the ERCOT initiative to more accurately model wind-powered generators.  The method that ERCOT has chosen causes many unintended consequences.  These comments provide an alternative which avoids the unintended consequences.

The current protocols define a WGR as the whole wind-powered facility up to the point of interconnection.  Applying this definition to all the references to Generation Resources, Resources, units, and WGRs make sense.  There is a physical meaning to the WGR, meters exist that measure relevant parameters associated with the WGR, and processes and procedures are in place to schedule and report relative to the WGR.

ERCOT’s proposed redefinition of a WGR creates a fictitious unit comprised of an aggregation of Wind-powered Turbine Generators (WTGs) of the same type.  This aggregation of WTGs, defined on the low side of the step-up-to-transmission transformer, has no single physical presence.  There can be no meter point for the aggregation.  Among the various protocol requirements that would now apply to this fictitious unit is a requirement to measure and telemeter KW, KVAR, and voltage.  No single point exists where these can be measured.  Any synthesis of existing or new measurements to create these quantities would have to be defined.  This is just one example of the hundreds of references to “unit” in the protocols that now apply to these fictitious units.

This revision is intended to provide exactly the same functionality as the one proposed by ERCOT without redefining “WGR”.  The concept is to leave the definition of WGR as it is today and create an aggregation of WTGs of the same type for modeling purposes.  Exactly the same information will be provided for this aggregation as in ERCOT’s version and ERCOT can achieve exactly the same modeling objective.

| Overall Market Benefit | Improve system voltage management. |
| --- | --- |
| Overall Market Impact | Reduce the likelihood of equipment damage or outage. |
| Consumer Impact | Not clear. |

Revised Proposed Protocol Language

2.1	Definitions

Point of Interconnection (POI)

The location(s) where a Generation Entity’s interconnection Facilities connects to the Transmission Facilities as reflected in the Standard Generation Interconnection Agreement (SGIA) between a Generation Entity and a Transmission and/or Distribution Service Provider (TDSP).

Wind-powered Generation Resource (WGR)

A Generation Resource that is powered by wind.

2.2	Acronyms

POI		Point of Interconnection

GSU		Generation Step Up Transformer

SGIA		Standard Generation Interconnection Agreement

WTG		Wind-powered Turbine Generator

6.5.7	Voltage Support Service

All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than twenty (20) MVA or those units connected at the same Point of Interconnection (POI) that have gross generating unit ratings aggregating to greater than twenty (20) MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service (VSS).

6.5.7.1	Installed Reactive Power Capability Requirement for Generation Resources Required to Provide VSS

(1)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT.  	Generation Resources shall comply with the following Reactive Power requirements:  an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the ERCOT Transmission Grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the POI.  The Reactive Power requirements shall be available at all MW output levels and may be met through a combination of the Generation Resource’s Unit Reactive Limit (URL), which is the generating unit’s dynamic leading and lagging operating capability, and/or dynamic VAR capable devices.  For Wind-powered Generation Resources (WGRs), the Reactive Power requirements shall be available at all MW output levels at or above 10% of the WGR’s nameplate capacity.  When a WGR is operating below 10% of its nameplate capacity and is unable to support voltage at the POI, ERCOT may require a WGR to disconnect from the ERCOT System.  The Reactive Power requirements of this paragraph shall apply to all Generation Resources except as otherwise provided in paragraphs (2) through (4) below.

(2)	WGRs that commenced operation on or after February 17, 2004, and have a signed Standard Generation Interconnection Agreement (SGIA) on or before November 1, 2009, must be capable of producing a defined quantity of Reactive Power to maintain a Voltage Profile established by ERCOT in accordance with the Reactive Power requirements established in paragraph (1) above.  However, the Reactive Power requirements may be met through a combination of the WGR’s URL and/or automatically switchable static VAR capable devices and/or dynamic VAR capable devices.  WGRs shall comply with the Reactive Power requirements of this paragraph by no later than December 31, 2010, unless it is known by July 31, 2010, that related retrofits are required by the Voltage Ride-Through study conducted in accordance with Operation Guide Section 3.1.4.6.1, Protective Relaying Requirement and Voltage Ride-Through Requirement for Wind-powered Generation Resources, in which event ERCOT may in its discretion modify the deadline for an affected WGR.  ERCOT, in its sole discretion, also may grant an extension of time for other reasons.

(3)	Qualified renewable Generation Resources (as described in Section 14, State of Texas Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the Reactive Power requirements established in paragraph (1) above, will be required to maintain a Reactive Power requirement as defined by the qualified renewable Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(4)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the Reactive Power requirements established in paragraph (1) above, will be required to maintain a Reactive Power requirement as defined by the Generation Resource’s URL that was submitted to ERCOT and established per the criteria in the Operating Guides.

(5)	For purposes of meeting the Reactive Power requirements in paragraphs (1) and (2) above, multiple generation units including wind-powered turbines shall, at a Generation Entity’s option, be treated as a single Generation Resource or WGR if the units are connected to the same transmission bus.

(6)	Generation Entities may submit to ERCOT specific proposals to meet the Reactive Power requirements established in paragraph (1) above by employing a combination of the URL and added VAR capability, provided that the added VAR capability shall be automatically switchable static and/or dynamic VAR devices. ERCOT may, at its sole discretion, either approve or deny a specific proposal, provided that in either case, ERCOT shall provide the submitter an explanation of its decision.

(7)	  A Generation Resource and TDSP may enter into an agreement in which the Generation Resource compensates the TDSP to provide VSS to meet the Reactive Power requirements of paragraph (1) above in part or in whole.  The TDSP shall certify to ERCOT that the agreement complies with the Reactive Power requirements of paragraph (1).

(8)	Unless specifically approved by ERCOT, no unit equipment replacement or modification at a Generation Resource shall reduce the capability of the unit below the Reactive Power requirements that applied prior to the replacement/modification.

(9)	Generation Resources shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT (conveyed by way of their QSE) unless equipment damage is imminent.

(10)	A WGR’s QSE, selected for this purpose, must provide Real Time SCADA points that communicate to ERCOT the number of Wind-powered Turbine Generators (WTGs) that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid as well as other WTG status information.  WTGs of the same model and size and located behind the same generation step-up-to-transmission transformer must be aggregated together to form a WTG aggregation.  The following Real Time SCADA points must be communicated to ERCOT for each WTG aggregation:

(a)	The number of WTGs that are not able to communicate and whose status is unknown;

(b) 	The number of  WTGs out of service and not available for operation; and

(c)	The number of WTGs that are available for real power and/or Reactive Power injection into the ERCOT Transmission Grid.

WGRs must comply with the requirements listed above by no later than six months after the effective date of this paragraph.

(11) 	For the purpose of complying with the Reactive Power requirements under this Section, Reactive Power losses that occur on privately-owned transmission lines behind the POI may be compensated by automatically switchable static VAR capable devices.

(12)	ERCOT and the TSPs shall, at a minimum, represent WGRs in the ERCOT and TSP Real Time control systems and their off-line studies to include: step-up-to-transmission transformers, substation reactive devices, and the equivalent of the WTG aggregation connected to each step-up-to-transmission transformer.

6.7.6	Deployment of Voltage Support Service

(1)	ERCOT, or Transmission Service Providers (TSPs) designated by ERCOT, will instruct Generation Resources required to provide Voltage Support Service (VSS) to make adjustments for voltage support within the Unit Reactive Limit (URL) capacity limits provided by the QSE to ERCOT.  Generation Resources providing VSS will not be requested to reduce megawatt output so as to provide additional Megavolt Ampere Reactive (MVAR), nor will they be requested to operate on a voltage schedule outside the URL specified by the QSE without a Dispatch Instruction requesting unit-specific Dispatch or an OOME instruction.

(2)	ERCOT and Transmission and/or Distribution Service Providers (TDSPs) shall develop operating procedures specifying Voltage Profiles of transmission controlled reactive Resources to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, step-up transformer tap settings will be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

(3)	The TSP, under ERCOT direction, is responsible for monitoring and ensuring that all Generation Resources required to provide VSS dynamic reactive sources in a local area are deployed in approximate proportion to their respective installed Reactive Power capability requirements.

(4)	All Generation Resources required to provide VSS shall support the transmission voltage at the POI to the ERCOT Transmission Grid, or at the transmission bus in accordance with paragraph (5) of Section 6.5.7.1, Generation Resources Required to Provide VSS Installed Reactive Capability, as directed by ERCOT within the operating Reactive Power capability of the unit(s).

(5)	The QSEs providing VSS shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Service Deployment Performance Measures.