| PRR Number | 833 | PRR Title | Primary Frequency Response Requirement from Existing WGRs |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Date of Decision |  | October 22, 2009 |  |  |
| Proposed Effective Date |  | To be determined. |  |  |
| Priority and Rank Assigned |  | To be determined. |  |  |
| Protocol Section Requiring Revision |  | 5.9.1.3, Wind-powered Generation Resource (WGR) Primary Frequency Response (new) |  |  |
| Revision Description |  | This Protocol Revision Request (PRR) places a Primary Frequency Response requirement on WGRs that was not covered by PRR824, Primary Frequency Response from WGRs. |  |  |
| Reason for Revision |  | To require all WGRs to provide Primary Frequency Response. |  |  |
| Overall Market Benefit |  | Possible added reliability and similar treatment for existing WGRs as that given to prospective wind farms. Maintain system frequency better with additional wind generation in the ERCOT Region, which shall allow greater utilization of wind generation. |  |  |
| Overall Market Impact |  | Greater requirements are placed on existing WGRs. |  |  |
| Consumer Impact |  | Greater reliability but also possibly greater cost. |  |  |
| Credit Impacts |  | Unknown. |  |  |
| Relevance to Nodal Market |  | May require similar changes to Nodal Protocols. |  |  |
| Nodal Protocol Section Requiring Revision |  | 8.5.3, Wind-powered Generation Resource (WGR) Primary Frequency Response |  |  |
| Procedural History |  | - On 9/22/09, PRR833 was posted. - On 9/25/09, Calpine comments were posted. - On 10/12/09, Wind Coalition comments were posted. - On 10/19/09, ROS comments were posted. - On 10/22/09, PRS considered PRR833. |  |  |
| PRS Decision |  | On 10/22/09, PRS voted to recommend approval of PRR833 as revised by PRS via roll call vote. All Market Segments were present for the vote. |  |  |
| Summary of PRS Discussion |  | On 10/22/09, there was discussion regarding retrofitting WGRs with Primary Frequency Response capability and ERCOT’s interpretation of the retrofitting being “technically infeasible”. There was concern expressed by some Market Participant’s regarding the cost benefit of PRR833. |  |  |

| Quantitative Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost |  | Impact Area | Monetary Impact |
|  | 1 | WGRs would need to install governor response | Less than $500,000 per WGR |
|  | 2 | Lost Production due to high frequency | Depends on the price of power. |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit |  | Impact Area | Monetary Impact |
|  | 1 | Provides automatic response to frequency, primarily to high frequency excursions, in addition to the response from conventional generation units. Should help avoid excessive frequency excursions | Difficult to quantify. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Sponsor |  |
| --- | --- |
| Name | Kenan Ögelman |
| E-mail Address | kogelman@cpsenergy.com |
| Company | CPS Energy |
| Phone Number | 512 542-7594 |
| Cell Number | 512 423-3570 |
| Market Segment | Municipal |

| Market Rules Staff Contact |  |
| --- | --- |
| Name | Yvette M. Landin |
| E-Mail Address | ylandin@ercot.com |
| Phone Number | (512) 248-4513 |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Summary |
| Calpine 092209 | Supported approval of PRR833. |
| Wind Coalition 101209 | Recommended rejection of PRR833. |
| ROS 101909 | Recommended approval of PRR833 as submitted. |

Proposed Protocol Language Revision

- 5.9.1.3		Wind-powered Generation Resource (WGR) Primary Frequency Response

Wind-powered Generation Resources (WGRs) with Standard Generation Interconnection  Agreements (SGIA) signed after January 1, 2010 shall provide Primary Frequency Response to frequency deviations from 60.000 Hz.  The WGR automatic control system design shall have an adjustable dead band that can be set as specified in the ERCOT Operating Guides.  The Primary Frequency Response shall be similar to the droop characteristic of five-percent (5%) used by conventional generators.  For WGRs with SGIA executed on or prior to January 1, 2010, those not already equipped with Primary Frequency Response shall by December 1, 2011 acquire that capability.  Those WGRs that cannot technically be retrofitted with Primary Frequency Response capability shall submit an attestation to ERCOT by [three months after effective date of this PRR], explaining the technical infeasibility.  At ERCOT’s sole discretion, those WGRs for which Primary Frequency Response is technically infeasible may be granted a permanent exemption from the requirement.  ERCOT shall make a determination within one hundred eighty (180) Business Days.  If ERCOT does not grant an exemption, the WGR shall acquire the capability to provide Primary Frequency Response within twenty-four (24) months of being notified of that determination.