## Slide 1: American Electric Power Services Corporation Corpus Christi Area Improvements Project
November 5, 2009
Technical Advisory Committee
Jay Teixeira
Manager, Regional Planning

## Slide 2: Project Need - Background
Four discrete drivers for this project:
  Barney Davis repower interconnection agreement signed in June 2008
  Nueces Bay repower interconnection agreement signed in June 2008
  Reliability improvements needed ……
  Difficulty in scheduling maintenance outages in Corpus Christi area
AEPSC submitted the Corpus Christi Improvements Project for RPG review in March 2009
  Includes interconnection projects, summer peak reliability projects, maintenance reliability projects, and congestion relief projects
  Comments received from area industrial customers indicating the potential for the projects to have a significant negative affect on their facilities
  Comments not resolved during Study Mode – AEP and customers continued to work together during ERCOT Independent Review
ERCOT Independent Review began in May 2009
Technical Advisory Committee
November 5, 2009

## Slide 3: Description of Recommendation – Total Cost $101.2 M
Technical Advisory Committee
November 5, 2009
  Build new Gila substation:
    Relocate Koch Upriver – Nueces Bay 138 kV line into Gila
    Relocate Highway 9 – Nueces Bay 138 kV double-circuit into Gila
    Relocate Whitepoint – Nueces Bay 138 kV line #2 into Gila
  Rebuild/ reconductor Valero East – Highway 9 69 kV line
  Reconductor Lon Hill – Hearn Road 69 kV line
  Build 138 kV line Barney Davis – Laguna and install new 138/69 kV autotransformer at Laguna
  Rebuild Barney Davis – Alazan – Nelson Sharpe 138 kV line
  Upgrade Westside – Cabaniss 138 kV line terminal equipment
  Upgrade both Lon Hill 138/69 kV autotransformers

## Slide 4: Discussion of Options
Nueces Bay Interconnection
  Four options considered
  Option chosen - Build new Gila substation with 3 lines moved from Nueces Bay – Cost = $39.71 M
Reliability analysis with Maintenance outages
  To allow Airline autotransformer maintenance:
    Build 138 kV line Barney Davis – Laguna and install new 138/69 kV autotransformer at Laguna – Cost = $15.1 M
  To allow Koch Upriver autotransformer maintenance:
    Reconductor Lon Hill-Hearn Road 69 kV line and rebuild/ reconductor Highway 9- Valero East 69 kV line - Cost = $6.6 M
  Generation redispatch, including generation from industrial generators, needed during these maintenance periods
Summer Peak Reliability analysis (no Maintenance Outages)
  2014 Summer Peak
  Upgrade both Lon Hill 138/69 kV autotransformers – $11.8 M
Technical Advisory Committee
November 5, 2009

## Slide 5: Discussion of Options
Congestion Analysis
  2014 Economic case from 2009 Five-Year Transmission Plan
  Two options:
    Rebuild Barney Davis-Alazan-Nelson Sharpe 138 kV line such that the Rate B is 717 MVA, bypass the Nelson Sharpe PST, Upgrade Westside-Cabaniss 138 kV line terminal equipment
      Cost = $27.0 M
    Build a new Barney Davis-Nelson Sharpe 138 kV line on new ROW, Upgrade Westside-Cabaniss 138 kV line terminal equipment
      Cost = $41.6 M
Other considerations
  Option 1 should not require CCN and may be implemented to reduce congestion sooner; output of Barney Davis restricted while line is being rebuilt
  Option 2 would require CCN and may take longer to implement
  Option 1 costs less with superior performance
Option 1 chosen
Technical Advisory Committee
November 5, 2009

## Slide 6: Stakeholder Review
The Stakeholder review period for this project was held in April 2009
There were dissenting comments on the submitted project but none on this recommended package
Technical Advisory Committee
November 5, 2009

## Slide 7: ERCOT Support for the Project
ERCOT will be requesting that the projects recommended as part of the Corpus Christi Area Improvements project be endorsed by the ERCOT Board.
Technical Advisory Committee
November 5, 2009

## Slide 8
Questions?
November 5, 2009
Technical Advisory Committee