## Slide 1: RTWG Report to TAC
November 5, 2009
Henry Durrwachter

## Slide 2: RTWG Meeting of October 6
Presentation on Utility Scale Solar Generation Integration – Hala Balouz, Electric Power Engineers (EPE)
  GEMINI 30 MW Solar Photovoltaic Generation Project
  Inverters and Grid Interconnection Requirements
  Developer concerns or challenges related to ERCOT voltage and frequency requirements for inverters used on solar installations
Updated Issues List
Reviewed draft 3rd Quarter TRIP Report

## Slide 3: GEMINI 30 MW Solar
34.4 MW (dc) / 30 MW (ac)
171,104 Suntech modules
370 acres
20-degree Tracking Technology
60 X 500 kW Inverters

## Slide 4: Satcon PowerGate Plus 500kW Inverter Voltage Settings
Voltage Range (% VNOMINAL ) | ERCOT Delay to Trip for Wind Generation | Satcon
110% < V | Generator Discretion | In Compliance – Adjustable trip time between .16s and 1.00s
90% ≤ V ≤ 110% | No automatic tripping (Continuous operation | In Compliance – Continuous operation from 88% to 110%
50% ≤ V < 90% | 1.1s to 1.8s | In Compliance – Adjustable up to 2.00s
20% ≤ V < 50% | 20s to 1.1s | Trips after .16s
0 < V < 20% | .15 to 20s | Trips instantly
V = 0 | .15s | Trips instantly
Source: PowerGate Plus Installation, Operation, and Maintenance
Guide & ERCOT Operating Guides Section 3.1.4

## Slide 5: Satcon PowerGate Plus 500kW Inverter Frequency Specifications
Frequency Range (Hz) | ERCOT Delay to Trip | Satcon
60.5 < f | Generator responsibility | In Compliance – adjustable trip time between .10s and .16s
59.4 < f ≤ 60.5 | No automatic tripping (Continuous operation) | In Compliance - will operate with the gird frequency between 59.3-60.5Hz as default setting
58.4 < f ≤ 59.4 | Not less than 9 minutes | can only ride-through for 5 minutes (300 seconds)
58.0 < f ≤ 58.4 | Not less than 30 seconds | In Compliance - 0.16 seconds (adjustable, max 300 sec) down to 57 Hz.
57.5 < f ≤ 58.0 | Not less than 2 seconds | In Compliance - 0.16 seconds (adjustable, max 300 sec) down to 57 Hz.
f ≤ 57.5 | No time delay required | In Compliance – Instant tripping at 57 Hz
Source: PowerGate Plus Installation, Operation, and Maintenance
Guide

## Slide 6: Technical Challenges Raised
The need for enhanced interconnection procedures and standards to address reactive power control, voltage and frequency ride-through.
Work on the inverter side to lessen the power quality impacts and improve voltage and frequency compliance.

## Slide 7: 3rd Quarter TRIP Report - Highlights
This report covers 4 months (not 3) in order to align the report with normal quarterly reporting periods; future reports will cover 3 month periods.
Total new wind generating capacity in ERCOT as of September 30, 2009 = 8,515 MW, an increase of 380 MW from the last report.
  Panther Creek III (200 MW in Sterling County)
  Papalote Creek 1 Wind (180 MW in San Patricio County)
Total new renewable capacity in ERCOT increased from 8,278 MW to 8,660 MW, an increase of 382 MW from the last report.
Two wind farms signed Generation Interconnect Agreements since the last report:
  Rattlesnake Wind Farm (200 MW in McCulloch County)
  Cedro Hill Wind (150 MW in Webb County)

## Slide 8: Installed Wind Generation Capacity in ERCOT

## Slide 9: 3rd Quarter TRIP Report - Highlights
Significant Events
  Wind Workshop III (June), which focused on the ERCOT Low Voltage Ride-Through study
  PUCT Workshop (Docket No. 37339)(August)
    Identification of challenges related to reliability
    Identification of reliability tools
    Identification of incentives to implement such tools
    Cost allocation issues

## Slide 10: RTWG Recommendation to TAC
Approve the 3rd Quarter TRIP as submitted by RTWG for distribution to the ERCOT Board and to the Public Utility Commission of Texas.

## Slide 11: Questions?