## Slide 1: Proposed Changes for the 2010 Methodology for Determining Ancillary Service Requirements
TAC Update
05 November, 2009
John Dumas

## Slide 2: Agenda
Proposed changes to the Non-spin Reserve Service (NSRS) requirement
Resulting NSRS requirements using the proposed methodology
Conclusions and questions

## Slide 3: Overview of Proposed Changes
The only changes for 2010 are to the requirement calculations for NSRS
As oppose to analyzing the last 90 days, ERCOT will instead analyze the last 30 days and the same month of the previous year
  Same thing that is done for Regulation Service requirement calculations
Beyond calculating the 95th percentile, ERCOT will also calculate the average uncertainty in the net load forecast to determine if there is a tendency in the forecast to over-forecast
Lastly, ERCOT will consider that the size of the largest unit
  Done to cover the loss of the largest unit during periods of higher risk

## Slide 4: Details of NSRS Requirement Calculations
Using the same 4 hours blocks, ERCOT will calculate the 95th percentile of the net load forecast uncertainty using the 30 days prior to the study and the same month of the previous year for analysis
The Regulation Up Service requirements will be subtracted from the 95th percentile values to determine an initial NSRS requirement for each block
ERCOT will also calculate the average net load forecast uncertainty to determine if there has been a tendency towards over-forecasting net load for any block of hours
If this tendency is observed, the calculated value will be added to the initially calculated NSRS requirement (requirement determined using the 95th percentile analysis)

## Slide 5: Details of NSRS Requirement Calculations cont.
Concurrently, the same average uncertainty value will be subtracted from the ERCOT load forecast during the month for the set of hours to which is applies
  This value will be capped at 1000 MW (WMS recommended 1500 MW)
  Shifts MWs from Load Forecast to NSRS requirement for periods during which over-forecasting has been historically observed
A floor of the single largest unit will be applied to on-peak hours (HE 7 – 22)
  Protects against risk of loss of generation
  The periods during which this risk is the highest may not correlate with the periods during which net load forecast uncertainty is the highest
The NSRS requirement will then be posted in the usual fashion

## Slide 6: Methodology Results – August ‘09
Current Methodology
Proposed Methodology
IE | NSRS Requirement
1 | 799
2 | 799
3 | 1230
4 | 1230
5 | 1230
6 | 1230
7 | 1172
8 | 1172
9 | 1172
10 | 1172
11 | 1249
12 | 1249
13 | 1249
14 | 1249
15 | 376
16 | 376
17 | 376
18 | 376
19 | 588
20 | 588
21 | 588
22 | 588
23 | 799
24 | 799
IE | 95th Percentile - Reg. Up Requirement | Negative Net Load Forecast Average Error (Capped at -1500 MW) | NSRS Requirement (With Average Error and On-peak Floor)
1 | 730 | -304 | 1034
2 | 730 | -304 | 1034
3 | 1569 | 0 | 1569
4 | 1569 | 0 | 1569
5 | 1569 | 0 | 1569
6 | 1569 | 0 | 1569
7 | 1829 | 0 | 1829
8 | 1829 | 0 | 1829
9 | 1829 | 0 | 1829
10 | 1829 | 0 | 1829
11 | 1570 | -449 | 2019
12 | 1570 | -449 | 2019
13 | 1570 | -449 | 2019
14 | 1570 | -449 | 2019
15 | 461 | -1500 | 1961
16 | 461 | -1500 | 1961
17 | 461 | -1500 | 1961
18 | 461 | -1500 | 1961
19 | 0 | -1500 | 1500
20 | 0 | -1500 | 1500
21 | 0 | -1500 | 1500
22 | 0 | -1500 | 1500
23 | 730 | -304 | 1034
24 | 730 | -304 | 1034

## Slide 7: Methodology Results – October ‘09
Current Methodology
Proposed Methodology
IE | NSRS Requirement
1 | 737
2 | 737
3 | 1015
4 | 1015
5 | 1015
6 | 1015
7 | 766
8 | 766
9 | 766
10 | 766
11 | 874
12 | 874
13 | 874
14 | 874
15 | 0
16 | 0
17 | 0
18 | 0
19 | 0
20 | 0
21 | 0
22 | 0
23 | 737
24 | 737
IE | 95th Percentile - Reg. Up Requirement | Negative Net Load Forecast Average Error (Capped at -1500 MW) | NSRS Requirement (With Average Error and On-peak Floor)
1 | 1083 | -476 | 1559
2 | 1083 | -476 | 1559
3 | 1282 | -175 | 1457
4 | 1282 | -175 | 1457
5 | 1282 | -175 | 1457
6 | 1282 | -175 | 1457
7 | 1168 | -49 | 1354
8 | 1168 | -49 | 1354
9 | 1168 | -49 | 1354
10 | 1168 | -49 | 1354
11 | 493 | -1096 | 1589
12 | 493 | -1096 | 1589
13 | 493 | -1096 | 1589
14 | 493 | -1096 | 1589
15 | 31 | -1500 | 1531
16 | 31 | -1500 | 1531
17 | 31 | -1500 | 1531
18 | 31 | -1500 | 1531
19 | 460 | -1492 | 1952
20 | 460 | -1492 | 1952
21 | 460 | -1492 | 1952
22 | 460 | -1492 | 1952
23 | 1083 | -476 | 1559
24 | 1083 | -476 | 1559

## Slide 8: Conclusions
Makes use of additional historical data to capture both recent observations and possible seasonal tendencies
Attempts to shift MWs from the ERCOT load forecast to the NSRS requirement during periods in which the net load forecast has tended to over-forecast
Addresses concern that a greater risk of loss of generation may not coincide with a greater risk of net load forecast uncertainty