| PRR Number | 830 | PRR Title | Reactive Power Capability Requirement |
| --- | --- | --- | --- |
| Date |  | November 10, 2009 |  |
| Submitter’s Information |  |  |  |
| Name |  | Ken Donohoo |  |
| E-mail Address |  | kdonoho1@oncor.com |  |
| Company |  | Oncor Electric Delivery Company LLC |  |
| Phone Number |  | 214-743-6823 |  |
| Cell Number |  |  |  |
| Market Segment |  | Investor Owned Utility (IOU) |  |

Comments

Oncor Electric Delivery Company LLC is very pleased to support ERCOT's
independence and objectivity in maintaining reliability in operations
and planning activities.  Oncor supports ERCOT's efforts to maintain
system reliability with PRR830 and provides the following material and
attached documents.

For the bulk power system to operate reliably, it must be designed and
operated based on the following principles:

*       The total generation (MW & Mvar) at any moment must be kept
equal to total electricity consumption and losses on the system

*       The electricity is allowed to flow through the transmission
system in accordance with physical laws and cannot be directed to flow
through specific lines

*       The system must be designed with reserve capacity in generation
(MW & Mvar) and transmission to allow for uninterrupted service when
contingencies occur

Voltage, a pressure-like quantity, is a measure of the electromotive
force necessary to maintain a flow of electricity on a transmission
line.  Voltage fluctuations can occur due to variations in electricity
demand, lack of reactive reserve and to failures on transmission
equipment.  Constraints on the maximum voltage levels are set by the
design of the transmission line and station equipment.  If the maximum
is exceeded, short circuits (faults), radio interference, and noise may
occur.  Also, transformers and other equipment at stations and/or
customer facilities may be damaged or destroyed.  Minimum voltage
constraints also exist based on the power requirements of the customers
and lack of reactive reserve.  Low voltages cause inadequate operation
of equipment and may damage motors.

Voltage on a transmission line tends to "drop" from the sending end to
the receiving end and varies based upon the flow.  The voltage drop
along the AC line is almost directly proportional to reactive power
flows and line reactance (impedance).  The line reactance increases with
the length of the line.  Capacitors and inductive reactors are
installed, as needed, on lines and in stations to, in part; control the
amount of voltage drop or rise.  This is important because voltage
levels and current levels determine the power that can be delivered to
the customers.

A variety of reactive power (Mvar) producing equipment exists.  They can
generally be broken down into two categories; "Dynamic Resources" and
"Static Resources".  The total production of reactive power must equal
customer demand plus losses under normal, fault and contingency
conditions.

Small Mvar production shortages will result in degradation of grid
voltage, while larger Mvar production shortages lead to severe low
voltage or collapse.  Over production Mvar results in high voltage with
possible long term damage to grid facilities, generation equipment and
customer facilities.  Reactive power must be constantly
produced/absorbed locally and cannot be transported over long distances.
Reactive energy (Mvar) cannot be transmitted as far as real energy (MW).
This is primarily due to the bulk electric transmission line impedances
which have a naturally large X to R ratio usually in the range of 5 to
25.

High voltage transmission lines are a local source of shunt reactive
energy (line charging).  This local reactive energy source is similar to
a fixed static capacitor connected to each end of the line.  However,
reactive Mvar losses on heavily loaded transmission lines often exceed
the local static reactive energy produced by line charging.  Large X to
R ratios produces significant difference in MW losses compared to Mvar
losses.  Due to this X to R ratio Mvar losses are typically 5 to 25
times higher than MW losses and are constantly varying.

Generators, static var compensators (SVCs), static compensators
(STATCOMs), other Flexible AC Transmission Systems (FACTS) and
synchronous condensers provide dynamic reactive power with various time
responses to quickly changing system conditions.

Under low voltage conditions, static capacitors used in stations (and
line charging) do not produce maximum reactive power as reliably as
dynamic self excited power equipment because capacitor reactive power
output depends on substation voltage.  Capacitor reactive power output
changes in proportion to the square of voltage magnitude.  For example
if substation voltage declines from 100% to 90% of nominal voltage,
static reactive power output declines from 100% of capability to 81%.
Low voltage also increases Mvar needed by motor loads further degrading
the voltage.

Dynamic reactive resources are used to adapt to rapidly changing
conditions on the transmission system, such as faults, sudden loss of
generators or transmission facilities.  In contrast switched static
devices are typically used to adapt to slowly changing system conditions
such as daily and seasonal load cycles and changes to scheduled
transactions.

Static capacitor resources have lower capital cost than dynamic devices,
and from a systems point of view, static capacitors are used to provide
normal or intact-system voltage support.  Locating static capacitors and
dynamic reactive devices near to reactive load/losses, increases their
effectiveness.  Dynamic reactive resources are used to adapt to rapidly
changing conditions on the transmission system, such as sudden loss of
generators, faults or transmission facilities.

An appropriate combination of both static and dynamic resources is
needed to ensure reliable operation of the transmission system under
normal and changing conditions.

Revised Proposed Protocol Language

None proposed