ERCOT Operations Report

October 2009 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration (s) |  |
| --- | --- | --- | --- |
| 10/1/2009 16:28 | 59.85 | 34 | Unit trip with 580 MW |
| 10/1/2009 18:01 | 60.12 | 644 | SCE + 1278 MW in 12 min. Out of Down Regulation |
| 10/3/2009 19:00 | 59.87 | 36 | Unit trip with 525 MW |
| 10/6/2009 21:46 | 59.89 | 4 | Unit trip with 260 MW |
| 10/7/2009 22:05 | 59.90 | 6 | SCE - 1550 MW in 12 min. |
| 10/8/2009 10:48 | 60.13 | 185 | SCE + 880 MW in 5 min. |
| 10/9/2009 0:03 | 60.11 | 44 | SCE + 1000 MW in 10 min. Out of Down Regulation |
| 10/11/2009 18:06 | 59.86 | 94 | Unit trip with 655 MW |
| 10/12/2009 2:27 | 59.83 | 104 | Multiple unit trips with 733 MW |
| 10/13/2009 10:38 | 59.89 | 2 | Unit trip with 173 MW |
| 10/14/2009 18:05 | 60.10 | 4 | Load dropped by 611 MW in 10 min, Wind +211 Mw in 10 min. Out of Down Regulation |
| 10/15/2009 6:43 | 59.90 | 4 | Unit trip with 585 MW |
| 10/26/2009 4:56 | 59.90 | 6 | Unit trip with 395 MW |
| 10/29/2009 20:05 | 60.12 | 187 | Out of Down Regulation |
| 10/30/2009 21:23 | 59.84 | 4 | Unit trip with 600 MW |

Note: Time of frequency excursions outside the range of +/- 0.1 Hz.

Deployed Responsive (Reported Above)

| Time deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- |
| 10/1 16:28:00 | 10/1 16:43:56 | 0:15:56 | 612.49 |  |
| 10/3 19:00:28 | 10/3 19:12:44 | 0:12:16 | 506.88 |  |
| 10/6 21:46:54 | 10/6 22:02:12 | 0:15:18 | 401.28 |  |
| 10/7 22:05:54 | 10/7 22:15:40 | 0:09:46 | 385.45 |  |
| 10/11 18:06:21 | 10/11 18:27:23 | 0:21:02 | 596.65 |  |
| 10/12 02:27:26 | 10/12 02:51:47 | 0:24:21 | 718.09 |  |
| 10/13 10:38:32 | 10/13 11:01:58 | 0:23:26 | 401.28 |  |
| 10/15 06:43:20 | 10/15 06:53:18 | 0:09:58 | 385.45 |  |
| 10/16 00:04:21 | 10/16 00:13:23 | 0:09:02 | 343.21 | SCE change -500 MW in 8m and slow unit response. |
| 10/21 14:40:04 | 10/21 14:54:16 | 0:14:12 | 327.36 | Unit Trip |
| 10/25 21:02:32 | 10/25 21:14:36 | 0:12:04 | 337.94 | Slow unit response and Cat. 2 OOME VDI's for transmission security |
| 10/26 04:55:56 | 10/26 05:12:32 | 0:16:36 | 374.90 |  |
| 10/26 06:08:32 | 10/26 06:25:56 | 0:17:24 | 332.64 | SCE change -500 in 10m, slow unit response |
| 10/29 08:06:06 | 10/29 08:23:10 | 0:17:04 | 327.36 | SCE change -500 MW in 4m |
| 10/29 14:04:14 | 10/29 14:24:42 | 0:20:28 | 327.36 | SCE change -500 MW in 7m, slow unit response |
| 10/29 17:06:38 | 10/29 17:19:50 | 0:13:12 | 343.21 | Unit Trip |
| 10/30 18:51:06 | 10/30 19:02:47 | 0:11:41 | 343.21 | Out of up regulation, SCE change -450 in 13m |
| 10/30 21:23:26 | 10/30 21:47:29 | 0:24:03 | 691.68 |  |

Day-Ahead OOMC and RPRS Capacity Purchases

| Details | OOMC | RPRS S1 | RPRS S2 | RPRS S1+S2 | RMR | Total |
| --- | --- | --- | --- | --- | --- | --- |
| DFW | 95 | 0 | 5 | 5 | 0 | 100 |
| Western | 0 | 5 | 12 | 17 | 4 | 21 |
| Houston | 0 | 10 | 5 | 15 | 0 | 15 |
| Northeast | 5 | 0 | 5 | 5 | 0 | 10 |
| E RIO | 9 | 0 | 0 | 0 | 0 | 9 |
| San Antonio | 5 | 1 | 3 | 4 | 0 | 9 |
| Austin | 0 | 5 | 4 | 9 | 0 | 9 |
| North | 0 | 2 | 7 | 9 | 0 | 9 |
| W RIO | 4 | 0 | 0 | 0 | 0 | 4 |
| South | 2 | 1 | 1 | 2 | 0 | 4 |
| Corpus | 2 | 1 | 0 | 1 | 0 | 3 |
| Bryan Area | 0 | 2 | 0 | 2 | 0 | 2 |
| Laredo | 0 | 1 | 0 | 1 | 0 | 1 |
| Total | 122 | 28 | 42 | 70 | 4 | 196 |

| Historical Totals | Oct-09 | Oct-08 | Sep-09 |
| --- | --- | --- | --- |
| Austin | 5 | 2 | 1 |
| Bryan Area | 2 | 0 | 0 |
| Corpus | 3 | 19 | 0 |
| DFW | 95 | 0 | 7 |
| E RIO | 9 | 5 | 1 |
| Houston | 10 | 0 | 3 |
| Laredo | 1 | 2 | 2 |
| North | 2 | 2 | 12 |
| Northeast | 5 | 0 | 0 |
| San Antonio | 6 | 0 | 1 |
| South | 3 | 2 | 1 |
| W RIO | 4 | 95 | 0 |
| Western | 9 | 6 | 11 |
| Total | 154 | 133 | 39 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Oak Creek - Ballinger 138KV | Miles - Rowena 69KV | 10 |
| Graham - Long Creek 345KV | San Angelo Power Station - Shrew 138KV | 8 |
| Austrop- Daffin - Decker 138KV | Austrop - Decker 138KV | 8 |
| Base Case Overload | Ena Snyder - MEC Plainview TAP 69KV | 7 |
| Morgan Creek - Eskota 138KV | Eskota Switch 138/69KV Autotransformer | 6 |
| Twin Butte - San Angelo Red Creek 345KV | Twin Butte 345/138KV transformer | 6 |
| Abilene South - Eskota 138KV | Trent - Merkel 69KV | 6 |
| Nicole - Oak Creek 138KV | San Angelo Concho - Veribest 69KV | 6 |
| Abilene Mulberry Creek - Bitter Creek & Long Creek 345KV | Trent - Merkel 69KV | 5 |
| Dilley Switch - San Miguel Switch 138KV | Derby - Pearsall 69KV | 5 |
| Elm Mott - Bosque Switch 345KV | Bosque Switch - Lake Whitney 138KV | 5 |
| Base Case | Magic Valley Electric Cooperative Palmhurst - Magic Valley Electric Cooperative Merrit - Magic Valley Electric Cooperative Pharr 138KV | 4 |
| Oak Creek - Ballinger 138KV | San Angelo Concho - Veribest 69KV | 4 |
| Bosque Switch - Lake Whitney 138KV | Olsen - Bosque Switch 138KV | 3 |
| Dilley Switch - North Laredo 138KV | Asherton - North Laredo 138KV | 3 |
| Tradinghouse - Elm Mott 345KV | Whitney TU autotransformer 345/138 kV | 3 |
| Abilene Mulberry Creek - Bitter Creek & Long Creek - Sweetwater Generating Plant 345KV | Radium - Anson 69KV | 3 |
| Aspermont - Paint Creek 138KV | Aspermont 138/69KV autotransformer | 3 |
| Base Case | San Angelo Power Station - Shrew 138KV - 102% of 143 MVA rating. | 3 |
| Base Case | Sonora - Cauthorn 138KV - 100% of 151 MVA rating. | 3 |
| Hill Country 345/138KV Transformer T3 | Hill Country 345/138KV Transformer T2 | 3 |
| Tradinghouse - Venus 345KV | Elm Mott - Rogers Hill | 3 |
| Fisher Road 345/138KV AT | Certain Teed - Wichita Falls Cogen Switch 138KV | 2 |
| Spur 138/69KV autotransformer | Jayton CSW - Spur 69KV1 | 2 |
| Spur 138/69KV autotransformer | Spur - Girard tap 69KV | 2 |
| Abilene - Eskota South West 138KV | Eskota Switch - Merkel 69KV | 2 |
| Aspermont - Spur 138KV | Jayton - Spur 69KV | 2 |
| Base Case | No Trees - No Trees Switch 138KV | 2 |
| Base Case | Friend Ranch - Sonora 138KV | 2 |
| Garfield - Onion Creek - Hicross AEN 138KV | Lytton Springs 345/138KV Autotransformer #2 | 2 |
| Graham - Bowman Switch - Parker Switch 345KV | Willow Creek - Parker Switch 345KV | 2 |
| Graham - Long Creek 345KV | Abilene South - Putnam 138KV | 2 |
| Lobo - Laredo VFT North 138KV | North Laredo - Wormser Road 138KV | 2 |
| Nicole - Oak Creek 138KV | San Angelo Concho - Miles 69KV | 2 |
| Roma Southwest- Falcon Switch 138KV | Freer - San Diego 69KV | 2 |
| San Angelo Red Creek - Comanche Switch 345KV | San Angelo Concho - Veribest 69KV | 2 |
| San Angelo Red Creek - San Angelo North 138KV | Twin Butte 345/138KV T1 XFMR | 2 |
| Sandow Switch - Temple Switch 345KV | Hearne 138/69KV Auto AT1 | 2 |
| Singleton - Obrien and Singleton - TH Wharton 345KV | San Angelo - Shrew 138KV | 2 |
| Baytown Energy Center - Chambers 345KV | Baytown Energy Center 345/138KV Autotransformer #1 | 1 |
| Comanche Peak SES - Decordova SES and Wolf Hollow - Rocky Creek 345KV | San Angelo Power Station - Shrew Tap | 1 |
| Falfurrias - North Edinburg 138KV | Alice - North Ella 69KV | 1 |
| Trinidad - Stryker Creek & Mt Enterprise 345KV | Lufkin Switch - Lufkin Chipper Mill 138KV | 1 |
| Lon Hill - North Edinburg 345KV | Harlingen Switch - Raymondville 69KV | 1 |
| Base Case Overload | Magic Valley - Palm 4 138KV | 1 |
| Big Brown - Jewett 345KV | Jewett - Big Brown 345KV | 1 |
| Dilley Switch - North Laredo 138KV | Asherton - North Laredo 138KV | 1 |
| Garfield - Hicross and Onion Creek - Pilot Knob 138KV | Grove - Advance Ckt_946 138KV | 1 |
| Ingleside DuPoint - Whitepoint 138KV | Whitepoint - Rincon 138KV | 1 |
| Luling - Lockhart 138KV | Lockhart 138/69KV transformer | 1 |
| Morgan Creek - Eskota 138KV | Trent - Merkel 69KV | 1 |
| Oak Creek - Ballinger 138KV | Abilene South - Cedar Gap TEC 69KV | 1 |
| Santa Anna - Ballinger 138KV | Ballinger - Humble Ballinger 69KV - 111% | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| West – North | 8 |
| North – Houston | 7 |

New RAP, PCAP (Date indicates last update of RAP, PCAP not implementation date.)

None

New Procedures/Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 10/01/2009 | Shift Supervisor Desk V 4 Rev 7 | 443 |
| 10/01/2009 | Transmission and Security Desk V 4 Rev 7 | 442 |
| 10/01/2009 | Frequency Control Desk V4 Rev 6 | 441 |

## Blackout/Load Shed Incidences

None

EEA

None

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

None

Communication

None

## ERCOT peak (Unofficial)

10/08 	   17:00 49,100 MW

Yearly MTLF Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison for the ERCOT Forecast |  |  |  |  |
| --- | --- | --- | --- | --- |
| Month | MAPE for MTLF at 16:00 Day-Ahead |  |  |  |
|  | 2006 | 2007 | 2008 | 2009 |
| January | 4.79 | 4.55 | 3.30 | 4.11 |
| February | 4.81 | 3.75 | 3.59 | 3.49 |
| March | 4.95 | 2.70 | 3.29 | 3.24 |
| April | 5.59 | 3.00 | 2.45 | 2.66 |
| May | 3.59 | 3.22 | 3.01 | 2.90 |
| June | 2.65 | 4.46 | 2.81 | 2.89 |
| July | 2.62 | 4.29 | 2.55 | 2.83 |
| August | 2.09 | 3.11 | 3.66 | 3.07 |
| September | 4.03 | 3.78 | 4.99 | 3.68 |
| October | 3.63 | 3.08 | 2.79 | 2.92 |
| November | 3.28 | 2.95 | 2.60 | NA |
| December | 3.44 | 3.74 | 4.54 | NA |
| Annual Average | 3.79 | 3.55 | 3.29 | 3.18 |

OCN, Advisory, Watch & Emergency Notices

Capacity

| Date | Start | End | Event |
| --- | --- | --- | --- |
| 10/4/09 | 19:45 | 21:00 | Advisory issued for ARRS below 3000 MW. |
| 10/8/09 | 9:00 | 20:20 | OCN Issued for Projected Reserve Capacity Shortage for HE 16:00-22:00. |
| 10/11/09 | 19:12 | 21:36 | Advisory issued for ARRS below 3000 MW. |
| 10/12/09 | 7:15 | 10:55 | Advisory issued for ARRS below 3000 MW. |
| 10/12/09 | 11:50 | 18:20 | Advisory issued for ARRS below 3000 MW. |
| 10/14/09 | 9:15 | 11:00 | OCN issued for projected capacity shortage for HE 16 - 18. |
| 10/14/09 | 11:00 | 18:00 | Watch issued due to a projected reserve capacity shortage for HE 16 - 18. |
| 10/14/09 | 11:20 | 20:00 | Advisory issued for ARRS below 3000 MW. |
| 10/15/09 | 14:02 | 19:40 | Advisory issued for ARRS below 3000 MW. |
| 10/21/09 | 7:24 | 11:05 | Advisory issued for ARRS below 3000 MW. |
| 10/21/09 | 20:12 | 22:10 | Advisory issued for ARRS below 3000 MW. |
| 10/25/09 | 10:05 | 14:30 | OCN issued due to projected reserve capacity shortage for hours 17:00 - 20:00. |
| 10/25/09 | 11:30 | 20:05 | Advisory issued due to ARRS below 3000 MW. |
| 10/29/09 | 3:30 | 7:15 | OCN issued for projected reserve capacity shortage for hours 13:00 to 17:00 and HE 20:00. |
| 10/29/09 | 5:52 | 8:45 | OCN issued for projected Balancing Energy Service up bids for hours HE 08:00, 11:00 to 17:00, 20:00 and 21:00. |
| 10/29/09 | 6:56 | 8:45 | Advisory issued for ARRS below 3000 MW. |

Transmission Watch

10/05  16:05	Transmission Watch issued due to a forced generator outage causing the post contingency loss of San Miguel 138KV - San Miguel 69KV overloads Derby - Pearsall 69KV.  ERCOT received emergency energy from CFE across the Laredo VFT.

10/13  09:15	Transmission Watch issued due to forced transmission outage.  ERCOT initiated a Block Load Transfer (BLT) at Presidio Substation transferring up to 5 MW of ERCOT load to CFE.

Emergency Notice

10/28  13:38	Market Emergency Notice issued due to failure to meet the Ancillary Service Market timeline.

Texas RE Event Analysis

10/06   10:33	Drumwright SPS activated.

10/12 10:05  ERCOT EMS System down due to the application database Memory Replication Service (MRS) slowing and becoming out-of-date, which caused the standby EMS to become unavailable before the primary EMS fails.

10/18  15:20 ERCOT EMS System down due to the application database Memory Replication Service (MRS) slowing and becoming out-of-date, which caused the standby EMS to become unavailable before the primary EMS fails.

10/28   13:38	Market Emergency Notice issued for Ancillary Services Market delay.

Others

10/13  10:30	ERCOT Held IE 10:30 Real-time Balancing deployments for IE 10:45 due to short-term load forecast error and resumed with IE 11:00.

10/19  07:30	ERCOT initiated a Block Load Transfer (BLT) at Estelline Substation transferring up to 1 MW of ERCOT load to Southwest Power Pool (SPP) for a planned transmission outage.

10/20  00:15	ERCOT initiated a Block Load Transfer (BLT) at Estelline Substation transferring up to 1 MW of ERCOT load to Southwest Power Pool (SPP) for a planned transmission outage.

10/21  00:15	ERCOT initiated a Block Load Transfer (BLT) at Estelline Substation transferring up to 1 MW of ERCOT load to Southwest Power Pool (SPP) for a planned transmission outage.

10/22  00:15	ERCOT initiated a Block Load Transfer (BLT) at Estelline Substation transferring up to 1 MW of ERCOT load to Southwest Power Pool (SPP) for a planned transmission outage.

10/29  07:20	ERCOT initiated a Block Load Transfer (BLT) at Estelline Substation transferring up to 1.5 MW from ERCOT to Southwest Power Pool (SPP) for a planned transmission outage.

10/21  20:45	ERCOT held IE 20:45 Real-time Balancing deployments and resumed with IE 21:15.