## Introduction
TLF = Transmission Loss Factor
SIEL = Settlement Interval ERCOT system Load
SSC = Seasonal Slope Coefficient = (SONLF - SOFFLF)/(SONL - SOFFL)
SIC = Seasonal Intercept Coefficient = [(SOFFLF * SONL) - (SONLF * SOFFL)]/(SONL - SOFFL)
SONLF = Seasonal on-peak percent loss factor
SOFFLF = Seasonal off-peak percent loss factor
SONL = Seasonal on-peak Load value
SOFFL = Seasonal off-peak Load value

## 2010_Transmission_Losses
TRANSMISSION LOSS FACTORS for 2010 as of 11/11/2009
Data from Seasonal SSWG Base Cases Updated with updates received by 9/17/09
Transmission Loss is from 60 kV or higher reporting only
NOIE INTERNAL refers to generation, load and losses behind NOIE meters
|  | ERCOT TOTAL |  |  |  | AEN NOIE INTERNAL TOTAL |  |  |  |  | CPS NOIE INTERNAL TOTAL |  |  |  |  | COG NOIE INTERNAL TOTAL |  |  |  |  | GEUS NOIE INTERNAL TOTAL |  |  |  |  | COD NOIE INTERNAL TOTAL |  |  |  |  | BPUB NOIE INTERNAL TOTAL |  |  |  |  | BTU NOIE INTERNAL TOTAL |  |  |  |  | COCS NOIE INTERNAL TOTAL
Case Type | Base Case Name | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV | Total Base Case Loss MW | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen) | Base Case Generation MW | Base Case Load MW | Base Case Loss above 60 kV MW | Total Base Case Loss MW | External (load+loss-gen)
Spring On Peak | 2010_SPG1 | 63727.3 | 62277.7 | 1352.69 | 1448.31 | 1210 | 2231.8 | 47.22 | 50.16 | 1071.96 | 2052.8 | 4232 | 21.49 | 24.29 | 2203.49 | 108.6 | 320.3 | 2.4 | 2.4 | 214.1 | 23 | 56.9 | 0.14 | 0.14 | 34.04 | 0 | 329.1 | 3 | 3 | 332.1 | 43 | 263 | 0.27 | 0.27 | 220.27 | 0 | 306.5 | 2.63 | 2.63 | 309.13 | 0 | 111.9 | 0.23 | 0.23 | 112.13
Spring Off Peak | 2010_SPG2 | 38883.9 | 38171.5 | 654.76 | 711.56 | 430 | 927.8 | 14.25 | 15 | 512.8 | 1784.3 | 2116 | 10.26 | 12.56 | 344.26 | 37.2 | 142.6 | 0.58 | 0.58 | 105.98 | 0 | 35.6 | 0.04 | 0.04 | 35.64 | 0 | 107.4 | 0.95 | 0.95 | 108.35 | 36 | 137 | 0.07 | 0.07 | 101.07 | 0 | 222.5 | 1.15 | 1.15 | 223.65 | 0 | 54.5 | 0.08 | 0.08 | 54.58
Summer On Peak | 2010_SUM1 | 74506.6 | 72839.5 | 1545.89 | 1666.31 | 1361 | 2443 | 56.33 | 59.44 | 1141.44 | 4637 | 5043 | 39.46 | 47.13 | 453.13 | 387.3 | 497 | 5.9 | 5.9 | 115.6 | 67 | 96.1 | 0.52 | 0.52 | 29.62 | 0 | 363.5 | 2.4 | 2.4 | 365.9 | 113 | 283 | 0.32 | 0.32 | 170.32 | 199 | 349.4 | 4.19 | 4.19 | 154.59 | 0 | 198.5 | 0.26 | 0.26 | 198.76
Summer Off Peak | 2010_SUM2 | 43908.8 | 43035.6 | 809.59 | 872.18 | 751 | 1186.2 | 23.1 | 24.58 | 459.78 | 2529 | 2572 | 14.81 | 18.34 | 61.34 | 45.6 | 150.9 | 0.87 | 0.87 | 106.17 | 25 | 58.8 | 0.15 | 0.15 | 33.95 | 0 | 195 | 0.8 | 0.8 | 195.8 | 81 | 131 | 0.15 | 0.15 | 50.15 | 2 | 199.9 | 1.54 | 1.54 | 199.44 | 0 | 92.6 | 0.08 | 0.08 | 92.68
Fall On Peak | 2010_FAL1 | 59299.5 | 58074.9 | 1133.65 | 1223.8 | 1119 | 2040 | 41.25 | 43.96 | 964.96 | 2742.1 | 3841 | 23.5 | 27.27 | 1126.17 | 101.3 | 313.1 | 2.02 | 2.02 | 213.82 | 54 | 82.7 | 0.33 | 0.63 | 29.33 | 0 | 297.5 | 1.5 | 1.5 | 299 | 47 | 271 | 0.29 | 0.29 | 224.29 | 0 | 328.8 | 3.4 | 3.4 | 332.2 | 0 | 147.2 | 0.35 | 0.35 | 147.55
Fall Off Peak | 2010_FAL2 | 36339.4 | 35616.1 | 669.77 | 722.81 | 356 | 854.9 | 15.62 | 16.4 | 515.3 | 2463 | 1959 | 12.14 | 15.44 | -488.56 | 29.9 | 135.4 | 0.48 | 0.48 | 105.98 | 16 | 51.6 | 0.1 | 0.38 | 35.98 | 0 | 136.4 | 0.81 | 0.81 | 137.21 | 44 | 130 | 0.06 | 0.06 | 86.06 | 0 | 169.4 | 1.15 | 1.15 | 170.55 | 0 | 70.4 | 0.04 | 0.04 | 70.44
Winter On Peak | 2011_WIN1 | 59191.2 | 57754.2 | 1344.44 | 1435.98 | 916 | 1760.8 | 43.02 | 45.1 | 889.9 | 2953 | 3160 | 18.14 | 22.2 | 229.2 | 161 | 372.1 | 2.41 | 2.41 | 213.51 | 35 | 66.7 | 0.2 | 0.33 | 32.03 | 0 | 216 | 2.3 | 2.3 | 218.3 | 18 | 233 | 0.28 | 0.28 | 215.28 | 0 | 205.3 | 1.69 | 1.69 | 206.99 | 0 | 140.3 | 0.16 | 0.16 | 140.46
Winter Off Peak | 2011_WIN2 | 39400.9 | 38528.4 | 814.35 | 871.53 | 379 | 928.3 | 24.19 | 25.23 | 574.53 | 2343 | 2054 | 11.94 | 14.96 | -274.04 | 42.2 | 152.1 | 0.56 | 0.56 | 110.46 | 0 | 39.2 | 0.05 | 0.05 | 39.25 | 0 | 119.9 | 0.97 | 0.97 | 120.87 | 0 | 119 | 0.07 | 0.07 | 119.07 | 0 | 151 | 0.93 | 0.93 | 151.93 | 0 | 71.8 | 0.04 | 0.04 | 71.84
Self Serve Load Modeled in Base Cases that does not contribute to transmission losses. | [8 empty] | NOIE TOTALS
Case Type | Base Case Name | CNP Self Serve MW | AEP Self Serve MW | TNMP Self Serve MW | BTU Self Serve MW | ONCOR Self Serve MW | AEP DC Ties Model MW | TOTAL |  | NOIE LOAD MW | NOIE External Resources MW | NOIE Load Served from Internal Resources MW | NOIE TOTAL Loss Above 60 kV | Base Case Name
Spring On Peak | 2010_SPG1 | 2824.4 | 1321.44 | 483 | 3.7 | 148.4 | 0 | 4780.94 |  | 7851.5 | 4497.22 | 3354.28 | 77.38 | 2010_SPG1
Spring Off Peak | 2010_SPG2 | 2824.4 | 1284.31 | 483 | 3.7 | 148.4 | 0 | 4743.81 |  | 3743.4 | 1486.33 | 2257.07 | 27.38 | 2010_SPG2
Summer On Peak | 2010_SUM1 | 2874.4 | 1321.44 | 483 | 2.2 | 148.4 | 0 | 4829.44 |  | 9273.5 | 2629.36 | 6644.14 | 109.38 | 2010_SUM1
Summer Off Peak | 2010_SUM2 | 2874.4 | 1283.8 | 483 | 2.2 | 148.4 | 0 | 4791.8 |  | 4586.4 | 1199.31 | 3387.09 | 41.5 | 2010_SUM2
Fall On Peak | 2010_FAL1 | 2874.4 | 1321.44 | 483 | 3 | 148.4 | 0 | 4830.24 |  | 7321.3 | 3337.32 | 3983.98 | 72.64 | 2010_FAL1
Fall Off Peak | 2010_FAL2 | 2874.4 | 1269.53 | 483 | 3 | 148.4 | 0 | 4778.33 |  | 3507.1 | 632.96 | 2874.14 | 30.4 | 2010_FAL2
Winter On Peak | 2011_WIN1 | 2874.4 | 1372.08 | 483 | 4.5 | 148.4 | 0 | 4882.38 |  | 6154.2 | 2145.67 | 4008.53 | 68.2 | 2011_WIN1
Winter Off Peak | 2011_WIN2 | 2874.4 | 1372.08 | 483 | 4.5 | 148.4 | 0 | 4882.38 |  | 3635.3 | 913.91 | 2721.39 | 38.75 | 2011_WIN2
SEASON | ERCOT WITH SELF SERVE LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF |  | SONL | SOFFL | SONLF | SOFFLF
SPRING | 58946.36 | 34140.09 | 2.295% | 1.918% |  | 2231.8 | 927.8 | 2.072% | 1.513% |  | 4232 | 2116 | 0.5052% | 0.4825% |  | 320.3 | 142.6 | 0.7437% | 0.4051% |  | 56.9 | 35.6 | 0.2454% | 0.1122% |  | 329.1 | 107.4 | 0.9033% | 0.8768% |  | 263 | 137 | 0.1026% | 0.05107% |  | 306.5 | 222.5 | 0.8508% | 0.5142% |  | 111.9 | 54.5 | 0.2051% | 0.1466%
SUMMER | 69677.16 | 39117 | 2.219% | 2.07% |  | 2443 | 1186.2 | 2.254% | 1.91% |  | 5043 | 2572 | 0.7764% | 0.5725% |  | 497 | 150.9 | 1.173% | 0.5732% |  | 96.1 | 58.8 | 0.5382% | 0.2545% |  | 363.5 | 195 | 0.6559% | 0.4086% |  | 283 | 131 | 0.1129% | 0.1144% |  | 349.4 | 199.9 | 1.185% | 0.7645% |  | 198.5 | 92.6 | 0.1308% | 0.08632%
FALL | 54469.26 | 31561.07 | 2.081% | 2.122% |  | 2040 | 854.9 | 1.982% | 1.794% |  | 3841 | 1959 | 0.6081% | 0.6159% |  | 313.1 | 135.4 | 0.641% | 0.3533% |  | 82.7 | 51.6 | 0.3974% | 0.1934% |  | 297.5 | 136.4 | 0.5017% | 0.5903% |  | 271 | 130 | 0.1069% | 0.04613% |  | 328.8 | 169.4 | 1.023% | 0.6743% |  | 147.2 | 70.4 | 0.2372% | 0.05679%
WINTER | 54308.82 | 34518.52 | 2.476% | 2.359% |  | 1760.8 | 928.3 | 2.385% | 2.54% |  | 3160 | 2054 | 0.5708% | 0.5779% |  | 372.1 | 152.1 | 0.6435% | 0.3668% |  | 66.7 | 39.2 | 0.299% | 0.1274% |  | 216 | 119.9 | 1.054% | 0.8025% |  | 233 | 119 | 0.12% | 0.05879% |  | 205.3 | 151 | 0.8165% | 0.6121% |  | 140.3 | 71.8 | 0.1139% | 0.05568%
TRANSMISSION LOSS FACTORS FOR INSTALLATION IN ERCOT SYSTEMS IN RED BOXES
SEASON | ERCOT WITH SELF SERVE, MODEL & NOIE INTERNAL LOAD CORRECTIONS |  |  |  |  | AEN NOIE INTERNAL |  |  |  |  | CPS NOIE INTERNAL |  |  |  |  | COG NOIE INTERNAL |  |  |  |  | GEUS NOIE INTERNAL |  |  |  |  | COD NOIE INTERNAL |  |  |  |  | BPUB NOIE INTERNAL |  |  |  |  | BTU NOIE INTERNAL |  |  |  |  | COCS NOIE INTERNAL
| SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC |  |  |  | SSC | SIC
SPRING | 1.5194e-05 | 1.3991 |  |  |  | 0.0004289 | 1.1147 |  |  |  | 1.0725e-05 | 0.45984 |  |  |  | 0.0019057 | 0.13333 |  |  |  | 0.0062539 | -0.11041 |  |  |  | 0.00011978 | 0.86392 |  |  |  | 0.00040863 | -0.0049137 |  |  |  | 0.0040069 | -0.37734 |  |  |  | 0.00102 | 0.090986
SUMMER | 4.8751e-06 | 1.879 |  |  |  | 0.0002734 | 1.5859 |  |  |  | 8.2507e-05 | 0.36031 |  |  |  | 0.0017335 | 0.31165 |  |  |  | 0.0076069 | -0.19283 |  |  |  | 0.0014679 | 0.12234 |  |  |  | -9.384e-06 | 0.1156 |  |  |  | 0.0028127 | 0.20224 |  |  |  | 0.00042014 | 0.047414
FALL | -1.7843e-06 | 2.1785 |  |  |  | 0.00015834 | 1.659 |  |  |  | -4.1381e-06 | 0.62399 |  |  |  | 0.0016194 | 0.13398 |  |  |  | 0.0065602 | -0.14508 |  |  |  | -0.00055036 | 0.66541 |  |  |  | 0.00043095 | -0.0098911 |  |  |  | 0.0021907 | 0.30319 |  |  |  | 0.0023492 | -0.1086
WINTER | 5.8806e-06 | 2.1562 |  |  |  | -0.00018585 | 2.7122 |  |  |  | -6.4838e-06 | 0.59126 |  |  |  | 0.0012576 | 0.17554 |  |  |  | 0.0062387 | -0.11717 |  |  |  | 0.0026127 | 0.48925 |  |  |  | 0.00053718 | -0.0051354 |  |  |  | 0.0037632 | 0.043884 |  |  |  | 0.0008501 | -0.0053582