## 1) General Information
CenterPoint Energy Distribution Loss Factor for 2010, R2
General Information on Distribution Loss Factor:
The Distribution Loss Factor is a percent that ERCOT will use to determine distribution losses for each Distribution Service Provider.
See ERCOT Protocols Section 13: Transmission and Distribution Losses, which was updated in January, 2009.
According to this protocol, ERCOT will calculate Distribution Loss Factors for each Settlement Interval of the Operating Day for
settlement purposes. Distribution Loss Factors will be calculated from the data provided by Distribution Service Providers using
the following equation
SILFi = F1 * (SIELi/AAL) + F2 + F3 / (SIELi / AAL)
Where:
i = interval (15 minutes)
SILFi = Settlement Interval Distribution Loss Factor
SIELi = Settlement Interval estimated ERCOT System Load
AAL = Annual Interval Average ERCOT System Load
F1, F2, F3 = Coefficients derived from regression analysis of the TDSP loss study results
AAL = Annual Total System MWh / (Number of settlement intervals in the year) Typically = 365 days * 24 hrs * 4 intervals
AAL value for use in 2010 = 8,785 MWH
AAL value for use in 2009 = 9,043 MWH
AAL value used in 2008 = 8,794 MWH
Customer Coding for CenterPoint Energy:
Distribution customers that take service at secondary voltage are coded "D"
Distribution customers that take service at primary voltage are coded "E"
CenterPoint Energy customers taking service at transmission level voltages have no distribution losses associated with their energy
delivery. Therefore, each transmission ESI-ID account has been coded with a "T", and their losses are determined by ERCOT rules for
transmission customers.
For "D" Secondary Customers
F1 = 0.016540
F2 = 0.000280
F3 = 0.019990
AAL for ERCOT (15 mins) = 8,785
For "E" Primary Customers
F1 = 0.010710
F2 = 0.000021
F3 = 0.001810
AAL for ERCOT (15 mins) = 8,785
Assumptions
1. Assume AAL for CNP corresponds to AAL for ERCOT
2. However, the peak for CNP is proportionately greater than the peak for ERCOT relative to AAL.
Ratio of Peak to AAL
|  | CNP | ERCOT
|  | 2.0507 | 1.808
Ratio of Peak to AAL for CNP is not proportional to ERCOT
|  |  | 15 mins |  | 1 hour
| CNP Peak (15 mins) |  | 3531.25 |  | 14125
| CNP AAL (15 mins) |  | 1722 |  | 6888
| ERCOT Peak (15mins) |  | 15883.5 |  | 63534
| ERCOT AAL (15 mins) |  | 8785 |  | 35140
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % losses (and DLF) above AAL are
increased an amount that is consistent with this higher loading at peak, so that when ERCOT hits peak, % losses will correspond to CNP peak.
Methodology upon which the calculation of loss factor was made:
Over the years, CenterPoint Energy has developed system loss equations for each part of the system. Equations for distribution
substation transformer losses, distribution primary conductor losses, distribution transformer losses and secondary conductor losses
were utilized to calculate the total losses on the CenterPoint Energy distribution system for various load levels. See Tab 3 - Loss Equations.
|  | Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
The constants (A & B) for each of the equations were updated in 2009 as follows:
1. Substation Transformer Losses
The current substation transformer database was used to determine the total "No-load" losses for all transformers on the system.
| This database contains test data for every substation transformer. | [5 empty] | 20.312
| The total no-load losses are 20.312 MW, which is a slight increase from the 18.586 MW used in 2006, 2007 and 2008. | [5 empty] | 53.531
| Also, the database provided the total "Load" losses for the transformers on the system at rated trf load. | [5 empty] | 73.843
This value is 53.531 MW at 16,700 MVA, which is a slight increase from 49.202 MW at 15,269 MVA used in 2006, 2007 and 2008,
but it is a reduction relative to the load squared.
This results in a total of 73.843 MW of substation transformer losses at approximately 16,700 MW at CNP.
The constants in the system loss equations were adjusted to match this result. See Tab 3.
As a result the A constant decreased and the B constant increased.
The result is a slight decrease in total losses for substation transformers as compared to 2006.
2. Primary Conductor Losses
The primary conductor losses for 2007 were considered to be similar to the losses in 2006, but the constant for the system loss
equation was increased 2.5% due to the increased loading on our circuits which is a result of our revised design criteria.
The design criteria allows higher loadings due to an increase in switching operations under contingency conditions from
2 pairs of switching operations to 4 pairs of switching operations.
For 2010, there is no further change in the system loss equations.
3. Distribution Transformer Losses
An inventory of the distribution transformers was downloaded from the GIS system. For every size transformer
the "No-load" losses and "Load" losses were determined by various test reports. This information was entered
| for each size of transformer to determine the total "No-load" losses and the total "Load" losses for the distribution transformers. | [5 empty] | 130.794
| Additionally, a TLM (Transformer Load Maintenance) Program was used to calculate no-load and load losses. | [5 empty] | 100.576
| Since the no-load losses used in the TLM program were based on older/higher values from 1985 and the spreadsheet | [5 empty] | 231.37
used more current test values from 2000-2005, the results of the two programs were averaged together to get
a balanced result for no-load losses for a distribution system that has both old and new transformers.
The load losses from both methods were very close so the load losses from GIS were used.
The no-load losses for 2009 are 130.794 MW versus 120.235 MW in 2006, 2007 and 2008.
The load losses for 2009 are 100.576 MW at system peak versus 91.300 MW at system peak in 2006, 2007 and 2008.
The constants in the system loss equations for 2010 for distribution transformers were adjusted accordingly.
4. Secondary Conductor Losses
The constant in the system loss equation for secondary losses for 2010 is same as used in previous years.
5. AAL for ERCOT
The AAL for ERCOT was updated based on information from ERCOT. The new value for 2010 is 8,875 MWH for 15 minutes.
DLF Coefficients (F1, F2 and F3)
For both primary and secondary customers, the F1, F2 and F3 coefficients were selected to provide a curve fit with the loss equations that were
developed above. F1 impacts the right side of the curve, F2 impacts the middle/entire curve, and F3 impacts the left side of the curve. These
coefficents were continually adjusted to get a curve fit in the most critical areas. See spreadsheet and graphs in Tab 2 - Loss Analysis.
Overall results:
|  |  |  | 2008 | 2009 for use in 2010
For "E" Primary Customers |  |  | DLF at AAL | 1.267% | 1.254%
|  |  | DLF at ERCOT Peak | 2.018% | 2.039%
|  |  |  | 2008 | 2009 for use in 2010
For "D" Secondary Customers |  |  | DLF at AAL | 3.535% | 3.681%
|  |  | DLF at ERCOT Peak | 4.034% | 4.124%
Questions:
If you have any questions, please call Richard Moffatt at CenterPoint Energy at 713-945-4162
or email at richard.moffatt@centerpointenergy.com.
CenterPoint Energy Distribution Loss Factor For 2010 R2.xls
2009-11-06

## Loss Comparison (hidden)
Loss Comparison With Different A/B Constants |  |  |  |  | Loss Analysis 02.xls
|  | Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
|  | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 1995 | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 2001 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| 2001 Modified | #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| Load |  | Sub Trf Losses |  | Primary Cond Losses |  | Dist Trf Losses |  | Sec Cond Losses |  | Total Losses | Total Losses
| (MW) |  | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%) | (MW) | (%)
1995 | 4000 |  | 22.7412 | 0.5685% | 16.6095 | 0.4152% | 106.3877 | 2.66% | 6.3214 | 0.158% | 152.0598 | 3.801%
2001 | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 4000 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 7600 |  | 37.0131 | 0.9253% | 60.0587 | 1.501% | 130.2566 | 3.256% | 23.1303 | 0.5783% | 250.4587 | 3.296%
2001 | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 7600 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
1995 | 11200 |  | 60.1434 | 1.504% | 130.3012 | 3.258% | 168.4144 | 4.21% | 50.0129 | 1.25% | 408.8719 | 3.651%
2001 | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2001 M | 11200 |  | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
Note: All % calculations are based on the total load which is shown in column 2.

## Loss Analysis 1995 (hidden)
HL&P Distribution Loss Analysis |  |  | 1995 |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | 19.2415 | 2380.7585 | 5.9514 | 2374.8071 | 100.482 | 2274.325 | 2.2011 | 127.8761 | 79.0922 | 48.7838 | 5.328% | 1.041% | 4.287% | 2.845% | 2.484% | 3.296% | 68.2691 | 59.607
2 | 2800 | 19.9524 | 2780.0476 | 8.1151 | 2771.9325 | 101.6834 | 2670.2491 | 3.0341 | 132.7851 | 92.2743 | 40.5108 | 4.742% | 1.214% | 3.528% | 2.879% | 1.863% | 3.296% | 80.6186 | 52.1665
3 | 3200 | 20.7726 | 3179.2274 | 10.6129 | 3168.6145 | 103.0686 | 3065.5459 | 3.999 | 138.453 | 105.4563 | 32.9967 | 4.327% | 1.388% | 2.939% | 2.914% | 1.413% | 3.296% | 93.2456 | 45.2075
4 | 3600 | 21.7022 | 3578.2978 | 13.4444 | 3564.8534 | 104.6369 | 3460.2165 | 5.0949 | 144.8784 | 118.6383 | 26.2401 | 4.024% | 1.561% | 2.463% | 2.949% | 1.076% | 3.296% | 106.1501 | 38.7284
5 | 4000 | 22.7412 | 3977.2588 | 16.6095 | 3960.6493 | 106.3877 | 3854.2617 | 6.3214 | 152.0598 | 131.8204 | 20.2394 | 3.801% | 1.734% | 2.067% | 2.983% | 0.8182% | 3.296% | 119.3321 | 32.7277
6 | 4400 | 23.8895 | 4376.1105 | 20.1079 | 4356.0027 | 108.3204 | 4247.6823 | 7.6778 | 159.9955 | 145.0024 | 14.9931 | 3.636% | 1.908% | 1.728% | 3.018% | 0.6183% | 3.296% | 132.7917 | 27.2038
7 | 4800 | 25.1472 | 4774.8528 | 23.9392 | 4750.9137 | 110.4343 | 4640.4793 | 9.1634 | 168.6841 | 158.1844 | 10.4997 | 3.514% | 2.081% | 1.433% | 3.053% | 0.4616% | 3.296% | 146.5287 | 22.1554
8 | 5200 | 26.5142 | 5173.4858 | 28.1032 | 5145.3826 | 112.729 | 5032.6536 | 10.7777 | 178.1241 | 171.3665 | 6.7576 | 3.425% | 2.255% | 1.171% | 3.087% | 0.3381% | 3.296% | 160.5433 | 17.5808
9 | 5600 | 27.9906 | 5572.0094 | 32.5997 | 5539.4098 | 115.2037 | 5424.2061 | 12.52 | 188.3139 | 184.5485 | 3.7654 | 3.363% | 2.428% | 0.9345% | 3.122% | 0.2407% | 3.296% | 174.8354 | 13.4785
10 | 6000 | 29.5764 | 5970.4236 | 37.4283 | 5932.9954 | 117.8578 | 5815.1376 | 14.3897 | 199.2521 | 197.7305 | 1.5216 | 3.321% | 2.602% | 0.7192% | 3.157% | 0.1641% | 3.296% | 189.405 | 9.8471 | Highlighted Area Represents 96% Range
11 | 6400 | 31.2715 | 6368.7285 | 42.5887 | 6326.1398 | 120.6908 | 6205.449 | 16.3862 | 210.9372 | 210.9126 | 0.024651 | 3.296% | 2.775% | 0.5207% | 3.191% | 0.1045% | 3.296% | 204.2522 | 6.685
12 | 6800 | 33.076 | 6766.924 | 48.0808 | 6718.8432 | 123.702 | 6595.1412 | 18.5089 | 223.3677 | 224.0946 | -0.72694 | 3.285% | 2.949% | 0.3362% | 3.226% | 0.05869% | 3.296% | 219.3768 | 3.9908
13 | 7200 | 34.9898 | 7165.0102 | 53.9042 | 7111.1059 | 126.8908 | 6984.2152 | 20.7571 | 236.542 | 237.2766 | -0.73466 | 3.285% | 3.122% | 0.1632% | 3.261% | 0.02449% | 3.296% | 234.779 | 1.763
14 | 7600 | 37.0131 | 7562.9869 | 60.0587 | 7502.9282 | 130.2566 | 7372.6717 | 23.1303 | 250.4587 | 250.4587 | 0 | 3.296% | 3.296% | 0% | 3.296% | 0% | 3.296% | 250.4587 | 0
15 | 8000 | 39.1456 | 7960.8544 | 66.544 | 7894.3104 | 133.7988 | 7760.5116 | 25.6279 | 265.1163 | 263.6407 | 1.4756 | 3.314% | 3.469% | -0.155% | 3.33% | -0.01625% | 3.296% | 266.4159 | -1.2996
16 | 8400 | 41.3876 | 8358.6124 | 73.3597 | 8285.2527 | 137.5168 | 8147.7359 | 28.2492 | 280.5133 | 276.8228 | 3.6905 | 3.339% | 3.642% | -0.303% | 3.365% | -0.02544% | 3.296% | 282.6506 | -2.1373
17 | 8800 | 43.7389 | 8756.2611 | 80.5057 | 8675.7554 | 141.41 | 8534.3454 | 30.9936 | 296.6482 | 290.0048 | 6.6434 | 3.371% | 3.816% | -0.4449% | 3.4% | -0.02858% | 3.296% | 299.1628 | -2.5146
18 | 9200 | 46.1996 | 9153.8004 | 87.9817 | 9065.8188 | 145.4777 | 8920.341 | 33.8606 | 313.5196 | 303.1868 | 10.3328 | 3.408% | 3.989% | -0.5815% | 3.434% | -0.02645% | 3.296% | 315.9526 | -2.433
19 | 9600 | 48.7696 | 9551.2304 | 95.7873 | 9455.4431 | 149.7195 | 9305.7236 | 36.8496 | 331.126 | 316.3689 | 14.7571 | 3.449% | 4.163% | -0.7135% | 3.469% | -0.01973% | 3.296% | 333.0199 | -1.8939
20 | 10000 | 51.449 | 9948.551 | 103.9224 | 9844.6286 | 154.1346 | 9690.494 | 39.9599 | 349.4659 | 329.5509 | 19.915 | 3.495% | 4.336% | -0.8415% | 3.504% | -0.008988% | 3.296% | 350.3646 | -0.89877
21 | 10400 | 54.2378 | 10345.7622 | 112.3865 | 10233.3757 | 158.7226 | 10074.6531 | 43.1909 | 368.5378 | 342.7329 | 25.8049 | 3.544% | 4.51% | -0.966% | 3.538% | 0.005297% | 3.296% | 367.9869 | 0.55086
22 | 10800 | 57.1359 | 10742.8641 | 121.1796 | 10621.6845 | 163.4827 | 10458.2018 | 46.5421 | 388.3403 | 355.915 | 32.4253 | 3.596% | 4.683% | -1.087% | 3.573% | 0.02272% | 3.296% | 385.8868 | 2.4536
23 | 11200 | 60.1434 | 11139.8566 | 130.3012 | 11009.5554 | 168.4144 | 10841.141 | 50.0129 | 408.8719 | 369.097 | 39.7749 | 3.651% | 4.857% | -1.206% | 3.608% | 0.04293% | 3.296% | 404.0641 | 4.8079
24 | 11600 | 63.2602 | 11536.7398 | 139.7512 | 11396.9886 | 173.5171 | 11223.4715 | 53.6027 | 430.1312 | 382.279 | 47.8522 | 3.708% | 5.03% | -1.322% | 3.642% | 0.06562% | 3.296% | 422.5189 | 7.6123
25 | 12000 | 66.4864 | 11933.5136 | 149.5292 | 11783.9844 | 178.7903 | 11605.1941 | 57.3109 | 452.1168 | 395.4611 | 56.6557 | 3.768% | 5.203% | -1.436% | 3.677% | 0.09055% | 3.296% | 441.2513 | 10.8654
26 | 12400 | 69.822 | 12330.178 | 159.635 | 12170.543 | 184.2332 | 11986.3098 | 61.1369 | 474.827 | 408.6431 | 66.1839 | 3.829% | 5.377% | -1.548% | 3.712% | 0.1175% | 3.296% | 460.2612 | 14.5658
27 | 12800 | 73.267 | 12726.733 | 170.0682 | 12556.6648 | 189.8453 | 12366.8195 | 65.0801 | 498.2606 | 421.8251 | 76.4355 | 3.893% | 5.55% | -1.658% | 3.746% | 0.1462% | 3.296% | 479.5486 | 18.712
| % Losses at Peak = | 0.5724% |  | 1.336% |  | 1.512% |  | 0.5262%
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified

## 2) Loss Analysis 2009
|  | CenterPoint Energy Distribution Loss Factor For 2010 R2.xls | [13 empty] | With Scaling | Using F1, F2 & F3 Coefficients |  |  | With Scaling
ERCOT | ERCOT |  | CNP | CNP |  | PELCAR | Primary | Total | Total |  |  | 2009 | Secondary | 2009 | 2009 | 2009 | 2010 | 2010 | Total | 2009 | Adjustment for % Losses |  | 2008 | 2008
Load (15 min) | Load (1 hr) |  | Load (15 min) | Input To Sub Trfs | Sub Trf Losses | Input to Dist Sys | Conductor Losses | Primary Losses | Primary Loss % | Input to Dist Trfs | Dist Trf Losses | Input To Secondary | Conductor Losses | Total Losses | Total Losses | Total Losses | DLF | DLF | Primary Loss % | Primary Loss % | Sec | Pri | Primary MW Losses | Sec MW Losses
|  |  |  | (MW) | (MW) | (MW) | (MW) |  |  | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | Secondary | Primary
SIEL | [15 empty] | 0% |  |  |  | 0%
|  |  |  | 50 | 20.3125 | 29.6875 | 0.0010042 | 20.3135 | 40.63% | 29.6865 | 130.7944 | -101.1079 | 0.0036236 | 151.1116 | 302.2% | 302.2%
|  |  |  | 135 | 20.3155 | 114.6845 | 0.014986 | 20.3305 | 15.06% | 114.6695 | 130.8006 | -16.1311 | 9.2235e-05 | 151.1312 | 111.9% | 111.9%
|  |  |  | 500 | 20.36 | 479.64 | 0.26212 | 20.6221 | 4.124% | 479.3779 | 130.9098 | 348.468 | 0.043042 | 151.575 | 30.31% | 30.31%
1275.4065 | 5101.626 |  | 250 | 1000 | 20.5039 | 979.4961 | 1.0931 | 21.5971 | 2.16% | 978.4029 | 131.2766 | 847.1264 | 0.25437 | 153.128 | 15.31% | 15.31%
3060.9756 | 12243.9024 | 1 | 600 | 2400 | 21.4176 | 2378.5824 | 6.4463 | 27.8639 | 1.161% | 2372.1361 | 133.6306 | 2238.5055 | 1.7762 | 163.2706 | 6.803% | 6.803% | 6.341% | 0.8947% | 1.161% | 1.161% |  |  | 27.8639 | 163.2706
3571.1382 | 14284.5528 | 2 | 700 | 2800 | 21.8168 | 2778.1832 | 8.7942 | 30.611 | 1.093% | 2769.389 | 134.6602 | 2634.7288 | 2.4606 | 167.7318 | 5.99% | 5.99% | 5.618% | 0.8827% | 1.093% | 1.093% |  |  | 30.611 | 167.7318
4081.3008 | 16325.2033 | 3 | 800 | 3200 | 22.2775 | 3177.7225 | 11.5055 | 33.783 | 1.056% | 3166.217 | 135.8476 | 3030.3695 | 3.2551 | 172.8856 | 5.403% | 5.403% | 5.099% | 0.8893% | 1.056% | 1.056% |  |  | 33.783 | 172.8856
4591.4634 | 18365.8537 | 4 | 900 | 3600 | 22.7996 | 3577.2004 | 14.58 | 37.3796 | 1.038% | 3562.6204 | 137.1922 | 3425.4282 | 4.1591 | 178.7309 | 4.965% | 4.965% | 4.717% | 0.9082% | 1.038% | 1.038% |  |  | 37.3796 | 178.7309
5101.626 | 20406.5041 | 5 | 1000 | 4000 | 23.3831 | 3976.6169 | 18.0177 | 41.4008 | 1.035% | 3958.5992 | 138.6935 | 3819.9057 | 5.1722 | 185.2665 | 4.632% | 4.632% | 4.431% | 0.9357% | 1.035% | 1.035% |  |  | 41.4008 | 185.2665
5611.7886 | 22447.1545 | 6 | 1100 | 4400 | 24.028 | 4375.972 | 21.8183 | 45.8463 | 1.042% | 4354.1537 | 140.3511 | 4213.8026 | 6.2938 | 192.4913 | 4.375% | 4.375% | 4.214% | 0.9696% | 1.042% | 1.042% |  |  | 45.8463 | 192.4913
6121.9512 | 24487.8049 | 7 | 1200 | 4800 | 24.7344 | 4775.2656 | 25.9817 | 50.7161 | 1.057% | 4749.2839 | 142.1643 | 4607.1196 | 7.5236 | 200.404 | 4.175% | 4.175% | 4.049% | 1.008% | 1.057% | 1.057% |  |  | 50.7161 | 200.404
6632.1138 | 26528.4553 | 8 | 1300 | 5200 | 25.5021 | 5174.4979 | 30.5077 | 56.0098 | 1.077% | 5143.9902 | 144.1328 | 4999.8574 | 8.861 | 209.0036 | 4.019% | 4.019% | 3.925% | 1.05% | 1.077% | 1.077% |  |  | 56.0098 | 209.0036
7142.2764 | 28569.1057 | 9 | 1400 | 5600 | 26.3313 | 5573.6687 | 35.396 | 61.7274 | 1.102% | 5538.2726 | 146.256 | 5392.0166 | 10.3055 | 218.2889 | 3.898% | 3.898% | 3.831% | 1.095% | 1.102% | 1.102% |  | 0 | 61.7274 | 218.2889
7652.439 | 30609.7561 | 10 | 1500 | 6000 | 27.222 | 5972.778 | 40.6467 | 67.8686 | 1.131% | 5932.1314 | 148.5334 | 5783.598 | 11.8567 | 228.2587 | 3.804% | 3.804% | 3.764% | 1.143% | 1.131% | 1.144% |  | 1 | 68.6115 | 228.2587
8162.6016 | 32650.4065 | 11 | 1600 | 6400 | 28.174 | 6371.826 | 46.2594 | 74.4334 | 1.163% | 6325.5666 | 150.9645 | 6174.6021 | 13.514 | 238.9119 | 3.733% | 3.733% | 3.716% | 1.192% | 1.163% | 1.188% |  | 2 | 76.0182 | 238.9119
8672.7642 | 34691.0569 | 12 | 1700 | 6800 | 29.1874 | 6770.8126 | 52.2341 | 81.4215 | 1.197% | 6718.5785 | 153.5488 | 6565.0297 | 15.2771 | 250.2474 | 3.68% | 3.68% | 3.686% | 1.243% | 1.197% | 1.235% | 0 | 3 | 83.9472 | 250.2474
9182.9268 | 36731.7073 | 13 | 1800 | 7200 | 30.2623 | 7169.7377 | 58.5705 | 88.8328 | 1.234% | 7111.1672 | 156.2857 | 6954.8814 | 17.1454 | 262.2639 | 3.643% | 3.659% | 3.669% | 1.295% | 1.234% | 1.283% | 1 | 4 | 92.3985 | 263.4239
9693.0894 | 38772.3577 | 14 | 1900 | 7600 | 31.3986 | 7568.6014 | 65.2685 | 96.6671 | 1.272% | 7503.3329 | 159.1749 | 7344.158 | 19.1184 | 274.9604 | 3.618% | 3.65% | 3.665% | 1.348% | 1.272% | 1.334% | 2 | 5 | 101.3719 | 277.4093
10203.252 | 40813.0081 | 15 | 2000 | 8000 | 32.5964 | 7967.4036 | 72.3279 | 104.9243 | 1.312% | 7895.0757 | 162.2157 | 7732.86 | 21.1957 | 288.3357 | 3.604% | 3.653% | 3.67% | 1.402% | 1.312% | 1.386% | 3 | 6 | 110.8671 | 292.2024
10713.4146 | 42853.6585 | 16 | 2100 | 8400 | 33.8555 | 8366.1445 | 79.7486 | 113.6041 | 1.352% | 8286.3959 | 165.4078 | 8120.9881 | 23.3768 | 302.3887 | 3.6% | 3.664% | 3.684% | 1.457% | 1.352% | 1.439% | 4 | 7 | 120.8841 | 307.802
11223.5772 | 44894.3089 | 17 | 2200 | 8800 | 35.1761 | 8764.8239 | 87.5304 | 122.7064 | 1.394% | 8677.2936 | 168.7505 | 8508.5431 | 25.6612 | 317.1182 | 3.604% | 3.684% | 3.706% | 1.512% | 1.394% | 1.493% | 5 | 8 | 131.4226 | 324.2071
11733.7398 | 46934.9593 | 18 | 2300 | 9200 | 36.5581 | 9163.4419 | 95.6731 | 132.2311 | 1.437% | 9067.7689 | 172.2434 | 8895.5255 | 28.0486 | 332.5231 | 3.614% | 3.711% | 3.734% | 1.568% | 1.437% | 1.549% | 6 | 9 | 142.4826 | 341.4164
12243.9024 | 48975.6098 | 19 | 2400 | 9600 | 38.0015 | 9561.9985 | 104.1765 | 142.178 | 1.481% | 9457.822 | 175.886 | 9281.936 | 30.5383 | 348.6023 | 3.631% | 3.744% | 3.768% | 1.625% | 1.481% | 1.605% | 7 | 10 | 154.0637 | 359.4289
12754.065 | 51016.2602 | 20 | 2500 | 10000 | 39.5063 | 9960.4937 | 113.0405 | 152.5468 | 1.525% | 9847.4532 | 179.6778 | 9667.7753 | 33.1299 | 365.3546 | 3.654% | 3.782% | 3.806% | 1.682% | 1.525% | 1.662% | 8 | 11 | 166.1659 | 378.2435
13264.2276 | 53056.9106 | 21 | 2600 | 10400 | 41.0726 | 10358.9274 | 122.265 | 163.3375 | 1.571% | 10236.6625 | 183.6184 | 10053.0441 | 35.823 | 382.7789 | 3.681% | 3.826% | 3.849% | 1.739% | 1.571% | 1.719% | 9 | 12 | 178.7889 | 397.8589
13774.3902 | 55097.561 | 22 | 2700 | 10800 | 42.7002 | 10757.2998 | 131.8496 | 174.5499 | 1.616% | 10625.4501 | 187.7071 | 10437.743 | 38.6172 | 400.8741 | 3.712% | 3.873% | 3.896% | 1.797% | 1.616% | 1.777% | 10 | 13 | 191.9327 | 418.2741
14284.5528 | 57138.2114 | 23 | 2800 | 11200 | 44.3893 | 11155.6107 | 141.7944 | 186.1837 | 1.662% | 11013.8163 | 191.9435 | 10821.8727 | 41.5118 | 419.6391 | 3.747% | 3.924% | 3.947% | 1.855% | 1.662% | 1.836% | 11 | 14 | 205.5971 | 439.488
14794.7154 | 59178.8618 | 24 | 2900 | 11600 | 46.1399 | 11553.8601 | 152.0991 | 198.2389 | 1.709% | 11401.7611 | 196.3272 | 11205.4339 | 44.5066 | 439.0728 | 3.785% | 3.978% | 4% | 1.913% | 1.709% | 1.895% | 12 | 15 | 219.7818 | 461.4994
15304.878 | 61219.5122 | 25 | 3000 | 12000 | 47.9518 | 11952.0482 | 162.7635 | 210.7153 | 1.756% | 11789.2847 | 200.8576 | 11588.4271 | 47.601 | 459.1739 | 3.826% | 4.036% | 4.057% | 1.972% | 1.756% | 1.954% | 13 | 16 | 234.4867 | 484.3073
15815.0407 | 63260.1626 | 26 | 3100 | 12400 | 49.8252 | 12350.1748 | 173.7875 | 223.6127 | 1.803% | 12176.3873 | 205.5342 | 11970.8531 | 50.7946 | 479.9415 | 3.87% | 4.096% | 4.116% | 2.031% | 1.803% | 2.014% | 14 | 17 | 249.7117 | 507.9104
16325.2033 | 65300.813 | 27 | 3200 | 12800 | 51.76 | 12748.24 | 185.171 | 236.9309 | 1.851% | 12563.0691 | 210.3566 | 12352.7125 | 54.0869 | 501.3744 | 3.917% | 4.159% | 4.177% | 2.09% | 1.851% | 2.074% | 15 | 18 | 265.4566 | 532.3077
16835.3659 | 67341.4634 | 28 | 3300 | 13200 | 53.7562 | 13146.2438 | 196.9136 | 250.6698 | 1.899% | 12949.3302 | 215.3242 | 12734.006 | 57.4774 | 523.4714 | 3.966% | 4.223% | 4.241% | 2.149% | 1.899% | 2.134% | 16 | 19 | 281.7212 | 557.4981
17345.5285 | 69382.1138 | 29 | 3400 | 13600 | 55.8138 | 13544.1862 | 209.0154 | 264.8292 | 1.947% | 13335.1708 | 220.4366 | 13114.7342 | 60.9658 | 546.2316 | 4.016% | 4.29% | 4.306% | 2.208% | 1.947% | 2.195% | 17 | 20 | 298.5054 | 583.4805
17855.6911 | 71422.7642 | 30 | 3500 | 14000 | 57.9328 | 13942.0672 | 221.476 | 279.4089 | 1.996% | 13720.5911 | 225.6933 | 13494.8978 | 64.5515 | 569.6537 | 4.069% | 4.359% | 4.373% | 2.268% | 1.996% | 2.256% | 18 | 21 | 315.8089 | 610.2537
18365.8537 | 73463.4146 | 31 | 3600 | 14400 | 60.1133 | 14339.8867 | 234.2954 | 294.4088 | 2.045% | 14105.5912 | 231.0938 | 13874.4975 | 68.2341 | 593.7367 | 4.123% | 4.429% | 4.442% | 2.328% | 2.045% | 2.317% | 19 | 22 | 333.6316 | 637.8167
18876.0163 | 75504.065 | 32 | 3700 | 14800 | 62.3552 | 14737.6448 | 247.4734 | 309.8286 | 2.093% | 14490.1714 | 236.6376 | 14253.5338 | 72.0132 | 618.4794 | 4.179% | 4.501% | 4.512% | 2.388% | 2.093% | 2.378% | 20 | 23 | 351.9734 | 666.1683
19386.1789 | 77544.7154 | 33 | 3800 | 15200 | 64.6585 | 15135.3415 | 261.0098 | 325.6683 | 2.143% | 14874.3317 | 242.3242 | 14632.0075 | 75.8883 | 643.8809 | 4.236% | 4.574% | 4.584% | 2.448% | 2.143% | 2.44% | 21 | 24 | 370.8341 | 695.3075
19896.3415 | 79585.3659 | 34 | 3900 | 15600 | 67.0233 | 15532.9767 | 274.9045 | 341.9277 | 2.192% | 15258.0723 | 248.1531 | 15009.9192 | 79.859 | 669.9398 | 4.294% | 4.649% | 4.657% | 2.508% | 2.192% | 2.501% | 22 | 25 | 390.2134 | 725.2332
21299.2886 | 85197.1545 |  | 4175 | 16700 | 73.843 | 16626.157 | 314.9605 | 388.8035 | 2.328% | 16311.1965 | 264.9126 | 16046.2838 | 91.2675 | 744.9837 | 4.461% |  | 4.863% | 2.673% | 2.328%
8785 | 35140 |  | 1722 | 6888
15 min | ERCOT |  | 15 min | CNP | [12 empty] | Secondary | Primary
8785 | 35140 | AAL | 1722 | 6888 | 28.6917 | 6859.3083 | 53.6084 | 82.3001 | 1.195% | 6805.6999 | 144.0376 | 6661.6623 | 15.7301 | 242.0678 | 3.514% |  | 3.681% | 1.254% | At ERCOT AAL
15883.5 | 63534 | Peak | 3531.25 | 14125 | 61.0828 | 14063.9172 | 225.3642 | 286.4471 | 2.028% | 13838.5529 | 218.6497 | 13619.9032 | 65.753 | 570.8497 | 4.041% |  | 4.124% | 2.039% | At ERCOT Peak
18015.1169 | [14 empty] | Scaling for % Losses
CNP peak is proportionately higher than CNP AAL as compared to ERCOT peak vs ERCOT AAL, so % Losses above AAL are scaled proportionately ---> | [14 empty] | Secondary | Primary |  | 2009
(When ERCOT is at peak, CNP is four intervals below peak, so % losses at ERCOT peak are scaled up to match % losses at CNP peak.) | [14 empty] | 0.29% | 0.26% |  | For Secondary Distribution Customers "D"
|  |  |  | Substation Transformers |  | Primary Conductor |  |  |  | Distribution Transformers |  | Secondary Conductor | [5 empty] | Secondary Constants
|  |  |  | B Constant | A Constant | B Constant | A Constant |  |  | B Constant | A Constant | B Constant | A Constant
|  |  | 2009 Values ----> | 20.312 | 1.9194e-07 | 0 | 1.1394e-06 |  | 2009 Values ----> | 130.794 | 5.041e-07 | 0 | 3.5446e-07
|  |  | 2008 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2008 Values |  |  | F1 = | 0.01654 | right
|  |  | 2007 Values ----> | 18.586 | 2.13e-07 | 0 | 1.1394e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <--- 2007 Values |  |  | F2 = | 0.00028 | middle
[17 empty] | F3 = | 0.01999 | left
|  |  |  | 17.273 | 3.4176e-07 | 0 | 1.05e-06 | <--- 1995 |  | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | <--- 1995
|  |  |  | 19.73 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2001 |  | 115.01 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2001 |  |  |  | For Primary Distribution Customers "E"
|  |  |  | 20.2955 | 2.9981e-07 | 0 | 1.1116e-06 | <--- 2004/2006 |  | 133.2966 | 5.6399e-07 | 0 | 3.5446e-07 | <--- 2004/2006 |  |  |  | Primary Constants
|  |  |  | 2.866% increase in Sub Trf nameplate MVA from 2001 to 2004 | [5 empty] | 15.9% 1ncrease in distribution trf nameplate KVA from 2001 to 2004
|  |  | 2007 Start Values ----> | 18.586 | 2.13e-07 | 0 | 1.1116e-06 |  |  | 120.235 | 5.139e-07 | 0 | 3.5446e-07 | <---2007 Start Value |  |  | F1 = | 0.01071 | right
|  |  |  | New values as per updated |  | Add 2.5 % to 2006 values due |  |  |  | New values as per updated | [6 empty] | F2 = | 2.1e-05 | middle
|  |  | 2007 Adjustments ----> | substation trf review. |  | to increased loading on circuits |  |  |  | distribution trf review. | [6 empty] | F3 = | 0.00181 | left
|  |  |  | Decrease from 2006 values. |  | as per revised Design Criteria |  |  |  | Decrease from 2006 values. |  | No change to 2006 values.
[11 empty] | AAL for ERCOT (15 mins) = 8,785 |  |  | DLF = F1 * (SIEL/AAL) + F2 + F3 / (SIEL/AAL)
(See graphs below and to the right)
AAL for ERCOT = 8,785 for 15 minutes
2009
Secondary Constants
F1 = | 0.01654 | right
F2 = | 0.00028 | middle
F3 = | 0.01999 | left

## 3) Loss Equations
System Loss Equations For CenterPoint Energy for 2010 DLF |  |  |  |  | Sept 28,2009
| Losses = | AX2 + B
A = Constant
B = Constant
X = Input to System (MW)
Substation Transformers
| 73.843 = | A * (16700 * 16700) + 20.312
| A = | 1.9194e-07
| B = | 20.312 | Total No-Load Losses For Substation Transformers = 20.312 MW
Total Load Losses = 53.531 MW at 16,700 MW load level
[5 empty] | 2009 | 2008
[5 empty] | 20.312 | 18.586
[5 empty] | 53.531 | 49.203
[5 empty] | 73.843 | 67.789
Primary Conductor
| A = | 1.1394e-06 |  | <---- Revised in 2007, no change since then.
| B = | 0
Distribution Transformers
| 231.37 = | A * (14125 * 14125) + 130.794
| A = | 5.041e-07
| B = | 130.794 | Total No-Load Losses For Distribution Transformers = 130.794 MW
Total Load Losses = 100.576 MW at 14,125 MW load level
[5 empty] | 2009 | 2008
[5 empty] | 130.794 | 120.235
[5 empty] | 100.576 | 91.3
[5 empty] | 231.37 | 211.535
Secondary Conductor
| A = | 3.5446e-07 | Same value as used in previous years.
| B = | 0

## Loss Analysis 2001 Mod (hidden)
HL&P Distribution Loss Analysis |  |  | 2001 Modified |  | Loss Analysis 02.xls | [6 empty] | K = | 0 | K = | 0.8 | K = | 1
|  |  | PELCAR | [7 empty] | Difference |  | Tangent ? | Difference | K Formula | Difference | K Formula | Losses Based | Difference
| Input to Sub Trfs | Sub Trf Losses | Input to Dist Sys | Pri Cond Losses | Input to Dist Trfs | Dist Trf Losses | Input to Secondary | Secondary Losses | Total Losses | Tangent ? | Losses - Tangent | Total Losses | K = 0.0 | Loss - (K=0.0) | K = 0.8 | Loss - (K=0.8) | K = 1.0 | On K = 0.8 | Loss - (K=0.8)
| (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (MW) | (%) | (%) | (%) | (%) | (%) | (%) | (MW) | (MW)
1 | 2400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
2 | 2800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
3 | 3200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
4 | 3600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
5 | 4000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
6 | 4400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
7 | 4800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
8 | 5200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
9 | 5600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
10 | 6000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
11 | 6400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
12 | 6800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
13 | 7200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
14 | 7600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
15 | 8000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
16 | 8400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
17 | 8800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
18 | 9200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
19 | 9600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
20 | 10000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
21 | 10400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
22 | 10800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
23 | 11200 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
24 | 11600 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
25 | 12000 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
26 | 12400 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
27 | 12800 | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF!
| % Losses at Peak = | #REF! |  | #REF! |  | #REF! |  | #REF!
400
| Substation Transformers |  | Primary Conductor |  | Distribution Transformers |  | Secondary Conductor
| B Constant | A Constant | B Constant | A Constant | B Constant | A Constant | B Constant | A Constant
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF!
| 17.273 | 3.4176e-07 | 0 | 1.05e-06 | 97.167 | 5.878e-07 | 0 | 4.2553e-07 | 1995
| #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | #REF! | 2001
| #REF! | #REF! | 0 | 1.413e-06 | #REF! | #REF! | 0 | #REF! | 2001 Modified