| PRR Number | 838 | PRR Title | Fast Response Distributed Energy Resource (DER) |
| --- | --- | --- | --- |
| Date | November 19, 2009 |
| Submitter’s Information |
| Name | The Performance, Disturbance, Compliance Working Group (PDCWG), Sydney Niemeyer Vice chair |
| E-mail Address | Sydney.niemeyer@nrgenergy.com |
| Company | NRG Texas LP |
| Phone Number | 713-795-6108 |
| Cell Number | 832-655-0410 |
| Market Segment | ROS Working Group |

Comments

    - Responsive Reserve Service (paragraph 15)

The DER is included with the Load acting as a Resource as stated in paragraph 8 and paragraph 1(b), however, DER will not be on-line and providing energy during the same time period of a disturbance (NERC C point of Interconnection frequency) as the requirements of Load acting as a Resource.  Unloaded Generation Resources that are On-line, through governor action, and Load acting as a Resource do respond in time to minimize the lowest frequency during a disturbance and reduce the risk of UFLS.

A DER unit that is Off-line will be synchronizing to the grid during the reset period of a disturbance, i.e. between the NERC C point and B point.  The submitter should provide test data indicating the DER unit’s successful synchronizing during this fast changing frequency period.

A DER unit that is On-line must have the same capabilities and amount limitations as other On-line Generation Resources as stated in paragraph (1).

An On-line DER unit must not be on a UFLS circuit.

Ramping of DER units in aggregate must not contribute to frequency excursions.

DER units clearly have the potential of providing a valuable service to the ERCOT Interconnection, but the PDCWG does not believe that Responsive Reserve Service is the appropriate service.

Revised Proposed Protocol Language

None.